## gd2010toPresentFields
Gas Distribution System Incident Reports for 2010 - Present (PHMSA Form 7100.1 Rev. 4-2019) - Data Dictionary for Flagged Data file
Field Name | Data Type | Field Name Description | Form Location
DATAFILE_AS_OF | DATE | Data as of date | Not on the form
FF | VARCHAR2 | Identify if incident was cause by fire first or not | Not on the form
SIGNIFICANT | VARCHAR2 | Identify if record meets the significant criteria or not: If incident is NOT ‘FF’ and If there was fatality, injury, or total property damage is $50K or more in 1984 dollars, then SIGNIFICANT=’YES’, else SIGNIFICANT=’NO’. | Not on the form
SERIOUS | VARCHAR2 | Identify if record meets the SERIOUS criteria or not: If there was fatality or injury and if FF criteria is false then SERIOUS = ‘YES’ else SERIOUS = ’NO’ | Not on the form
REPORT_NUMBER | NUMBER | PHMSA DOT assigned unique identifier for report | Top of first page
SUPPLEMENTAL_NUMBER | NUMBER | PHMSA DOT assigned unique identifier for report submission | Top of first page
REPORT_RECEIVED_DATE | DATE | Date when Original Report submitted | Top of first page
REPORT_TYPE | VARCHAR2 | Report Type (Original, Supplemental, Final) | PART A - KEY REPORT INFORMATION
OPERATOR_ID | NUMBER | Operator's OPS-issued Operator Identification number | PART A - KEY REPORT INFORMATION
NAME | VARCHAR2 | Operator Name | PART A - KEY REPORT INFORMATION
OPERATOR_STREET_ADDRESS | VARCHAR2 | Operator Address - Street | PART A - KEY REPORT INFORMATION
OPERATOR_CITY_NAME | VARCHAR2 | Operator Address - City | PART A - KEY REPORT INFORMATION
OPERATOR_STATE_ABBREVIATION | VARCHAR2 | Operator Address - State | PART A - KEY REPORT INFORMATION
OPERATOR_POSTAL_CODE | VARCHAR2 | Operator Address - Zip | PART A - KEY REPORT INFORMATION
LOCAL_DATETIME | DATE | Local time (24-hr clock) and date of the Incident | PART A - KEY REPORT INFORMATION
TIME_ZONE | VARCHAR2 | Time Zone for local time | PART A - KEY REPORT INFORMATION
DAYLIGHT_SAVINGS_IND | VARCHAR2 | Is Daylight Saving in effect? (Yes/No) | PART A - KEY REPORT INFORMATION
IYEAR | NUMBER | Year incident occurred, derived from incident date | Not on the form
LOCATION_STREET_ADDRESS | VARCHAR2 | Incident Address, Street | PART A - KEY REPORT INFORMATION
LOCATION_CITY_NAME | VARCHAR2 | Incident Address, City | PART A - KEY REPORT INFORMATION
LOCATION_COUNTY_NAME | VARCHAR2 | Incident Address, County | PART A - KEY REPORT INFORMATION
LOCATION_STATE_ABBREVIATION | VARCHAR2 | Incident Address, State | PART A - KEY REPORT INFORMATION
LOCATION_POSTAL_CODE | VARCHAR2 | Incident Address, Zip Code | PART A - KEY REPORT INFORMATION
LOCATION_LATITUDE | NUMBER | Incident Location Latitude | PART A - KEY REPORT INFORMATION
LOCATION_LONGITUDE | NUMBER | Incident Location Longitude | PART A - KEY REPORT INFORMATION
FLOW_CONT_KEY_CRIT_IND | VARCHAR2 | Method of Flow Control / "Key/Critical" Valve – inspected in accordance with Part 192.747 | PART A - KEY REPORT INFORMATION
FLOW_CONT_MAIN_VALVE_IND | VARCHAR2 | Method of Flow Control / Main Valve other than "Key/Critical" | PART A - KEY REPORT INFORMATION
FLOW_CONT_SERVICE_VALVE_IND | VARCHAR2 | Method of Flow Control / Service (curb) Valve | PART A - KEY REPORT INFORMATION
FLOW_CONT_METER_REG_IND | VARCHAR2 | Method of Flow Control / Meter/Regulator shut-off Valve | PART A - KEY REPORT INFORMATION
FLOW_CONT_EXCESS_FLOW_IND | VARCHAR2 | Method of Flow Control / Excess flow valve | PART A - KEY REPORT INFORMATION
FLOW_CONT_SQUEEZE_OFF_IND | VARCHAR2 | Method of Flow Control / Squeeze-Off | PART A - KEY REPORT INFORMATION
FLOW_CONT_STOPPLE_FITNG_IND | VARCHAR2 | Method of Flow Control / Stopple fitting | PART A - KEY REPORT INFORMATION
FLOW_CONT_OTHER_IND | VARCHAR2 | Method of Flow Control / Other | PART A - KEY REPORT INFORMATION
FLOW_CONT_OTHER_DETAIL | VARCHAR2 | Method of Flow Control / Other, specify | PART A - KEY REPORT INFORMATION
NRC_RPT_DATETIME | DATE | National Response Center time and date of initial telephonic report | PART A - KEY REPORT INFORMATION
NRC_RPT_NUM | VARCHAR2 | National Response Center Report Number | PART A - KEY REPORT INFORMATION
ADDITIONAL_NRC_REPORT_NUMBERS | VARCHAR2 | Additional NRC Report numbers submitted by the operator | PART A - KEY REPORT INFORMATION
COMMODITY_RELEASED_TYPE | VARCHAR2 | Type of Commodity released | PART A - KEY REPORT INFORMATION
COMMODITY_DETAILS | VARCHAR2 | Other Commodity Sub-type Name | PART A - KEY REPORT INFORMATION
UNINTENTIONAL_RELEASE | NUMBER | Estimated volume of gas released unintentionally in Thousand Cubic Feet (MCF) | PART A - KEY REPORT INFORMATION
INTENTIONAL_RELEASE | NUMBER | Estimated volume of intentional and controlled release/blowdown in Thousand Cubic Feet (MCF) | PART A - KEY REPORT INFORMATION
FATALITY_IND | VARCHAR2 | Fatalities (Yes, No) | PART A - KEY REPORT INFORMATION
NUM_EMP_FATALITIES | NUMBER | Number of Fatalities of Operator Employees | PART A - KEY REPORT INFORMATION
NUM_CONTR_FATALITIES | NUMBER | Number of Fatalities of Contractor Employees working for the Operator | PART A - KEY REPORT INFORMATION
NUM_ER_FATALITIES | NUMBER | Number of Fatalities of Non-Operator emergency responders | PART A - KEY REPORT INFORMATION
NUM_WORKER_FATALITIES | NUMBER | Number of Fatalities of Workers working on the right-of-way, but not associated with this Operator | PART A - KEY REPORT INFORMATION
NUM_GP_FATALITIES | NUMBER | Number of Fatalities of General Public | PART A - KEY REPORT INFORMATION
FATAL | NUMBER | Total number of Fatalities | PART A - KEY REPORT INFORMATION
INJURY_IND | VARCHAR2 | Injuries (Yes, No) | PART A - KEY REPORT INFORMATION
NUM_EMP_INJURIES | NUMBER | Number of Injuries of Operator Employees | PART A - KEY REPORT INFORMATION
NUM_CONTR_INJURIES | NUMBER | Number of Injuries of Contractor Employees working for the Operator | PART A - KEY REPORT INFORMATION
NUM_ER_INJURIES | NUMBER | Number of Injuries of Non-Operator emergency responders | PART A - KEY REPORT INFORMATION
NUM_WORKER_INJURIES | NUMBER | Number of Injuries of Workers working on the right-of-way, but not associated with this Operator | PART A - KEY REPORT INFORMATION
NUM_GP_INJURIES | NUMBER | Number of Injuries of General Public | PART A - KEY REPORT INFORMATION
INJURE | NUMBER | Total number of Injuries | PART A - KEY REPORT INFORMATION
IGNITE_IND | VARCHAR2 | Commodity ignite (Yes, No) | PART A - KEY REPORT INFORMATION
IGNITE_DATETIME | DATE | If gas ignite, Local time of ignition (year/month/day/hr) | PART A - KEY REPORT INFORMATION
HOW_EXTINGUISHED | VARCHAR2 | How was the fire extinguished? | PART A - KEY REPORT INFORMATION
HOW_EXTINGUISHED_OTHER_DETAIL | VARCHAR2 | If how was the fire extinguished is "Other", specify | PART A - KEY REPORT INFORMATION
GAS_CONSUMED_BY_FIRE_IN_MCF | NUMBER | Estimated volume of gas consumed by fire (in mcf) | PART A - KEY REPORT INFORMATION
EXPLODE_IND | VARCHAR2 | Commodity exploded (Yes, No) | PART A - KEY REPORT INFORMATION
NUM_PUB_EVACUATED | NUMBER | Number of general public evacuated | PART A - KEY REPORT INFORMATION
INCIDENT_IDENTIFIED_DATETIME | DATE | Time sequence - Local time operator identified Incident | PART A - KEY REPORT INFORMATION
COMMUNICATION_STATE_FED_IND | VARCHAR2 | Did the operator communicate with Local, State, or Federal Emergency Responders about the incident? (Yes/No) | PART A - KEY REPORT INFORMATION
PARTY_INITIATED_COMMUNICATION | VARCHAR2 | Which party initiated communication about the incident? (Operator/Local/State/Federal Emergency Responder) | PART A - KEY REPORT INFORMATION
INITIAL_RESPONDER_COM_DATETIME | DATE | Local time of initial Operator and Local/State/Federal Emergency Responder communication (year/month/day/hr) | PART A - KEY REPORT INFORMATION
ON_SITE_DATETIME | DATE | Time sequence - Local time operator resources arrived on site | PART A - KEY REPORT INFORMATION
CONFIRMED_DISCOVERY_DATETIME | DATE | Local time of confirmed discovery | PART A - KEY REPORT INFORMATION
FEDERAL | VARCHAR2 | Onshore - Federal land (Yes, No, Null) | PART B - ADDITIONAL LOCATION INFORMATION
LOCATION_TYPE | VARCHAR2 | Location of Incident | PART B - ADDITIONAL LOCATION INFORMATION
INCIDENT_AREA_TYPE | VARCHAR2 | Area of Incident | PART B - ADDITIONAL LOCATION INFORMATION
INCIDENT_AREA_SUBTYPE | VARCHAR2 | Area of Incident Sub-type | PART B - ADDITIONAL LOCATION INFORMATION
INCIDENT_AREA_DETAILS | VARCHAR2 | Area of Incident Sub-type Details | PART B - ADDITIONAL LOCATION INFORMATION
DEPTH_OF_COVER | VARCHAR2 | Onshore Underground - Depth-of-Cover (in) | PART B - ADDITIONAL LOCATION INFORMATION
OTHER_UNDERGROUND_FACILITIES | VARCHAR2 | Were other underground facilities found within 12 inches of the failure location? Yes/No | PART B - ADDITIONAL LOCATION INFORMATION
CROSSING | VARCHAR2 | Incident occurred in crossing (Yes, No, Null) | PART B - ADDITIONAL LOCATION INFORMATION
BRIDGE_CROSSING_IND | VARCHAR2 | Onshore - Bridge Crossing (Yes, Null) | PART B - ADDITIONAL LOCATION INFORMATION
BRIDGE_TYPE | VARCHAR2 | Onshore - Bridge Type | PART B - ADDITIONAL LOCATION INFORMATION
RAILROAD_CROSSING_IND | VARCHAR2 | Onshore - Railroad Crossing (Yes, Null) | PART B - ADDITIONAL LOCATION INFORMATION
RAILROAD_TYPE | VARCHAR2 | Onshore - Railroad Type | PART B - ADDITIONAL LOCATION INFORMATION
ROAD_CROSSING_IND | VARCHAR2 | Onshore - Road Crossing (Yes, Null) | PART B - ADDITIONAL LOCATION INFORMATION
ROAD_TYPE | VARCHAR2 | Onshore - Road Type | PART B - ADDITIONAL LOCATION INFORMATION
WATER_CROSSING_IND | VARCHAR2 | Onshore - Water Crossing (Yes, Null) | PART B - ADDITIONAL LOCATION INFORMATION
WATER_TYPE | VARCHAR2 | Onshore - Water Type | PART B - ADDITIONAL LOCATION INFORMATION
WATER_NAME | VARCHAR2 | Onshore - Name of body of water, if commonly known | PART B - ADDITIONAL LOCATION INFORMATION
WATER_DEPTH | VARCHAR2 | Approx. water depth(ft) at the point of the Incident | PART B - ADDITIONAL LOCATION INFORMATION
WATER_SUBTYPE | VARCHAR2 | Incident occured in Water crossing / Water crossing Sub Type | PART B - ADDITIONAL LOCATION INFORMATION
PIPE_FACILITY_TYPE | VARCHAR2 | Pipeline/facility Interstate or Intrastate | PART C - ADDITIONAL FACILITY INFORMATION
PIPE_TYPE_OTHER | VARCHAR2 | Type of pipeline system - Other Type of Pipeline system | PART C - ADDITIONAL FACILITY INFORMATION
SYSTEM_PART_INVOLVED | VARCHAR2 | Part of system involved in Incident | PART C - ADDITIONAL FACILITY INFORMATION
SYSTEM_PART_DETAILS | VARCHAR2 | Part of system involved - Other part of system involved | PART C - ADDITIONAL FACILITY INFORMATION
INSTALLATION_YEAR | NUMBER | Year Part of system installed that involved in Incident | PART C - ADDITIONAL FACILITY INFORMATION
MANUFACTURED_YEAR | VARCHAR2 | Year item involved in Incident was manufactured | PART C - ADDITIONAL FACILITY INFORMATION
CUSTOMER_TYPE | VARCHAR2 | Indicate the customer type when Part of system involved in Incident is other than "Main", "Main Valve", "District Regulator/Metering Station", or "Other" | PART C - ADDITIONAL FACILITY INFORMATION
WAS_EFV_INSTALLED_BEFORE_IND | VARCHAR2 | Was an EFV installed on the service line before the time of the incident? Yes/No | PART C - ADDITIONAL FACILITY INFORMATION
EVF_ACTIVATION_IND | VARCHAR2 | Did the EFV activate? Yes/No | PART C - ADDITIONAL FACILITY INFORMATION
CURB_VALVE_INST_BEFORE_INC_IND | VARCHAR2 | Was a curb valve installed on the service line before the time of the incident? Yes/No | PART C - ADDITIONAL FACILITY INFORMATION
PIPE_DIAMETER | NUMBER | Nominal diameter of Pipe (in) | PART C - ADDITIONAL FACILITY INFORMATION
PIPE_SPECIFICATION | VARCHAR2 | Pipe specification | PART C - ADDITIONAL FACILITY INFORMATION
PIPE_MANUFACTURER | VARCHAR2 | Type of Pipe Seam - Pipe manufacturer | PART C - ADDITIONAL FACILITY INFORMATION
MATERIAL_INVOLVED | VARCHAR2 | Material involved in Incident | PART C - ADDITIONAL FACILITY INFORMATION
MATERIAL_DETAILS | VARCHAR2 | Material involved - Other Material than Carbon Steel Details | PART C - ADDITIONAL FACILITY INFORMATION
STEEL_SEAM_TYPE | VARCHAR2 | When Material involved in Incident is Steel, specify seam type | PART C - ADDITIONAL FACILITY INFORMATION
STEEL_SEAM_TYPE_DETAILS | VARCHAR2 | When Material involved in Incident is Steel, specify seam type Other | PART C - ADDITIONAL FACILITY INFORMATION
WT_STEEL | NUMBER | Wall thickness (in) of Steel | PART C - ADDITIONAL FACILITY INFORMATION
PLASTIC_TYPE | VARCHAR2 | Type of Plastic involved in Incident | PART C - ADDITIONAL FACILITY INFORMATION
PLASTIC_DETAILS | VARCHAR2 | Type of Plastic - Other Plastic Details | PART C - ADDITIONAL FACILITY INFORMATION
PLASTIC_SDR | VARCHAR2 | Type of Plastic - Standard Dimension Ratio (SDR) of Plastic | PART C - ADDITIONAL FACILITY INFORMATION
WT_PLASTIC | NUMBER | Type of Plastic - Wall thickness (in) of Plastic | PART C - ADDITIONAL FACILITY INFORMATION
WT_PLASTIC_UNKNOWN_IND | VARCHAR2 | Type of Plastic - Wall thickness (in) of Plastic Unknown | PART C - ADDITIONAL FACILITY INFORMATION
MATERIAL_PE_PIPE_CODE | VARCHAR2 | Designation Code of PE Pipe Material (e.g. 2046, 3408) | PART C - ADDITIONAL FACILITY INFORMATION
RELEASE_TYPE | VARCHAR2 | Type of Incident involved | PART C - ADDITIONAL FACILITY INFORMATION
PUNCTURE_AXIAL | NUMBER | Mechanical Puncture - Approx. size - Axial (in.) | PART C - ADDITIONAL FACILITY INFORMATION
PUNCTURE_CIRCUM | NUMBER | Mechanical Puncture - Approx. size - Circumferential (in.) | PART C - ADDITIONAL FACILITY INFORMATION
LEAK_TYPE | VARCHAR2 | Leak Type | PART C - ADDITIONAL FACILITY INFORMATION
LEAK_TYPE_OTHER | VARCHAR2 | Leak Type Other Details | PART C - ADDITIONAL FACILITY INFORMATION
RUPTURE_ORIENT | VARCHAR2 | Rupture Orientation (Circumferential, Longitudinal, Other) | PART C - ADDITIONAL FACILITY INFORMATION
RUPTURE_DETAILS | VARCHAR2 | Rupture Orientation Other Details | PART C - ADDITIONAL FACILITY INFORMATION
RUPTURE_LENGTH | NUMBER | Rupture - Approx. size (in.) (length circumferentially or axially) | PART C - ADDITIONAL FACILITY INFORMATION
RUPTURE_WIDTH | NUMBER | Rupture - Approx. size (in.) (widest opening) | PART C - ADDITIONAL FACILITY INFORMATION
RELEASE_TYPE_DETAILS | VARCHAR2 | Type of Incident Other Details | PART C - ADDITIONAL FACILITY INFORMATION
CLASS_LOCATION_TYPE | VARCHAR2 | Class Location of Incident | PART D - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_OPER_PAID | NUMBER | Estimated Property Damage - Estimated cost of public and non-Operator private property damage | PART D - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_OPER_PAID_CURRENT | NUMBER | Converted Property Damage to Current Year dollars using the GDP (Chained) Price Index of FY 2024 and the calendar year of incident date from the FY 2023 Historical Tables, Table 10.1 - Gross Domestic Product and Deflators Used in the Historical Tables: 1940–2027 | Not on the form
EST_COST_PROP_DAMAGE | NUMBER | Estimated Property Damage - Estimated cost of Operator’s property damage & repairs | PART D - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_PROP_DAMAGE_CURRENT | NUMBER | Converted Property Damage to Current Year dollars using the GDP (Chained) Price Index of FY 2024 and the calendar year of incident date from the FY 2023 Historical Tables, Table 10.1 - Gross Domestic Product and Deflators Used in the Historical Tables: 1940–2027 | Not on the form
EST_COST_EMERGENCY | NUMBER | Estimated Property Damage - Estimated cost of Operator’s emergency response | PART D - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_EMERGENCY_CURRENT | NUMBER | Converted Property Damage to Current Year dollars using the GDP (Chained) Price Index of FY 2024 and the calendar year of incident date from the FY 2023 Historical Tables, Table 10.1 - Gross Domestic Product and Deflators Used in the Historical Tables: 1940–2027 | Not on the form
EST_COST_OTHER | NUMBER | Estimated Property Damage - Estimated other costs | PART D - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_OTHER_CURRENT | NUMBER | Converted Property Damage to Current Year dollars using the GDP (Chained) Price Index of FY 2024 and the calendar year of incident date from the FY 2023 Historical Tables, Table 10.1 - Gross Domestic Product and Deflators Used in the Historical Tables: 1940–2027 | Not on the form
EST_COST_OTHER_DETAILS | VARCHAR2 | Estimated Property Damage - Estimated other costs Specified | PART D - ADDITIONAL CONSEQUENCE INFORMATION
GAS_COST_IN_MCF | NUMBER | Cost of Gas Released, Cost of Gas in $ per thousand standard cubic feet (mcf) | PART D - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_UNINTENTIONAL_RELEASE | NUMBER | Estimated Property Damage - Estimated cost of gas released unintentionally | PART D - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_UNINTENT_REL_CURRENT | NUMBER | Converted Cost of Commodity Loss to Current Year dollars using Gas Citygate Prices of 2024 and the year of the incident from Energy Information Administration with incidents occurring in 2025 using the 2024 Gas Citygate Price. | Not on the form
EST_COST_INTENTIONAL_RELEASE | NUMBER | Estimated Property Damage - Estimated cost of gas released intentionally during controlled release/blowdown | PART D - ADDITIONAL CONSEQUENCE INFORMATION
EST_COST_INTENT_REL_CURRENT | NUMBER | Converted Cost of Commodity Loss to Current Year dollars using Gas Citygate Prices of 2024 and the year of the incident from Energy Information Administration with incidents occurring in 2025 using the 2024 Gas Citygate Price. | Not on the form
TOTAL_COST | NUMBER | Total of all costs (Sum of EST_COST_OPER_PAID,EST_COST_PROP_DAMAGE,EST_COST_EMERGENCY,EST_COST_OTHER,EST_COST_INTENTIONAL_RELEASE,EST_COST_UNINTENTIONAL_RELEASE) | PART D - ADDITIONAL CONSEQUENCE INFORMATION
TOTAL_COST_IN84 | NUMBER | Converted all non-commodity Property Damage to 1984 dollars using the GDP (Chained) Price Index of FY 1984 and the year of incident date from the FY 2023 Historical Tables, Table 10.1 - Gross Domestic Product and Deflators Used in the Historical Tables: 1940–2027. Converted all commodity Property Damage to 1984 dollars using Gas Citygate Prices of 1984 and the year of the incident date from Energy Information Administration with incidents occurring in 2025 using the 2024 Gas Citygate Price. | Not on the form
TOTAL_COST_CURRENT | NUMBER | Converted all non-commodity Property Damage to Current Year dollars using the GDP (Chained) Price Index of FY 2024 and the calendar year of incident date from the FY 2023 Historical Tables, Table 10.1 - Gross Domestic Product and Deflators Used in the Historical Tables: 1940–2027. Converted all commodity Property Damage to Current Year dollars using Gas Citygate Prices of 2024 and the year of the incident date from Energy Information Administration with incidents occurring in 2025 using the 2024 Gas Citygate Price. | Not on the form
COMMERCIAL_AFFECTED | NUMBER | Estimated number of customers out of service - Commercial entities affected | PART D - ADDITIONAL CONSEQUENCE INFORMATION
INDUSTRIAL_AFFECTED | NUMBER | Estimated number of customers out of service - Industrial entities affected | PART D - ADDITIONAL CONSEQUENCE INFORMATION
RESIDENCES_AFFECTED | NUMBER | Estimated number of customers out of service - Residences affected | PART D - ADDITIONAL CONSEQUENCE INFORMATION
NUM_PERSONS_HOSP_NOT_OVNGHT | NUMBER | Estimated number of persons with injuries requiring treatment in a medical facility but not requiring overnight in-patient hospitalization | PART D - ADDITIONAL CONSEQUENCE INFORMATION
NUM_INJURED_TREATED_BY_EMT | NUMBER | Estimated number of persons with injuries requiring treatment by EMTs at the site of incident: | PART D - ADDITIONAL CONSEQUENCE INFORMATION
NUM_RESIDENT_BUILDING_AFFCTD | NUMBER | Number of residential buildings affected (evacuated or required repair or gas service interrupted) | PART D - ADDITIONAL CONSEQUENCE INFORMATION
NUM_BUSINESS_BUILDING_AFFCTD | NUMBER | Number of business buildings affected (evacuated or required repair or gas service interrupted) | PART D - ADDITIONAL CONSEQUENCE INFORMATION
ACCIDENT_PSIG | NUMBER | Estimated pressure at the point and time of the Incident (psig) | PART E - ADDITIONAL OPERATING INFORMATION
NORMAL_PSIG | NUMBER | Normal operating pressure at the point and time of the Incident (psig) | PART E - ADDITIONAL OPERATING INFORMATION
MOP_PSIG | NUMBER | Maximum Operating Pressure (MOP) at the point and time of the Incident (psig) | PART E - ADDITIONAL OPERATING INFORMATION
MOP_CFR_SECTION | VARCHAR2 | MAOP established by 49 CFR section | PART E - ADDITIONAL OPERATING INFORMATION
MAOP_ESTABLISHED_DATE | DATE | Date MAOP established | PART E - ADDITIONAL OPERATING INFORMATION
ACCIDENT_PRESSURE | VARCHAR2 | Describe the pressure on the system or facility relating to the Incident (exceed MOP or not) | PART E - ADDITIONAL OPERATING INFORMATION
GAS_ODORIZED_SYSTEM_TYPE | VARCHAR2 | Type of odorization system for gas at the point of failure | PART E - ADDITIONAL OPERATING INFORMATION
GAS_ODORIZED_SYS_OTHER_DETAIL | VARCHAR2 | Type of odorization system for gas at the point of failure, specify Other | PART E - ADDITIONAL OPERATING INFORMATION
GAS_ODORIZED_LEVEL | NUMBER | Odorant level near the point of failure measured after the failure | PART E - ADDITIONAL OPERATING INFORMATION
GAS_ODORIZED_LVL_NOT_MSRD_IND | VARCHAR2 | Odorant level near the point of failure Not measured indicator | PART E - ADDITIONAL OPERATING INFORMATION
SCADA_IN_PLACE_IND | VARCHAR2 | Supervisory Control and Data Acquisition (SCADA)-based system in place on the pipeline or facility involved in the Incident (Yes, No, Null) | PART E - ADDITIONAL OPERATING INFORMATION
SCADA_OPERATING_IND | VARCHAR2 | SCADA operating at the time of the Incident (Yes, No, Null) | PART E - ADDITIONAL OPERATING INFORMATION
SCADA_FUNCTIONAL_IND | VARCHAR2 | SCADA fully functional at the time of the Incident (Yes, No, Null) | PART E - ADDITIONAL OPERATING INFORMATION
SCADA_DETECTION_IND | VARCHAR2 | SCADA -based information (such as alarm (s), event(s), and/or volume or pack | PART E - ADDITIONAL OPERATING INFORMATION
SCADA_CONF_IND | VARCHAR2 | SCADA -based information (such as alarm (s), event(s), and/or volume or pack | PART E - ADDITIONAL OPERATING INFORMATION
ACCIDENT_IDENTIFIER | VARCHAR2 | How Incident was identified for the Operator | PART A - KEY REPORT INFORMATION
ACCIDENT_DETAILS | VARCHAR2 | How Incident was identified for the Operator - Other Details | PART A - KEY REPORT INFORMATION
OPERATOR_TYPE | VARCHAR2 | Specify Type of Operator | PART A - KEY REPORT INFORMATION
INVESTIGATION_STATUS | VARCHAR2 | Investigation initiated into whether or not the controller(s) or control room issues were the cause of or a contributing factor to the Incident (Yes, No, Not necessary) | PART E - ADDITIONAL OPERATING INFORMATION
INVESTIGATION_STATUS_DETAILS | VARCHAR2 | Investigation Initiated - Not necessary Details | PART E - ADDITIONAL OPERATING INFORMATION
INVEST_SCHEDULE_IND | VARCHAR2 | Investigation reviewed schedule (Yes, Null) | PART E - ADDITIONAL OPERATING INFORMATION
INVEST_NO_SCHEDULE_IND | VARCHAR2 | Investigation did not review schedule (Yes, Null) | PART E - ADDITIONAL OPERATING INFORMATION
INVEST_NO_SCHEDULE_IND_DETAILS | VARCHAR2 | Investigation did not review schedule - Details | PART E - ADDITIONAL OPERATING INFORMATION
INVEST_NO_CONTROL_ROOM_IND | VARCHAR2 | Investigation initiated - No control room issues (Yes, Null) | PART E - ADDITIONAL OPERATING INFORMATION
INVEST_NO_CONTROLLER_IND | VARCHAR2 | Investigation initiated - No controller issues (Yes, Null) | PART E - ADDITIONAL OPERATING INFORMATION
INVEST_INCORRECT_ACTION_IND | VARCHAR2 | Investigation initiated - Incorrect controller action or controller error (Yes, Null) | PART E - ADDITIONAL OPERATING INFORMATION
INVEST_FATIGUE_IND | VARCHAR2 | Investigation initiated - That fatigue may have affected the controller(s) involved or impacted the involved controller(s) response (Yes, Null) | PART E - ADDITIONAL OPERATING INFORMATION
INVEST_INCORRECT_PROCEDURE_IND | VARCHAR2 | Investigation initiated - Incorrect procedures (Yes, Null) | PART E - ADDITIONAL OPERATING INFORMATION
INVEST_INCORRECT_CONTROL_IND | VARCHAR2 | Investigation initiated - Incorrect control room equipment operation (Yes, Null) | PART E - ADDITIONAL OPERATING INFORMATION
INVEST_MAINT_IND | VARCHAR2 | Investigation initiated - Maintenance activities that affected control room operations, procedures, and/or controller response (Yes, Null) | PART E - ADDITIONAL OPERATING INFORMATION
INVEST_OTHER_IND | VARCHAR2 | Investigation initiated - Other area (Yes, Null) | PART E - ADDITIONAL OPERATING INFORMATION
INVEST_OTHER_IND_DETAILS | VARCHAR2 | Investigation initiated - Other area Details | PART E - ADDITIONAL OPERATING INFORMATION
EMPLOYEE_DRUG_TEST_IND | VARCHAR2 | Operator employees tested under the post-Incident drug and alcohol testing requirements of DOT’s Drug & Alcohol Testing regulations (Yes, No) | PART F - DRUG & ALCOHOL TESTING INFORMATION
NUM_EMPLOYEES_TESTED | NUMBER | Number of employees tested | PART F - DRUG & ALCOHOL TESTING INFORMATION
NUM_EMPLOYEES_FAILED | NUMBER | Number of employees failed | PART F - DRUG & ALCOHOL TESTING INFORMATION
CONTRACTOR_DRUG_TEST_IND | VARCHAR2 | Operator contractor employees tested under the post-Incident drug and alcohol testing requirements of DOT’s Drug & Alcohol Testing regulations (Yes, No) | PART F - DRUG & ALCOHOL TESTING INFORMATION
NUM_CONTRACTORS_TESTED | NUMBER | Number of contractors tested | PART F - DRUG & ALCOHOL TESTING INFORMATION
NUM_CONTRACTORS_FAILED | NUMBER | Number of contractors failed | PART F - DRUG & ALCOHOL TESTING INFORMATION
CAUSE | VARCHAR2 | Apparent Cause of the Incident | PART G - APPARENT CAUSE
CAUSE_DETAILS | VARCHAR2 | Sub-Cause of Incident | PART G - APPARENT CAUSE
MAP_SEVEN_CAUSE | VARCHAR2 | Cause by PHMSA for 20 year incident trending | Not on the form
MAP_SEVEN_SUBCAUSE | VARCHAR2 | SubCause by PHMSA for 20 year incident trending | Not on the form
MAP_EIGHT_CAUSE | VARCHAR2 | Cause by PHMSA for 20 year incident trending | Not on the form
MAP_EIGHT_SUBCAUSE | VARCHAR2 | SubCause by PHMSA for 20 year incident trending | Not on the form
INTERNAL_EXTERNAL | VARCHAR2 | Corrosion Failure Sub-Cause (Internal, External) | PART G1 - Corrosion Failure
VISUAL_EXAM_RESULTS | VARCHAR2 | External Corrosion - Visual Examination | PART G1 - Corrosion Failure
VISUAL_EXAM_DETAILS | VARCHAR2 | External Corrosion - Other Visual Examination Details | PART G1 - Corrosion Failure
GALVANIC_CORROSION_IND | VARCHAR2 | External Corrosion Type - Galvanic | PART G1 - Corrosion Failure
ATMOSPHERE_CORROSION_IND | VARCHAR2 | External Corrosion Type - Atmosphere | PART G1 - Corrosion Failure
STRAY_CURRENT_CORROSION_IND | VARCHAR2 | External Corrosion Type - Stray Current | PART G1 - Corrosion Failure
MICROBIOLOGICAL_CORROSION_IND | VARCHAR2 | External Corrosion Type - Microbiological | PART G1 - Corrosion Failure
SELECTIVE_SEAM_CORROSION_IND | VARCHAR2 | External Corrosion Type - Selective Seam | PART G1 - Corrosion Failure
OTHER_CORROSION_IND | VARCHAR2 | External Corrosion Type - Other | PART G1 - Corrosion Failure
CORROSION_TYPE_DETAILS | VARCHAR2 | External Corrosion Type - Other Details | PART G1 - Corrosion Failure
STRAY_CURRENT_TYPE | VARCHAR2 | External Corrosion Type - Stray Current - Specify | PART G1 - Corrosion Failure
STRAY_CURRENT_DETAILS | VARCHAR2 | External Corrosion Type - Stray Current - Describe the stray current source | PART G1 - Corrosion Failure
FIELD_EXAM_BASIS_IND | VARCHAR2 | External Corrosion Type Based on - Field Examination | PART G1 - Corrosion Failure
METALLURGICAL_BASIS_IND | VARCHAR2 | External Corrosion Type Based on - Metallurgical Analysis | PART G1 - Corrosion Failure
OTHER_BASIS_IND | VARCHAR2 | External Corrosion Type Based on - Other Analysis | PART G1 - Corrosion Failure
CORROSION_BASIS_DETAILS | VARCHAR2 | External Corrosion Type Based on - Other Analysis Details | PART G1 - Corrosion Failure
UNDERGROUND_LOCATION | VARCHAR2 | External Corrosion - Failed item buried under the ground (Yes, No, Null) | PART G1 - Corrosion Failure
UNDER_CATHODIC_PROTECTION_IND | VARCHAR2 | External Corrosion Under Ground - Under Cathodic Protection (Yes, No, Null) | PART G1 - Corrosion Failure
CATHODIC_PRO_START_YEAR | VARCHAR2 | Year Cathodic Protection Started (Yes, No, Null) | PART G1 - Corrosion Failure
SHIELDING_EVIDENT | VARCHAR2 | Shielding, tenting, or disbonding of coating evident at the point of Incident (Yes, No, Null) | PART G1 - Corrosion Failure
CATHODIC_SURVEY_TYPE | VARCHAR2 | Cathodic Survey Type (Yes, No, Null) | PART G1 - Corrosion Failure
CP_ANNUAL_SURVEY_IND | VARCHAR2 | Cathodic Protection Annual Survey (Yes, No, Null) | PART G1 - Corrosion Failure
CLOSE_INTERVAL_SURVEY_IND | VARCHAR2 | Close Interval Survey (Yes, No, Null) | PART G1 - Corrosion Failure
OTHER_CP_SURVEY_IND | VARCHAR2 | Other Cathodic Protection Survey (Yes, No, Null) | PART G1 - Corrosion Failure
CP_ANNUAL_SURVEY_YEAR | NUMBER | Cathodic Protection Annual Survey Year (Yes, No, Null) | PART G1 - Corrosion Failure
CLOSE_INTERVAL_SURVEY_YEAR | NUMBER | Close Interval Survey Year (Yes, No, Null) | PART G1 - Corrosion Failure
OTHER_CP_SURVEY_YEAR | NUMBER | Other Cathodic Protection Survey Year (Yes, No, Null) | PART G1 - Corrosion Failure
OTHER_CP_SURVEY_DETAILS | VARCHAR2 | If one or more Cathodic Protection Survey been conducted at the point of the incident is "Other", Describe other CP survey | PART G1 - Corrosion Failure
EXTERNALLY_COATED | VARCHAR2 | Failed item externally coated or painted (Yes, Null) | PART G1 - Corrosion Failure
PRIOR_DAMAGE | VARCHAR2 | External Corrosion - Observable damage to the coating or paint in the vicinity of the corrosion (Yes, No, Null) | PART G1 - Corrosion Failure
COATING_TYPE | VARCHAR2 | External Corrosion - Coating Type | PART G1 - Corrosion Failure
COATING_TYPE_DETAILS | VARCHAR2 | Coating Type - Other Coating Type Details | PART G1 - Corrosion Failure
FIELD_APPLIED_IND | VARCHAR2 | External Corrosion - Field Applied? (Yes/No/Unknown) | PART G1 - Corrosion Failure
INT_VISUAL_EXAM_RESULTS | VARCHAR2 | Internal Corrosion - Visual Examination Results | PART G1 - Corrosion Failure
INT_VISUAL_EXAM_DETAILS | VARCHAR2 | Internal Corrosion - Other Visual Examination Results Details | PART G1 - Corrosion Failure
INT_CORROSIVE_COMMODITY_IND | VARCHAR2 | Internal Corrosion Cause - Corrosive Commodity (Yes, Null) | PART G1 - Corrosion Failure
INT_WATER_ACID_IND | VARCHAR2 | Internal Corrosion Cause - Water drop-out/Acid (Yes, Null) | PART G1 - Corrosion Failure
INT_MICROBIOLOGICAL_IND | VARCHAR2 | Internal Corrosion Cause - Microbiological (Yes, Null) | PART G1 - Corrosion Failure
INT_EROSION_IND | VARCHAR2 | Internal Corrosion Cause - Erosion (Yes, Null) | PART G1 - Corrosion Failure
INT_OTHER_CORROSION_IND | VARCHAR2 | Internal Corrosion Cause - Other (Yes, Null) | PART G1 - Corrosion Failure
INT_CORROSION_TYPE_DETAILS | VARCHAR2 | Internal Corrosion Cause - Other Details | PART G1 - Corrosion Failure
INT_FIELD_EXAM_BASIS_IND | VARCHAR2 | Internal Corrosion Cause Based on - Field Examination (Yes, Null) | PART G1 - Corrosion Failure
INT_METALLURGICAL_BASIS_IND | VARCHAR2 | Internal Corrosion Cause Based on - Metallurgical Analysis (Yes, Null) | PART G1 - Corrosion Failure
INT_OTHER_BASIS_IND | VARCHAR2 | Internal Corrosion Cause Based on - Other Analysis (Yes, Null) | PART G1 - Corrosion Failure
INT_CORROSION_BASIS_DETAILS | VARCHAR2 | Internal Corrosion Cause Based on - Other Analysis Details | PART G1 - Corrosion Failure
INT_LOW_POINT_PIPE_LOC_IND | VARCHAR2 | Internal Corrosion Location - Low point in pipe (Yes, Null) | PART G1 - Corrosion Failure
INT_ELBOW_LOC_IND | VARCHAR2 | Internal Corrosion Location - Elbow (Yes, Null) | PART G1 - Corrosion Failure
INT_DROP_OUT_LOC_IND | VARCHAR2 | Internal Corrosion Location - Drop-out | PART G1 - Corrosion Failure
INT_OTHER_LOC_IND | VARCHAR2 | Internal Corrosion Location - Other (Yes, Null) | PART G1 - Corrosion Failure
CORROSION_LOCATION_DETAILS | VARCHAR2 | Internal Corrosion Location - Other Details | PART G1 - Corrosion Failure
CORROSION_INHIBITORS | VARCHAR2 | Internal Corrosion - Commodity treated with corrosion inhibitors or biocides (Yes, No, Null) | PART G1 - Corrosion Failure
LIQUID_FOUND | VARCHAR2 | Internal Corrosion -Liquids found in the distribution system at the point of Incident (Yes, No, Null) | PART G1 - Corrosion Failure
COR_HYDROTEST_LEAK_SURVEY_DATE | VARCHAR2 | Date of the most recent Leak Survey conducted | PART G1 - Corrosion Failure
COR_HYDROTEST_CONDUCTED_IND | VARCHAR2 | Has one or more pressure test been conducted since original construction at the point of the Incident(Yes, No, Null) | PART G1 - Corrosion Failure
COR_HYDROTEST_CONDUCTED_YEAR | VARCHAR2 | Most recent year tested | PART G1 - Corrosion Failure
COR_HYDROTEST_PRESSURE | VARCHAR2 | Test pressure (psig) | PART G1 - Corrosion Failure
NATURAL_FORCE_TYPE | VARCHAR2 | Natural Force Damage Sub-Cause | PART G2 - Natural Force Damage
EARTH_SUBTYPE | VARCHAR2 | Natural Force Damage - Sub-type of Earth Movement, NOT due to Heavy Rains/Floods | PART G2 - Natural Force Damage
HEAVY_RAINS_SUBTYPE | VARCHAR2 | Natural Force Damage - Sub-type of Heavy Rains/Floods | PART G2 - Natural Force Damage
LIGHTNING_SUBTYPE | VARCHAR2 | Natural Force Damage - Sub-type of Lightning | PART G2 - Natural Force Damage
TEMPERATURE_SUBTYPE | VARCHAR2 | Natural Force Damage - Sub-type of Temperature | PART G2 - Natural Force Damage
NF_OTHER_DETAILS | VARCHAR2 | Natural Force Damage - Other Natural Force Damage, or Sub-type Details | PART G2 - Natural Force Damage
NF_EXTREME_WEATHER_IND | VARCHAR2 | Natural Force Damage - Natural forces causing incident generated in conjunction with an extreme weather event (Yes, No, Null) | PART G2 - Natural Force Damage
NF_HURRICANE_IND | VARCHAR2 | Natural Force Damage - Extreme weather - Hurricane (Yes, Null) | PART G2 - Natural Force Damage
NF_TROPICAL_STORM_IND | VARCHAR2 | Natural Force Damage - Extreme weather - Tropical Storm (Yes, Null) | PART G2 - Natural Force Damage
NF_TORNADO_IND | VARCHAR2 | Natural Force Damage - Extreme weather - Tornado (Yes, Null) | PART G2 - Natural Force Damage
NF_OTHER_IND | VARCHAR2 | Natural Force Damage - Extreme weather - Other type (Yes, Null) | PART G2 - Natural Force Damage
NF_EXTREME_WEATHER_DETAILS | VARCHAR2 | Natural Force Damage - Extreme weather - Other type Details | PART G2 - Natural Force Damage
PARTY_TYPE | VARCHAR2 | Excavation Damage Sub-Cause | PART G3 - Excavation Damage
EX_HYDROTEST_LEAK_SURVEY_DATE | VARCHAR2 | Excavation Damage - Leak Survey Date conducted | PART G3 - Excavation Damage
EX_HYDROTEST_CONDUCTED_IND | VARCHAR2 | Excavation Damage - Hydrotest or other pressure test conducted (Yes, No, Null) | PART G3 - Excavation Damage
EX_HYDROTEST_CONDUCTED_YEAR | VARCHAR2 | Pressure test conducted year | PART G3 - Excavation Damage
EX_HYDROTEST_PRESSURE | VARCHAR2 | Test pressure (psig) | PART G3 - Excavation Damage
PRIOR_NOTIFICATION_IND | VARCHAR2 | Excavation Damage by Third Party - Operator get prior notification of the excavation activity (Yes, No, Null) | PART G3 - Excavation Damage
ONE_CALL_SYSTEM_IND | VARCHAR2 | Excavation Damage by Third Party - Notification from One-Call System (Yes, Null) | PART G3 - Excavation Damage
EXCAVATOR_IND | VARCHAR2 | Excavation Damage by Third Party - Notification from Excavator (Yes, Null) | PART G3 - Excavation Damage
CONTRACTOR_IND | VARCHAR2 | Excavation Damage by Third Party - Notification from Contractor (Yes, Null) | PART G3 - Excavation Damage
LANDOWNER_IND | VARCHAR2 | Excavation Damage by Third Party - Notification from Landowner (Yes, Null) | PART G3 - Excavation Damage
STATE_LAW_EXEMPT_IND | VARCHAR2 | Per the primary Incident Investigator results, did State law exempt the excavator from notifying the one-call center? (Yes/No/Unknown) | PART G3 - Excavation Damage
STATE_LAW_EXEMPT_TYPE | VARCHAR2 | If State law exempt the excavator from notifying the one-call center, what was exempt | PART G3 - Excavation Damage
STATE_LAW_EXEMPT_DETAIL | VARCHAR2 | If State law exempt the excavator from notifying the one-call center, and "Other" exempt, specify | PART G3 - Excavation Damage
STATE_LAW_EXEMPT_AUTHORITY | VARCHAR2 | If State law exempt the excavator from notifying the one-call center, Exempting authority | PART G3 - Excavation Damage
STATE_LAW_EXEMPT_CRITERIA | VARCHAR2 | If State law exempt the excavator from notifying the one-call center, Exempting criteria | PART G3 - Excavation Damage
NOTIFY_CGA_DIRT | VARCHAR2 | Excavation Damage - Do you want PHMSA to upload CGA-DIRT Program questions to CGA-DIRT.com (Yes, No, Null) | PART G3 - Excavation Damage
PUBLIC_ROW_IND | VARCHAR2 | Excavation Damage - Type of Right-of-Way (ROW) - Public | PART G3 - Excavation Damage
PUBLIC_SUBTYPE | VARCHAR2 | Excavation Damage - Type of ROW - Public Sub-type | PART G3 - Excavation Damage
PRIVATE_ROW_IND | VARCHAR2 | Excavation Damage - Type of ROW - Private | PART G3 - Excavation Damage
PRIVATE_SUBTYPE | VARCHAR2 | Excavation Damage - Type of ROW - Private Sub-type | PART G3 - Excavation Damage
PIPELINE_EASEMENT_ROW_IND | VARCHAR2 | Excavation Damage - Type of ROW - Pipeline Property/Easement | PART G3 - Excavation Damage
POWER_TRANSMISSION_ROW_IND | VARCHAR2 | Excavation Damage - Type of ROW - Power/Transmission Line | PART G3 - Excavation Damage
RAILROAD_ROW_IND | VARCHAR2 | Excavation Damage - Type of ROW - Railroad | PART G3 - Excavation Damage
PUBLIC_UTIL_EASEMENT_ROW_IND | VARCHAR2 | Excavation Damage - Type of ROW - Dedicated Public Utility Easement | PART G3 - Excavation Damage
FEDERAL_LAND_ROW_IND | VARCHAR2 | Excavation Damage - Type of ROW - Federal Land | PART G3 - Excavation Damage
UNKNOWN_ROW_IND | VARCHAR2 | Excavation Damage - Type of ROW - Unknown/Other | PART G3 - Excavation Damage
JOINT_TRENCH_IND | VARCHAR2 | Excavation Damage - Facility part of Joint Trench (Yes, No, Null) | PART G3 - Excavation Damage
CROSS_BORE_IND | VARCHAR2 | Excavation Damage - Event involved a Cross Bore (Yes, No, Null) | PART G3 - Excavation Damage
DEPTH_OF_GRADE | VARCHAR2 | Excavation Damage - Measured depth from grade | PART G3 - Excavation Damage
DEPTH_OF_GRADE_DETAIL | VARCHAR2 | Excavation Damage - Measured depth from grade in inches | PART G3 - Excavation Damage
EXCAVATOR_TYPE | VARCHAR2 | Excavation Damage - Type of excavator | PART G3 - Excavation Damage
EXCAVATOR_EQUIPMENT | VARCHAR2 | Excavation Damage - Type of excavation equipment | PART G3 - Excavation Damage
WORK_PERFORMED | VARCHAR2 | Excavation Damage - Type of work performed | PART G3 - Excavation Damage
ONE_CALL_NOTIFIED_IND | VARCHAR2 | Excavation Damage - One-Call Center notified (Yes, No, Null) | PART G3 - Excavation Damage
ONE_CALL_TICKET_NUM | VARCHAR2 | Excavation Damage - One-Call ticket number | PART G3 - Excavation Damage
ONE_CALL_CENTER_NAME | VARCHAR2 | State where more than a single One-Call Center exists, list name of One-Call | PART G3 - Excavation Damage
WHITE_LINED_IND | VARCHAR2 | Excavation Damage - Work area white lined (Yes, No, Unknown, Null) | PART G3 - Excavation Damage
LOCATOR_TYPE | VARCHAR2 | Excavation Damage - Type of Locator | PART G3 - Excavation Damage
VISIBLE_MARKS | VARCHAR2 | Excavation Damage - Facility locate marks visible in the area of excavation (No, Yes, Data not collected, Unknown/Other) | PART G3 - Excavation Damage
SERVICE_INTERRUPTION | VARCHAR2 | Excavation Damage - Damage cause an interruption in service (No, Yes, Data not collected, Unknown/Other) | PART G3 - Excavation Damage
SERVICE_INTERRUPTION_HOURS | NUMBER | Excavation Damage - Duration of the interruption in service (hours) | PART G3 - Excavation Damage
ROOT_CAUSE_CATEGORY | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Root Cause Category | PART G3 - Excavation Damage
ROOT_CAUSE_TYPE | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Root Cause Type | PART G3 - Excavation Damage
ROOT_CAUSE_TYPE_OTHER | VARCHAR2 | Excavation Damage CGA-DIRT Program questions - Root Cause Type Other Details | PART G3 - Excavation Damage
OUTSIDE_FORCE_TYPE | VARCHAR2 | Other Outside Force Damage Sub-Cause | PART G4 - Other Outside Force Damage
VEHICLE_SUBTYPE | VARCHAR2 | Other Outside Force Damage - Sub-cause Damage by Car, Truck .. - Vehicle Sub-type | PART G4 - Other Outside Force Damage
OSF_HURRICANE_IND | NUMBER | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Hurricane (Yes, Null) | PART G4 - Other Outside Force Damage
OSF_TROPICAL_STORM_IND | NUMBER | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Tropical Storm (Yes, Null) | PART G4 - Other Outside Force Damage
OSF_TORNADO_IND | NUMBER | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Tornado (Yes, Null) | PART G4 - Other Outside Force Damage
OSF_HEAVY_RAINS_IND | NUMBER | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Heavy Rains/Flood (Yes, Null) | PART G4 - Other Outside Force Damage
OSF_OTHER_WEATHER_IND | NUMBER | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Other type (Yes, Null) | PART G4 - Other Outside Force Damage
OSF_OTHER_WEATHER_DETAILS | VARCHAR2 | Other Outside Force Damage - Sub-cause Damage by Boats, Barges.. - Extreme weather - Other type Details | PART G4 - Other Outside Force Damage
OSF_HYDROTEST_LEAK_SURVEY_DATE | VARCHAR2 | Leak Survey Date conducted | PART G4 - Other Outside Force Damage
OSF_HYDROTEST_CONDUCTED_IND | VARCHAR2 | One or more Hydrotest or other pressure test conducted | PART G4 - Other Outside Force Damage
OSF_HYDROTEST_CONDUCTED_YEAR | VARCHAR2 | Pressure test conducted year | PART G4 - Other Outside Force Damage
OSF_HYDROTEST_PRESSURE | VARCHAR2 | Test pressure (psig) | PART G4 - Other Outside Force Damage
INTENTIONAL_SUBTYPE | VARCHAR2 | Other Outside Force Damage - Sub-cause Intentional Damage - Intentional Damage Sub-type | PART G4 - Other Outside Force Damage
INTENTIONAL_DETAILS | VARCHAR2 | Other Outside Force Damage - Sub-cause Intentional Damage - Intentional Damage Sub-type Other Details | PART G4 - Other Outside Force Damage
OSF_OTHER_DETAILS | VARCHAR2 | Other Outside Force Damage - Sub-cause Other Details | PART G4 - Other Outside Force Damage
DRIVER_ISSUED_CITATION_IND | VARCHAR2 | Other Outside Force Damage - Was the driver of the vehicle or equipment issued one or more citations related to the incident? (Yes/No/Unknown) | PART G4 - Other Outside Force Damage
CITATION_SPEED_IND | VARCHAR2 | Other Outside Force Damage - The nature of the citations - "Excessive Speed" | PART G4 - Other Outside Force Damage
CITATION_RECKLESS_IND | VARCHAR2 | Other Outside Force Damage - The nature of the citations - "Reckless Driving" | PART G4 - Other Outside Force Damage
CITATION_DUI_IND | VARCHAR2 | Other Outside Force Damage - The nature of the citations - "Driving Under the Influence" | PART G4 - Other Outside Force Damage
CITATION_OTHER_IND | VARCHAR2 | Other Outside Force Damage - The nature of the citations - "Other" | PART G4 - Other Outside Force Damage
CITATION_OTHER_DETAIL | VARCHAR2 | Other Outside Force Damage - The nature of the citations - "Other", specify | PART G4 - Other Outside Force Damage
DRIVER_IN_CONTROL_IND | VARCHAR2 | Other Outside Force Damage - Was the driver under control of the vehicle at the time of the collision? (Yes/No/Unknown) | PART G4 - Other Outside Force Damage
ESTIMATED_SPEED | NUMBER | Other Outside Force Damage - Estimated speed of the vehicle at the time of impact (miles per hour) | PART G4 - Other Outside Force Damage
VEHICLE_TYPE | VARCHAR2 | Other Outside Force Damage - Type of vehicle | PART G4 - Other Outside Force Damage
VEHICLE_TRAVEL_FROM | VARCHAR2 | Other Outside Force Damage - Where did the vehicle travel from to hit the pipeline facility? | PART G4 - Other Outside Force Damage
VEHICLE_TRAVEL_DISTANCE_FT | NUMBER | Other Outside Force Damage - Shortest distance from "traveling from" to the damaged pipeline facility (in feet) | PART G4 - Other Outside Force Damage
PROTECTIONS_INSTALLED_IND | VARCHAR2 | Other Outside Force Damage - At the time of the Incident, were protections installed to protect the damaged pipeline facility from vehicular damage? (Yes/No) | PART G4 - Other Outside Force Damage
PROTECTION_BOLLARDS_POST_IND | VARCHAR2 | Other Outside Force Damage - Protections installed, type of protection "Bollards/Guard Posts" | PART G4 - Other Outside Force Damage
PROTECTION_BARRICADES_IND | VARCHAR2 | Other Outside Force Damage - Protections installed, type of protection "Barricades - include Jersey barriers and fences in instructions" | PART G4 - Other Outside Force Damage
PROTECTION_GUARD_RAILS_IND | VARCHAR2 | Other Outside Force Damage - Protections installed, type of protection "Guard Rails" | PART G4 - Other Outside Force Damage
PROTECTION_METER_BOX_IND | VARCHAR2 | Other Outside Force Damage - Protections installed, type of protection "Meter Box" | PART G4 - Other Outside Force Damage
PROTECTION_INGRESS_REGRESS_IND | VARCHAR2 | Other Outside Force Damage - Protections installed, type of protection "Ingress or Regress at a Residence" | PART G4 - Other Outside Force Damage
PROTECTION_OTHER_IND | VARCHAR2 | Other Outside Force Damage - Protections installed, type of protection "Other" | PART G4 - Other Outside Force Damage
PROTECTION_OTHER_DETAIL | VARCHAR2 | Other Outside Force Damage - Protections installed, type of protection "Other", specify | PART G4 - Other Outside Force Damage
PWJF_FAILURE_TYPE | VARCHAR2 | Pipe, Weld, or Joint Failure Sub-Cause | PART G5 - Pipe, Weld, or Joint Failure
PIPE_BODY_SUBTYPE | VARCHAR2 | Pipe, Weld, or Joint Failure Body of Pipe - Sub-type of Body of Pipe | PART G5 - Pipe, Weld, or Joint Failure
PIPE_BODY_DETAILS | VARCHAR2 | Pipe, Weld, or Joint Failure Body of Pipe - Other Sub-type of Body of Pipe Details | PART G5 - Pipe, Weld, or Joint Failure
BUTT_WELD_SUBTYPE | VARCHAR2 | Pipe, Weld, or Joint Failure ButtWeld - Sub-type of Butt Weld | PART G5 - Pipe, Weld, or Joint Failure
BUTT_WELD_DETAILS | VARCHAR2 | Pipe, Weld, or Joint Failure ButtWeld - Other Sub-type of Butt Weld Details | PART G5 - Pipe, Weld, or Joint Failure
FILLET_WELD_SUBTYPE | VARCHAR2 | Pipe, Weld, or Joint Failure Fillet Weld - Sub-type of Fillet Weld | PART G5 - Pipe, Weld, or Joint Failure
FILLET_WELD_DETAILS | VARCHAR2 | Pipe, Weld, or Joint Failure Fillet Weld - Other Fillet Weld Subtype Details | PART G5 - Pipe, Weld, or Joint Failure
PIPE_SEAM_SUBTYPE | VARCHAR2 | Pipe, Weld, or Joint Failure Pipe Seam - Sub-type of Pipe Seam | PART G5 - Pipe, Weld, or Joint Failure
PIPE_SEAM_DETAILS | VARCHAR2 | Type of Pipe Seam - Pipe Seam Other Details | PART G5 - Pipe, Weld, or Joint Failure
MEC_FITTING_INVOLVED | VARCHAR2 | Specify the Mechanical Fitting Involved | PART G5 - Pipe, Weld, or Joint Failure
MEC_FITTING_INVLVD_DTL | VARCHAR2 | Specify the Mechanical Fitting Involved -Specify Other | PART G5 - Pipe, Weld, or Joint Failure
MEC_FITTING_TYPE | VARCHAR2 | Specify the Type of Mechanical Fitting | PART G5 - Pipe, Weld, or Joint Failure
MEC_FTTNG_TYPE_DETAIL | VARCHAR2 | Specify the Type of Mechanical Fitting - Specify Other | PART G5 - Pipe, Weld, or Joint Failure
MEC_MANUFACTURER | VARCHAR2 | Fitting Manufacturer | PART G5 - Pipe, Weld, or Joint Failure
MEC_PART_NUMBER | VARCHAR2 | Part or Model Number | PART G5 - Pipe, Weld, or Joint Failure
MEC_FITTING_MATERIAL | VARCHAR2 | Fitting Material | PART G5 - Pipe, Weld, or Joint Failure
MEC_FITTING_MATERIAL_DETAIL | VARCHAR2 | Fitting Material - Specify Other | PART G5 - Pipe, Weld, or Joint Failure
MEC_HOW_FAILURE_OCCURED | VARCHAR2 | How did the joint failure occur | PART G5 - Pipe, Weld, or Joint Failure
MEC_HOW_FAILURE_OCCURED_DTL | VARCHAR2 | How did the joint failure occur - Specify Other | PART G5 - Pipe, Weld, or Joint Failure
PLASTIC_JOINT_SUBTYPE | VARCHAR2 | Pipe, Weld, or Joint Failure - Fusion Joint Sub-type | PART G5 - Pipe, Weld, or Joint Failure
PLASTIC_JOINT_DETAILS | VARCHAR2 | Pipe, Weld, or Joint Failure - Fusion Joint Sub-type Details | PART G5 - Pipe, Weld, or Joint Failure
FPW_INSTALLED_YEAR | VARCHAR2 | Pipe, Weld, or Joint Failure Fusion Joint - Year installed | PART G5 - Pipe, Weld, or Joint Failure
FPW_OTHER_ATTR | VARCHAR2 | Pipe, Weld, or Joint Failure Fusion Joint - Other attributes | PART G5 - Pipe, Weld, or Joint Failure
FPW_FIRST_PLASTIC_TYPE | VARCHAR2 | Pipe, Weld, or Joint Failure Fusion Joint - First Material being joined - Type of Plastic Joint | PART G5 - Pipe, Weld, or Joint Failure
FPW_FIRST_PLASTIC_TYPE_OTHER | VARCHAR2 | Pipe, Weld, or Joint Failure Fusion Joint - First Material being joined - Other Type of Plastic Joint Details | PART G5 - Pipe, Weld, or Joint Failure
FPW_SECOND_PLASTIC_TYPE | VARCHAR2 | Pipe, Weld, or Joint Failure Fusion Joint - Second Material being joined - Type of Plastic Joint | PART G5 - Pipe, Weld, or Joint Failure
FPW_SECOND_PLASTIC_TYPE_OTHER | VARCHAR2 | Pipe, Weld, or Joint Failure Fusion Joint - Second Material being joined - Other Type of Plastic Joint Details | PART G5 - Pipe, Weld, or Joint Failure
PWJF_FAILURE_DETAILS | VARCHAR2 | Pipe, Weld, or Joint Failure - Other Pipe, Weld or Joint Failure Details | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_DENT_IND | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Dent | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_GOUGE_IND | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Gouge | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_PIPE_BEND_IND | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Pipe Bend | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_ARC_BURN_IND | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Arc Burn | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_CRACK_IND | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Crack | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_LACK_FUSION_IND | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Lack of Fusion | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_LAMINATION_IND | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Lamination | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_BUCKLE_IND | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Buckle | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_WRINKLE_IND | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Wrinkle | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_MISALIGNMENT_IND | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Misalignment | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_BURNT_STEEL_IND | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Burnt Steel | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_OTHER_IND | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Other | PART G5 - Pipe, Weld, or Joint Failure
ADDITIONAL_FACTOR_DETAILS | VARCHAR2 | Pipe, Weld, or Joint Failure Additional factor - Other Factor Details | PART G5 - Pipe, Weld, or Joint Failure
RESULT_CONSTRUCTION_IND | VARCHAR2 | Pipe, Weld, or Joint Failure - Incident Result of Construction defect | PART G5 - Pipe, Weld, or Joint Failure
RESULT_MATERIAL_IND | VARCHAR2 | Pipe, Weld, or Joint Failure - Incident Result of Material defect | PART G5 - Pipe, Weld, or Joint Failure
RESULT_DESIGN_IND | VARCHAR2 | Pipe, Weld, or Joint Failure - Incident Result of Design defect | PART G5 - Pipe, Weld, or Joint Failure
RESULT_PREVIOUS_IND | VARCHAR2 | Pipe, Weld, or Joint Failure - Incident Result of Previous damage | PART G5 - Pipe, Weld, or Joint Failure
RESULT_CONSTRUCTION_SUBTYPE | VARCHAR2 | Pipe, Weld, or Joint Failure - Incident Result of Construction defect Sub-type | PART G5 - Pipe, Weld, or Joint Failure
RESULT_MATERIAL_SUBTYPE | VARCHAR2 | Pipe, Weld, or Joint Failure - Incident Result of Material Sub-type | PART G5 - Pipe, Weld, or Joint Failure
RESULT_MATERIAL_DETAILS | VARCHAR2 | Pipe, Weld, or Joint Failure - Incident Result of Material Details | PART G5 - Pipe, Weld, or Joint Failure
HYDROTEST_CONDUCTED_IND | VARCHAR2 | Pipe, Weld, or Joint Failure - One or more Hydrotest or other pressure test conducted since original | PART G5 - Pipe, Weld, or Joint Failure
HYDROTEST_CONDUCTED_YEAR | VARCHAR2 | Year Hydrotest conducted | PART G5 - Pipe, Weld, or Joint Failure
HYDROTEST_PRESSURE | VARCHAR2 | Test pressure (psig) | PART G5 - Pipe, Weld, or Joint Failure
EQ_FAILURE_TYPE | VARCHAR2 | Equipment Failure Sub-Cause | PART G6 - Equipment Failure
CONTROL_VALVE_IND | VARCHAR2 | Equipment Failure - Specify Malfunction of Control/Relief Equipment - Control Valve (Yes, Null) | PART G6 - Equipment Failure
INSTRUMENTATION_IND | VARCHAR2 | Equipment Failure - Specify Malfunction of Control/Relief Equipment - Instrumentation (Yes, Null) | PART G6 - Equipment Failure
SCADA_IND | VARCHAR2 | Equipment Failure - Specify Malfunction of Control/Relief Equipment - SCADA (Yes, Null) | PART G6 - Equipment Failure
COMMUNICATIONS_IND | VARCHAR2 | Equipment Failure - Specify Malfunction of Control/Relief Equipment - Communications (Yes, Null) | PART G6 - Equipment Failure
BLOCK_VALVE_IND | VARCHAR2 | Equipment Failure - Specify Malfunction of Control/Relief Equipment - Block Valve (Yes, Null) | PART G6 - Equipment Failure
CHECK_VALVE_IND | VARCHAR2 | Equipment Failure - Specify Malfunction of Control/Relief Equipment - Check Valve (Yes, Null) | PART G6 - Equipment Failure
RELIEF_VALVE_IND | VARCHAR2 | Equipment Failure - Specify Malfunction of Control/Relief Equipment - Relief Valve (Yes, Null) | PART G6 - Equipment Failure
POWER_FAILURE_IND | VARCHAR2 | Equipment Failure - Specify Malfunction of Control/Relief Equipment - Power Failure (Yes, Null) | PART G6 - Equipment Failure
STOPPLE_CONTROL_FITTING_IND | VARCHAR2 | Equipment Failure - Specify Malfunction of Control/Relief Equipment - Stopple/Control Fitting (Yes, Null) | PART G6 - Equipment Failure
PRESSURE_REGULATOR_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Pressure Regulator (Yes, Null) | PART G6 - Equipment Failure
OTHER_CONTROL_RELIEF_IND | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Other Control/Relief (Yes, Null) | PART G6 - Equipment Failure
OTHER_CONTROL_RELIEF_DETAILS | VARCHAR2 | Equipment Failure Malfunction of Control/Relief Equipment - Other Control/Relief Details | PART G6 - Equipment Failure
OTHER_STRIPPED_IND | VARCHAR2 | Equipment Failure - Specify Threaded Connection/Coupling Failure | PART G6 - Equipment Failure
OTHER_STRIPPED_DETAILS | VARCHAR2 | Equipment Failure - Specify Threaded Connection/Coupling Failure Other Details | PART G6 - Equipment Failure
OTHER_NON_THREADED_IND | VARCHAR2 | Equipment Failure - Specify Non-threaded Connection Failure | PART G6 - Equipment Failure
OTHER_NON_THREADED_DETAILS | VARCHAR2 | Equipment Failure - Specify Non-threaded Connection Failure Other Details | PART G6 - Equipment Failure
VALVE_OTHER_IND | VARCHAR2 | Equipment Failure Valve - Other Valve | PART G6 - Equipment Failure
VALVE_OTHER_DETAILS | VARCHAR2 | Equipment Failure Valve - Other Valve Details | PART G6 - Equipment Failure
VALVE_TYPE | VARCHAR2 | Type of Valve | PART G6 - Equipment Failure
EQ_MANUFACTURER | VARCHAR2 | Equipment Failure Valve - Manufacture | PART G6 - Equipment Failure
EQ_MANUFACTURE_YEAR | VARCHAR2 | Equipment Failure Valve - Year of Manufacture of Valve | PART G6 - Equipment Failure
VALVE_MATERIAL | VARCHAR2 | Equipment Failure - Valve Material | PART G6 - Equipment Failure
VALVE_MATERIAL_DETAILS | VARCHAR2 | Equipment Failure - Valve Material, "Other", specify | PART G6 - Equipment Failure
EQ_FAILURE_DETAILS | VARCHAR2 | Equipment Failure Other Equipment Failure Details | PART G6 - Equipment Failure
OPERATION_TYPE | VARCHAR2 | Incorrect Operation Sub-Cause | PART G7 - Incorrect Operation
OPERATION_DETAILS | VARCHAR2 | Incorrect Operation - Other Incorrect Operation Details | PART G7 - Incorrect Operation
RELATED_INADEQUATE_PROC_IND | VARCHAR2 | Incorrect Operation Incident related to - Inadequate procedure (Yes, Null) | PART G7 - Incorrect Operation
RELATED_NO_PROC_IND | VARCHAR2 | Incorrect Operation Incident related to - No procedure established (Yes, Null) | PART G7 - Incorrect Operation
RELATED_FAILURE_FOLLOW_IND | VARCHAR2 | Incorrect Operation Incident related to - Failure to follow procedure (Yes, Null) | PART G7 - Incorrect Operation
RELATED_OTHER_IND | VARCHAR2 | Incorrect Operation Incident related to - Other (Yes, Null) | PART G7 - Incorrect Operation
OPERATION_RELATED_DETAILS | VARCHAR2 | Incorrect Operation Incident related to - Other Details | PART G7 - Incorrect Operation
CATEGORY_TYPE | VARCHAR2 | Incorrect Operation - Category type that caused incident | PART G7 - Incorrect Operation
OPERATOR_QUALIFICATION_IND | VARCHAR2 | Incorrect Operation - Operator Qualification Program (Yes, No, Null) | PART G7 - Incorrect Operation
QUALIFIED_INDIVIDUALS | VARCHAR2 | Incorrect Operation - Qualification of individuals performing the task(s) | PART G7 - Incorrect Operation
OTHER_TYPE | VARCHAR2 | Other Incident Cause Sub-Cause | PART G8 - Other Incident Cause
MISC_DETAILS | VARCHAR2 | Other Incident Cause - Miscellaneous Details | PART G8 - Other Incident Cause
UNKNOWN_SUBTYPE | VARCHAR2 | Other Incident Cause - Unknown Sub-type | PART G8 - Other Incident Cause
INCIDENT_UNKNOWN_COMMENTS | VARCHAR2 | Other Incident Cause - Investigation complete, cause of Incident unknown, specify | PART G8 - Other Incident Cause
EXTRNL_COR_GALVANIC_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Galvanic" | PART J - CONTRIBUTING FACTORS
EXTRNL_COR_ATMOSPHERIC_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Atmospheric" | PART J - CONTRIBUTING FACTORS
EXTRNL_COR_STRAY_CURRENT_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Stray Current Induced" | PART J - CONTRIBUTING FACTORS
EXTRNL_COR_MICROBIOLOGIC_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Microbiologically Induced" | PART J - CONTRIBUTING FACTORS
EXTRNL_COR_SELECTIVE_SEAM_IND | VARCHAR2 | Contributing Factors - External Corrosion, "Selective Seam" | PART J - CONTRIBUTING FACTORS
INTRNL_COR_CORROSIVE_CMDTY_IND | VARCHAR2 | Contributing Factors - Internal Corrosion, "Corrosive Commodity" | PART J - CONTRIBUTING FACTORS
INTRNL_COR_WTR_DRPOUT_ACID_IND | VARCHAR2 | Contributing Factors - Internal Corrosion, "Water drop-out/Acid" | PART J - CONTRIBUTING FACTORS
INTRNL_COR_MICROBIOLOGIC_IND | VARCHAR2 | Contributing Factors - Internal Corrosion, "Microbiological" | PART J - CONTRIBUTING FACTORS
INTRNL_COR_EROSION_IND | VARCHAR2 | Contributing Factors - Internal Corrosion, "Erosion" | PART J - CONTRIBUTING FACTORS
NF_EARTH_MOVEMENT_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Earth Movement, NOT due to Heavy Rains/Floods" | PART J - CONTRIBUTING FACTORS
NF_HEAVY_RAINS_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Heavy Rains/Floods" | PART J - CONTRIBUTING FACTORS
NF_LIGHTNING_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Lightning" | PART J - CONTRIBUTING FACTORS
NF_TEMPERATURE_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Temperature" | PART J - CONTRIBUTING FACTORS
NF_HIGH_WINDS_IND | VARCHAR2 | Contributing Factors - Natural Forces, "High Winds" | PART J - CONTRIBUTING FACTORS
NF_SNOW_ICE_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Snow/Ice" | PART J - CONTRIBUTING FACTORS
NF_VEGITATION_ROOT_IND | VARCHAR2 | Contributing Factors - Natural Forces, "Tree/Vegetation Root" | PART J - CONTRIBUTING FACTORS
EXCVTN_DMG_OPERATOR_IND | VARCHAR2 | Contributing Factors - "Excavation Damage by Operator (First Party)" | PART J - CONTRIBUTING FACTORS
EXCVTN_DMG_OP_CONTRACTOR_IND | VARCHAR2 | Contributing Factors - "Excavation Damage by Operator’s Contractor (Second Party)" | PART J - CONTRIBUTING FACTORS
EXCVTN_DMG_THIRD_PARTY_IND | VARCHAR2 | Contributing Factors - "Excavation Damage by Third Party" | PART J - CONTRIBUTING FACTORS
EXCVTN_DMG_PREVIOUS_DAMAGE_IND | VARCHAR2 | Contributing Factors - "Previous Damage due to Excavation Activit"y | PART J - CONTRIBUTING FACTORS
OSF_NEARBY_INDUSTRIAL_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Nearby Industrial, Man-made, or Other Fire/Explosion" | PART J - CONTRIBUTING FACTORS
OSF_VEHICLE_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Damage by Car, Truck, or Other Motorized Vehicle/Equipment NOT Engaged in Excavation" | PART J - CONTRIBUTING FACTORS
OSF_BOAT_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Damage by Boats, Barges, Drilling Rigs, or Other Adrift Maritime Equipment" | PART J - CONTRIBUTING FACTORS
OSF_OTHER_MARITIME_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Routine or Normal Fishing or Other Maritime Activity NOT Engaged in Excavation" | PART J - CONTRIBUTING FACTORS
OSF_ELECTRICAL_ARCING_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Electrical Arcing from Other Equipment or Facility" | PART J - CONTRIBUTING FACTORS
OSF_PREVIOUS_MECHANICAL_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Previous Mechanical Damage NOT Related to Excavation" | PART J - CONTRIBUTING FACTORS
OSF_INTENTIONAL_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Intentional Damage" | PART J - CONTRIBUTING FACTORS
OSF_OTHER_UNDERGROUND_IND | VARCHAR2 | Contributing Factors - Other Outside Force, "Other underground facilities buried within 12 inches of the failure location" | PART J - CONTRIBUTING FACTORS
PWF_DESIGN_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Design-related" | PART J - CONTRIBUTING FACTORS
PWF_CONSTRUCTION_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Construction-related" | PART J - CONTRIBUTING FACTORS
PWF_INSTALLATION_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Installation-related" | PART J - CONTRIBUTING FACTORS
PWF_FABRICATION_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Fabrication-related" | PART J - CONTRIBUTING FACTORS
PWF_MANUFACTURING_IND | VARCHAR2 | Contributing Factors - Pipe/Weld Failure, "Original Manufacturing-related" | PART J - CONTRIBUTING FACTORS
EQF_CONTROL_RELEAF_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Malfunction of Control/Relief Equipment" | PART J - CONTRIBUTING FACTORS
EQF_THREADED_COUPLING_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Threaded Connection/Coupling Failure" | PART J - CONTRIBUTING FACTORS
EQF_NON_THREADED_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Non-threaded Connection Failure" | PART J - CONTRIBUTING FACTORS
EQF_VALVE_FAILURE_IND | VARCHAR2 | Contributing Factors - Equipment Failure, "Valve Failure" | PART J - CONTRIBUTING FACTORS
IO_DAMAGE_BY_OPERATOR_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Damage by Operator or Operator’s Contractor NOT Excavation and NOT Vehicle/Equipment Damage" | PART J - CONTRIBUTING FACTORS
IO_VALVE_POSITION_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Valve Left or Placed in Wrong Position, but NOT Resulting in Overpressure" | PART J - CONTRIBUTING FACTORS
IO_EQUIPMENT_OVERPRESSURE_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Pipeline or Equipment Overpressured" | PART J - CONTRIBUTING FACTORS
IO_NOT_INSTALLED_PROPERLY_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Equipment Not Installed Properly" | PART J - CONTRIBUTING FACTORS
IO_WRONG_EQUIPMENT_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Wrong Equipment Specified or Installed" | PART J - CONTRIBUTING FACTORS
IO_INADEQUATE_PROCEDURE_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Inadequate Procedure" | PART J - CONTRIBUTING FACTORS
IO_NO_PROCEDURE_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "No procedure established" | PART J - CONTRIBUTING FACTORS
IO_FOLLOW_PROCEDURE_IND | VARCHAR2 | Contributing Factors - Incorrect Operation, "Failure to follow procedures" | PART J - CONTRIBUTING FACTORS
PREPARER_NAME | VARCHAR2 | Preparer's Name (Person filing the report) | PART I - PREPARER AND AUTHORIZED PERSON
PREPARER_TITLE | VARCHAR2 | Preparer's Title | PART I - PREPARER AND AUTHORIZED PERSON
PREPARER_EMAIL | VARCHAR2 | Preparer's Email address | PART I - PREPARER AND AUTHORIZED PERSON
PREPARER_TELEPHONE | VARCHAR2 | Preparer’s Telephone number | PART I - PREPARER AND AUTHORIZED PERSON
PREPARER_FAX | VARCHAR2 | Preparer's Facsimile number | PART I - PREPARER AND AUTHORIZED PERSON
LOCAL_CONTACT_NAME | VARCHAR2 | Local Contact Name | PART I - PREPARER AND AUTHORIZED PERSON
LOCAL_CONTACT_EMAIL | VARCHAR2 | Local Contact Email | PART I - PREPARER AND AUTHORIZED PERSON
LOCAL_CONTACT_TELEPHONE | VARCHAR2 | Local Contact Phone | PART I - PREPARER AND AUTHORIZED PERSON
AUTHORIZER_NAME | VARCHAR2 | Authorized Signature’s name | PART I - PREPARER AND AUTHORIZED PERSON
AUTHORIZER_TITLE | VARCHAR2 | Authorized Title | PART I - PREPARER AND AUTHORIZED PERSON
AUTHORIZER_TELEPHONE | VARCHAR2 | Authorized Telephone number | PART I - PREPARER AND AUTHORIZED PERSON
AUTHORIZER_EMAIL | VARCHAR2 | Authorized Email address | PART I - PREPARER AND AUTHORIZED PERSON
NARRATIVE | VARCHAR2 | Narrative description of the incident | PART H - NARRATIVE DESCRIPTION OF THE INCIDENT

## gd2010toPresent
DATAFILE_AS_OF | FF | SIGNIFICANT | SERIOUS | REPORT_NUMBER | SUPPLEMENTAL_NUMBER | REPORT_RECEIVED_DATE | REPORT_TYPE | OPERATOR_ID | NAME | OPERATOR_STREET_ADDRESS | OPERATOR_CITY_NAME | OPERATOR_STATE_ABBREVIATION | OPERATOR_POSTAL_CODE | LOCAL_DATETIME | TIME_ZONE | DAYLIGHT_SAVINGS_IND | IYEAR | LOCATION_STREET_ADDRESS | LOCATION_CITY_NAME | LOCATION_COUNTY_NAME | LOCATION_STATE_ABBREVIATION | LOCATION_POSTAL_CODE | LOCATION_LATITUDE | LOCATION_LONGITUDE | FLOW_CONT_KEY_CRIT_IND | FLOW_CONT_MAIN_VALVE_IND | FLOW_CONT_SERVICE_VALVE_IND | FLOW_CONT_METER_REG_IND | FLOW_CONT_EXCESS_FLOW_IND | FLOW_CONT_SQUEEZE_OFF_IND | FLOW_CONT_STOPPLE_FITNG_IND | FLOW_CONT_OTHER_IND | FLOW_CONT_OTHER_DETAIL | NRC_RPT_DATETIME | NRC_RPT_NUM | ADDITIONAL_NRC_REPORT_NUMBERS | COMMODITY_RELEASED_TYPE | COMMODITY_DETAILS | UNINTENTIONAL_RELEASE | INTENTIONAL_RELEASE | FATALITY_IND | NUM_EMP_FATALITIES | NUM_CONTR_FATALITIES | NUM_ER_FATALITIES | NUM_WORKER_FATALITIES | NUM_GP_FATALITIES | FATAL | INJURY_IND | NUM_EMP_INJURIES | NUM_CONTR_INJURIES | NUM_ER_INJURIES | NUM_WORKER_INJURIES | NUM_GP_INJURIES | INJURE | IGNITE_IND | IGNITE_DATETIME | HOW_EXTINGUISHED | HOW_EXTINGUISHED_OTHER_DETAIL | GAS_CONSUMED_BY_FIRE_IN_MCF | EXPLODE_IND | NUM_PUB_EVACUATED | INCIDENT_IDENTIFIED_DATETIME | COMMUNICATION_STATE_FED_IND | PARTY_INITIATED_COMMUNICATION | INITIAL_RESPONDER_COM_DATETIME | ON_SITE_DATETIME | CONFIRMED_DISCOVERY_DATETIME | FEDERAL | LOCATION_TYPE | INCIDENT_AREA_TYPE | INCIDENT_AREA_SUBTYPE | INCIDENT_AREA_DETAILS | DEPTH_OF_COVER | OTHER_UNDERGROUND_FACILITIES | CROSSING | BRIDGE_CROSSING_IND | BRIDGE_TYPE | RAILROAD_CROSSING_IND | RAILROAD_TYPE | ROAD_CROSSING_IND | ROAD_TYPE | WATER_CROSSING_IND | WATER_TYPE | WATER_NAME | WATER_DEPTH | WATER_SUBTYPE | PIPE_FACILITY_TYPE | PIPE_TYPE_OTHER | SYSTEM_PART_INVOLVED | SYSTEM_PART_DETAILS | INSTALLATION_YEAR | MANUFACTURED_YEAR | CUSTOMER_TYPE | WAS_EFV_INSTALLED_BEFORE_IND | EVF_ACTIVATION_IND | CURB_VALVE_INST_BEFORE_INC_IND | PIPE_DIAMETER | PIPE_SPECIFICATION | PIPE_MANUFACTURER | MATERIAL_INVOLVED | MATERIAL_DETAILS | STEEL_SEAM_TYPE | STEEL_SEAM_TYPE_DETAILS | WT_STEEL | PLASTIC_TYPE | PLASTIC_DETAILS | PLASTIC_SDR | WT_PLASTIC | WT_PLASTIC_UNKNOWN_IND | MATERIAL_PE_PIPE_CODE | RELEASE_TYPE | PUNCTURE_AXIAL | PUNCTURE_CIRCUM | LEAK_TYPE | LEAK_TYPE_OTHER | RUPTURE_ORIENT | RUPTURE_DETAILS | RUPTURE_LENGTH | RUPTURE_WIDTH | RELEASE_TYPE_DETAILS | CLASS_LOCATION_TYPE | EST_COST_OPER_PAID | EST_COST_OPER_PAID_CURRENT | EST_COST_PROP_DAMAGE | EST_COST_PROP_DAMAGE_CURRENT | EST_COST_EMERGENCY | EST_COST_EMERGENCY_CURRENT | EST_COST_OTHER | EST_COST_OTHER_CURRENT | EST_COST_OTHER_DETAILS | GAS_COST_IN_MCF | EST_COST_UNINTENTIONAL_RELEASE | EST_COST_UNINTENT_REL_CURRENT | EST_COST_INTENTIONAL_RELEASE | EST_COST_INTENT_REL_CURRENT | TOTAL_COST | TOTAL_COST_IN84 | TOTAL_COST_CURRENT | COMMERCIAL_AFFECTED | INDUSTRIAL_AFFECTED | RESIDENCES_AFFECTED | NUM_PERSONS_HOSP_NOT_OVNGHT | NUM_INJURED_TREATED_BY_EMT | NUM_RESIDENT_BUILDING_AFFCTD | NUM_BUSINESS_BUILDING_AFFCTD | ACCIDENT_PSIG | NORMAL_PSIG | MOP_PSIG | MOP_CFR_SECTION | MAOP_ESTABLISHED_DATE | ACCIDENT_PRESSURE | GAS_ODORIZED_SYSTEM_TYPE | GAS_ODORIZED_SYS_OTHER_DETAIL | GAS_ODORIZED_LEVEL | GAS_ODORIZED_LVL_NOT_MSRD_IND | SCADA_IN_PLACE_IND | SCADA_OPERATING_IND | SCADA_FUNCTIONAL_IND | SCADA_DETECTION_IND | SCADA_CONF_IND | ACCIDENT_IDENTIFIER | ACCIDENT_DETAILS | OPERATOR_TYPE | INVESTIGATION_STATUS | INVESTIGATION_STATUS_DETAILS | INVEST_SCHEDULE_IND | INVEST_NO_SCHEDULE_IND | INVEST_NO_SCHEDULE_IND_DETAILS | INVEST_NO_CONTROL_ROOM_IND | INVEST_NO_CONTROLLER_IND | INVEST_INCORRECT_ACTION_IND | INVEST_FATIGUE_IND | INVEST_INCORRECT_PROCEDURE_IND | INVEST_INCORRECT_CONTROL_IND | INVEST_MAINT_IND | INVEST_OTHER_IND | INVEST_OTHER_IND_DETAILS | EMPLOYEE_DRUG_TEST_IND | NUM_EMPLOYEES_TESTED | NUM_EMPLOYEES_FAILED | CONTRACTOR_DRUG_TEST_IND | NUM_CONTRACTORS_TESTED | NUM_CONTRACTORS_FAILED | CAUSE | CAUSE_DETAILS | MAP_SEVEN_CAUSE | MAP_SEVEN_SUBCAUSE | MAP_EIGHT_CAUSE | MAP_EIGHT_SUBCAUSE | INTERNAL_EXTERNAL | VISUAL_EXAM_RESULTS | VISUAL_EXAM_DETAILS | GALVANIC_CORROSION_IND | ATMOSPHERE_CORROSION_IND | STRAY_CURRENT_CORROSION_IND | MICROBIOLOGICAL_CORROSION_IND | SELECTIVE_SEAM_CORROSION_IND | OTHER_CORROSION_IND | CORROSION_TYPE_DETAILS | STRAY_CURRENT_TYPE | STRAY_CURRENT_DETAILS | FIELD_EXAM_BASIS_IND | METALLURGICAL_BASIS_IND | OTHER_BASIS_IND | CORROSION_BASIS_DETAILS | UNDERGROUND_LOCATION | UNDER_CATHODIC_PROTECTION_IND | CATHODIC_PRO_START_YEAR | SHIELDING_EVIDENT | CATHODIC_SURVEY_TYPE | CP_ANNUAL_SURVEY_IND | CLOSE_INTERVAL_SURVEY_IND | OTHER_CP_SURVEY_IND | CP_ANNUAL_SURVEY_YEAR | CLOSE_INTERVAL_SURVEY_YEAR | OTHER_CP_SURVEY_YEAR | OTHER_CP_SURVEY_DETAILS | EXTERNALLY_COATED | PRIOR_DAMAGE | COATING_TYPE | COATING_TYPE_DETAILS | FIELD_APPLIED_IND | INT_VISUAL_EXAM_RESULTS | INT_VISUAL_EXAM_DETAILS | INT_CORROSIVE_COMMODITY_IND | INT_WATER_ACID_IND | INT_MICROBIOLOGICAL_IND | INT_EROSION_IND | INT_OTHER_CORROSION_IND | INT_CORROSION_TYPE_DETAILS | INT_FIELD_EXAM_BASIS_IND | INT_METALLURGICAL_BASIS_IND | INT_OTHER_BASIS_IND | INT_CORROSION_BASIS_DETAILS | INT_LOW_POINT_PIPE_LOC_IND | INT_ELBOW_LOC_IND | INT_DROP_OUT_LOC_IND | INT_OTHER_LOC_IND | CORROSION_LOCATION_DETAILS | CORROSION_INHIBITORS | LIQUID_FOUND | COR_HYDROTEST_LEAK_SURVEY_DATE | COR_HYDROTEST_CONDUCTED_IND | COR_HYDROTEST_CONDUCTED_YEAR | COR_HYDROTEST_PRESSURE | NATURAL_FORCE_TYPE | EARTH_SUBTYPE | HEAVY_RAINS_SUBTYPE | LIGHTNING_SUBTYPE | TEMPERATURE_SUBTYPE | NF_OTHER_DETAILS | NF_EXTREME_WEATHER_IND | NF_HURRICANE_IND | NF_TROPICAL_STORM_IND | NF_TORNADO_IND | NF_OTHER_IND | NF_EXTREME_WEATHER_DETAILS | PARTY_TYPE | EX_HYDROTEST_LEAK_SURVEY_DATE | EX_HYDROTEST_CONDUCTED_IND | EX_HYDROTEST_CONDUCTED_YEAR | EX_HYDROTEST_PRESSURE | PRIOR_NOTIFICATION_IND | ONE_CALL_SYSTEM_IND | EXCAVATOR_IND | CONTRACTOR_IND | LANDOWNER_IND | STATE_LAW_EXEMPT_IND | STATE_LAW_EXEMPT_TYPE | STATE_LAW_EXEMPT_DETAIL | STATE_LAW_EXEMPT_AUTHORITY | STATE_LAW_EXEMPT_CRITERIA | NOTIFY_CGA_DIRT | PUBLIC_ROW_IND | PUBLIC_SUBTYPE | PRIVATE_ROW_IND | PRIVATE_SUBTYPE | PIPELINE_EASEMENT_ROW_IND | POWER_TRANSMISSION_ROW_IND | RAILROAD_ROW_IND | PUBLIC_UTIL_EASEMENT_ROW_IND | FEDERAL_LAND_ROW_IND | UNKNOWN_ROW_IND | JOINT_TRENCH_IND | CROSS_BORE_IND | DEPTH_OF_GRADE | DEPTH_OF_GRADE_DETAIL | EXCAVATOR_TYPE | EXCAVATOR_EQUIPMENT | WORK_PERFORMED | ONE_CALL_NOTIFIED_IND | ONE_CALL_TICKET_NUM | ONE_CALL_CENTER_NAME | WHITE_LINED_IND | LOCATOR_TYPE | VISIBLE_MARKS | SERVICE_INTERRUPTION | SERVICE_INTERRUPTION_HOURS | ROOT_CAUSE_CATEGORY | ROOT_CAUSE_TYPE | ROOT_CAUSE_TYPE_OTHER | OUTSIDE_FORCE_TYPE | VEHICLE_SUBTYPE | OSF_HURRICANE_IND | OSF_TROPICAL_STORM_IND | OSF_TORNADO_IND | OSF_HEAVY_RAINS_IND | OSF_OTHER_WEATHER_IND | OSF_OTHER_WEATHER_DETAILS | OSF_HYDROTEST_LEAK_SURVEY_DATE | OSF_HYDROTEST_CONDUCTED_IND | OSF_HYDROTEST_CONDUCTED_YEAR | OSF_HYDROTEST_PRESSURE | INTENTIONAL_SUBTYPE | INTENTIONAL_DETAILS | OSF_OTHER_DETAILS | DRIVER_ISSUED_CITATION_IND | CITATION_SPEED_IND | CITATION_RECKLESS_IND | CITATION_DUI_IND | CITATION_OTHER_IND | CITATION_OTHER_DETAIL | DRIVER_IN_CONTROL_IND | ESTIMATED_SPEED | VEHICLE_TYPE | VEHICLE_TRAVEL_FROM | VEHICLE_TRAVEL_DISTANCE_FT | PROTECTIONS_INSTALLED_IND | PROTECTION_BOLLARDS_POST_IND | PROTECTION_BARRICADES_IND | PROTECTION_GUARD_RAILS_IND | PROTECTION_METER_BOX_IND | PROTECTION_INGRESS_REGRESS_IND | PROTECTION_OTHER_IND | PROTECTION_OTHER_DETAIL | PWJF_FAILURE_TYPE | PIPE_BODY_SUBTYPE | PIPE_BODY_DETAILS | BUTT_WELD_SUBTYPE | BUTT_WELD_DETAILS | FILLET_WELD_SUBTYPE | FILLET_WELD_DETAILS | PIPE_SEAM_SUBTYPE | PIPE_SEAM_DETAILS | MEC_FITTING_INVOLVED | MEC_FITTING_INVLVD_DTL | MEC_FITTING_TYPE | MEC_FTTNG_TYPE_DETAIL | MEC_MANUFACTURER | MEC_PART_NUMBER | MEC_FITTING_MATERIAL | MEC_FITTING_MATERIAL_DETAIL | MEC_HOW_FAILURE_OCCURED | MEC_HOW_FAILURE_OCCURED_DTL | PLASTIC_JOINT_SUBTYPE | PLASTIC_JOINT_DETAILS | FPW_INSTALLED_YEAR | FPW_OTHER_ATTR | FPW_FIRST_PLASTIC_TYPE | FPW_FIRST_PLASTIC_TYPE_OTHER | FPW_SECOND_PLASTIC_TYPE | FPW_SECOND_PLASTIC_TYPE_OTHER | PWJF_FAILURE_DETAILS | ADDITIONAL_DENT_IND | ADDITIONAL_GOUGE_IND | ADDITIONAL_PIPE_BEND_IND | ADDITIONAL_ARC_BURN_IND | ADDITIONAL_CRACK_IND | ADDITIONAL_LACK_FUSION_IND | ADDITIONAL_LAMINATION_IND | ADDITIONAL_BUCKLE_IND | ADDITIONAL_WRINKLE_IND | ADDITIONAL_MISALIGNMENT_IND | ADDITIONAL_BURNT_STEEL_IND | ADDITIONAL_OTHER_IND | ADDITIONAL_FACTOR_DETAILS | RESULT_CONSTRUCTION_IND | RESULT_MATERIAL_IND | RESULT_DESIGN_IND | RESULT_PREVIOUS_IND | RESULT_CONSTRUCTION_SUBTYPE | RESULT_MATERIAL_SUBTYPE | RESULT_MATERIAL_DETAILS | HYDROTEST_CONDUCTED_IND | HYDROTEST_CONDUCTED_YEAR | HYDROTEST_PRESSURE | EQ_FAILURE_TYPE | CONTROL_VALVE_IND | INSTRUMENTATION_IND | SCADA_IND | COMMUNICATIONS_IND | BLOCK_VALVE_IND | CHECK_VALVE_IND | RELIEF_VALVE_IND | POWER_FAILURE_IND | STOPPLE_CONTROL_FITTING_IND | PRESSURE_REGULATOR_IND | OTHER_CONTROL_RELIEF_IND | OTHER_CONTROL_RELIEF_DETAILS | OTHER_STRIPPED_IND | OTHER_STRIPPED_DETAILS | OTHER_NON_THREADED_IND | OTHER_NON_THREADED_DETAILS | VALVE_OTHER_IND | VALVE_OTHER_DETAILS | VALVE_TYPE | EQ_MANUFACTURER | EQ_MANUFACTURE_YEAR | VALVE_MATERIAL | VALVE_MATERIAL_DETAILS | EQ_FAILURE_DETAILS | OPERATION_TYPE | OPERATION_DETAILS | RELATED_INADEQUATE_PROC_IND | RELATED_NO_PROC_IND | RELATED_FAILURE_FOLLOW_IND | RELATED_OTHER_IND | OPERATION_RELATED_DETAILS | CATEGORY_TYPE | OPERATOR_QUALIFICATION_IND | QUALIFIED_INDIVIDUALS | OTHER_TYPE | MISC_DETAILS | UNKNOWN_SUBTYPE | INCIDENT_UNKNOWN_COMMENTS | EXTRNL_COR_GALVANIC_IND | EXTRNL_COR_ATMOSPHERIC_IND | EXTRNL_COR_STRAY_CURRENT_IND | EXTRNL_COR_MICROBIOLOGIC_IND | EXTRNL_COR_SELECTIVE_SEAM_IND | INTRNL_COR_CORROSIVE_CMDTY_IND | INTRNL_COR_WTR_DRPOUT_ACID_IND | INTRNL_COR_MICROBIOLOGIC_IND | INTRNL_COR_EROSION_IND | NF_EARTH_MOVEMENT_IND | NF_HEAVY_RAINS_IND | NF_LIGHTNING_IND | NF_TEMPERATURE_IND | NF_HIGH_WINDS_IND | NF_SNOW_ICE_IND | NF_VEGITATION_ROOT_IND | EXCVTN_DMG_OPERATOR_IND | EXCVTN_DMG_OP_CONTRACTOR_IND | EXCVTN_DMG_THIRD_PARTY_IND | EXCVTN_DMG_PREVIOUS_DAMAGE_IND | OSF_NEARBY_INDUSTRIAL_IND | OSF_VEHICLE_IND | OSF_BOAT_IND | OSF_OTHER_MARITIME_IND | OSF_ELECTRICAL_ARCING_IND | OSF_PREVIOUS_MECHANICAL_IND | OSF_INTENTIONAL_IND | OSF_OTHER_UNDERGROUND_IND | PWF_DESIGN_IND | PWF_CONSTRUCTION_IND | PWF_INSTALLATION_IND | PWF_FABRICATION_IND | PWF_MANUFACTURING_IND | EQF_CONTROL_RELEAF_IND | EQF_THREADED_COUPLING_IND | EQF_NON_THREADED_IND | EQF_VALVE_FAILURE_IND | IO_DAMAGE_BY_OPERATOR_IND | IO_VALVE_POSITION_IND | IO_EQUIPMENT_OVERPRESSURE_IND | IO_NOT_INSTALLED_PROPERLY_IND | IO_WRONG_EQUIPMENT_IND | IO_INADEQUATE_PROCEDURE_IND | IO_NO_PROCEDURE_IND | IO_FOLLOW_PROCEDURE_IND | PREPARER_NAME | PREPARER_TITLE | PREPARER_EMAIL | PREPARER_TELEPHONE | PREPARER_FAX | LOCAL_CONTACT_NAME | LOCAL_CONTACT_EMAIL | LOCAL_CONTACT_TELEPHONE | AUTHORIZER_NAME | AUTHORIZER_TITLE | AUTHORIZER_TELEPHONE | AUTHORIZER_EMAIL | NARRATIVE
2025-03-31 10:13 | NO | YES | NO | 20100001 | 15047 | 2010-03-11 12:47 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-02-13 23:35 |  |  | 2010 | 1617 EAST 9TH STREET | STOCKTON | SAN JOAQUIN | CA | 95201 | 37.9319 | -121.2613 | [9 empty] | 2010-02-14 01:40 | 931232 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-02-14 00:05 |  |  |  | 2010-02-14 00:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUN | [9 empty] | OTHER | [8 empty] | SECONDARY IGNITION | CLASS 3 LOCATION | 100000 | 132110.949511739 | 500 | 660.554747558695 | 2000 | 2642.21899023478 | 0 | 0 |  |  | 0 | 0 |  | 0 | 102500 | 56084.302929565785 | 135413.723249532475 | 0 | 0 | 1 |  |  |  |  | 1 | 1 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | FIRE FIRST | [154 empty] | LAURENCE DENISTON | SR. PROGRAM MANAGER | lcd1@pge.com | 925.974.4313 |  |  |  |  | GLEN CARTER |  |  | No Email Address | A FIRE AT AN UNOCCUPIED HOME OCCURRED AT APPROXIMATELY 2335 HOURS ON 2/13/10. THE FIRE DEPARTMENT CALLED AT PG&E AT APPROXIMATELY 0005 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED AT 0020 HOURS. THE FIRE DEPARTMENT AND GSR WERE UNABLE TO SHUT OFF THE SERVICE VALVE AT THE METER DUE TO DAMAGE TO THE VALVE BY THE FIRE. A GAS CREW WAS CALLED AND THEY CUT OFF THE GAS SERVICE AT THE MAIN AT APPROXIMATELY 02:30. ACCORDING TO THE FIRE DEPARTMENT THE THE FIRE APPEARS TO HAVE STARTED IN ONE OF THE CLOSETS IN THE HOME. THE HOUSE FIRE DAMAGED THE GAS METER WHICH RELEASED NATURAL GAS RESULTING IN A SECONDARY IGNITION. THE FIRE DAMAGE TO THE HOME RESULTED IN PROPERTY DAMAGES EXCEEDING $50,000. THERE WERE NO INJURIES AND NO FATALITIES. NO MAJOR MEDIA WAS PRESENT.
2025-03-31 10:13 | NO | NO | NO | 20100002 | 15553 | 2010-03-12 18:01 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2010-02-16 10:38 |  |  | 2010 | 3835 SANDPIPER COVE RUN | SOUTH BEND | ST. JOSEPH | IN | 46628 | 41.7293 | -86.2753 | [9 empty] | 2010-02-16 13:45 | 931402 |  | NATURAL GAS |  | 310 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 20 | 2010-02-16 10:38 |  |  |  | 2010-02-16 11:18 |  | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | UNDER SOIL MIGRATED TO HOUSE | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1990 | [5 empty] | 3 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 3 | 1 | [7 empty] | CLASS 3 LOCATION | 40000 | 52844.3798046956 | 5000 | 6605.54747558695 | 10000 | 13211.0949511739 | 0 | 0 |  |  | 2500 | 1727.346278317152103559870550161812297735 |  | 0 | 57500 | 31691.9126462379198381877022653721682848 | 74388.3685097736021035598705501618122977 | 0 | 0 | 64 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | ELECTRIC | NO |  |  |  | CONTRACT LOCATOR | YES | YES | 13 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | JOHN CURTIS | MANAGER SYSTEM INTEGRITY AND DESIGN | jlcurtis@nisource.com | 219-962-0425 | 219-962-0404 |  |  |  | JOHN CURTIS | MANAGER SYSTEM INTEGRITY AND DESIGN | 219-962-0425 | jlcurtis@nisource.com | CONTRACTOR BORING ELECTRIC LINE PARALLEL TO 3" DISTRIBUTION LINE AT 45 PSI. HIT LINE, WHILE TAKING PRECAUTIONS TO SHUT DOWN SYSTEM, GAS MIGRATED TO NEARBY HOUSE AND EXPLODED. THERE WAS A REQUEST BY PHMSA THROUGH THE INDIANA PUBLIC SERVICE COMMISSION TO PROVIDE ADDTIONAL INFORMATION, AND/OR UPDATE SOME DATA FIELDS. ALL WERE COMPLETED AS REQUESTED EXCEPT PART G REQUESTING TO COMPLETE THE SECTION FOR PREVIOUS DAMAGE DUE TO EXCAVATION. THERE WAS NO PREVIOUS DAMAGE DUE TO EXCAVATION RELATED TO THIS INCIDENT. THE INFORMATION FOR THE ITEMS REQUESTED IS: 1. DATE OF MOST RECENT LEAK SURVEY CONDUCTED - ANSWER IS 3-11-2010. 2. HAS ONE OR MORE PRESSURE TEST BEEN COMPLETED SINCE ORIGINAL CONSTRUCTION AT THE POINT OF INCIDENT - ANSWER IS NONE. WITH ALL OF THE REQUESTED INFORMATION UPDATED THIS INCIDENT WILL BE CLOSED.
2025-03-31 10:13 | NO | NO | NO | 20100003 | 15023 | 2010-03-15 14:06 | SUPPLEMENTAL FINAL | 31840 | UNISOURCE ENERGY SERVICES | 2901 W. SHAMRELL BLVD. | FLAGSTAFF | AZ | 86001 | 2010-02-22 20:57 |  |  | 2010 | 8725 COUNTRY CLUB DRIVE | PINETOP | NAVAJO | AZ | 85935 | 34.1093 | -109.8601 | [9 empty] | 2010-02-22 22:22 | 931971 |  | NATURAL GAS |  | 14 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2010-02-22 20:57 |  |  |  | 2010-02-22 21:50 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1999 | [8 empty] | STEEL |  | OTHER | ERW | 0.113 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 153 | 202.12975275296067 | 2420 | 3197.0849781840838 |  | 0 |  |  | 75 | 51.82038834951456310679611650485436893204 |  | 0 | 2648 | 1455.789687718739737145631067961165048544 | 3451.035119286559033106796116504854368932 | 0 | 0 | 1 |  |  |  |  | 50 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | SNOW ACCUMULATION ON THE METER SET ASSEMBLY | NO | [218 empty] | ROBERT ADAMS | SHOW LOW DISTRICT MANAGER | radams@uesaz.com | 928 532-3801 | 928 537-3994 |  |  |  | ROBERT ADAMS | SHOW LOW DISTRICT MANAGER | 928 532-3801 | radams@uesaz.com | ON 2/22/10 PINETOP FIRE DEPARTMENT RESPONDED TO A FIRE @ 8725 COUNTRY CLUB DRIVE AND NOTIFIED UNISOURCE ENERGY SERVICES THAT THE FIRE WAS AT THE GAS METER AND APPEARED TO INVOLVE ESCAPING GAS. UPON ARRIVAL IT WAS DETERMINED THAT THE METER SET ASSEMBLY HAD BEEN DAMAGED; GAS WAS ESCAPING, AND HAD IGNITED. THE SERVICE LINE WAS DISCONNECTED. THIS ACTION EXTINGUISHED THE GAS FIRE. THE FIRE DEPARTMENT EXTINGUISHED A SMALL AREA OF THE ADJACENT STRUCTURE THAT HAD CAUGHT FIRE. TTHE PROBABLE CAUSE FOR THE DAMAGE TO THE METER SET ASSEMBLY WAS THE FORCE EXERTED UPON IT BY SIX PLUS FEET OF SNOW AND ICE THAT HAD ACCUMULATED AND FALLEN FROM THE ROOF OF THE ADJACENT STRUCTURE. ON 2/23/10 THE AFFECTED RISER WAS REPLACED THE SERVICE LINE TESTED AND RECONNECTED BY UES CONSTRUCTION PERSONNEL. ON 4/14/10, A SUPPLIMENTAL FILE WAS UPDATED WITH CORRECTED 14 MCF OF LOST GAS AND $0. ESTIMATED COST FOR PUBLIC AND NON OPERATOR PRIVATE PROPERTY DAMAGE PAID/REINBURSED BY THE OPERATOR. AN UPDATED TOTAL FOR THE ESTIMATED COST TO THE OPERATOR IS $2,648. ON 5/5/10, A SUPPLIMENTAL FILE WAS UPDATED WITH THIS ADDITIONAL INFORMATION BASED ON A CONVERSATION WITH ANGELA DOW OF PHMSA ON 5/5/10. THE COST OF REPAIRS, AS PROVIDED BY THE CONTRACTOR PERFORMING THE WORK TO THE STRUCTURE ARE $25,000.THESE COSTS ARE BEING COVERED BY PARTIES OTHER THAN THE OPERATOR.
2025-03-31 10:13 | NO | YES | YES | 20100004 | 15003 | 2010-03-16 18:52 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2010-02-18 19:05 |  |  | 2010 | 359 HAWTHORNE CIRCLE | MOUNT PROSPECT | COOK | IL | 60056 | 42.0367 | -87.9431 | [9 empty] | 2010-02-18 21:30 | 931640 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO |  | 2010-02-18 19:05 |  |  |  | 2010-02-18 19:06 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1976 | [5 empty] | 1 | ASTM B88 | UNKNOWN | COPPER | [10 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 20000 | 26422.1899023478 | 500 | 660.554747558695 | 1500 | 1981.664242676085 | 0 | 0 |  |  | 5 | 3.45469255663430420711974110032362459547 |  | 0 | 22005 | 12040.8022753236468996763754045307443366 | 29067.8635851392143042071197411003236246 | 1 | 0 | 0 |  |  |  |  | 58 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | NO | [22 empty] | 2009-11-18 | NO | [227 empty] | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | lquezad@nicor.com | 6303882316 |  |  |  |  | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | 6303882316 | lquezad@nicor.com | CREW WAS DIGGING A HOLE TO FIX A SERVICE LINE LEAK AT A PRIVATE RESIDENCE WHEN AN UNKNOWN IGNITION SOURCE IGNITED THE GAS IN THE HOLE CAUSING FLASH BURNS TO THE FACE OF ONE EMPLOYEE. NOTE: PART C 3.A REQUIRES PIPE DIAMETER. THE DIAMETER OF THE SERVICE LINE INVOLVED IS 5/8" OD, WHICH IS EQUIVALENT TO 0.625" OD. THE DATABASE DOES NOT ALLOW FOR ENTRY OF 0.625 AS AN ACCEPTABLE NUMBER, THEREFORE THE NUMBER 1 WILL BE ENTERED TO ALLOW THIS REPORT TO BE ACCEPTED BY THE DATABASE CONTRAINTS.
2025-03-31 10:13 | NO | YES | YES | 20100005 | 15639 | 2010-03-22 15:57 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD. NE STE, 20 | ALBUQUERQUE | NM | 87109 | 2010-02-21 01:38 |  |  | 2010 | 303 COUNTY RD. 6100 | KIRTLAND | SAN JUAN | NM | 87417 | 36.7435 | -108.3338 | [9 empty] | 2010-03-22 14:30 | 931939 |  | NATURAL GAS |  | 5625 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO |  |  |  |  | NO | 0 | 2010-03-21 01:45 |  |  |  | 2010-03-21 03:32 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | CAR HIT METER BREAKING LOOP | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 119 | 157.21202991896941 | 189 | 249.68969457718671 | 4500 | 5944.992728028255 | DAMAGE TO THE CAR, DAMAGE TO A FENCE AND DAMAGE TO A TELEPHONE POLE. |  | 35 | 24.18284789644012944983818770226537216828 |  | 0 | 4843 | 2653.134730506712729734627831715210355987 | 6376.077300420851249449838187702265372168 | 0 | 0 | 0 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAR HIT METER. CONTROLLERS ACTIONS OR CONTROL ROOM ISSUES NOT INVOLVED. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | GARY G ROYBAL | MANAGER DOT PIPELINE SAFETY COMPLIANCE | gary.roybal@nmgco.com | 505-697-3636 | 505-697-4481 |  |  |  | ED KACER | VICE PRESIDENT TECHNICAL SERVICES | 505-697-3303 | ed.kacer@nmgco.com | A SAN JUAN COUNTY DEPUTY SHERIFF WAS IN PURSUIT OF A VEHICLE WHEN IT CRASHED INTO THE COMPANY'S METER SET, A FENCE AND A TELEPHONE POLE. THE DRIVER OF THE VEHICLE WAS INJURED AND TAKEN TO THE HOSIPTAL FOR TREATMENT. THE RELEASE OF GAS FROM THE COMPANY'S FACILITIES WAS NOT THE CAUSE OF THE DRIVER'S INJURIES WHICH REQUIRED MEDICAL ATTENTION OR DAMAGES.
2025-03-31 10:13 | NO | YES | NO | 20100006 | 15422 | 2010-03-24 14:21 | SUPPLEMENTAL FINAL | 31636 | NORTHERN STATES POWER CO OF MINNESOTA | 414 NICOLLET MALL | MINNEAPOLIS | MN | 55402 | 2010-02-01 10:07 |  |  | 2010 | 2014 VILLARD AVENUE | SAINT PAUL | RAMSEY | MN | 55116-2538 | 44.9096 | -93.1852 | [9 empty] | 2010-02-01 11:34 | 930206 |  | NATURAL GAS |  | 20 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2010-02-01 10:07 |  |  |  | 2010-02-01 10:32 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1991 | [5 empty] | 2 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 0.3 | [7 empty] | CLASS 3 LOCATION | 300000 | 396332.848535217 | 6000 | 7926.65697070434 | 5000 | 6605.54747558695 | 0 | 0 |  |  | 150 | 103.640776699029126213592233009708737864 |  | 0 | 311150 | 170263.8563336756609902912621359223300971 | 410968.6937582073191262135922330097087379 | 0 | 0 | 15 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | MECHANICAL DAMAGE CAUSED BY SEWER CLEANING CONTRACTOR OPERATING SEWER CLEARING EQUIPMENT. | [154 empty] | DANIEL J WOEHRLE | MANAGER GAS SYSTEM ENGINEERING | daniel.j.woehrle@xcelenergy.com | 6512292211 | 6512292376 |  |  |  | DANIEL J WOEHRLE | MANAGER GAS SYSTEM ENGINEERING | 6512292211 | daniel.j.woehrle@xcelenergy.com | 2" POLYETHYLENE GAS MAIN WAS PUNCTURED DURING THE CLEARING OF THE SANITARY SEWER SERVICE BY THIRD PARTY FROM WITHIN THE HOUSE AT 2014 VILLARD AVENUE. GAS ESCAPED INTO THE HOUSE THROUGH THE SEWER SERVICE AND WAS IGNITED BY AN UNDERTERMINED SOURCE OF IGNITION.
2025-03-31 10:13 | NO | YES | YES | 20100007 | 15007 | 2010-03-24 15:59 | ORIGINAL FINAL | 5300 | FLORENCE GAS DEPT, CITY OF | 110 W. COLLEGE ST. / P.O. BOX 937 | FLORENCE | AL | 35631 | 2010-01-29 23:55 |  |  | 2010 | 316 HERMITAGE DRIVE | FLORENCE | LAUDERDALE | AL | 35630 | 34.8066 | -87.6757 | [9 empty] | 2010-01-30 01:30 | 930054 |  | NATURAL GAS |  | 14000 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO |  | 2010-01-30 00:12 |  |  |  | 2010-01-30 00:23 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1989 | [8 empty] | OTHER | METER | [9 empty] | OTHER | [8 empty] | TRUCK HIT METER SET BREAKING IT AWAY FRO | CLASS 3 LOCATION |  | 0 | 300 | 396.332848535217 | 960 | 1268.2651153126944 | 90000 | 118899.8545605651 | HOUSE DAMAGE AND TRUCK DAMAGE |  | 153 | 105.713592233009708737864077669902912621 |  | 0 | 91413 | 50031.971607035176370097087378640776699 | 120670.1661166460211087378640776699029126 | 0 | 0 | 1 |  |  |  |  | 23 | 23 | 26 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | FIRE DEPARTMENT |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | TRUCK HIT GAS METER NOT CAUSING ANY REDUCTION IN SYSTEMS OPERATING PRESSURE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | RANDY FANNIN | PUBLIC AFFAIRS SAFETY COORDINATOR | rfannin@florenceal.org | 2567185114 | 2567606387 |  |  |  | MICHAEL DOYLE | MANAGER | 2567185100 | mdoyle@florence.org | A VEHICLE TRAVELING EAST ON HERMITAGE DRIVE LEFT THE ROADWAY AND HIT THE RESIDENCE AT 316 HERMITAGE DRIVE. THE TRUCK STRUCK THE HOUSE WHERE THE GAS METER WAS SET BREAKING THE METER OFF AT THE RISER. THE GAS WAS IGNITED AND THE HOUSE AND TRUCK WERE BOTH A TOTAL LOSS. THE OCCUPANTS IN THE TRUCK LEFT THE SCENE ON FOOT AND THE DRIVER WAS ARRESTED LATER THAT AFTERNOON. THE OWNER OF THE HOUSE. JAMES ROBERT WATSON, HAD TO CLIMB OUT OF THE SECOND FLOOR WINDOW TO ESCAPE THE FIRE. IN DOING SO, HE SLIPPED AND FELL TO THE GROUND BREAKING HIS BACK IN 3 PLACES AND ALSO BREAKING HIS PELVIS. HE WAS TAKEN TO ECM HOSPITAL IN FLORENCE AND THEN TRANSFERRED TO HUNTSVILLE HOSPITAL WHERE HE WAS ADMITTED FOR A NUMBER OF DAYS. THE SERVICEMEN WHO RESPONDED SQUEEZED THE SERVICE LINE OFF TO STOP THE FLOW OF GAS SO THE FIRE DEPARTMENT COULD CONTAIN THE FIRE. AFTER THE FIRE WAS EXTINGUISHED TO A SAFE POINT; THE SERVICE LINE WAS KILLED. THE SERVICE LINE WILL NOT BE PUT BACK DUE TO THE HOUSE BEING A TOTAL LOSS. I HAVE INCLUDED THE FLORENCE POLICE REPORT, THE FLORENCE FIRE DEPARTMENT REPORT, AND STATEMENTS OF OUR SERVICE DEPARTMENT PERSONNEL.
2025-03-31 10:13 | NO | NO | NO | 20100008 | 15008 | 2010-03-25 13:30 | ORIGINAL FINAL | 8040 | AMERENIP | 500 SOUTH 27TH STREET | DECATUR | IL | 62525 | 2010-02-26 14:17 |  |  | 2010 | 718 ELLIOTT STREET | KEWANEE | HENRY | IL | 61443 | 41.2351 | -89.9301 | [9 empty] | 2010-02-26 16:10 | 932473 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2010-02-26 14:17 |  |  |  | 2010-02-26 14:18 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1969 | [8 empty] | OTHER | GAS REGULATOR | [9 empty] | OTHER | [8 empty] | NO RELEASE - HIGH DELIVERY PRESSURE | CLASS 3 LOCATION | 0 | 0 | 550 | 726.6102223145645 | 315 | 416.14949096197785 | 0 | 0 |  |  | 0 | 0 |  | 0 | 865 | 473.29680033243321 | 1142.75971327654235 | 6 | 0 | 0 |  |  |  |  | 9 | 1 | 2 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [218 empty] | JEROME THEMIG | MANAGER OF GAS COMPLIANCE | jthemig@ameren.com | 217-625-6804 | 217-625-6803 |  |  |  | JEROME THEMIG | MANAGER OF GAS COMPLIANCE | 217-625-6804 | jthemig@ameren.com | AMERENIP RECEIVED A CALL FROM AN OCCUPANT AT AN OFFICE BUILDING AT 718 ELLIOTT IN KEWANEE REPORTING A GAS IGNITION ASSOCIATED WITH A FURNACE. AMERENIP QUALIFIED EMPLOYEES RESPONDED TO THE CALL AND UPON ARRIVAL FOUND THAT THE BUILDING WAS BEING VENTILATED BY THE KEWANEE FIRE DEPARTMENT. THE AMERENIP GAS FACILITIES WERE INITIALLY INSPECTED AND DISCOVERED THAT A LEAKING DOWNSPOUT WAS DRIPPING ON THE GAS PRESSURE REGULATOR WHICH ICED OVER CAUSING A SUSPECTED HIGHER THAN NORMAL DELIVERY PRESSURE. UPON FURTHER INVESTIGATION THE DELIVERY PRESSURE WAS CHECKED AND FOUND TO BE 8.9 PSIG TO CUSTOMER APPLIANCES THAT NORMALLY RECEIVE 0.25 PSIG GAS PRESSURE. THIS HIGHER THAN NORMAL PRESSURE APPARENTLY CAUSED AN IMPROPER OPERATION OF THE A FURNACE AND A SUBSEQUENT GAS IGNITION. ESTIMATED PROPERTY DAMAGE IS $18,000 WHICH IS LESS THAN THE $50,000 THRESHOLD FOR A REPORTABLE INCIDENT; HOWEVER, UPON REPORTING THIS EVENT TO THE ILLINOIS COMMERCE COMMISSION, THE MANAGER OF PIPELINE SAFETY RECOMMENDED THAT THIS BE REPORTED AS AN EVENT THAT IS SIGNIFICANT, IN THE JUDGMENT OF THE OPERATOR, EVEN THOUGH IT DID NOT MEET THE CRITERIA OF PARAGRAPH (1) OR (2) IN CFR 49 191.3. NOTE - THE OPERATOR NAME AND ADDRESS ARE INCORRECT IN THE PHMSA DATA BASE. PLEASE UPDATE PER THE FOLLOWING LETTER THAT WAS SUBMITTED TO PHMSA IN EARLY 2009. MARCH 30, 2009 LISTED BELOW IS INFORMATION WE ARE PROVIDING TO UPDATE YOUR DATABASE REGARDING AMEREN SUBSIDIARIES AND THEIR RESPECTIVE MERGER / CONTACT INFORMATION. AMEREN CORPORATION WAS CREATED DECEMBER 31, 1997 BY THE MERGER OF MISSOURI'S UNION ELECTRIC COMPANY AND THE NEIGHBORING CENTRAL ILLINOIS PUBLIC SERVICE COMPANY IT IS NOW A HOLDING COMPANY FOR SEVERAL POWER COMPANIES: AMERENUE, UNION ELECTRIC COMPANY, 1997 AMERENCIPS, CENTRAL ILLINOIS PUBLIC SERVICE COMPANY, 1997 AMERENCILCO, CENTRAL ILLINOIS LIGHT COMPANY, 2003 AMERENIP, ILLINOIS POWER COMPANY, 2004 OPERATOR ID PRIOR COMPANY NAME CURRENT COMPANY NAME YEAR OF NAME CHANGE 2204 CENTRAL ILLINOIS PUBLIC SERVICE COMPANY AMERENCIPS 1997 2200 CENTRAL ILLINOIS LIGHT COMPANY AMERENCILCO 2003 8040 ILLINOIS POWER COMPANY AMERENIP 2004 20050 AMERENUE (ILLINOIS OPERATIONS) AMERENCIPS 2005 BEGAN REPORTING AS OPERATOR ID 2204 IN 2005 20050 UNION ELECTRIC COMPANY (MISSOURI OPERATIONS) AMERENUE 1997 AMEREN (UE) MISSOURI - NAME OF OPERATOR ADDITIONAL CONTACT INFO: 1310 INDUSTRIAL DRIVE JEFFERSON CITY, COLE COUNTY MISSOURI 65109 AMEREN (CIPS, IP, CILCO) ILLINOIS - NAME OF OPERATOR ADDITIONAL CONTACT INFO: 2125 EAST STATE ROUTE #104 PAWNEE, SANGAMON COUNTY ILLINOIS 62558 SINCERELY, JEROME S. THEMIG MANAGER, GAS COMPLIANCE AND TRAINING (217) 625-6804
2025-03-31 10:13 | NO | NO | NO | 20100009 | 15009 | 2010-03-26 09:23 | ORIGINAL | 32227 | THE NATURAL GAS COMPANY, LLC | 2115 MCDUFFIE ST., #A | HOUSTON | TX | 77019-6523 | 2010-02-17 11:45 |  |  | 2010 | 9059 TUMBLEWOOD DRIVE | BEACH CITY | CHAMBERS | TX | 77523 | 29.7499 | -94.8416 | [12 empty] | NATURAL GAS |  | 63 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-02-17 11:50 |  |  |  | 2010-02-17 12:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2007 | [5 empty] | 2 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | [9 empty] | CLASS 2 LOCATION | 0 | 0 | 290 | 383.1217535840431 | 500 | 660.554747558695 |  | 0 |  |  | 487 | 336.487055016181229773462783171521035599 |  | 0 | 1277 | 743.529732043138488478964401294498381877 | 1380.163556158919329773462783171521035599 | 0 | 0 | 0 |  |  |  |  | 58 | 58 | 67 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | CONTRACTOR INSTALLING WATER TAP | [154 empty] | MICHAEL R LANNOU | PRESIDENT | natgasco@gmail.com | 7135280569 | 7135280569 |  |  |  | MICHAEL R LANNOU | PRESIDENT | 7135280569 | natgasco@gmail.com | CONTRACTOR INSTALLING WATER TAP AND HIT LINE WITH BACKHOE WHEN DIGGING.
2025-03-31 10:13 | YES | NO | NO | 20100010 | 15039 | 2010-03-27 02:01 | SUPPLEMENTAL FINAL | 12876 | QUESTAR GAS COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2010-02-25 19:37 |  |  | 2010 | 415 S 100 E | PLEASANT GROVE | UTAH | UT | 84062 | 40.3589 | -111.7388 | [9 empty] | 2010-02-25 20:35 | 932341 |  | NATURAL GAS |  | 36 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 30 | 2010-02-25 19:47 |  |  |  | 2010-02-25 20:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2005 | [8 empty] | STEEL |  |  |  | 0.113 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 1000 | 1321.10949511739 | 5000 | 6605.54747558695 | 0 | 0 |  |  | 151 | 104.331715210355987055016181229773462783 |  | 0 | 6151 | 3379.496531104742770226537216828478964401 | 8030.988685914695987055016181229773462783 | 13 | 0 | 6 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | JEFFREY D. HANSEN | SUPERVISOR INTEGRITY MANAGEMENT | jeff.hansen@questar.com | 801-324-3645 | 801-324-3300 |  |  |  | VAUGHN W. SHOSTED | GENERAL MANAGER OPERATIONS SUPPPORT | 801-324-3384 | vaughn.shosted@questar.com | QUESTAR GAS EMERGENCY DISPATCH RECEIVED A CALL AT 7:47 P.M. FROM PLEASANT GROVE EMERGENCY DISPATCH REGARDING A POSSIBLE EXPLOSION LOCATED AT 85 EAST STATE STREET, IN PLEASANT GROVE, UTAH. QUESTAR PERSONNEL RESPONDED ON SITE AT APPROXIMATELY 8:00 P.M. UPON ARRIVAL, THE HOME LOCATED AT 415 SOUTH 100 EAST WAS COMPLETELY DESTROYED, AND NATURAL GAS WAS ESCAPING NEAR THE FOUNDATION OF THE HOME FROM WHERE THE GAS METER ONCE WAS. THE FORCE OF THE HOME EXPLODING CAUSED THE METER TO BE SEVERED FROM THE SERVICE LINE AND CAUSED THE UNINTENTIONAL RELEASE OF NATURAL GAS. THE GAS DID NOT IGNITE OR EXPLODE. THE METER WAS LOCATED APPROXIMATELY TEN FEET FROM THE FOUNDATION OF THE HOME. THE 3/4 INCH NIPPLE GOING INTO THE REGULATOR HAD FAILED DUE TO THE FORCE OF THE EXPLOSION. IMMEDIATELY UPON ARRIVAL QUESTAR PERSONNEL PERFORMED TESTS TO CHECK FOR GAS IN THE GROUND AROUND THE DAMAGED HOUSE AND IN THE SEWER MANHOLES. NO GAS WAS DETECTED IN THE GROUND, IN THE TELEPHONE DUCT WORK OR IN THE SEWER. QUESTAR PERSONNEL THEN BEGAN TO SECURE THE SITE AND CUT AND CAPPED THE DAMAGE SERVICE LINE. THE SERVICE LINE WAS LEAK TESTED FROM THE CUT TO THE RISER. NO LEAKS WERE DETECTED. THE REMAINDER OF THE SERVICE LINE WAS LEAK TESTED FROM THE CUT TO THE MAIN AND THEN PERMANENTLY RETIRED. NO LEAKS WERE DETECTED. ONCE THE DAMAGED SERVICE LINE WAS SECURED ADDITIONAL LEAK SURVEYS WERE CONDUCTED IN THE AREA TO ENSURE THAT THERE WAS NO LEAKING GAS IN THE GENERAL VICINITY. THE ADDITIONAL LEAK SURVEY INCLUDED ALL SURFACE STREETS, DUCTS, SEWERS, AND GAS LINE LOCATIONS WITHIN A TWO BLOCK LIMIT OF THE DAMAGED HOME. NO LEAKS WERE DISCOVERED. THE HOME WAS VACANT AT THE TIME OF THE EXPLOSION. NO INJURIES OR FATALITIES WERE REPORTED AS A RESULT OF THIS EXPLOSION. THE CAUSE OF THE EXPLOSION IS STILL UNDER INVESTIGATION AT THIS TIME BY THE PLEASANT GROVE POLICE DEPARTMENT AND UTAH STATE FIRE MARSHALL. UPDATE: BASED ON THE TESTING PERFORMED AT THE SITE, THE SOURCE OF THE LEAK IS BELIEVED TO HAVE COME FROM CUSTOMER OWNED PIPING INSIDE THE HOME.
2025-03-31 10:13 | NO | YES | NO | 20100011 | 15011 | 2010-03-29 11:57 | ORIGINAL FINAL | 2432 | FLORIDA CITY GAS | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2010-03-01 10:56 |  |  | 2010 | HWY 520 @HUBERT HUMPHREY BRIDGE | COCOA |  | FL | 32922 | 28.3555 | -80.7141 | [9 empty] | 2010-03-01 16:15 | 932687 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-03-01 10:56 |  |  |  | 2010-03-01 13:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | UNDER WATER | 4 |  | YES | [6 empty] | YES | UNCASED |  | 8 |  | PRIVATELY OWNED |  | MAIN |  | 1968 | [5 empty] | 6 | API 5L | UNKNOWN | STEEL |  | SEAMLESS | SEAMLESS ERW | 0.344 | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 1 LOCATION | 0 | 0 | 125000 | 165138.68688967375 | 5000 | 6605.54747558695 |  | 0 |  |  | 70 | 48.36569579288025889967637540453074433657 |  | 0 | 130070 | 71176.052132943644595469255663430420712 | 171792.6000610535802588996763754045307443 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) WERE NOT INVESTIGATED DUE TO THERE WERE NO POSSIBLE CONTRIBUTING FACTORS BY THEIR ACTIONS TO CAUSE THIS INCIDENT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | [197 empty] | NON-THREADED CONNECTION FAILURE | [14 empty] | GASKET | [68 empty] | REBEKAH FLICKINGER | COMPLIANCE ENGINEER | rflickin@aglresources.com | 4045843094 |  |  |  |  | RICHARD LONN | DIRECTOR REGULATORY COMPLIANCE | 4045843552 | rlonn@aglresources.com | BUBBLES WERE OBSERVED AND AN ODOR OF NATURAL GAS WAS DETECTED BY A PERSON FISHING ON THE INDIAN RIVER NEAR HWY 520 @ THE HUBERT HUMPHREY BRIDGE (SOUTH SIDE) THIS PERSON NOTIFIED FCG WHO RESPONDED AND DETERMINED THERE WAS A COUPLING LEAKING ON A 6" STEEL MAIN. THE DEPTH OF WATER IS APPROX 8FT DEEP AND THE PIPE IS COVERED WITH APPROX 4FT GROUND. A QUALIFIED DIVE TEAM WAS UTILIZED TO UNCOVER THE MAIN AND MAKE THE REPAIR.
2025-03-31 10:13 | NO | YES | NO | 20100012 | 15012 | 2010-03-31 15:56 | ORIGINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2010-01-18 04:38 |  |  | 2010 | 1700 ROUTE 27 | EDISON | MIDDLESEX | NJ | 08817 | 40.5111 | -74.4081 | [9 empty] | 2010-01-18 05:58 | 928871 |  | NATURAL GAS |  | 3682 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 30 | 2010-01-18 04:38 | [5 empty] | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1959 | [5 empty] | 16 | ANSI/AWWA | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 50.2 | 0.3 |  | CLASS 4 LOCATION | 425500 | 562132.090172449445 | 2390 | 3157.4516933305621 | 44966 | 59405.00955744855874 |  | 0 |  |  | 33675 | 23267.3543689320388349514563106796116505 |  | 0 | 506531 | 280253.4128150096291443883495145631067961 | 647961.9057921606046749514563106796116505 | 0 | 0 | 1 |  |  |  |  | 32 | 32 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 8 | 0 | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [56 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | OTHER |  |  |  | UNKNOWN | NO | [218 empty] | CHRIS LAROSA | REGULATORY ANALYST | christopher.larossa@pseg.com | 9734307986 | 9736241937 |  |  |  | MICHAEL SCHMID | SOUTHERN DIVISION MANAGER | 6092392470 | michael.schmid@pseg.com | AT APPROXIMATELY 3:05AM PUBLIC SERVICE ELECTRIC AND GAS (PSE&G) RECEIVED A CALL FROM EDISON FIRE DEPARTMENT REPORTING A WIDESPREAD GAS ODOR ON ROUTE 27 EDISON. A PSE&G SERVICE TECHNICIAN WAS DISPATCHED AND ARRIVED ON THE SCENE AT 3:20AM TO DISCOVER THE WIDESPREAD GAS ODOR COMING FROM A CRACK IN THE ROAD IN FRONT OF 1700 ROUTE 27. AT 3:45AM THE ELECTRIC METER WAS PULLED TO 1700 ROUTE 27 EDISON AND BUILDING EVACUATIONS WERE INITIATED IN THE VICINITY OF THE GAS LEAK, WITH ASSISTANCE FROM EDISON FIRE DEPARTMENT. A PSE&G CREW MEMBER BEGAN VENTING OVER THE MAIN AT APPROXIMATELY 3:50AM TO RELIEVE THE GAS BUILD-UP WHICH WAS NOW BUCKLING THE ROADWAY. AT APPROXIMATLEY 4:38AM THE STRUCTURE AT 1700 ROUTE 27 EXPLODED. THE SOURCE OF THE GAS LEAK WAS DETERMINED TO BE A CIRCUMFERENTIAL CRACK IN THE 16" CAST IRON GAS MAIN ON ROUTE 27. PERMANENT REPAIRS WERE COMPLETE AT 1:05PM JANUARY 18 2010. THERE WERE NO INJURIES TO ANY PSE&G EMPLOYEES THE PUBLIC OR EMERGENCY PERSONNEL. AS A RESULT OF THE INCIDENT A TOTAL OF TWELVE HOMES WERE EVACUATED OF THIRTY PEOPLE AND SIX COMMERCIAL BUILDINGS THAT WERE CLOSED FOR THE NIGHT WERE FORCED TO REMAIN CLOSED THROUGHOUT THE REPAIR. *QUESTION 17B WAS LEFT BLANK BECAUSE OF SYSTEMS INABILITY TO INPUT DATE AND GREATER THAN THE OPERATOR IDENTIFIED DATE AND TIME. AS THE DESCRIPTION ABOVE INDICATES THE INCIDENT DID OCCUR AFTER PSE&G PERSONNEL ARRIVED AT THE LOCATION.
2025-03-31 10:13 | NO | YES | YES | 20100013 | 15189 | 2010-03-31 16:04 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2010-01-12 20:53 |  |  | 2010 | 708 ELMA AVE | ELGIN | COOK | IL | 60120 | 42.0614 | -88.263 | [9 empty] | 2010-01-12 21:56 | 928418 |  | NATURAL GAS |  | 160 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 5 | 5 | YES |  |  |  |  | YES |  | 2010-01-12 20:53 |  |  |  | 2010-01-12 20:53 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1959 | [5 empty] | 2.375 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 350000 | 462388.3232910865 | 6300 | 8322.989819239557 | 3800 | 5020.216081446082 | 0 | 0 |  |  | 1100 | 760.032362459546925566343042071197411003 |  | 0 | 361200 | 197736.8059940144133288025889967637540453 | 476491.561554231685925566343042071197411 | 0 | 0 | 6 |  |  |  |  | 25 | 25 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [11 empty] | YES |  |  |  | NO | [86 empty] | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | lquezad@nicor.com | 630-388-2316 |  |  |  |  | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | 630-388-2316 | lquezad@nicor.com | NATURAL GAS FROM CRACKED STEEL MAIN MIGRATED INTO RESIDENTIAL STRUCTURE RESULTING IN AN EXPLOSION
2025-03-31 10:13 | YES | NO | NO | 20100014 | 33345 | 2010-04-02 11:08 | SUPPLEMENTAL | 17360 | RICHMOND, CITY OF | 730 E BROAD STREET 6TH FLOOR | RICHMOND | VA | 23219 | 2010-02-05 11:58 |  |  | 2010 | 3601 ECHOWAY RD | RICHMOND | CHESTERFIELD | VA | 23237 | 37.4418 | -77.466 | [9 empty] | 2010-02-05 13:45 | 930600 |  | NATURAL GAS |  | 6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-02-05 11:58 |  |  |  | 2010-02-05 12:19 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1989 | [8 empty] | OTHER | METER SET | [9 empty] | RUPTURE |  |  |  |  | OTHER | BURN HOLE | 1 | 1 |  | CLASS 4 LOCATION | 0 | 0 | 126 | 166.45979638479114 | 2229 | 2944.75306461666231 | 0 | 0 |  |  | 29 | 20.03721682847896440129449838187702265372 |  | 0 | 2384 | 1307.106656257964288122977346278317152104 | 3131.250077829932414401294498381877022654 | 0 | 0 | 1 |  |  |  |  | 23 | 23 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | SANG YI | PRINCIPAL ENGINEER | sang.yi@richmondgasworks.com | 8046468052 |  |  |  |  | SANG YI | PRINCIPAL ENGINEER | 8046468052 | sang.yi@richmondgasworks.com | CALL CENTER RECEIVED A CALL AROUND 11:58 AM ON FEBRUARY 5TH 2010 FROM FIRE OR POLICE DEPARTMENT. OUR TECHNICIAN WAS IMMEDIATELY DISPATCHED AND ARRIVED AT THE SCENE ON 12:19 PM. UPON ARRIVAL, TECHNICIAN CLOSED THE CURB VALVE TO MAKE SAFE. THE FIRE DEPARTMENT DETERMINED THAT NATURAL GAS WAS NOT THE INITIATING SOURCE OF THE FIRE EVENT. THE GAS METER WAS MELTED DUE TO FIRE CAUSED BY UNKNOWN SOURCE.
2025-03-31 10:13 | NO | NO | NO | 20100015 | 15287 | 2010-04-05 13:29 | SUPPLEMENTAL FINAL | 11768 | LOS ALAMOS COUNTY UTILITIES | 1000 CENTRAL AVENUE SUITE 130 | LOS ALAMOS | NM | 87544 | 2010-03-25 15:38 |  |  | 2010 | 4600 ESPERANZA | LOS ALAMOS | LOS ALAMOS | NM | 87544 | 35.5327 | -106.1931 | [9 empty] | 2010-03-26 10:00 | 935196 |  | NATURAL GAS |  | 15000 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 50 | 2010-03-25 15:38 |  |  |  | 2010-03-25 15:47 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | 1999 | [8 empty] | STEEL |  | SEAMLESS | SEAMLESS | 0.113 | [6 empty] | OTHER | [8 empty] | METER SET STRUCK BY AN AUTOMOBILE. | CLASS 3 LOCATION | 0 | 0 | 2500 | 3302.773737793475 | 600 | 792.665697070434 | 0 | 0 |  |  | 450 | 310.922330097087378640776699029126213592 |  | 0 | 3550 | 1983.829545385778370873786407766990291262 | 4406.361764960996378640776699029126213592 | 2 | 0 | 0 |  |  |  |  | 20 | 20 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | PHILLIP VALDEZ | GAS WATER SEWER SUPERINTENDENT | phillip.valdez@lacnm.us | 505-662-8149 | 505-662-8005 |  |  |  | JOHN ARROWSMITH | UTILITIES MANAGER | 505-662-8272 | john.arrowsmith@lacnm.us | MR. PHILLIP VALDEZ, GAS, WATER, AND SEWER SUPERINTENDENT WAS NOTIFIED BY TELEPHONE AT 15:38 THAT THERE WAS A FIRE AT THE QUEMAZON SUBDIVISION MONTESSORI SCHOOL LOCATED AT 4600 ESPERANZA ST. IN LOS ALAMOS NEW MEXICO. AFTER ARRIVING ON THE SCENE AT 4600 ESPERANZA ST. MR. VALDEZ FOUND THAT A VEHICLE HAD LEFT THE ROADWAY, STRUCK A GAS METER AND BROKE OFF THE RISER, AND CONTINUED INTO THE SIDE OF THE BUILDING. THE BUILDING AND THE VEHICLE WERE ON FIRE. THE DRIVER OF THE VEHICLE AND ITS OTHER OCCUPANTS AND THE OCCUPANTS OF THE BUILDING WERE EVACUATED WITH NO INJURIES BEING REPORTED. THE LOS ALAMOS COUNTY FIRE DEPARTMENT RESPONDED TO THE FIRE AND AND PUT OUT THE BLAZING VEHICLE AND BUILDING BUT FLAMES CONTINUED TO COME FROM THE RISER WHICH HAD THE VEHICLE ATOP OF IT. THE FIRE DEPARTMENT CALLED IN A TOW TRUCK WHICH REMOVED THE VEHICLE FROM THE BUILDING AND FROM ATOP OF THE RISER, AT WHICH TIME THEY EXTINGUISHED THE FLAMES COMING FROM THE RISER. A LOS ALAMOS COUNTY GAS TECHNICIAN PLACED A CLIMAX PLUG INTO THE RISER AND SHUT OF THE FLOW OF GAS. THE AREA WAS BAR TESTED WITH A CGI TESTER AND A FLAME IONIZATION UNIT TO TEST FOR ANY POSSIBLE GAS LEAKAGE. NO LEAKS WERE DETECTED AND THE SERVICE LINE WAS THEN SQUEEZED OFF AND CAPPED TEN (10) FEET FROM THE RISER. GAS TECHNICIANS CHECKED THE AREA THE FOLLOWING DAY FOR LEAKS AND NONE WERE DETECTED.
2025-03-31 10:13 | NO | YES | NO | 20100017 | 15017 | 2010-04-08 12:43 | ORIGINAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 800 LASALLE AVENUE | MINNEAPOLIS | MN | 55402 | 2010-02-23 12:35 |  |  | 2010 | WEST 50TH & ARDEN AV | EDINA | HENNEPIN | MN | 55425 | 44.9128 | -93.3362 | [9 empty] | 2010-02-23 16:29 | 932124 |  | NATURAL GAS |  | 1395 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 60 | 2010-02-23 12:35 |  |  |  | 2010-02-23 12:52 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1986 | [5 empty] | 3.5 | ASTM02513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 6 | 7.3 | [7 empty] | CLASS 3 LOCATION | 218900 | 289190.868481196671 | 13734 | 18144.11780594223426 | 67658 | 89383.62622065237262 | 25350 | 33490.1257012258365 | OVERSIGHT, SUPPORT, REGULATORY RESPONSE |  | 8215 | 5676.059870550161812297734627831715210356 |  | 0 | 333857 | 183430.2445275303610362847896440129449838 | 435884.7980795672761922977346278317152104 | 0 | 0 | 10 |  |  |  |  | 7 | 10 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 10001968 | NOT APPLICABLE |  | CONTRACT LOCATOR | YES | YES | 9 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | KRIS TANDE | DAMAGE PREVENTION SUPERVISOR | kristine.tande@centerpointenergy.com | 6128618692 | 6128618565 |  |  |  | KRIS TANDE | DAMAGE PREVENTION SUPERVISOR | 6128618692 | kristine.tande@centerpointenergy.com | GAS TRAVELED FROM A DAMAGED 3" POLY MAIN TO 5000 ARDEN AVE IN EDINA MINNESOTA WHERE AN EXPLOSION AND FIRE OCCURRED. A THIRD PARTY DAMAGED THE CENTERPOINT ENERGY MAIN DURING A DIRECTIONAL BORING PROCESS TO INSTALL TELECOMMUNICATIONS.
2025-03-31 10:13 | YES | NO | NO | 20100018 | 15018 | 2010-04-13 14:06 | ORIGINAL FINAL | 4483 | ENSTAR NATURAL GAS CO | 3000 SPENARD ROAD | ANCHORAGE | AK | 99503 | 2010-04-06 13:45 |  |  | 2010 | 16789 W. HELMS DR | BIG LAKE | MATANUSKA SUSITNA BOROUGH | AK | 99652 | 61.534 | -149.873 | [9 empty] | 2010-04-06 18:50 | 936342 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2010-04-06 13:45 |  |  |  | 2010-04-06 14:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2009 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 3408 | LEAK |  |  | OTHER | BURN HOLE | [5 empty] | CLASS 3 LOCATION | 100000 | 132110.949511739 | 1000 | 1321.10949511739 |  | 0 |  | 0 |  |  | 10 | 6.90938511326860841423948220064724919094 |  | 0 | 101010 | 55269.9486187960717993527508090614886731 | 133438.9683919696586084142394822006472492 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | DAVID W. BREDIN | DIRECTOR OF OPERATIONS | dave.bredin@enstarnaturalgas.com | 907-264-3745 | 907-562-0053 |  |  |  | DAVID W. BREDIN | DIRECTOR OF OPERATIONS | 907-264-3745 | dave.bredin@enstarnaturalgas.com | THIS IS A "FIRE FIRST" INCIDENT. A FIRE STARTED INSIDE THE SHOP/GARAGE. THE 1/2" CTS POLYETHYLENE SERVICE LINE MELTED INSIDE THE STEEL RISER RELEASING NATURAL GAS. THE REGULATOR AND METER WERE BURNED IN THE FIRE. THE STRUCTURE WAS A TOTAL LOSS. NATURAL GAS IS NOT BELIEVED TO HAVE CAUSED OR CONTRIBUTED TO THE FIRE.
2025-03-31 10:13 | NO | YES | YES | 20100020 | 15185 | 2010-05-04 11:26 | SUPPLEMENTAL FINAL | 2364 | DUKE ENERGY OHIO | 139 EAST FOURTH ST | CINCINNATI | OH | 45202 | 2010-04-05 16:08 |  |  | 2010 | 4044 ASHWOOD COURT | WITHAMSVILLE | CLERMONT | OH | 45245 | 39.0669 | -84.2763 | [9 empty] | 2010-04-05 18:17 | 936190 |  | NATURAL GAS |  | 4 |  | YES | 0 | 1 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-04-05 16:09 |  |  |  | 2010-04-05 16:25 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | OTHER | NATURAL GAS DISTRIBUTION, PUBLICLY TRADE | SERVICE RISER |  | 1997 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | OTHER | [8 empty] | CONTRACTOR CUT SERVICE AT BASE OF EXISTING SERVICE RISER IN ORDER TO INSTALL NEW SERVICE RISER. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 24 | 16.58252427184466019417475728155339805825 |  | 0 | 24 | 15.33980582524271844660194174757281553398 | 16.58252427184466019417475728155339805825 | 0 | 0 | 1 |  |  |  |  | 14 | 14 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM NOTIFIED BY DISPATCH (WILLLIAM HUNTER) - ALSO RECEIVED CALLS FROM GAS OPERATING PERSONNEL (SUE GILB, JIM CALLAHAN) | [12 empty] | NO |  |  | YES | 1 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | CONTRACTOR PERFORMING TASK DID NOT FOLLOW OPERATING PROCEDURE FOR "SQUEEZING-OFF" THE PE TUBING TO STOP THE FLOW OF GAS PRIOR TO PERFORMING TASK. |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | JAMES T CALLAHAN | LEAD REGULATORY COMPLIANCE SPECIALIST - GAS OPS | jim.callahan@duke-energy.com | 513-287-2824 | 513-651-5229 |  |  |  | JAMES E MEHRING | VP GAS OPERATIONS | 513-287-2535 | jim.mehring@duke-energy.com | RLA INVESTMENTS, INC. IS PERFORMING MAINTENANCE ACTIVITIES IN VARIOUS LOCATIONS OF DUKE ENERGY OHIO'S SERVICE TERRITORY PURSUANT TO A CONTRACT WITH DUKE ENERGY OHIO. THE MAINTENANCE ACTIVITIES INVOLVE THE REPLACEMENT OF NATURAL GAS SERVICE RISERS IN CONNECTION WITH DUKE ENERGY OHIO'S RISER REPLACEMENT PROGRAM. ON MONDAY, APRIL 5, 2010, AT APPROXIMATELY 4:08PM, CODY FAUL, AN EMPLOYEE OF RLA INVESTMENTS, WAS PERFORMING MAINTENANCE ACTIVITIES AT 4044 ASHWOOD CT., WITHAMSVILLE, OH IN CLERMONT COUNTY. MR. FAUL, A MEMBER OF A TWO-MAN RISER CREW, WAS WORKING ALONE AT THE TIME OF THE ACCIDENT. IT IS BELIEVED THAT MR. FAUL WAS PERFORMING A FULL GAS SERVICE RISER REPLACEMENT BY CONNECTING THE EXISTING GAS SERVICE PIPE TO THE NEW RISER USING A STAB CONNECTION FITTING PRIOR TO BEING DISCOVERED UNRESPONSIVE. MR. FAUL WAS TRANSPORTED TO A LOCAL HOSPITAL AND PRONOUNCED DEAD ON ARRIVAL. THIS INCIDENT IS CURRENTLY UNDER INVESTIGATION. NOTE: IT IS OUR UNDERSTANDING THAT ONLY A DRUG TEST WAS ADMINISTERED ON THE CREW LEADER (DAVID SMITH), NOT AN ALCOHOL TEST. AS OF 6-2-10, INCIDENT IS STILL UNDER INVESTIGATION, WAITING ON ACTUAL CAUSE OF DEATH REPORT FROM CORONER AND TOXICOLOGY REPORT. AS OF 6-30-10, THE DEATH OF CODY FAUL WAS RULED ACCIDENTAL AND THAT THE CAUSE OF DEATH WAS ASPHYXIATION (DUE TO METHANE GAS EXPOSURE). ALSO, ACCORDING TO THE TOXICOLOGY REPORT, NO DRUGS WERE FOUND IN HIS SYSTEM.
2025-03-31 10:13 | NO | YES | NO | 20100021 | 15024 | 2010-05-07 14:38 | ORIGINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2010-04-09 13:30 |  |  | 2010 | 64 RUTGERS PLACE | CLIFTON CITY | PASSAIC COUNTY | NJ | 07013 | 40.8796 | -74.1748 | [9 empty] | 2010-04-09 14:35 | 936612 |  | NATURAL GAS |  | 530 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 3 | 2010-04-09 13:30 | [5 empty] | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1959 | [5 empty] | 1 | ASTM A53 |  | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | LEAK |  |  | OTHER | DAMAGE SEVERED SERVICE | [5 empty] | CLASS 4 LOCATION | 345000 | 455782.77581549955 | 0 | 0 | 6500 | 8587.211718263035 | 0 | 0 |  |  | 7340 | 5071.488673139158576051779935275080906149 |  | 0 | 358840 | 197019.5457018041957249190938511326860841 | 469441.4762069017435760517799352750809061 | 0 | 0 | 0 |  |  |  |  | 13.3 | 13.5 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 12 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | UNKNOWN/OTHER | YES | 100961298 | NEW JERSEY ONE CALL |  | UTILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | CHRIS LAROSSA |  | christopher.larossa@pseg.com | [5 empty] | JORGE CARDENAS |  |  | No Email Address | AT APPROXIMATELY 12:42 PM, PUBLIC SERVICE ELECTRIC AND GAS (PSE&G) RECEIVED A CALL FROM CASTLETON ENVIRONMENTAL OF A DAMAGED SERVICE AND GAS LEAK AT 64 RUTGERS PLACE, CLIFTON. A PSE&G SERVICE TECHNICIAN WAS DISPATCHED, AND ARRIVED ON THE SCENE AT 1:07 PM, AND COMMENCES A LEAK INVESTIGATION. AT APPROXIMATELY 1:30 PM THE STRUCTURE AT 64 RUTGERS PLACE EXPLODED. THE SOURCE OF THE GAS LEAK WAS DETERMINED TO BE A SEPARATION OF THE SERVICE LINE AT THE HEAD OF THE SERVICE JUST INSIDE THE FOUNDATION WALL.
2025-03-31 10:13 | NO | NO | NO | 20100022 | 15025 | 2010-05-10 16:38 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-01-09 16:27 |  |  | 2010 | HEMLOCK ST & O ST | EUREKA | HUMBOLDT | CA | 95501 | 40.7732 | -124.1528 | [9 empty] | 2010-01-09 23:35 | 928133 |  | NATURAL GAS |  | 102 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 16 | 2010-01-09 19:45 |  |  |  | 2010-01-09 20:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN | [7 empty] | 1 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION |  | 0 | 500 | 660.554747558695 | 2000 | 2642.21899023478 |  | 0 |  |  |  | 0 |  | 0 | 2500 | 1367.909827550385 | 3302.773737793475 | 0 | 0 | 2 |  |  |  |  | 45 | 45 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [56 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | EARTHQUAKE |  |  |  |  | NO | [218 empty] | LAURENCE DENISTON | PROGRAM MANAGER | lcd1@pge.com | 9259744313 |  |  |  |  | LAURENCE DENISTON | PROGRAM MANAGER | 9259744313 | lcd1@pge.com | ON 1/19/10 AT APPROXIMATELY 1627 HOURS A 6.5 MAGNITUDE EARTHQUAKE STRUCK THE EUREKA AREA. AT APPROXIMATLEY 1945 HOURS PG&E WAS NOTIFIED OF A GAS LEAK ON A 0.75-INCH STEEL SERVICE IN THE INTERSECTION OG HEMLOCK AND 0 STREETS. THE LEAK APPEARS TO HAVE BEEN CAUSED BY THE EARTHQUAKE. THE EUREKA POLICE AND FIRE DEPARTMENTS WERE ON SCENE AND BLOCKED OFF THE AREA. THE FIRE DEPARTMENT EVACUATED 16 HOMES AS A PRECAUTION. PG&E CREWS WERE ON SCENE AT 2030 HOURS. PROPERTY DAMAGES WERE LESS THAN $50,000. THERE WERE NO FATALITIES OR INJURIES AS A RESULT OF THIS INCIDENT. THIS INCIDENT BECAME REPORTABLE WHEN DOT OFFICE OF PIPELINE SAFETY BECAME AWARE OF THIS INCIDENT DUE TO NEWS COVERAGE.
2025-03-31 10:13 | NO | NO | NO | 20100023 | 15026 | 2010-05-10 16:58 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-02-07 16:27 |  |  | 2010 | 3944 17TH AVENUE | SACRAMENTO | SACRAMENTO | CA | 94203 | 38.5373 | -121.4608 | [9 empty] | 2010-02-07 23:35 | 930696 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-02-07 02:08 |  |  |  | 2010-02-07 02:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUM METER | [9 empty] | OTHER | [8 empty] | ARSON & SECONDARY IGNITION | CLASS 3 LOCATION |  | 0 | 1000 | 1321.10949511739 | 2000 | 2642.21899023478 |  | 0 |  |  |  | 0 |  | 0 | 3000 | 1641.491793060462 | 3963.32848535217 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 0.75 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [156 empty] | LAURENCE DENISTON | PROGRAM MANAGER | lcd1@pge.com | 9259744313 | 9259741412 |  |  |  | BRIAN DAUBIN |  |  | No Email Address | A HOUSE EXPLOSION AND FIRE OCCURRED AT APPROXIMATELY 0208 HOURS ON 2/7/10. THE FIRE DEPARTMENT CALLED AT PG&E AT 0213 HOURS. PG&E PERSONNEL ARRIVED AT 0245 HOURS. THE FIRE DEPARTMENT HAD SHUT OFF THE SERVICE VALVE AND REMOVED THE METER BEFORE PG&E ARRIVED. THE HOUSE WAS UNOCCUPIED AT THE TIME OF THE EXPLOSION. THE GAS SERVICE ACCOUNT WAS ACTIVE AND THE GAS SERVICE WAS ON (CONTRARY TO INITIAL REPORT). THE CAUSE OF THE EXPLOSION IS UNDETERMINED AT THE TIME OF THIS REPORT, BUT THE FIRE DEPARTMENT HAS INDICATED THE CAUSE APPEARS TO BE ARSON. AFTER THE EXPLOSION, PG&E PERFORMED A LEAK SURVEY OF THE SERVICE, THE SERVICES ON BOTH SIDES OF THIS ADDRESS, AND THE GAS MAIN IN THE FRONT OF ALL THREE OF THESE ADDRESSES. NO INDICATION OF GAS WAS FOUND. PG&E ALSO PERFORMED BAR HOLE TESTS OVER THE SERVICE AT 3944 17TH AVENUE AND FOUND NO INDICATION OF GAS. THE GAS SERVICE WAS CUT OFF AT THE MAIN, AND WILL BE RE-CONNECTED WHEN THE CUSTOMER IS READY FOR SERVICE.
2025-03-31 10:13 | NO | NO | NO | 20100024 | 15028 | 2010-05-12 10:56 | ORIGINAL FINAL | 4060 | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2010-01-25 14:30 |  |  | 2010 | 2022 WEST 83RD STREET | CLEVELAND | CUYAHOGA | OH | 44102-3803 | 41.4765 | -81.7421 | [9 empty] | 2010-01-25 21:31 | 792079 |  | NATURAL GAS |  | 6156 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 3 | 2010-01-25 15:19 |  |  |  | 2010-01-25 15:24 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1.25 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.191 | [6 empty] | OTHER | [8 empty] | VANDALISM/ARSON | CLASS 3 LOCATION |  | 0 |  | 0 | 10000 | 13211.0949511739 |  | 0 |  |  | 50 | 34.54692556634304207119741100323624595469 |  | 0 | 10050 | 5503.597239004128996763754045307443365696 | 13245.641876740243042071197411003236246 | 0 | 0 | 27 |  |  |  |  | 0.6 | 0.6 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [156 empty] | STEVEN W BUCK | TECHNICAL CONSULTANT | steven.w.buck@dom.com | 3304018033 | 8665214877 |  |  |  | STEVEN W BUCK | TECHNICAL CONSULTANT | 3304018033 | steven.w.buck@dom.com | ON MONDAY, JANUARY 25, 2010 AT APPROXIMATELY 2:30PM A SINGLE-FAMILY HOME AT 2022 WEST 63RD STREET, CLEVELAND, OH (CUYAHOGA COUNTY) WAS INVOLVED IN AN EXPLOSION/FIRE. THE GAS SERVICE LINE WAS SHUT-OFF AT APPROXIMATELY 4:30PM. A LEAK SURVEY OF THE MAIN LINES AND SERVICE LINES ON W. 83RD BETWEEN MADISON AND LORAIN REVEALED NO INDICATIONS OF GAS NEAR THE STRUCTURE. A SERVICE LEAK AT 2131 WEST 83RD STREET WAS DETECTED DURING THE LEAK SURVEY. THIS SERVICE LINE WAS REPLACED UPON DISCOVERY. ON TUESDAY, JANUARY 26TH, 2010 THE SERVICE LINE AT 2022 W. 83RD WAS AIR TESTED AT OPERATING PRESSURE WITH NO PRESSURE LOSS. AN ODOR TEST WAS CONDUCTED AT 2028 WAST 83RD STREET. THE RESULTS OF THIS ODOR TEST REVEALED ODOR LEVELS WELL WITHIN DOT COMPLIANCE LEVELS. OUR INVESTIGATION REVEALED AN ODOR COMPLAINT AT THIS RESIDENCE ON JANUARY 18TH. DOMINION PERSONNEL RESPONDED TO THE CALL AND MET WITH THE CLEVELAND FIRE DEPARTMENT. DOMINION FOUND THE METER DISCONNECTED AND THE METER SHUT-OFF VALVE IN THE HALF OPEN POSITION. THE SHUT-OFF VALVE WAS CLOSED BY THE DOMINION TECHNICIAN AND SECURED WITH A LOCKING DEVICE. THE TECHNICIAN PLACED A 3/4 INCH PLUG IN THE OPEN END OF THE VALVE. THE TECHNICIAN ALSO ATTEMPTED TO CLOSE THE CURB-SLOP VALVE, BUT COULD NOT. THE SERVICE LINE WAS THEN BAR HOLE TESTED UTILIZING A COMBUSTIBLE GAS INDICATOR FROM THE STREET TO THE STRUCTURE. AS A RESULT. NO LEAKAGE WAS DISCOVERED. A SECOND ATTEMPT TO CTOSE THE CURB BOX VALVE ON JANUARY 19TH ENDED WHEN BLOCKAGE WAS DISCOVERED IN THE VALVE BOX. THE VALVE BOX WAS IN THE PROCESS OF BEING SCHEDULED FOR EXCEVATLON AND SHUT OFF BY A CONSTRUCTION CREW AT THE TIME OF THE INCIDENT. AN INVESTIGATION OF THE INCIDENT SITE DETERMINED THE CAUSE TO BE ARSON AS APPROXIMATELY 6 INCHES OF SERVICE LINE AND THE METER SHUT-OFF VALVE (WITH LOCKING DEVICE STILL INTACT), DETACHED FROM THE SERVICE LINE, WERE RECOVERED INSIDE THE STRUCTURE.
2025-03-31 10:13 | NO | YES | NO | 20100025 | 15305 | 2010-05-12 12:28 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 800 LASALLE AVENUE | MINNEAPOLIS | MN | 55402 | 2010-04-13 04:45 |  |  | 2010 | 7433 GIRARD AVE NO. | BROOKLYN PARK | HENNEPIN | MN | 55444 | 45.0905 | -93.299 | [9 empty] | 2010-04-13 07:40 | 936887 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-04-13 04:52 |  |  |  | 2010-04-13 04:52 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1982 | [8 empty] | OTHER | COPPER RISER, AMERICAN 175 METER | [9 empty] | OTHER | [8 empty] | LIGHTENING STRICK ON SERVICE RISER & METER. | CLASS 3 LOCATION | 172500 | 227891.387907749775 | 300 | 396.332848535217 | 250 | 330.2773737793475 | 0 | 0 |  |  | 0 | 0 |  | 0 | 173050 | 94686.7182630376497 | 228617.9981300643395 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SINGLE METER ON A 5/8" SERVICE | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | CRYSTAL GORRES | SPECIALIST | crystal.gorres@centerpointenergy.com | 612-861-8689 |  |  |  |  | KRIS TANDE | SUPERVISOR LINE LOCATING AND DAMAGE PREVENTION | 612-861-8692 | kristine.tande@centerpointenergy.com | LIGHTENING STRUCK A TREE AND THE METER SET RESULTING IN A FIRE.
2025-03-31 10:13 | YES | NO | NO | 20100026 | 15199 | 2010-05-12 13:56 | SUPPLEMENTAL FINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 820 WEST BROADWAY, PO BOX 32030 | LOUISVILLE | KY | 40202 | 2010-04-12 16:20 |  |  | 2010 | 10220 SADDLE POINTE DRIVE | LOUISVILLE | JEFFERSON | KY | 40291 | 38.0964 | -85.5846 | [10 empty] | 936857 |  | NATURAL GAS |  | 16.95 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2010-04-12 17:07 |  |  |  | 2010-04-12 17:33 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1998 | [8 empty] | OTHER | ALUMINUM METER | [9 empty] | OTHER | [8 empty] | FALLING DEBRIS FROM ONGOING RESIDENTIAL STRUCTURE FIRE STRUCK THE METER AND REGULATOR, DAMAGING THE FACILITIES AND IGNITING NATURAL GAS. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 200 | 264.221899023478 | 0 | 0 |  |  | 95 | 65.63915857605177993527508090614886731392 |  | 0 | 295 | 170.152850928949893851132686084142394822 | 329.861057599529779935275080906148867314 | 0 | 0 | 1 |  |  |  |  | 60 | 52.47 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | JIM DIMAS | SR. CORPORATE ATTORNEY | jim.dimas@lge-ku.com | 5026273712 | 5026273367 |  |  |  | JIM DIMAS | SR. CORPORATE ATTORNEY | 5026273712 | jim.dimas@lge-ku.com
2025-03-31 10:13 | NO | YES | NO | 20100027 | 16154 | 2010-05-19 09:33 | SUPPLEMENTAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2010-04-19 10:58 |  |  | 2010 | OLD GEORGETOWN ROAD & GEORGETOWN FRANKLIN TURNPIKE | FRANKLIN TOWNSHIP | SOMERSET COUNTY | NJ | 07416 | 40.4145 | -74.594 | [9 empty] | 2010-04-19 13:40 | 937471 |  | NATURAL GAS |  | 3999.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-04-19 10:58 |  |  |  | 2010-04-19 11:41 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1994 | [5 empty] | 6 | ASTM D2513 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 4710 | MECHANICAL PUNCTURE | 5.6 | 17.7 | [7 empty] | CLASS 4 LOCATION | 145000 | 191560.87679202155 | 130 | 171.7442343652607 | 24366 | 32190.15395803032474 | 0 | 0 |  |  | 36664 | 25332.5695792880258899676375404530744337 |  | 0 | 206160 | 116176.2076845544819309255663430420711974 | 249255.3445637051613299676375404530744337 | 0 | 0 | 37 |  |  |  |  | 46 | 46 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 100771201 | NEW JERSEY ONE CALL |  | UTILITY OWNER | YES | YES | 24 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | CHRIS LAROSSA | REGULATORY ANALYST | christopher.larossa@pseg.com | [5 empty] | JORGE CARDENAS | VP ASSET MGMT CENTRALIZED SRVS. | 973-430-5100 | jorge.cardenas@pseg.com | ON APRIL 19, 2010, AT APPROXIMATELY 10:58AM A GAS DAMAGE WAS REPORTED IN THE VICINITY OF ROUTE 518 AND OLD GEORGETOWN ROAD IN FRANKLIN, NJ. A TRAP ROCK CONSTRUCTION CREW, WORKING FOR SOMERSET COUNTY UNDER MARKOUT REQUEST (100771201), WAS EXCAVATING USING MECHANIZED EQUIPMENT TO INSTALL NEW ROAD DRAINAGE PIPING. DURING THE EXCAVATION THE BACKHOE STRUCK A SIX INCH GAS MAIN, OPERATING AT 60PSI. THE BLOWING GAS SUBSEQUENTLY IGNITED, CAUSING DAMAGE TO THE BACKHOE, TWO DUMP TRUCKS, AND OVERHEAD ELECTRIC AND TELECOMMUNICATION FACILITIES. NO INJURIES OCCURRED AS A RESULT OF THE DAMAGE.
2025-03-31 10:13 | YES | NO | NO | 20100028 | 16690 | 2010-05-27 09:20 | SUPPLEMENTAL FINAL | 18408 | SOUTH CAROLINA ELECTRIC & GAS CO | 601 TAYLOR ROAD MAIL CODE J48 | CAYCE | SC | 29033 | 2010-05-11 12:05 |  |  | 2010 | 101 SPRING STREET | CHARLESTON | CHARLESTON | SC | 29403-5993 | 32.7908 | -79.9461 | [9 empty] | 2010-05-11 15:30 | 939868 |  | NATURAL GAS |  | 4.52 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-05-11 12:05 |  |  |  | 2010-05-11 12:17 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1968 | [5 empty] | 9.999 | HDPE 42 | YARDLEY | PLASTIC |  |  |  |  | UNKNOWN |  |  | 0.125 |  |  | OTHER | [8 empty] | THE SERVICEMAN DISCOVERED THE GAS SERVICE LINE FOR THE HOME AT THIS PROPERTY WAS DAMAGED BY AN EAST COAST PLUMBING WORKER WHILE SWEATING ON COPPER WATER LINE FITTINGS NEAR THE GAS SERVICE LINE USING A PROPANE TORCH. THE WALL THICKNESS OF THE DAMAGED PIPELINE IS 0.125 INCHES. THE FACILITY THAT HAD TO BE SHUT DOWN WAS THE GAS SERVICE LINE/METER SET. THE RESTART/RESTORATION OF THE FACILITY IS DEPENDENT ON REPAIRS TO THE CUSTOMER PROPERTY, AND AFTER THE CONTRACTOR REQUESTS A NEW SERVICE LINE | CLASS 3 LOCATION | 0 | 0 | 1847 | 2440.08923748181933 | 589 | 778.13349262414271 | 51600 | 68169.249948057324 | COST TO REPLACE THE SERVICE LINE ($1600) DAMAGE TO PRIVATE PROPERTY ($50,000) |  | 30 | 20.72815533980582524271844660194174757282 |  | 0 | 54066 | 29585.7249338865949420582524271844660194 | 71408.2008335030918652427184466019417476 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | CITY OF CHARLESTON FIRE DEPARTMENT |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | GUS CHAPMAN | MANAGER - DISTRIBUTION INTEGRITY | gchapman@scana.com | 803-217-9799 | 803-217-9799 |  |  |  | GUS CHAPMAN | MANAGER - DISTRIBUTION INTEGRITY | 803-217-9799 | gchapman@scana.com | ON MAY 11, 2010, AT APPROXIMATELY 12:05PM SCE&G RECEIVED NOTIFICATION THAT THE GAS SERVICE LINE FOR 101 SPRING STREET WAS DAMAGED AND ON FIRE. THE ORDER WAS DISPATCHED TO OUR SERVICEMAN AT 12:12PM AND HE ARRIVED AT 12:17PM. THE SERVICEMAN DISCOVERED THE GAS SERVICE LINE FOR THE HOME AT THIS PROPERTY WAS DAMAGED BY AN EAST COAST PLUMBING WORKER WHILE SWEATING ON COPPER WATER LINE FITTINGS NEAR THE GAS SERVICE LINE USING A PROPANE TORCH. THE PLASTIC SERVICE LINE WAS DAMAGED BY HEAT FROM THE PROPANE TORCH BEING USED BY THE PLUMBER. ALSO, THE ESCAPING GAS WAS SUBSEQUENTLY IGNITED BY AN UNDETERMINED SOURCE. THE WORKER WAS NOT INJURED AND NOT TREATED BY EMERGENCY PERSONNEL. THE FIRE DEPARTMENT ARRIVED AND CONTROLLED THE FIRE WITH WATER HOSES WHILE SCE&G EXCAVATED THE SERVICE TAPPING TEE. THE LEAK WAS SECURED BY RUNNING THE TAPPING TEE DOWN AT 1:56PM. BECAUSE DAMAGE TO THE STRUCTURE WILL LIKELY EXCEED $50,000, CEDRIC GREEN (SCE&G) NOTIFIED VERNON GAINEY OF SOUTH CAROLINA OFFICE OF REGULATORY STAFF AT 3:15PM AND THE DEPARTMENT OF TRANSPORTATION NATIONAL RESPONSE CENTER AT 3:30PM. EAST COAST PLUMBING COMPANY DID NOT HAVE A VALID LOCATE TICKET FOR THE WORK THEY WERE PERFORMING. IN ADDITION, THE SERVICE LINE FOR 101 SPRING STREET WAS LEAK SURVEYED ON MARCH 31, 2010; THE LEAK SURVEY TECHNICIAN DID NOT FIND A LEAK. SCE&G HAS NO RECORD OF PERFORMING SERVICE RELATED WORK INSIDE THE HOME FROM 2006 TO PRESENT. NOTE: THIS FORM (PART C; 3.A) WOULD NOT ACCEPT THE NOMINAL PIPE DIAMETER. THE NOMINAL PIPE DIAMETER IS 0.5 INCHES.
2025-03-31 10:13 | NO | YES | YES | 20100029 | 15034 | 2010-05-28 08:27 | ORIGINAL FINAL | 15462 | PECO ENERGY CO | 2301 MARKET STREET, S9-1 | PHILADELPHIA | PA | 19103 | 2010-04-26 11:30 |  |  | 2010 | 7 WOODHILL ROAD | NEWTOWN SQUARE | DELAWARE | PA | 19073 | 39.9916 | -75.38 | [9 empty] | 2010-04-28 08:45 | 938416 |  | NATURAL GAS |  | 27.41 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | NO |  |  |  |  | NO | 0 | 2010-04-26 11:42 |  |  |  | 2010-04-26 12:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1989 | [5 empty] | 0.5 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.625 |  | 2406 | LEAK |  |  | OTHER | STRUCK SERVICE PIPE | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 3440 | 4544.6166632038216 | 910 | 1202.2096405568249 | 0 | 0 |  |  | 120 | 82.91262135922330097087378640776699029126 |  | 0 | 4470 | 2456.86212906388349223300970873786407767 | 5829.738925119869800970873786407766990291 | 0 | 0 | 1 |  |  |  |  | 58 | 60 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, AS THIS WAS THIRD PARTY DAMAGE TO A SERVICE LINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 2010270175 | PA ONE-CALL |  | CONTRACT LOCATOR | YES | YES | 7 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | WILLIAM H CLARK JR. | GAS MANAGER CONSTRUCTION AND MAINTENANCE | william.clark@peco-energy.com | 610-941-1740 | 610-941-1507 |  |  |  | WILLIAM H CLARK JR. | GAS MANAGER CONSTRUCTION AND MAINTENANCE | 610-941-1740 | william.clark@peco-energy.com | AQUA AMERICA'S CONTRACT CREW, DANELLA, STRUCK A GAS SERVICE ON APRIL 26, 2010 WHEN INSTALLING A WATER SERVICE LINE. THE CREW DAMAGED THE GAS SERVICE WHEN IT DUG UP THE GROUND FOR INSTALLATION PURPOSES. AT 11:30AM, DANELLA'S CONTRACT FOREMAN LEADING THE CONTRACT CREW, DECIDED TO ATTEMPT TO STEM THE FLOW OF GAS. THE FOREMAN, WHO LACKED THE REQUISITE TRAINING TO PERFORM SUCH A TASK, DID SO WITHOUT PECO'S KNOWLEDGE OR AUTHORIZATION AND WITHOUT THE PROPER EQUIPMENT. ACCORDING TO THE DANELLA CREW, THE CONTRACT FOREMAN BECAME EXPOSED TO GAS AND TEMPORARILY LOST CONSCIOUSNESS. HE REGAINED CONSCIOUSNESS AND WAS TAKEN TO THE HOSPITAL AS A PRECAUTION. AT 12:15 AM, A PECO CREW ARRIVED TO REPAIR THE DAMAGED FACILITY AND THE CONTRACT FOREMAN HAD ALREADY LEFT THE SITE. ALTHOUGH THE CONTRACT FOREMAN STAYED OVERNIGHT IN THE HOSPITAL FOR MONITORING, PECO WAS NOT NOTIFIED OF THE HOSPITALIZATION UNTIL THE NEXT DAY, APRIL 27, 2010. PECO NOTIFIED THE PENNSYLVANIA PUBLIC UTILITY COMMISSION, GAS SAFETY DIVISION, OF THE HOSPITALIZATION WITHIN TWO HOURS AFTER IT BECAME AWARE OF THE HOSPITALIZATION.
2025-03-31 10:13 | YES | NO | NO | 20100030 | 15087 | 2010-05-29 16:10 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1100 H STREET, NW | WASHINGTON | DC | 20080 | 2010-04-29 17:43 |  |  | 2010 | 8738 OXWELL LANE | LAUREL | PRINCE GEORGE'S | MD | 20708 | 39.0643 | -76.8589 | [9 empty] | 2010-04-29 19:54 | 938593 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2010-04-29 17:43 |  |  |  | 2010-04-29 18:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2004 | [8 empty] | OTHER | CAST ALUMINUM | [9 empty] | OTHER | [8 empty] | OUTSIDE METER BUILD-UP CONSUMED BY FIRE. | CLASS 3 LOCATION |  | 0 |  | 0 | 8200 | 10833.097859962598 | 400000 | 528443.798046956 | APPROXIMATE VALUE OF DAMAGES TO THE BUILDING CAUSED BY THE FIRE. |  | 5 | 3.45469255663430420711974110032362459547 |  | 0 | 408205 | 223355.5124353071216996763754045307443366 | 539280.3505994752323042071197411003236246 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MICHAEL UPSHAW | SUPERVISOR - DOT PIPELINE SAFETY COMPLIANCE | mupshaw@washgas.com | 703-750-4479 | 703-750-5591 |  |  |  | DAVID W. SPANGLER | MANAGER - DOT PIPELINE SAFETY COMPLIANCE | 703-750-4341 | dspangler@washgas.com | WASHINGTON GAS RESPONDED TO THE SCENE OF A HOUSE FIRE AT 8738 OXWELL LANE IN LAUREL, MD ON 4/29/10 AT THE REQUEST OF THE PRINCE GEORGE'S FIRE BOARD. UPON ARRIVAL, THE METER VALVE WAS FOUND TO HAVE BEEN TURNED OFF BY THE FIRE DEPARTMENT. THE METER BUILD-UP WAS CONSUMED BY THE FIRE. THE RISER WAS CAPPED OFF. A GAS MIGRATION SURVEY WAS CONDUCTED AROUND THE PERIMETER OF THE HOUSE AND OVER THE SERVICE LINE TO THE MAIN. NO INDICATIONS WERE FOUND. ON 4/30/10, WASHINGTON GAS RETURNED TO THE SITE TO EXCAVATE THE SERVICE LINE IN THE YARD, CAP IT OFF, AND PERFORM A PRESSURE TEST ON IT. APPROXIMATELY 40 FEET OF SERVICE LINE WAS TESTED WITH NO LEAKS FOUND. THIS PORTION OF THE SERVICE LINE WAS ABANDONED IN PLACE AFTER THE PRESSURE TEST. WASHINGTON GAS BELIEVES THE FIRE STARTED ELSEWHERE IN THE HOUSE AND CONSEQUENTLY CONSUMED ITS FACILITIES.
2025-03-31 10:13 | NO | YES | YES | 20100031 | 15263 | 2010-06-04 19:45 | SUPPLEMENTAL FINAL | 31632 | NORTHWESTERN ENERGY LLC | 3010 W. 69TH ST. | SIOUX FALLS | SD | 57108 | 2010-05-06 13:52 |  |  | 2010 | 1206 2ND AVE WEST | COLUMBIA FALLS |  | MT | 59912 | 48.3679 | -114.1839 | [9 empty] | 2010-05-06 17:00 | 939397 |  | NATURAL GAS |  | 13 |  | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2010-05-06 13:52 |  |  |  | 2010-05-06 14:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1962 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | OTHER | [8 empty] | A BACKHOE STRUCK THE 3/4" SERVICE LINE. SERVICE LINE SEPERATED FROM THE MAIN AT THE SERVICE TEE, WHICH WAS UPSTREAM OF THE STRIKE. | CLASS 3 LOCATION | 200000 | 264221.899023478 | 2500 | 3302.773737793475 | 5000 | 6605.54747558695 | 0 | 0 |  |  | 100 | 69.09385113268608414239482200647249190939 |  | 0 | 207600 | 113600.4315442871329935275080906148867314 | 274199.3140879911110841423948220064724919 | 0 | 0 | 11 |  |  |  |  | 30 | 30 | 32 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM PRESSURE REMAINED STABLE AND WAS NOT AN ISSUE IN THE INCIDENT. | [12 empty] | YES | 3 | 0 | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | STREET LIGHT | YES | 2010180256 | MONTANA ONE CALL CENTER |  | CONTRACT LOCATOR | YES | YES |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | KEITH MEAGOR | DOT COORDINATOR | keith.meagor@northwestern.com | 4064972214 | 4064972048 |  |  |  | KEITH MEAGOR | DOT COORDINATOR | 4064972214 | keith.meagor@northwestern.com | **** 6/10/11 **** FINAL REPORT - ON MAY 27 AND MAY 28, 2010 THE INVESTIGATION FOR THIS INCIDENT WAS CONCLUDED. THE INVESTIGATION DETERMINED THAT GAS MIGRATED FROM THE DAMAGED SERVICE LINE TO MAIN CONNECTION. THE GAS MIGRATED THROUGH THE SOIL ALONG THE SEWER LINE TO THE FOUNDATION OF THE HOUSE. INVESTIGATION OF THE SERVICE LINE TO MAIN CONNECTION VERIFIED THAT THE EXCAVATOR STRUCK THE SERVICE LINE AND TORE THE SERVICE LINE OFF THE SERVICE AT THE WELD. NWE CONSIDERS THIS INCIDENT CLOSED WITH NO FURTHER INVESTIGATION REQUIRED. ADDITIONALLY - ON THE FORM COULD NOT ACCESS SECTION G3 - 13A. FOR THIS SECTION THE SERVICE LINE WAS REMOVED FROM SERVICE AND WILL NOT REINSTATED. **** 06/29/10 WORKED WITH DOT TO GET THE REPORT CORRECTED FROM 06/04/10. AFTER SOME CORRECTIONS THE FORM IS WORKING AND THIS SUPPLEMENTAL IS TO SHOW THOSE CORRECTIONS. THE SERVICE LINE THAT WAS DAMAGED WAS REMOVED FROM SERVICE, WHICH IS SHOWN IN PART A UNDER 13B AS "STILL SHUT DOWN". THERE IS NO NEW ADDITIONAL INFORMATION TO INCLUDE IN THIS REPORT, THIS IS ONLY A CORRECTED SUPPLEMENTAL UPDATE. **** ELECTRIC UTILITY EXCAVATING FOR A STREET LIGHT MOVE STRUCK UNMARKED STEEL SERVICE, WHICH SEPERATED FROM SERVICE TEE UPSTREAM AT MAIN. GAS MIGRATED AND ACCUMULATED IN ADJACENT RESIDENCE AND EXPLODED. NORTHWESTERN ENERGY'S ADDRESS AND CONTANCT INFORMATION IN THE FRON PART OF THIS REPORT IS NOT CORRECT. THIS HAS BEEN BROUGHT TO THE ATTENTION OF MTPSC STAFF JOEL TIERNEY AND PHMSA WESTEN REGION ACCIDENT COORDINATOR PETE KATCHMAR. THE CORRECT CORPORATE ADDRESS SHOULD BE 3010 W. 69TH STREET, SIOUX FALLS, SD 57108. *** TRIED TO SUBMIT ON 06/04/2010 AT 17:42 COULD NOT SUBMITT CORRECTLY BECAUSE OF ERROR RECIEVED IN PART G - SPECIFICALLY G3 REQUIRES 13.A IF "YES" IS SELECTED IN 13. YES IS THE CORRECT ANSWER, HOWEVER I DID NOT GET A DROP DOWN FOR 13 A. THEREFORE, I SELECTED "NO" AND INDICATED AS SUCH HERE. ****
2025-03-31 10:13 | YES | NO | NO | 20100032 | 15198 | 2010-06-07 15:56 | SUPPLEMENTAL FINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 820 WEST BROADWAY, PO BOX 32030 | LOUISVILLE | KY | 40202 | 2010-05-09 20:42 |  |  | 2010 | 6414 LIME RIDGE PLACE | LOUISVILLE | JEFFERSON | KY | 40222 | 38.2895 | -85.6313 | [9 empty] | 2010-05-09 22:25 | 939685 |  | NATURAL GAS |  | 2.36 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-05-09 20:42 |  |  |  | 2010-05-09 21:06 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1991 | [8 empty] | OTHER | ALUMINUM METER | [9 empty] | OTHER | [8 empty] | FALLING DEBRIS FROM ONGOING RESIDENTIAL STRUCTURE FIRE STRUCK THE METER AND REGULATOR, DAMAGING THE FACILITIES AND IGNITING NATURAL GAS. | CLASS 3 LOCATION | 0 | 0 | 200 | 264.221899023478 | 100 | 132.110949511739 | 0 | 0 |  |  | 11 | 7.60032362459546925566343042071197411003 |  | 0 | 311 | 171.179923642615779288025889967637540453 | 403.93317215981246925566343042071197411 | 0 | 0 | 1 |  |  |  |  | 49.5 | 49.5 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | JIM DIMAS | SR. CORPORATE ATTORNEY | jim.dimas@lge-ku.com | 502-627-3712 | 502-627-3367 |  |  |  | JIM DIMAS | SR. CORPORATE ATTORNEY | 502-627-3712 | jim.dimas@lge-ku.com | KPSC EXTERNAL/INVESTIGATION REPORT ATTACHED
2025-03-31 10:13 | NO | YES | YES | 20100033 | 15041 | 2010-06-10 18:48 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2010-05-11 14:38 |  |  | 2010 | 1516 S. 48TH CT. | CICERO | COOK | IL | 60804 | 41.8597 | -87.7449 | [9 empty] | 2010-05-11 20:22 | 939892 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO |  | 2010-05-11 14:38 |  |  |  | 2010-05-11 15:13 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 38 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1.5 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.145 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 3500 | 4623.883232910865 | 0 | 0 | 3550 |  | 50 | 34.54692556634304207119741100323624595469 |  | 0 | 3550 | 1947.031687373127996763754045307443365696 | 4658.430158477208042071197411003236245955 | 0 | 0 | 1 |  |  |  |  | 0.27 | 0.27 | 0.3 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [10 empty] | YES | BASED ON TYPE OF CORROSION FOUND IN SERVICE LINE NEAR THIS ONE. | YES | NO |  | NO | NO | [8 empty] | NO | NONE | [21 empty] | 2009-01-26 | NO | [227 empty] | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | lquezad@nicor.com | [5 empty] | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE |  | No Email Address | RELEASE OF GAS FROM 1-1/2" BARE STEEL SERVICE LINE MIGRATED TO CUSTOMER SEWER DRAIN PIPE IN BATHROOM, RESULTING IN IGNITION OF GAS .
2025-03-31 10:13 | NO | YES | NO | 20100034 | 15091 | 2010-06-11 14:23 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2010-04-15 15:52 |  |  | 2010 | 168 SADDLE MOUNTAIN DR. | CALHOUN | GORDON | GA | 30701-4662 | 34.4931 | -84.9112 | [9 empty] | 2010-04-15 17:05 | 937166 |  | NATURAL GAS |  | 23 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES |  | 2010-04-15 16:00 |  |  |  | 2010-04-15 16:24 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | INSIDE STRUCTURE | 1994 | [8 empty] | UNKNOWN | [10 empty] | LEAK |  |  | OTHER | INSIDE A STRUCTURE | [5 empty] | CLASS 2 LOCATION | 0 | 0 | 0 | 0 | 69100 | 91288.666112611649 | 6000000 | 7926656.97070434 | $6,000,000 IS THE ESTIMATED DAMAGE TO RESIDENCES IN VICINITY OF THE INCIDENT. |  | 100 | 69.09385113268608414239482200647249190939 |  | 0 | 6069200 | 3320856.52961202181939352750809061488673 | 8018014.73066808433508414239482200647249 | 0 | 0 | 25 |  |  |  |  | 0.25 | 0.25 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE IN CUSTOMER'S HOMES IS CONTROLLED BY A REGULATOR AT THE METER SET. THE RELEASE WAS INSIDE A RESIDENCE DOWNSTREAM OF THE AGLC SYSTEM. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | GAS RELEASE INSIDE OF THE RESIDENCE WAS DETERMINED TO BE INTENTIONAL BY THE AUTHORITIES INVESTIGATING THE INCIDENT. | [47 empty] | WILLIAM HORNE | COMPLIANCE ENGINEER | bhorne@aglresources.com | 4045843153 | 4045844807 |  |  |  | RICHARD LONN | DIRECTOR - REGULATORY COMPLIANCE | 4045843552 | rlonn@aglresources.com | ON APRIL 15, 2010 AGLC FIELD PERSONNEL WERE DISPATCHED TO THE SCENE OF AN APPARENT EXPLOSION AT A STRUCTURE IN A RESIDENTIAL NEIGHBORHOOD. UPON ARRIVAL, IT WAS DETERMINED THAT THERE HAD BEEN AN EXPLOSION, THE RESIDENCE INVOLVED WAS SEVERELY DAMAGED, AND SEVERAL RESIDENCES IN THE VICINITY ALSO SUSTAINED DAMAGE DUE TO THE EVENT. ON AUGUST 24, 2010 THE GEORGIA INSURANCE COMMISSIONER DETERMINED THAT THE RELEASE OCCURRED INSIDE OF A RESIDENCE, AND THAT IT WAS INTENTIONAL AND AN ACT OF ARSON.
2025-03-31 10:13 | NO | YES | NO | 20100035 | 15174 | 2010-06-11 15:32 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2010-02-16 15:05 |  |  | 2010 | 724 KING STREET | DENVER | DENVER | CO | 80204-3160 | 39.7283 | -105.0335 | [9 empty] | 2010-02-16 16:56 | 931427 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 10 | 2010-02-16 15:08 |  |  |  | 2010-02-16 15:25 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1940 | [5 empty] | 1.25 | API 5L | UNKNOWN | DUCTILE IRON | [10 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1.3 | 1.3 |  | CLASS 3 LOCATION | 200000 | 264221.899023478 | 250 | 330.2773737793475 | 1000 | 1321.10949511739 | 0 | 0 |  |  | 50 | 34.54692556634304207119741100323624595469 |  | 0 | 201300 | 110148.6990466085814967637540453074433657 | 265907.832817941080542071197411003236246 | 0 | 0 | 1 |  |  |  |  | 4.5 | 5 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | DIRECTIONAL DRILLING | NATURAL GAS | YES | 800009392 | NOT APPLICABLE |  | CONTRACT LOCATOR | YES | YES |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JOHN KARTUS | MANAGER CLAIM SERVICES | john.j.kartus@xcelenergy.com | 303-294-2665 | 303-294-2311 |  |  |  | JOHN KARTUS | MANAGER CLAIM SERVICES | 303-294-2665 | john.j.kartus@xcelenergy.com | CONTRACTOR FOR THE COMPANY WAS PERFORMING DIRECTIONAL BORING WORK ASSOCIATED WITH A SERVICE RENEWAL. THE EXISTING SERVICE WAS CONTACTED BY THE BORE HEAD CAUSING A MALLEABLE ELBOW TO BREAK. GAS MIGRATED INTO AN UNDERGROUND CELLAR RESULTING IN AN EXPLOSION AND FIRE.
2025-03-31 10:13 | YES | NO | NO | 20100036 | 15068 | 2010-06-14 19:29 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-05-17 03:00 |  |  | 2010 | 1459 CAPITOLA CIRCLE | STOCKTON | SAN JOAQUIN | CA | 95206 | 37.9284 | -121.3061 | [9 empty] | 2010-05-17 07:05 | 940455 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2010-05-17 03:29 |  |  |  | 2010-05-17 04:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | FIRE FIRST MELTED METER SET RELEASING GAS | CLASS 3 LOCATION | 100000 | 132110.949511739 | 500 | 660.554747558695 | 1500 | 1981.664242676085 | 0 | 0 |  |  | 0 | 0 |  | 0 | 102000 | 55810.720964055708 | 134753.16850197378 | 0 | 0 | 1 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | LAURENCE DENISTON | SR. PROGRAM MANAGER | lcd1@pge.com | 925 974 4313 |  |  |  |  | GLEN CARTER |  |  | No Email Address | A FIRE OCCURRED AT APPROXIMATELY 0300 HOURS ON 5/17/10 AT A HOME IN STOCKTON. THE FIRE DEPARTMENT CALLED PG&E AT APPROXIMATELY 03:29 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED AT 0400 HOURS. AT APPROXIMATELY 0500 HOURS, PG&E GAS CREWS SHUT OFF GAS FLOW TO THE HOUSE BY SQUEEZING THE LINE AT THE MAIN. THE FIRE ORIGINATED NEAR THE FENCE ON THE PROPERTY AND APPEARS TO BE CAUSED BY A CIGARETTE. THE FIRE RESULTED IN PROPERTY DAMAGES EXCEEDING $50,000 MAKING THIS A REPORTABLE INCIDENT. THERE WERE NO INJURIES OR FATALITIES. MAJOR MEDIA WAS NOT PRESENT.
2025-03-31 10:13 | NO | NO | NO | 20100037 | 15046 | 2010-06-14 19:51 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-04-25 16:30 |  |  | 2010 | 2841 RODNEY AVENUE | MODESTO | STANISLAUS | CA | 95350 | 37.6375 | -120.9416 | [9 empty] | 2010-04-25 21:19 | 938139 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2010-04-25 17:00 |  |  |  | 2010-04-25 17:30 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  |  |  | 0.75 | [6 empty] | OTHER | [8 empty] | AN ENERGIZED 12 KV ELECTRICAL LINE FELL AND CAME IN CONTACT WITH A HOUSE FACILITY; DUE TO A LACK OF GROUND AT THE ELECTRIC PANEL AT THE HOUSE, THE HOUSE WATER AND GAS LINE BECAME ENERGIZED. THE WATER PIPES CONDUCTED THE ELECTRICITY AT SEVERAL LOCATIONS WHERE THE HIGH VOLTAGE CAUSED DAMAGE TO GAS LINES RESULTING IN A LEAK IN THE SERVICE LINE. | CLASS 3 LOCATION | 0 | 0 | 5000 | 6605.54747558695 | 10000 | 13211.0949511739 |  | 0 |  |  | 0 | 0 |  | 0 | 15000 | 8207.45896530231 | 19816.64242676085 | 0 | 0 | 3 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | ELECTRICAL ARCING | [154 empty] | LAURENCE DENISTON | SR. PROGRAM MANAGER | lcd1@pge.com | 9259744313 |  |  |  |  | GLEN CARTER |  |  | No Email Address | AT APPROXIMATELY 1630 HOURS ON APRIL 25, 2010 AT 209 EL ROYA AVE., MODESTO, AN ENERGIZED 12 KV ELECTRICAL LINE FELL AND CAME IN CONTACT WITH A HOUSE FACILITY; DUE TO A LACK OF GROUND AT THE ELECTRIC PANEL AT THE HOUSE, THE HOUSE WATER AND GAS LINE BECAME ENERGIZED. THE WATER PIPES CONDUCTED THE ELECTRICITY AT SEVERAL LOCATIONS WHERE THE HIGH VOLTAGE CAUSED DAMAGE TO GAS LINES RESULTING IN A LEAK IN THE SERVICE LINE IN THE AFOREMENTIONED LOCATION AS WELL AS FIRES AT 2840 RODNEY AVENUE AND 2841 RODNEY AVENUE. THIS AREA IS WITHIN THE MODESTO IRRIGATION DISTRICT (MID) AND MID SUPPLIES AND MAINTAINS THE ELECTRIC SERVICE TO THE HOMES INVOLVED IN THIS INCIDENT. THE SUSPECTED CAUSE OF THE ELECTRIC LINE FALLING IS DESCRIBED IN THE 30-DAY LETTER. PG&E WAS NOTIFIED OF THE INCIDENT AT APPROXIMATELY 1700 HOURS AND THE GSR ARRIVED ON SCENE AT 1730 HOURS. THE GAS LINE WAS CUT AND CAPPED AT APPROXIMATELY 1900 HOURS. SERVICE TO 209 EL ROYA WAS RESTORED ON 4/25/10; SERVICE TO THE TWO REMAINING HOMES WILL BE RESTORED WHEN REPAIRS TO THE STRUCTURES ARE COMPLETED. THERE WERE NO FATALITIES OR INJURIES AND NO MAJOR MEDIA PRESENT. THIS INCIDENT IS REPORTABLE DUE TO PROPERTY DAMAGES EXCEEDING $50,000.
2025-03-31 10:13 | NO | YES | NO | 20100038 | 15050 | 2010-06-17 18:56 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2010-05-17 11:18 |  |  | 2010 | 10400 FRANKLIN AVENUE | FRANKLIN PARK | COOK | IL | 60131 | 41.9404 | -87.8854 | [9 empty] | 2010-05-19 14:29 | 940869 |  | NATURAL GAS |  | 215.65 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2010-05-17 11:18 |  |  |  | 2010-05-17 11:35 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 162 |  | YES |  |  | YES | CASED | [7 empty] | PRIVATELY OWNED |  | MAIN |  | 1965 | [5 empty] | 12 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 5.7 | 0 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 121000 | 159854.24890920419 | 92000 | 121542.07355079988 | 0 | 0 |  |  | 900 | 621.844660194174757281553398058252427184 |  | 0 | 213900 | 117121.1600257394039417475728155339805825 | 282018.1671201982447572815533980582524272 | 1 | 0 | 0 |  |  |  |  | 153 | 155 | 230 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | [6 empty] | YES | [7 empty] | CONTRACTOR | UNKNOWN/OTHER | ROAD WORK | YES | 540758 | JULIE - ONE CALL TICKET NUMBER IS X0540758 BUT 9A RETURNS ERROR STATING "PLEASE ENTER ONLY DIGITS" |  | CONTRACT LOCATOR | UNKNOWN/OTHER | YES | 48 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | lquezad@nicor.com | [5 empty] | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE |  | No Email Address | ROAD CONTRACTOR WAS DRIVING SHEET PILING FOR BRIDGE FOUNDATION AND STRUCK THE GAS MAIN.
2025-03-31 10:13 | NO | YES | YES | 20100043 | 30468 | 2010-06-28 15:58 | SUPPLEMENTAL | 12208 | MARTIN GAS INC | P.O. BOX 783 | HINDMAN | KY | 41822 | 2010-05-25 16:30 |  |  | 2010 | OLD RAILROAD STREET | MARTIN | FLOYD | KY | 41649 | 37.3415 | -82.4526 | [9 empty] | 2010-05-26 17:00 | 941661 |  | NATURAL GAS |  | 1000 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | YES | 0 | 2010-05-25 16:30 |  |  |  | 2010-05-25 16:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1990 | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | UNKNOWN | MECHANICAL PUNCTURE | 10 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 3000 | 3963.32848535217 | 0 | 0 |  |  | 5000 | 3454.692556634304207119741100323624595469 |  | 0 | 8000 | 4837.284673319361676375404530744336569579 | 7418.021041986474207119741100323624595469 | 9 | 0 | 80 |  |  |  |  | 18 | 18 | 80 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES |  | YES | [7 empty] | NO | YES | CITY STREET |  |  | YES | [9 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | WATER | NO |  |  |  | UTILITY OWNER | YES | YES | 4 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | JED WEINBERG | MGR. | johnp@cleangasinc.com | 606-785-0761 |  |  |  |  | JED WEINBERG | MGR. | 606-785-0761 | johnp@cleangasinc.com | SEE ATTACHED (2 PAGES) I AM COMPLETING THIS SUPPLEMENTAL REPORT AS OF 6.6.2018. THERE IS NO STAFF CURRENTLY EMPLOYED AT MARTIN GAS, INC. WHO WAS EMPLOYED AT THE TIME OF THE INCIDENT IN QUESTION. I CANNOT LOCATE A "WORK FILE" WHICH MIGHT CONTAIN THE INFORMATION THAT WAS CONTAINED WITHIN THIS PART H-NARRATIVE DESCRIPTION OF THE INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20100044 | 15079 | 2010-06-30 13:07 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-06-18 17:00 |  |  | 2010 | 3320 WEST CENTER STREET | ANDERSON | SHASTA | CA | 96007 | 40.4529 | -122.3056 | [9 empty] | 2010-06-18 20:00 | 994619 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-06-18 18:02 |  |  |  | 2010-06-18 18:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | STRUCTURE FIRE | CLASS 3 LOCATION | 0 | 0 | 2000 | 2642.21899023478 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 2000 | 1094.327862040308 | 2642.21899023478 | 0 | 0 | 0 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | OTHER | ARSON | [155 empty] | LAURENCE DENISTON |  | lcd1@pge.com | 925 974 4313 |  |  |  |  | GLEN CARTER |  |  | No Email Address | A STRUCTURE FIRE INVOLVED AN UNOCCUPIED HARDWARE STORE AND A SMALL COMMERCIAL 12-METER MANIFOLD. THERE WERE NO METERS ON THE MANIFOLD AND NO CUSTOMERS LOST SERVICE. THE HEAT FROM THE STRUCTURE FIRE MELTED A REGULATOR ON THE MANIFOLD WHICH IN TURN RELEASED GAS AND CONTRIBUTED TO THE FIRE. THE CAUSE IS OFFICIALLY UNDETERMINED; HOWEVER, ACCORDING TO THE FIRE DEPARTMENT THE CAUSE APPEARS TO BE ARSON WITH THE FIRE STARTING IN THE BACK OF THE BUILDING AND NOT FROM PG&E FACILITIES. PG&E WAS NOTIFIED OF THIS INCIDENT BY THE FIRE DEPARTMENT AT 1802 HOURS. THE GAS SERVICE REPRESENTATIVE ARRIVED ON SCENE AT 1830 HOURS. THE FIRE DEPARTMENT STOPPED THE FLOW OF GAS BY CLOSING THE SERVICE VALVE AND THE FIRE WAS EXTINGUISHED AT APPROXIMATELY 1900 HOURS. THIS INCIDENT WAS DETERMINED TO BE REPORTABLE DUE TO DAMAGES TO THE BUILDING EXCEEDING $50,000. THERE WERE NO FATALITIES AND NO INJURIES AS A RESULT OF THIS INCIDENT. LOCAL NEWS MEDIA WAS ON-SITE, BUT NO MAJOR MEDIA WAS PRESENT.
2025-03-31 10:13 | NO | YES | NO | 20100046 | 15060 | 2010-07-08 14:51 | ORIGINAL FINAL | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2010-06-25 17:54 |  |  | 2010 | 5454 W. GULF BANK | HOUSTON | HARRIS | TX | 77088 | 29.8841 | -95.4686 | [9 empty] | 2010-06-25 19:29 | 945518 |  | NATURAL GAS |  | 30.52 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 10 | 2010-06-25 17:54 |  |  |  | 2010-06-25 17:54 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1985 | [8 empty] | OTHER | CAST ALUMINUN | [9 empty] | OTHER | [8 empty] | VEHICLE RAN OVER METER/REGULATOR SET | CLASS 3 LOCATION | 0 | 0 | 89 | 117.57874506544771 | 1500 | 1981.664242676085 | 125000 | 165138.68688967375 | DAMAGE TO VEHICLE AND APARTMENT COMPLEX |  | 265 | 183.09870550161812297734627831715210356 |  | 0 | 126854 | 69434.3118865639963888478964401294498382 | 167421.0285829169008329773462783171521036 | 1 | 0 | 0 |  |  |  |  | 34.8 | 34.8 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LESLIE J. DAVENPORT | ADVANCED OPERATIONS COORDINATOR | leslie.davenport@centerpointenergy.com | 713/967/8025 | 713/923/9794 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713/207/5700 | steve.yarbrough@centerpointenergy.com | THIRD PARTY LOST CONTROL OF VEHICLE WHICH JUMPED (1) CONCRETE CURB STOP AND (1) CONCRETE CURB BEFORE RUNNING OVER METER SET ASSEMBLY AND CRASHING IN TO THE LAUNDRY ROOM OF THE INWOOD APARTMENTS. ESCAPING GAS FROM THE DAMAGED FACILITY IGNITED FROM UNDETERMINED/UNKNOWN IGNITION SOURCE.
2025-03-31 10:13 | NO | YES | NO | 20100047 | 15114 | 2010-07-12 14:01 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2010-06-17 10:37 |  |  | 2010 | M-13 & KAWKAWLIN RIVER (SOUTH BRIDGE ABUTMENT) | KAWKAWLIN |  | MI | 48631 | 43.6536 | -83.9444 | [9 empty] | 2010-06-18 09:45 | 944519 |  | NATURAL GAS |  | 500 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2010-06-17 10:37 |  |  |  | 2010-06-17 11:10 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1959 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | MECHANICAL PUNCTURE | [9 empty] | CLASS 2 LOCATION | 0 | 0 | 186200 | 245990.587990858018 | 20000 | 26422.1899023478 |  | 0 |  |  | 5000 | 3454.692556634304207119741100323624595469 |  | 0 | 211200 | 116020.9954566146544763754045307443365696 | 275867.4704498401222071197411003236245955 | 0 | 0 | 0 |  |  |  |  | 385 | 385 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY THIRD PARTY | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | DAVIS CONSTRUCTION WAS DRIVING SHEET PILING INTO GROUND AT THE SOUTH END OF A BRIDGE CROSSING THE KAWKAWLIN RIVER, THIS BRIDGE IS PART OF THE M-13 HIGHWAY. DURING THE INSTALLATION OF THE SHEET PILING A 6" HIGH PREESSURE MAIN WAS HIT WITH THE SHEET PILING CAUSING THE HIGH PRESSURE MAIN TO LEAK. | [154 empty] | GARY F EWERT | REGULATRORY SERVICES ENGINEER | gewert05@charter.net | 586-665-1142 |  |  |  |  | DAVID M MONTAGUE | DIRECTOR COMPLIANCE PROGRAMS | 517-788-0277 | dmmontague@cmsenergy.com | ON 6/17/2010 DAVIS CONSTRUCTION WAS DRIVING SHEET PILING INTO GROUND AT THE SOUTH END OF A BRIDGE CROSSING THE KAWKAWLIN RIVER, THIS BRIDGE IS PART OF THE M-13 HIGHWAY. DURING THE INSTALLATION OF THE SHEET PILING A 6" HIGH PRESSURE MAIN WAS HIT WITH THE SHEET PILING CAUSING THE HIGH PRESSURE MAIN TO LEAK.
2025-03-31 10:13 | NO | NO | NO | 20100048 | 15062 | 2010-07-12 15:28 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2010-05-16 16:38 |  |  | 2010 | 2293 NORTH MILFORD ROAD | HIGHLAND |  | MI | 48357 | 42.6628 | -83.613 | [9 empty] | 2010-05-16 19:10 | 940415 |  | NATURAL GAS |  | 46 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2010-05-16 16:38 |  |  |  | 2010-05-16 16:54 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET | [10 empty] | OTHER | GAS METER & REGULATOR SHELL | [9 empty] | OTHER | [8 empty] | A BURNING UNOCCUPIED TRUCK HIT RESIDENTIAL METER BREAKING OFF THE REGULATOR. | CLASS 3 LOCATION |  | 0 | 1000 | 1321.10949511739 | 1000 | 1321.10949511739 |  | 0 |  |  |  | 0 |  | 0 | 2000 | 1094.327862040308 | 2642.21899023478 | 0 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY SECONDARY IGNITION FROM A BURNING TRUCK ROLLING INTO OUR METER FACILITIES ON AN APARTMENT COMPLEX. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | GARY F EWERT | REGULATORY SERVICES ENGINEER | gfewert@cmsenergy.com | 586-665-1142 |  |  |  |  | DAVID M MONTAGUE | DIRECTOR - GAM COMPLIANCE PROGRAMS | 517-788-0277 | dmmontague@cmsenergy.com | AN UNOCCUPIED, BURNING TRUCK WITH A MANUAL TRANSMISSION ROLLED INTO A RESIDENTIAL TYPE GAS METER STAND AND APARTMENT BUILDING. THIS CAUSED THE REGULATOR TO BREAK OFF RESULTING IN SECONDARY IGNITION TO THE GAS AND THE APARTMENT COMPLEX. THERE WAS DAMAGE TO ONE APARTMENT UNIT, THE BUILDING ROOF AND SMOKE DAMAGE TO THE UNITS ON EACH SIDE OF THE DAMAGED APARTMENT.
2025-03-31 10:13 | YES | NO | NO | 20100049 | 15096 | 2010-07-12 19:17 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-06-22 04:00 |  |  | 2010 | 9586 SAN BENITO AVENUE | GERBER | TEHAMA | CA | 96035 | 40.0709 | -122.1624 | [9 empty] | 2010-06-22 09:09 | 945002 |  | NATURAL GAS |  | 100 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-06-22 05:18 |  |  |  | 2010-06-22 06:12 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | FIRE FIRST | CLASS 3 LOCATION | 0 | 0 | 2000 | 2642.21899023478 | 0 | 0 | 50000 | 66055.4747558695 | DAMAGES TO RESIDENTIAL STRUCTURE |  | 0 | 0 |  | 0 | 52000 | 28452.524413048008 | 68697.69374610428 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | LAURENCE DENISTON |  | lcd1@pge.com | 925 974 4313 |  |  |  |  | GLEN CARTER |  |  | No Email Address | A STRUCTURE FIRE RESULTED IN ONE FATALITY. THE HEAT FROM THE STRUCTURE FIRE MELTED THE REGULATOR AND METER WHICH RELEASED GAS AND CONTRIBUTED TO THE FIRE. FIRE DEPARTMENT PERSONNEL SHUT OFF THE GAS AT THE SERVICE VALVE PRIOR TO PG&E PERSONNEL BEING ON THE SCENE. ACCORDING TO THE FIRE DEPARTMENT THE CAUSE OF THE STRUCTURE FIRE WAS THE DAMAGE TO A LAMP ELECTRICAL CORD WHICH 'CAUSED THE WIRE AND OUTLET TO HEAT TO A POINT OF CAUSING AN IGNITION SOURCE WITHIN THE OUTLET OR WIRES CONNECTING TO THE OUTLET.' THE LAMP CORD WAS DAMAGED FROM A HEAVY OBJECT BEING POSITIONED ON THE CORD. A PG&E ELECTRIC TROUBLEMAN ARRIVED ON THE SCENE AT 0612 HOURS. A GAS SERVICE REPRESENTATIVE ARRIVED ON SCENE AT 0641. A LEAK SURVEY OF GAS FACILTIES IN THE AREA WAS CONDUCTED AND NO LEAKS WERE FOUND. THIS INCIDENT WAS DETERMINED TO BE REPORTABLE DUE TO A FATALITY AND DAMAGES EXCEEDING $50,000.
2025-03-31 10:13 | NO | NO | NO | 20100050 | 15064 | 2010-07-14 17:01 | ORIGINAL FINAL | 12438 | MIDDLE TENNESSEE NATURAL GAS UTIL DIST | P.O. BOX 670, 1030 WEST BROAD ST | SMITHVILLE | TN | 37166 | 2010-07-02 08:30 |  |  | 2010 | 1800 CHINKAPIN TRAIL | MONTEREY | PUTNAM | TN | 38574-0000 | 36.0484 | -85.2595 | [9 empty] | 2010-07-02 10:00 | 946324 |  | NATURAL GAS |  | 2.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-07-02 08:30 |  |  |  | 2010-07-02 08:50 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2009 | [5 empty] | 2 | ASTM D2513 | PHILLIPS -DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 8 | 1 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 1000 | 1321.10949511739 | 1000 | 1321.10949511739 |  | 0 | THIRD PARTY CON. HAD COST OF TRENCHER EST. AT $50,000. NOT AN OPERATOR COST. |  | 24 | 16.58252427184466019417475728155339805825 |  | 0 | 2024 | 1109.667667865550718446601941747572815534 | 2658.801514506624660194174757281553398058 | 0 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | TRENCHER | WATER | NO |  |  |  | UNKNOWN/OTHER | NO |  |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JAMES E. HODGES | VICE PRESIDENT ENGINEERING | jhodges@mtng.com | 615-597-4300 | 615-597-6331 |  |  |  | LESLIE B. ENOCH II | EXECUTIVE VP AND CEO | 615-597-4300 | lenoch@mtng.com | CONTRACTOR, W&O CONSTRUCTION, RUPTURED MIDDLE TENNESSEE NATURAL GAS UTILITY DISTRICT'S 2" PE GAS MAIN WHILE TRENCHING (VEMEER T855 TRENCHER) FOR WATER LINE INSTALLATION. THE ESCAPING GAS WAS IGNITED BY THE TRENCHER, AND THE TRENCHER BURNED. ONE CALL CENTER WAS NOT CALLED, OPERATOR WAS NOT CALLED BEFORE THE INCIDENT, PIPE WAS NOT LOCATED. DURING EMERGENCY RESPONSE, PIPE WAS SQUEEZED OFF AND CAPPED ON EACH SIDE OF THE INCIDENT TO STOP GAS FLOW. DAMAGED AREA OF PIPE WAS CUT OUT. A NEW SECTION OF PIPE WILL BE INSTALLED IN THIS AREA AT A LATER DATE. THIRD PARTY CONTRACTOR DAMAGES FROM THIS INCIDENT ARE ESTIMATED AT $50,000. OPERATOR DAMAGES ARE ESTIMATED AT $2,024.
2025-03-31 10:13 | NO | NO | NO | 20100051 | 15094 | 2010-07-16 16:20 | SUPPLEMENTAL FINAL | 8040 | AMERENIP | 500 SOUTH 27TH STREET | DECATUR | IL | 62525 | 2010-06-18 08:43 |  |  | 2010 | 1624 SCHOOL STREET | SCHRAM CITY |  | IL | 62049-1940 | 39.1561 | -89.4752 | [9 empty] | 2010-06-18 10:17 | 944536 |  | NATURAL GAS |  | 1833 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-06-18 08:43 |  |  |  | 2010-06-18 08:50 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | YES |  |  |  |  | YES | UNCASED, BORED/DRILLED | [5 empty] | PRIVATELY OWNED |  | SERVICE |  | 1964 | [5 empty] | 0.75 | GRADE B | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | OTHER | [8 empty] | 3RD PARTY EXCAVATOR SEVERED 3/4" SERVICE LINE. | CLASS 3 LOCATION | 0 | 0 | 21070 | 27835.7770621234073 | 42778 | 56514.42198213170942 | 0 | 0 |  |  | 11787 | 8144.092233009708737864077669902912621359 |  | 0 | 75635 | 42469.0848036971226890873786407766990291 | 92494.2912772648254578640776699029126214 | 0 | 0 | 1 |  |  |  |  | 330 | 380 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 1460029 | JULIE |  | CONTRACT LOCATOR | YES | YES | 31 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | CHARLES RAYOT | SUPERVISING ENGINEER | crayot@ameren.com | 217-625-6802 | 217-625-6803 |  |  |  | JEROME THEMIG | MANAGER GAS COMPLIANCE | 217-625-6804 | jthemig@ameren.com | HAIER PLUMBING REQUESTED A JULIE ONE-CALL JOINT MEET TICKET COVERING A LARGE SEWER AND WATERLINE PROJECT IN THE HILLSBORO AREA. DURING THE JOINT MEET, HAIER PLUMBING EXPLAINED TO LOCATORS IN ATTENDANCE WHAT THE PROJECT ENTAILED AND SHOWED THEM A MAP OF THE AREAS THAT NEEDED TO BE LOCATED FOR THE START OF THE PROJECT. WHEN HAIER NEEDED ADDITIONAL AREAS LOCATED, THEY STATED THEY WOULD CONTACT THE LOCATORS AND EXPLAIN WHAT AREAS SHOULD BE LOCATED NEXT. ON 6/14/2010 HAIER CONTACTED THE CONSOLIDATED UTILITY SERVICE (CUS) LOCATOR WORKING FOR AMEREN AND REQUESTED AN AREA OF RAILROAD STREET SOUTH OF IL RTE. 16 (SCHOOL STREET) TO BE LOCATED FOR A BORE ACROSS SCHOOL ST. WHEN THE CUS LOCATOR FOR AMEREN SHOWED UP TO THE LOCATION SPECIFIED, HE LOCATED THE 8" STEEL HIGH PRESSURE GAS MAIN AND BOTH HE AND THE EXCAVATOR FOR HAIER WALKED AROUND 1624 SCHOOL ST. TOGETHER LOOKING FOR A POSSIBLE GAS METER. NEITHER THE LOCATOR NOR HAIER NOTICED THE GAS METER OR FARM TAP FOR 1624 SCHOOL ST. ON 6/18/2010, HAIER WAS EXCAVATING IN RAILROAD STREET AND STRUCK THE UNMARKED 3/4" STEEL GAS SERVICE BETWEEN THE 8" HIGH PRESSURE STEEL MAIN ON THE EAST SIDE OF RAILROAD STREET AND THE FARM TAP SERVING 1624 SCHOOL ST. THE FARM TAP WAS OBSCURED BY VEGETATION AND LANDSCAPING TO THE EXTENT THAT HAIER CREW MEMBERS WERE STANDING NEXT TO IT WHEN THE DAMAGE OCCURRED AND DID NOT REALIZE IT WAS THERE UNTIL THEY HEARD THE GAS BLOWING FROM THE DAMAGE NEAR THE TAP. AMEREN RECEIVED A CALL FROM THE EXCAVATOR AT 0843 ON 6/18/2010 AND AN AMEREN FIRST RESPONDER WAS ON SITE AT 0850. EMERGENCY RESPONDERS INSURED THE AREA WAS SAFE INCLUDING THE STRUCTURE AT 1624 SCHOOL ST. IL RTE. 16 WAS SHUT DOWN AT 0925 AND ORDER WAS MADE TO CUT THE ELECTRIC SERVICE TO 1624 SCHOOL ST. DUE TO GAS IN AIR DUE TO EXCESSIVE WINDS. NO GAS WAS EVER DETECTED INSIDE THE STRUCTURE AT 1624 SCHOOL ST. CREWS WERE MOBILIZED TO SHUT OFF THE FLOW OF GAS AND REPAIR THE DAMAGED FACILITIES. SINCE THE SERVICE WAS HIT BETWEEN THE MAIN AND THE FARM TAP, THE 8" MAIN HAD TO BE EXCAVATED IN TWO LOCATIONS AT A SAFE DISTANCE FROM THE HIT WHERE TWO 8" LINE STOPPERS AND A BYPASS COULD BE WELDED ON THE MAIN ALLOWING STOPPERS TO BE SET TO STOP OFF THE FLOW OF GAS TO THE DAMAGED GAS FACILITIES. AT 1600, IL RTE. 16 WAS RE-OPENED. DUE TO THE EXTENT OF LARGE DIAMETER STEEL WORK THAT HAD TO BE COMPLETED COUPLED WITH A SEVERE ROUND OF THUNDERSTORMS THAT EVENING, GAS WAS SHUT DOWN AT 1016 ON 6/19/2010. THE SERVICE HAD BEEN SEVERED BY THE EXCAVATOR NEAR A 3/4" WELD ELBOW. CREWS MADE REPAIRS TO THE STEEL SERVICE LINE AND GAS WAS RESTORED TO THE CUSTOMER AT 1624 SCHOOL ST. AT 1630 ON 6/19/2010.
2025-03-31 10:13 | NO | YES | YES | 20100052 | 15136 | 2010-02-19 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2010-01-21 17:37 |  |  | 2010 | 2813 KESSLER | WICHITA FALLS | WICHITA | TX | 76309 | 33.8937 | -98.5293 | [9 empty] | 2010-01-21 19:32 | 929299 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2010-01-21 17:37 |  |  |  | 2010-01-21 17:53 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1.25 | API 5L | UNKNOWN | STEEL |  |  |  | 0.188 | [6 empty] | LEAK |  |  | OTHER | UNKNOWN DUE TO PIPE UNDER SLAB | [5 empty] | CLASS 3 LOCATION | 135000 | 178349.78184084765 |  | 0 | 3500 | 4623.883232910865 |  | 0 |  |  |  | 0 |  | 0 | 138500 | 75782.204446291329 | 182973.665073758515 | 0 | 0 | 0 |  |  |  |  | 21.5 | 21.5 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | THE LEAKING SECTION WAS NOT EXCAVATED | [11 empty] | YES | LEAKING SECTION OF PIPE WAS NOT EXCAVATED | [7 empty] | NO | [86 empty] | MARK HENDERSON | OPERATIONS MANAGER | mark.henderson@atmosenergy.com | 940-631-2457 | 940-696-7609 |  |  |  | MARCUS CHAPMAN | DIRECTOR OF COMPLIANCE | 214-206-2875 | marcus.chapman@atmosenergy.com | LEAK DEVELOPED ON SERVICE LINE UNDER FOUNDATION OF HOME, AN ADD-ON SECTION OF THE HOME WAS CONSTRUCTED ON TOP OF THE SERVICE LINE. GAS MIGRATED INTO THE HOME THROUGH A SEAM IN THE CONCRETE AND GAS IGNITED, INJURING ONE PERSON AND CAUSING THE HOUSE TO BE DESTROYED BY FIRE. SERVICE LINE WAS NOT EXCAVATED DUE TO THE STRUCTURE BEING OVER THE SERVICE LINE. CAUSE OF LEAK ON SERVICE LINE UNDETERMINED.
2025-03-31 10:13 | NO | YES | YES | 20100053 | 15712 | 2010-03-03 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY | DALLAS | TX | 75240 | 2010-01-31 03:42 |  |  | 2010 | 3521 FINLEY | IRVING | DALLAS | TX | 75062-3029 | 32.8541 | -96.994 | [9 empty] | 2010-01-31 12:00 | 930142 |  | NATURAL GAS |  |  |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 0 | 2010-01-31 03:42 |  |  |  | 2010-01-31 04:21 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 39 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1966 | [5 empty] | 1 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | UNDETERMINED AT THIS TIME | CLASS 3 LOCATION | 135000 | 178349.78184084765 | 0 | 0 | 15000 | 19816.64242676085 | 0 | 0 |  |  | 0 | 0 |  | 0 | 150000 | 82074.5896530231 | 198166.4242676085 | 0 | 0 | 0 |  |  |  |  | 48 | 20 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER'S ACTIONS DID NOT CONTRIBUTE TO LEAK | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | KEN PARKS | OPERATIONS MANAGER | ken.parks@atmosenergy.com | 8172763658 | 8172763665 |  |  |  | MARCUS CHAPMAN | DIRECTOR OF COMPLIANCE | 2142062875 | marcus.chapman@atmosenergy.com | ATMOS ENERGY DISCOVERED A LEAKING COMPRESSION COUPLING IN THE AREA WHERE THIS FIRE OCCURRED. THE LEAKING COMPONENT WAS PRESERVED IN ITS NATIVE STATE AND SENT TO A LABORATORY FOR TESTING TO DETERMINE THE CAUSE OF FAILURE. A FLOW RATE TEST WAS PERFORMED AND THE TEST REVEALED THAT THE LEAK RATE FROM THE LEAKING COMPONENT WAS NOT LARGE ENOUGH TO CAUSE AN ACCUMULATION OF A FLAMMABLE MIXTURE TO HAVE CONTRIBUTED TO THIS HOUSE FIRE. ATMOS ENERGY'S EXHAUSTIVE INVESTIGATION DID NOT IDENTIFY ANY OTHER SOURCES THAT COULD HAVE CONTRIBUTED TO THIS EVENT, THEREFORE THE CAUSE OF THIS FIRE IS UNDETERMINED.
2025-03-31 10:13 | YES | NO | NO | 20100055 | 15075 | 2010-07-20 12:19 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-06-23 02:00 |  |  | 2010 | 901 & 903 BUENA VISTA STREET | TAFT | KERN | CA | 93268 | 35.1318 | -119.4534 | [9 empty] | 2010-06-23 07:30 | 945126 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2010-06-23 02:44 |  |  |  | 2010-06-23 03:54 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | FIRE FIRST MELTED METER | CLASS 3 LOCATION | 0 | 0 | 2000 | 2642.21899023478 |  | 0 | 330000 | 435966.1333887387 | DAMAGES TO RESIDENTIAL PROPERTIES |  | 0 | 0 |  | 0 | 332000 | 181658.425098691128 | 438608.35237897348 | 0 | 0 | 2 |  |  |  |  | 15 | 15 | 18 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | LAURENCE DENISTON | SR. PROGRAM MANAGER | lcd1@pge.com | 925 974 4313 |  |  |  |  | GLEN CARTER |  |  | No Email Address | A STRUCTURE FIRE RESULTED IN PROPERTY DAMAGES TO TWO RESIDENCES. THE HEAT FROM THE STRUCTURE FIRE MELTED THE REGULATOR AND METER AT 903 BUENA VISTA STREET, CAUSING GAS TO BE RELEASED. THE GAS IGNITED AND CONTRIBUTED TO THE FIRE. GAS WAS SHUT OFF AT THE SERVICE VALVE BY PG&E PERSONNEL AT 0530 HOURS. THE GAS SERVICE TO 903 BUENA VISTA STREET WAS EXCAVATED AT PROPERTY LINE AND CUT OFF AT 0630 HOURS. THE CAUSE OF THE STRUCTURE FIRE IS YET TO BE DETERMINED, ALTHOUGH THE FIRE DEPARTMENT IS INVESTIGATING THE INCIDENT AS A POSSIBLE ARSON CASE. THE FIRE DAMAGE TO THE RESIDENCE AT 901 BUENA VISTA STREET DID NOT INVOLVE PG&E GAS FACILITIES. A LEAK SURVEY OF THIS SERVICE DETECTED NO LEAKAGE. THIS INCIDENT WAS DETERMINED TO BE REPORTABLE DUE TO DAMAGES EXCEEDING $50,000, AND THAT THE CAUSE OF THE FIRE IS YET TO BE DETERMINED.
2025-03-31 10:13 | YES | NO | NO | 20100056 | 15080 | 2010-07-20 13:56 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-07-05 09:30 |  |  | 2010 | 3820 25TH AVENUE | SACRAMENTO | SACRAMENTO | CA | 94203 | 38.5297 | -121.4659 | [9 empty] | 2010-07-05 12:30 | 946612 |  | NATURAL GAS |  | 4.6 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 4 | 0 | 0 | 4 | YES |  |  |  |  | YES | 0 | 2010-07-05 09:42 |  |  |  | 2010-07-05 10:16 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | HOUSE LINE LEFT OPEN. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 100000 | 132110.949511739 | DAMAGE TO SINGLE FAMILY RESIDENCE. |  | 0 | 0 |  | 0 | 100000 | 54716.3931020154 | 132110.949511739 | 0 | 0 | 1 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | LAURENCE DENISTON |  | lcd1@pge.com | 925 974 4313 |  |  |  |  | GLEN CARTER |  |  | No Email Address | A GAS EXPLOSION AND FIRE OCCURRED AT AN UNOCCUPIED HOME THAT WAS BEING RENOVATED FOR RENTAL. ON THE MORNING OF THE INCIDENT THE CONSTRUCTION WORKERS ARRIVED ON SITE, SMELLED GAS, NOTICED THE GAS METER TURNING RAPIDLY AND CALLED THE HOMEOWNER. THE HOMEOWNER, IN TURN, CALLED 911. WHEN THE FIRE DEPARTMENT ARRIVED THEY SHUT OFF THE GAS AND ELECTRIC METERS; IMMEDIATELY AFTER FIRE PERSONNEL ENTERED THE HOUSE, THE HOUSE EXPLODED RESULTING IN INJURIES TO FOUR FIREMEN. INSPECTION OF THE HOME RESULTED IN THE DISCOVERY OF THE HOUSE LINE TO THE GAS RANGE HAD BEEN DISCONNECTED AND THE APPLIANCE VALVE LEFT OPEN ALLOWING GAS TO BE RELEASED INSIDE THE HOUSE. PG&E CONDUCTED A SPECIAL LEAK SURVEY IN THE AREA ON THE DAY OF THE INCIDENT AND FOUND NO SIGNIFICANT LEAKS. TWO 'FUZZ' LEAKS WERE FOUND AT METER SETS IN THE AREA. AFTER CONDUCTING THE LEAK SURVEY, THE SERVICE LINE TO THE INCIDENT SITE WAS CUT OFF AT THE MAIN AND WAS PRESSURE TESTED AT 100 PSIG FOR 10 MIN BACK TO THE RISER VALVE. THE LINE HELD PRESSURE, INDICATING AN AIR TIGHT SEAL FROM THE MAIN TO THE RISER VALVE. ACCORDING TO FIRE DEPARTMENT INVESTIGATIONS, EVIDENCE SHOWS THE EXPLOSION WAS THE RESULT OF A 'DELIBERATE ACT'. PG&E HAS REQUESTED A COPY OF THE INVESTIGATION REPORT FROM THE FIRE DEPARTMENT. THIS INCIDENT WAS DETERMINED TO BE REPORTABLE DUE TO THE INJURIES, DAMAGES EXCEEDING $50,000 AND SACRAMENTO MEDIA BEING ON-SITE.
2025-03-31 10:13 | NO | NO | NO | 20100057 | 15073 | 2010-07-20 16:08 | ORIGINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY | DALLAS | TX | 75240 | 2010-01-03 15:54 |  |  | 2010 | NE 16TH STREET | AMARILLO | POTTER | TX | 79102-0000 | 35.2315 | -101.8165 | [9 empty] | 2010-01-03 17:37 | 927633 |  | NATURAL GAS |  | 6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2010-01-03 15:54 |  |  |  | 2010-01-03 16:32 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1950 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 60000 | 79266.5697070434 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 | 60000 | 32829.83586120924 | 79266.5697070434 | 0 | 0 | 1 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | NO | NONE | [21 empty] | 2009-03-06 | NO | [227 empty] | SHANNON HENZLER | SUPERVISOR MEASUREMENT | shannon.henzler@atmosenergy.com | 8067984423 | 8067984495 |  |  |  | RIC KISSINGER | VP TECHNICAL SERVICES | 8067984432 | ric.kissinger@atmosenergy.com | NATURAL GAS LEAKAGE DUE TO CORROSION MIGRATED UNDERGROUND TO A PIER AND BEAM CONSTRUCTED HOME WHICH WAS LOCATED APPROXIMATELY 15 FEET FROM THE GAS MAIN. THE HOMEOWNERS HAD RECENTLY REPLACED THEIR GAS SERVICE LINE ADJACENT TO THE MAIN WHICH APPEARS TO BE THE MIGRATION PATH TO THE HOME'S FOUNDATION. AN UNKNOWN IGNITION SOURCE IGNITED THE GAS THAT COLLECTED UNDER THE HOME AND DESTROYED THE HOUSE. NO SERIOUS INJURIES WERE REPORTED. THE LEAKING STEEL MAIN WAS REPLACED WITH 110 FEET OF PE MAIN.
2025-03-31 10:13 | NO | NO | NO | 20100058 | 15074 | 2010-07-21 14:01 | ORIGINAL | 2604 | COLUMBIA GAS OF VIRGINIA INC | 1809 COYOTE DRIVE | CHESTER | VA | 23836 | 2010-06-23 12:30 |  |  | 2010 | RT. 29 BYPASS | DANVILLE | PITTSYLVANIA | VA | 24540 | 36.6445 | -79.3643 | [9 empty] | 2010-06-23 22:24 | 945242 |  | NATURAL GAS |  | 536 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-06-23 12:49 |  |  |  | 2010-06-23 13:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1992 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.237 | [6 empty] | OTHER | [8 empty] | PIPE PULLED FROM WELDED FITTING. | CLASS 1 LOCATION |  | 0 | 48936 | 64649.81425306459704 |  | 0 |  | 0 |  |  | 2990 | 2065.906148867313915857605177993527508091 |  | 0 | 51926 | 28687.0982707970781504724919093851132686 | 66715.7204019319109558576051779935275081 | 0 | 1 | 4 |  |  |  |  | 400 | 400 | 800 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY DAMAGE | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | TRENCHER | TELECOMMUNICATIONS | YES | 16000098 | VIRGINIA UTILITY PROTECTION SERVICE ( VUPS ) |  | CONTRACT LOCATOR | NO | YES | 37 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | TIMOTHY BEELER | OPERATIONS COMPLIANCE MANAGER | tbeeler@nisource.com | 804-768-6404 | 804-768-5913 |  |  |  | TIMOTHY BEELER | OPERATIONS COMPLIANCE MANAGER | 804-768-6450 | tbeeler@nisource.com | ON JUNE 23, 2010 AT APPROXIMATELY 12:30 P.M. MICHEL'S CORPORATION STRUCK A COLUMBIA GAS OF VIRGINIA (CGV) 4" WELD TREATED HIGH PRESSURE (400 PSIG) PIPELINE WHILE EXCAVATING PERPENDICULAR TO THE FACILITY. AS A RESULT, SERVICE WAS LOST DOWNSTREAM TO FOUR (4) RESIDENTIAL AND ONE (1) INDUSTRIAL CUSTOMER FOR 37 1/2 HOURS. CREWS WORKED CONTINUOUSLY UNTIL REPAIRS WERE MADE AND SERVICE FULLY RESTORED ON 6/25/10 AT 4:10 A.M. UPON INVESTIGATION IT IS CONCLUDED THAT MICHEL'S CORPORATION HAD A VALID ONE CALL MISS UTILITY OF VIRGINIA LOCATE TICKET #B016000098 FOR THE AREA OF EXCAVATION. THIS LOCATE REQUEST WAS PERFORMED BY CONSOLIDATED UTILITY SERVICES ON 6/11/10. ULTIMATELY LOCATE TICKET #B016000098 WAS CLEARED IN THE MISS UTILITY OF VIRGINIA POSITIVE RESPONSE SYSTEM WITH A DISPOSITION OF "10" OR "MARKED". FURTHER INVESTIGATION REVEALED THAT ALTHOUGH CONSOLIDATED UTILITY SERVICES CLEARED OR CODED TICKET #B016000098 IT DID NOT MARK THE ENTIRE PARAMETER OF THE TICKET AS REQUESTED BY THE EXCAVATOR. AS A RESULT MICHEL'S CORPORATION PROCEEDED TO EXCAVATE WITHIN THE SCOPE OF THE TICKET, BUT BEYOND THE BOUNDS OF THE LOCATE MARKINGS PLACED BY CONSOLIDATED UTILITY SERVICES, WHICH ULTIMATELY RESULTED IN DAMAGE TO CGV'S PIPELINE.
2025-03-31 10:13 | YES | NO | NO | 20100059 | 15076 | 2010-07-27 13:32 | ORIGINAL | 17360 | RICHMOND, CITY OF | 730 E BROAD STREET 6TH FLOOR | RICHMOND | VA | 23219 | 2010-07-15 21:24 |  |  | 2010 | 3611 CROYDON ROAD | HENRICO | HENRICO | VA | 23223 | 37.565 | -77.3837 | [9 empty] | 2010-07-15 22:24 | 947882 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2010-07-15 21:55 |  |  |  | 2010-07-15 21:55 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | OTHER | CUSTOMER HOUSE LINE | OTHER | CUSTOMER HOUSE LINE | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | NO RELEASE OF GAS | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 120 | 158.5331394140868 | 0 | 0 |  |  | 0 | 0 |  | 0 | 120 | 65.65967172241848 | 158.5331394140868 | 0 | 0 | 1 |  |  |  |  | 21 | 21 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CARL V. JAMES | OPERATIONS MANAGER | carl.james@richmondgov.com | 804-646-8341 | 804-646-8399 |  |  |  | CARL V. JAMES | OPERATIONS MANAGER | 804-646-8341 | carl.james@richmondgov.com | JULY 16, 2010 OFFICE OF PIPELINE SAFETY PIPELINE AND HAZARDOUS MATERIALS SAFETY ADMIN. U.S. DEPARTMENT OF TRANSPORTATION INFORMATION RESOURCES MANAGER, PHP-10 1200 NEW JERSEY AVENUE, SE WASHINGTON, DC 20590-0001 RE: INCIDENT #947882 ' 3611 CROYDON ROAD, HENRICO, VA GENTLEMEN: THIS IS A FOLLOW-UP TO THE TELEPHONE CALL PLACED ON JULY 15, 2010 REGARDING INCIDENT #947882 WHICH OCCURRED AT 3611 CROYDON ROAD IN THE COUNTY OF HENRICO, VIRGINIA. THE INCIDENT, WHICH WAS REPORTED AT 22:24 ON THURSDAY 15, 2010, WAS A FIRE-FIRST INCIDENT AND NOT JURISDICTIONAL TO THE CITY OF RICHMOND, DEPARTMENT OF PUBLIC UTILITIES' GAS DISTRIBUTION SYSTEM. THIS CONCLUSION WAS REACHED AFTER CONFIRMING THAT THE FIRE STARTED ACCIDENTALLY IN A UTILITY CLOSET MORE THAN 15' FROM THE GAS METER. THE DAMAGE WAS CONTAINED TO THE UTILITY CLOSET AND THE CARPORT AREA OF THE STRUCTURE. ALL GAS PIPING WAS FOUND IN TACT AND GAS TIGHT. WHILE THE DAMAGE MAY HAVE REACHED THE $50,000 REPORTING THRESHOLD IT WAS DETERMINED BY MR. BILLY GARRETT OF HENRICO FIRE DEPARTMENT THAT NATURAL GAS WAS NOT INVOLVED. THE CITY OF RICHMOND, DEPARTMENT OF PUBLIC UTILITIES, PERFORMED A LEAK SURVEY OF THE OUTER PERIMETER OF THE BUILDING AND PRESSURE TESTED THE SERVICE LINE, AND NO LEAKAGE WAS FOUND. ALSO AT THE TIME, THE CITY OF RICHMOND, DEPARTMENT OF PUBLIC UTILITIES, HAD AN ODOROMETER TEST PERFORMED BY THE SUPERVISOR OF PRESSURE CONTROL. THIS TEST FOUND THE ODORANT TO BE IN THE ACCEPTABLE RANGE. BASED ON THE ABOVE FINDINGS, THE CITY OF RICHMOND CONCLUDES THERE WAS NO REPORTABLE INCIDENT. SINCERELY, CARL V. JAMES OPERATIONS MANAGER-GAS DISTRIBUTION 804/646-8341 CARL.JAMES@RICHMONDGOV .COM C: MIKE BELLMAN, DEPUTY DIRECTOR II, GAS & LIGHT BRIAN ROBERTS STATE CORPORATION COMMISSION
2025-03-31 10:13 | NO | NO | NO | 20100060 | 15081 | 2010-08-11 01:49 | ORIGINAL FINAL | 18112 | SAN DIEGO GAS & ELECTRIC CO | 8326 CENTURY PARK COURT | SAN DIEGO | CA | 92123 | 2010-07-25 17:00 |  |  | 2010 | 8136 CALICO STREET | SAN DIEGO | SAN DIEGO | CA | 92126 | 32.9087 | -117.1483 | [12 empty] | NATURAL GAS |  | 94 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 5 | 2010-07-25 17:00 |  |  |  | 2010-07-25 17:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1973 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | OTHER | 3/4" RISER SEVERED BELOW STOPCOCK |  |  |  | CLASS 3 LOCATION | 0 | 0 | 500 | 660.554747558695 | 250 | 330.2773737793475 |  | 0 |  |  | 550 | 380.016181229773462783171521035598705502 |  | 0 | 1300 | 761.910165093594464401294498381877022654 | 1370.848302567815962783171521035598705502 | 0 | 0 | 2 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | W. JEFF KOSKIE | PIPELINE SAFETY ADVISOR | wkoskie@semprautilities.com | 213 305-8660 | 213 244-8155 |  |  |  | W. JEFF KOSKIE | PIPELINE SAFETY ADVISOR | 213 305-8660 | wkoskie@semprautilities.com | ON JULY 25, 2010 A METER SET ASSEMBLY WAS DAMAGED WHEN A DRIVER LOST CONTROL OF HIS VEHICLE ON THE ROADWAY, CRASHING INTO A HOUSE, COMING TO REST ON A METER SET ASSEMBLY AND SHEERING THE RISER BELOW THE STOPCOCK. ESCAPING GAS FROM THE DAMAGED METER SET ASSEMBLY IGNITED, CAUSING OVER $50K DAMAGE TO THE HOME. ALTHOUGH THE DRIVER WAS INJURED FROM THE CRASH INTO THE HOME, NO INJURIES WERE ATTRIBUTED IN ANY WAY TO THE ESCAPING GAS OR RESULTING FIRE. THIS INCIDENT BECAME REPORTABLE TO THE DOT AND CPUC BASED UPON THE DOLLAR VALUE OF THE FIRE.
2025-03-31 10:13 | NO | YES | YES | 20100061 | 15084 | 2010-08-13 16:16 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2010-07-15 13:55 |  |  | 2010 | BIRMINGHAM HWY. @ TRAMORE PLACE | MILTON | FULTON | GA | 30004 | 34.1153 | -84.3388 | [9 empty] | 2010-07-15 16:19 | 947843 |  | NATURAL GAS |  | 210 |  | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2010-07-15 14:15 |  |  |  | 2010-07-15 14:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1988 | [5 empty] | 4 | PE 2406 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1.5 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 33886 | 44767.11635154787754 | 0 | 0 |  |  | 1362 | 941.058252427184466019417475728155339806 |  | 0 | 35248 | 19411.7309471314627158446601941747572816 | 45708.1746039750620060194174757281553398 | 0 | 0 | 47 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE ON THE MHP MAIN INVOLVED IN THE INCIDENT WAS CONTROLLED BY A LOCAL PRESSURE REGULATING STATION. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | STATE HIGHWAY | [12 empty] | UTILITY | AUGER | ELECTRIC | NO |  |  |  | UNKNOWN/OTHER | NO | YES | 8 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | WILLIAM HORNE | REGULATORY COMPLIANCE ENGINEER | bhorne@aglresources.com | 4045843153 | 4045844807 |  |  |  | RICHARD LONN | DIRECTOR - REGULATORY COMPLIANCE | 4045843522 | rlonn@aglresources.com | AN ELECTRIC UTILITY WAS INSTALLING A POWER POLE AT THE LOCATION OF THE INCIDENT AND AUGERED INTO A PLASTIC NATURAL GAS LINE CAUSING A RELEASE OF GAS. THE GAS IGNITED, AND AN ELECTRIC UTILITY EMPLOYEE IN A CRANE BUCKET ABOVE THE DAMAGE WAS BURNED AND REQUIRED HOSPITALIZATION. THERE WAS NO REQUEST MADE FOR A UTILITY MARK-OUT IN THE EXCAVATION AREA PRIOR TO EXCAVATION. A SUPPLEMENTAL REPORT IS REQUIRED BECAUSE THE ELECTRIC UTILITY EMPLOYEE HOSPITALIZED AS A RESULT OF THIS INCIDENT PASSED AWAY DUE TO INJURIES SUSTAINED IN THE INCIDENT. THE DEATH OCCURRED AFTER SUBMISSION OF THE INITIAL INCIDENT REPORT.
2025-03-31 10:13 | YES | NO | NO | 20100062 | 15530 | 2010-08-17 20:38 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2010-07-30 06:49 |  |  | 2010 | 890 E 59TH STREET | LOS ANGELES | LOS ANGELES | CA | 90001 | 33.9868 | -118.2596 | [9 empty] | 2010-07-30 10:00 | 949395 |  | NATURAL GAS |  | 0 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 100 | 2010-07-30 07:59 |  |  |  | 2010-07-30 08:08 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | ILLEGAL BYPASS |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | ILLEGAL BYPASS | 2010 | [8 empty] | OTHER | ILLEGAL COPPER BYPASS | [9 empty] | OTHER | [8 empty] | ILLEGAL BYPASS ALLOWING GAS TO ENTER OVEN AT 54 PSI | CLASS 3 LOCATION | 0 | 0 | 1000 | 1321.10949511739 | 1000 | 1321.10949511739 | 0 | 0 |  |  | 0 | 0 |  | 0 | 2000 | 1094.327862040308 | 2642.21899023478 | 0 | 0 | 0 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | JEFF KOSKIE | PIPELINE SAFETY ADVISOR | wkoskie@semprautilities.com | 213-305-8660 | 213-244-8155 |  |  |  | JEFF KOSKIE | PIPELINE SAFETY ADVISOR | 213-305-8660 | wkoskie@semprautilities.com | ON JULY 30, AT APPROXIMATELY 6:50 AM, AN EXPLOSION OCCURRED AT THIS LOCATION. ONE PERSON DIED FROM ELECTROCUTION AS A RESULT OF COMING IN CONTACT WITH DOWNED POWER LINES. A SECOND WAS HOSPITALIZED FROM INJURIES RESULTING FROM THE EXPLOSION. INVESTIGATION DETERMINED THAT THE METER SET ASSEMBLY HAD BEEN CLOSED AND LOCKED THE PREVIOUS DAY FOR NONPAYMENT. UPON OUR ARRIVAL AFTER THE INCIDENT, AN ILLEGAL BYPASS WAS DISCOVERED WHICH ALLOWED GAS TO ENTER THE HOUSELINE AT APPROXIMATELY 54 PSI. THE ILLEGAL BYPASS DID NOT PASS THROUGH THE EXISTING REGULATOR WHICH WOULD LOWER HOUSELINE PRESSURE TO APPROXIMATELY 1/3 PSI. SURVEILLANCE TAPES INDICATE THAT THE TWO PERSONS ELECTROCUTED AND INJURED WERE PERFORMING SOME SORT OF ACTIVITIES AT THE METER SET ASSEMBLY LOCATION MINUTES BEFORE THE EXPLOSION. GAS LOST ESTIMATES HAVE NOT BEEN CALCULATED AT THIS TIME DUE TO LIMITED ACCESS TO SITE. METER SET ASSEMBLY AND SERVICE PIPING HAVE BEEN REMOVED, PENDING RECONSTRUCTION OF DAMAGED BUILDING.
2025-03-31 10:13 | NO | NO | NO | 20100064 | 15085 | 2010-08-18 23:15 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHGTREE PLACE | ATLANTA | GA | 30302 | 2010-07-15 11:37 |  |  | 2010 | 1065 BRIARCLIFF ROAD | ATLANTA | DEKALB | GA | 30306 | 33.7831 | -84.3424 | [9 empty] | 2010-07-19 16:45 | 948218 |  | NATURAL GAS |  | 665.52 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-07-15 11:37 |  |  |  | 2010-07-15 11:50 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1924 | [5 empty] | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | MECHANICAL PUNCTURE |  | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 37843 | 49994.74662372738977 | 15390 | 20331.8751298566321 |  | 0 |  |  | 6071 | 4194.687702265372168284789644012944983819 |  | 0 | 59304 | 33007.5092552062138690550161812297734628 | 74521.3094558493940382847896440129449838 | 1 | 0 | 184 |  |  |  |  | 13 | 13 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | NATURAL GAS | YES | 6290301780 | UTILITY PROTECTION CENTER |  | CONTRACT LOCATOR | NO | YES | 9 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | RALPH T MCCOLLUM | SENIOR COMPLIANCE ENGINEER | rmccollu@aglresources.com | (404) 584-3733 | (404) 584-4708 |  |  |  | RICHARD R LONN | DIRECTOR REGULATORY COMPLIANCE | (404) 584-3552 | rlonn@aglresources.com | COMPANY'S CONTRACTOR WAS REPLACING EXISTING 12-INCH CAST IRON MAIN BY DIRECTIONAL BORING WHEN A 4-INCH CAST IRON STUB WAS BROKEN DURING THE BACK REAMING PROCESS.
2025-03-31 10:13 | NO | NO | NO | 20100065 | 15086 | 2010-08-20 08:09 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2010-05-20 14:08 |  |  | 2010 | 615 CLAFLIN AVE | VILLAGE OF MAMARONECK | WESTCHESTER | NY | 10543 | 40.9489 | -73.7026 | [12 empty] | NATURAL GAS |  | 3.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2010-05-20 14:08 |  |  |  | 2010-05-20 14:08 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1948 | [5 empty] | 2 | SCHEDULE 40 | UNKNOWN | STEEL |  |  |  | 0.154 | [6 empty] | OTHER | [8 empty] | REMOVAL OF STEEL TAPERED PLUG IN SERVICE TEE. | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 17900 | 23647.859962601281 | 0 | 0 |  |  | 15 | 10.36407766990291262135922330097087378641 |  | 0 | 17915 | 9803.821743901533299029126213592233009709 | 23658.2240402711839126213592233009708738 | 0 | 0 | 4 |  |  |  |  | 12 | 12 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | KEVIN FAGAN | OPERATING GENERAL SUPERVISOR | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | KEVIN FAGAN | OPERATING GENERAL SUPERVISOR | 718-319-2310 | fagank@coned.com | AT 1408 HRS ON 5/20/2010 THE VILLAGE OF MAMARONECK FIRE DEPARTMENT ADVISED THE GERC OF A POSSIBLE EXPLOSION WITH GAS INVOLVEMENT. THE GERC DISPATCHED A GDS MECHANIC AND SUPERVISOR, GAS CONSTRUCTION AND A GAS ERG. GDS RESPONDED AND REPORTED THAT A GAS CONSTRUCTION CREW WAS ON LOCATION WORKING AN EXISTING TYPE 2 LEAK. THE INVESTIGATION INDICATED THAT THE CREW WAS PREPARING TO INSTALL AN EXPANSION STOPPER IN A 2" STEEL SERVICE TEE ON A 4" MEDIUM PRESSURE STEEL MAIN WHEN THE GAS IGNITED. TWO GAS CONSTRUCTION MECHANICS WERE TAKEN VIA EMS TO SOUNDSHORE HOSPITAL WHERE THEY WERE TREATED AND RELEASED. MECHANIC A RECEIVED SECOND DEGREE BURNS, WHICH WERE SEVERAL INCHES IN LENGTH TO HIS FOREARMS. MECHANIC B SUSTAINED A SECOND DEGREE BURN, WHICH WAS ALSO SEVERAL INCHES IN LENGTH TO HIS RIGHT FOREARM AND A SMALL FIRST DEGREE BURN NEAR THE BACK OF HIS NECK. THE MECHANICS WERE BOTH BROUGHT TO CON EDISON'S RYE SERVICE CENTER FOR DRUG AND ALCOHOL TESTING AND BOTH MEHANICS TESTED NEGATIVE. CHANNEL 12 NEWS ARRIVED ON LOCATION AT 14:56, THE LEAK WAS TEMPORARILY SECURED AT 15:10 AND THE AREA WAS MADE SAFE. CREWS THEN INSTALLED A MECHANICAL CONTROL FITTING, INSERTED AN EXPANSION STOPPER AND CLOSED ONE MAIN VALVE AT 20:15 TO ISOLATE THE MAIN, INTERRUPTING SERVICE TO FOUR (4) RESIDENTIAL CUSTOMERS. THE SECTION OF MAIN IN THE EXCAVATION WAS REMOVED AND TAKEN TO THE GAS DEVELOPMENT LAB FOR ANALYSIS. THE GAS WAS BACK ON LINE AT 21:50 AND SERVICE WAS RESTORED TO THE AFFECTED CUSTOMERS. AN ICS STRUCTURE WAS ESTABLISHED AND THE COMMAND POST WAS LOCATED IN FRONT OF 611 CLAFLIN AVE. THIS WAS AN UPGRADED LEVEL INCIDENT.
2025-03-31 10:13 | YES | NO | NO | 20100066 | 15089 | 2010-08-24 09:51 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2010-07-25 16:04 |  |  | 2010 | 422 SISSON COURT | SILVER SPRING | MONTGOMERY | MD | 20902 | 39.0427 | -77.1787 | [9 empty] | 2010-07-25 21:24 | 948843 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2010-07-25 16:04 |  |  |  | 2010-07-25 16:29 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1996 | [8 empty] | OTHER | CAST ALUMINUM | [9 empty] | OTHER | [8 empty] | OUTSIDE METER DAMAGED BY FIRE. | CLASS 3 LOCATION |  | 0 |  | 0 | 3200 | 4227.550384375648 | 50000 | 66055.4747558695 | APPROXIMATE VALUE OF DAMAGES TO THE BUILDING CAUSED BY THE FIRE. |  | 5 | 3.45469255663430420711974110032362459547 |  | 0 | 53205 | 29112.3169231524516996763754045307443366 | 70286.4798328017823042071197411003236246 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MICHAEL UPSHAW | SUPERVISOR - DOT PIPELINE SAFETY COMPLIANCE | mupshaw@washgas.com | 703-750-4479 | 703-750-5591 |  |  |  | DAVID W. SPANGLER | MANAGER - DOT PIPELINE SAFETY COMPLIANCE | 703-750-4341 | dspangler@washgas.com | WASHINGTON GAS RECEIVED A CALL FROM THE MONTOGOMERY COUNTY FIRE BOARD AT 16:04 ON SUNDAY, JULY 25, 2010. THIS CALL WAS FOR 11507 LOVEJOY STREET, SILVER SPRING, MD. WASHINGTON GAS ARRIVED AT 16:29. WHILE ON SITE, THE FIRE DEPARTMENT MADE WASHINGTON GAS AWARE OF A FIRE AT 422 SISSON COURT, SILVER SPRING, MD. WASHINGTON GAS FOUND THE METER VALVE AT 422 SISSON COURT, SILVER SPRING, MD, HAD BEEN TURNED OFF BY THE FIRE DEPARTMENT. AFTER THE FIRE WAS EXTINGUISHED AND WASHINGTON GAS WAS ABLE TO GET CLOSER, IT WAS DETERMINED THAT THEY HAD SUFFERED DAMAGE TO THEIR METER. IT IS BELIEVED THAT THE DAMAGE TO THE HOUSE IS GREATER THAN $50,000. WASHINGTON GAS CONDUCTED A BAR AND TEST SURVEY AROUND THE PERIMETER OF 422 SISSON COURT AND OVER THE SERVICE ON THE EVENING OF JULY 25, 2010. NO LEAK INDICATIONS WERE DISCOVERED DURING THIS SURVEY. ON MONDAY, JULY 26, 2010, WASHINGTON GAS CONDUCTED A LEAK SURVEY OF THE ENTIRE QUAD. ONE GRADE 3 LEAK WAS FOUND AT 300 HILLSBORO DRIVE. A SEVERE ELECTRICAL STORM MOVED THROUGH THE AREA ON THE EVENING OF JULY 25, 2010, AND CAUSED SIGNIFICANT DAMAGE (DOWNED TREES, ELECTRIC LINES, LOSS OF POWER, ETC.). WASHINGTON GAS SUFFERED DAMAGE TO THEIR FACILITIES AS A RESULT OF A HOUSE FIRE.
2025-03-31 10:13 | NO | NO | NO | 20100067 | 16329 | 2010-08-31 12:32 | SUPPLEMENTAL FINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2010-08-26 11:19 |  |  | 2010 | 7812 EVANS STREET | OMAHA | DOUGLAS | NE | 68134 | 41.292 | -96.0339 | [9 empty] | 2010-08-26 14:17 | 952204 |  | NATURAL GAS |  | 12582 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-08-26 11:58 |  |  |  | 2010-08-26 12:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | IN OTHER ENCLOSED SPACE |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1998 | [5 empty] | 0.621 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | UNKNOWN | OTHER | [8 empty] | GAS SERVICE WAS DAMAGED FROM VEHICLE ACCIDENT | CLASS 1 LOCATION | 0 | 0 | 4000 | 5284.43798046956 | 987 | 1303.93507168086393 | 56000 | 73982.13172657384 | VIDE NODE BOX REPAIRS, VEHICLE LOSS |  | 57 | 39.38349514563106796116504854368932038835 |  | 0 | 61044 | 33406.3186999610834543106796116504854369 | 80609.8882738698949979611650485436893204 | 1 | 0 | 0 |  |  |  |  | 15 | 15 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE OCCURRED FROM OUTSIDE SOURCE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MIKE PALMESANO | CLAIMS MANAGER | mike_palmesano@mudnebr.com | 402-504-7108 | 402-504-5108 |  |  |  | MIKE PALMESANO | CLAIMS MANAGER | 402-504-7108 | mike_palmesano@mudnebr.com | THE RESPONSIBLE PARTY, SANDRA FABER, WAS REACHING FOR HER CELL PHONE AND FAILED TO MAKE A CURVE IN THE ROADWAY. SHE THEN STRUCK A VIDEO NODE BOX AND SEVERED THE GAS SERVICE TO THE VIDOE NODE BOX. THERE WAS AN IGNITION OF NATURAL GAS FROM THE ARCING OF THE RESERVE BATTERY CELLS, THIS WAS EXTINGUISHED BY THE OMAHA FIRE DEPARTMENT. 11/23/10- ON 9/7/10 THE GAS SERVICE TO 7812 EVANS WAS RECONNECTED AND BACK IN SERVICE. THE OUTCOME OF THE INVESTIGATION WAS THE DAMAGE WAS FROM THE MOTOR VEHICLE ACCIDENT AS CAPTIONED ABOVE. OUR FILE IS CLOSED IN REGARD TO THIS MATTER.
2025-03-31 10:13 | NO | NO | NO | 20100068 | 15093 | 2010-04-27 | ORIGINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2010-03-15 10:28 |  |  | 2010 | 104 E ELM DR | ELM MOTT | MCLENNAN | TX | 76640-9761 | 31.6716 | -97.1003 | [9 empty] | 2010-03-15 12:55 | 934009 |  | NATURAL GAS |  | 1363 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 150 | 2010-03-15 10:28 |  |  |  | 2010-03-15 11:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 32 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1977 | [5 empty] | 0.2 | ASTM D2513 | DRISCOLL | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | 2406 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION |  | 0 | 953 | 1259.01734884687267 |  | 0 |  | 0 |  |  | 119 | 82.22168284789644012944983818770226537217 |  | 0 | 1072 | 597.507096812368574297734627831715210356 | 1341.239031694769110129449838187702265372 | 1 | 0 | 0 |  |  |  |  | 10 | 10 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | HARRY JAMES FULLER | OPERATIONS SUPERVISOR | harry.fuller@atmosenergy.com | 2542242797 |  |  |  |  | MARC CHAPMAN | COMPLIANCE DIRECTOR | 2142062875 | marcus.chapman@atmosenergy.com | TXDOT HAD INSTALLED A 3" PVC PIPE OVER ATMOS' MAIN TO GET DEPTH SHOT ON THE MAIN. A CAR DROVE OVER THE PVC PIPE, SHOVING IT DOWN ON TOP OF A 2" POLY TEE CAUSING IT TO CRACK AT SOCKET FUSHION.
2025-03-31 10:13 | NO | YES | NO | 20100069 | 15640 | 2010-09-09 15:30 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD. NE. STE 20 | ALBUQUERQUE | NM | 87109 | 2010-08-11 17:45 |  |  | 2010 | INTERSECTION OF SQUAW RD. NW AND CALLE NORTENA | ALBUQUERQUE | BERNALILLO | NM | 87114 | 35.1796 | -106.6823 | [9 empty] | 2010-08-11 19:28 | 950686 |  | NATURAL GAS |  | 653 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-08-11 17:45 |  |  |  | 2010-08-11 18:01 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2007 | [5 empty] | 6.625 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.602 |  | 3408 | LEAK |  |  | OTHER | PIPE MELTED | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 9200 | 12154.207355079988 | 570 | 753.0324122169123 | 105000 | 138716.49698732595 | $75,000 - CONT.R BACKHOE $15,000 - ELEC. CO. $15,000 - PHONE CO.+ CABLE CO. |  | 3224 | 2227.585760517799352750809061488673139159 |  | 0 | 117994 | 64858.6516123740130913268608414239482201 | 153851.3225151406496527508090614886731392 | 0 | 0 | 12 |  |  |  |  | 56 | 56 | 56 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER ACTIONS OR CONTROL ROOM ISSUES WERE NOT INVOLVED IN THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | GARY G. ROYBAL | MANAGER DOT PIPELINE SAFETY COMPLIANCE | gary.roybal@nmgco.com | 505-697-3636 | 505-697-4481 |  |  |  | ED KACER | VP TECHNICAL SERVICES | 505-697-3303 | ed.kacer@nmgco.com | A CONTRACTOR WORKING FOR THE LOCAL ELECTRIC COMPANY EXPOSED NMGC'S 6IN PLASTIC MAINLINE, ELECTRICAL LINES, PHONE LINES AND CABLE LINES TO PERFORM WORK ON THE ELECTRICAL SYSTEM ON THE WESTSIDE OF ABQ. THE TRENCH WAS APPROX. 6'DX6'WX40'L AND THE MAIN WAS EXPOSED APPROX. 2.5' OFF THE GROUND AND SPANNED THE LENGTH OF THE TRENCH. ON AUG. 11, 2010, NMGC WAS NOTIFIED OF A FIRE AT THIS LOCATION. IT IS UNKNOWN HOW GAS WAS RELEASED FROM THE MAIN OR HOW IGNITION OCCURRED. THERE APPEARED TO BE NO ACTIVE EXCAVATION ACTIVITIES AT THE TIME OF THE INCIDENT. THE TRENCH WAS OPEN FOR AT LEAST 6 DAYS, IF NOT LONGER. THERE WAS AN ELECTRICAL FAULT THAT OCCURED IN THIS AREA ON THE AFTERNOON OF THE FIRE BUT IT IS INCONCLUSIVE WHETHER THIS WAS A FACTOR IN THE RELEASE OF GAS AND SUBSEQUENT IGNITION. ALL FACILITIES IN THE TRENCH MELTED AND A BACKHOE WAS BURNED (TOTALLED). NMGC PERFORMED A BARHOLE SURVEY UPSTREAM AND DOWNSTREAM OF THE LEAK AND NO GAS WAS DETECTED. NMGC WORKED WITH THE NM PIPELINE SAFETY BUREAU ON THE INVESTIGATION. THERE IS NO CONCLUSIVE EVIDENCE ON WHAT CAUSED THE RELEASE OF GAS AND SUBSEQUENT IGNITION. POSSIBLE CAUSES INCLUDE MECHANICAL DAMAGE TO THE PIPELINE, VANDALISM, ELECTRICAL MALFUNCTION OR A COMBINATION OF THESE SCENARIOS.
2025-03-31 10:13 | NO | YES | NO | 20100070 | 15235 | 2010-09-10 11:10 | SUPPLEMENTAL FINAL | 4060 | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2010-08-10 22:15 |  |  | 2010 | 1136 CARVER RD | CLEVELAND HEIGHTS | CUYAHOGA | OH | 44112 | 41.5252 | -81.5622 | [9 empty] | 2010-08-11 02:58 | 950558 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2010-08-10 22:25 |  |  |  | 2010-08-10 22:36 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1951 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | CORROSION LEAK AT THREADS | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 1000 | 1321.10949511739 | 5000 | 6605.54747558695 | 150000 | 198166.4242676085 | APPROXIMATELY $150,000 IN PROPERTY DAMAGES TO THE HOME |  | 6 | 4.14563106796116504854368932038834951456 |  | 0 | 156006 | 85361.4081906003346796116504854368932039 | 206097.2268693808011650485436893203883495 | 0 | 0 | 1 |  |  |  |  | 0.5 | 0.5 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | NO | NONE | [21 empty] | 2008-08-21 | NO | [227 empty] | STEVEN W. BUCK | TECHNICAL CONSULTANT | steven.w.buck@dom.com | 330-401-8033 | 866-521-4877 |  |  |  | STEVEN W. BUCK | TECHNICAL CONSULTANT | 330-401-8033 | steven.w.buck@dom.com | ON AUGUST 10, 2010 A HOME LOCATED AT 1136 CARVER RD, CLEVELAND HEIGHTS, OH WAS INVOLVED IN A FIRE. THE SERVICE LINE ENTERS THE HOME UNDERGROUND THROUGH THE GARAGE FLOOR TO A GAS METER LOCATED IN THE GARAGE. THE HOMEOWNER STATED THAT HE HAD SMELLED AN ODOR OF GAS IN THE EARLY MORNING BUT DISMISSED IT AS FUEL LEAKING FROM ONE OF THE CARS IN THE GARAGE. HOMEOWNER LEFT THE HOME FOR THE DAY AND RETURNED LATE EVENING ONCE AGAIN SMELLING AN ODOR OF GAS. HOMEOWNER NOTIFIED THE FIRE DEPARTMENT AND DOMINION OF THE ODOR AT APPROXIMATELY 22:15 THAT EVENING. FIRE DEPARTMENT ARRIVED AT THE SCENE AT 22:21 AND OBSERVED A FIRE IN THE GARAGE AND ATTIC OF THE STRUCTURE. DOMINION WAS NOTIFIED OF THE FIRE IMMEDIATELY AND ARRIVED ON SCENE AT 22:36. BURNING GAS WAS OBSERVED AT CRACKS BETWEEN THE GARAGE FLOOR/GARAGE WALL AND IN THE ATTIC SPACE ABOVE GAS METER. GAS WAS SHUT OFF AT THE CURB VALVE AT APPROXIMATELY 22:45. ON AUGUST 11, 2010 DOMINION TESTED THE SERVICE LINE AT 7 OUNCES OPERATING PRESSURE, SERVICE FAILED TO HOLD PRESSURE. ON AUGUST 11, 2010, THE INSURANCE INVESTIGATOR ALONG WITH DOMINION AND THE FIRE INVESTIGATOR REMOVED A PORTION OF THE SERVICE LINE FROM THE GAS METER TO OUTSIDE THE GARAGE WALL FOR FURTHER INVESTIGATION. ON NOVEMBER 30, 2010, THE INSURANCE INVESTIGATOR ALONG WITH DOMINION PERFORMED TESTING OF THE PORTION OF SERVICE LINE REMOVED. RESULTS INDICATE GENERAL CORROSION AT A THREADED JOINT OF PIPE AND A 90 DEGREE ELBOW CAUSING THE LEAKAGE.
2025-03-31 10:13 | NO | NO | NO | 20100071 | 16330 | 2010-09-20 16:38 | SUPPLEMENTAL FINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2010-09-18 06:30 |  |  | 2010 | 21021 W CIRCLE | OMAHA | DOUGLAS | NE | 68022 | 41.2005 | -96.2426 | [9 empty] | 2010-09-18 08:20 | 954450 |  | NATURAL GAS |  | 9868 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-09-18 06:45 |  |  |  | 2010-09-18 08:00 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 14 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 2010 | [5 empty] | 0.621 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | UNKNOWN | OTHER | [8 empty] | LIGHTNING STRUCK DWELLING AND WE SUSPECT GAS LEAK RESULTED FROM LIGHTNING STRIKE. | CLASS 1 LOCATION | 0 | 0 | 1000 | 1321.10949511739 | 500 | 660.554747558695 | 60000 | 79266.5697070434 | DWELLING DAMAGE FROM LIGHTNING STRIKE |  | 35 | 24.18284789644012944983818770226537216828 |  | 0 | 61535 | 33672.952307901283297734627831715210356 | 81272.4167976159251294498381877022653722 | 0 | 0 | 0 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SUSPECT DAMAGE WAS CAUSED BY LIGHTNING STRIKE. SIZE OF LEAK WAS SO SMALL THAT IT WAS NOT DETECTABLE BY SCADA. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | INTENSE HEAT FROM BURNING DEBRIS FROM DWELLING | [154 empty] | MICHAEL CONRAD | CLAIMS ADJUSTER | mike_conrad@mudnebr.com | 402-504-7165 | 402-504-5165 |  |  |  | MICHAEL CONRAD | CLAIMS ADJUSTER | 402-504-7165 | mike_conrad@mudnebr.com | ON SATURDAY SEPTEMEBER 18, 2010 THE DWELLING UNDER CONSTRUCTION AT 21021 W CIRCLE WAS APPARANTLY STRUCK BY LIGHTNING AT APPROXIAMTELY 0630HRS., THE GAS SERVICE TO THE DWELLING SUFFERED A GAS FAILURE BELOW GROUND AT APPROXMATELY 14" FROM THE SERVICE RISER AND IGNITED FROM THE EXTENSE HEAT FROM THE FIRE. THE OMAHA FIRE DEPARTMENT EXTINGUISHED THE FIRE ON BOTH THE SERVICE AND THE DWELLING. 2/13/12- OUR INVESTIGATION ASSISTED BY THE NENRASKA STATE FIRE MARSHAL'S OFFICE HAS DETERMINED THAT FAILURE OF THE TRANMISSION LINE WAS DIRECTLY RELATED TO INTENSE HEAT THAT WAS GENERATED FROM THE BURNIING DEBRIS THAT FELL FROM THE DWELLING. THE METROPOLITAN UTILITIES DISTRICT HAS CLOSED IT'S INVESTIGATION AND FILE IN REGARD TO THIS MATTER. 6/15/12- OUR INVESTIGATON REVEALED THAT THE DAMAGE/LOSS WAS THE DIRECT RESULT FROM THE INTENSE HEAT FROM THE BURNING DEBRIS THAT FELL FROM THE DWELLING ONTO THE METER SET AND GROUND SURROUNDING THE METER SET, THIS BURNING DEBRIS CAUSED THE GAS SERVICE TO MELT INSIDE THE PIGTAIL OF THE SERVICE RISER AND THE RELEASE OF THE NATURAL GAS.
2025-03-31 10:13 | YES | NO | NO | 20100072 | 15113 | 2010-09-22 13:15 | SUPPLEMENTAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2010-08-24 17:15 |  |  | 2010 | 825 OAK KNOLL DR | ASHLAND | JACKSON | OR | 97520 | 42.18 | -122.6616 | [9 empty] | 2010-08-24 20:15 | 952036 |  | NATURAL GAS |  | 114 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 100 | 2010-08-24 17:15 |  |  |  | 2010-08-24 17:29 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | HEAT FROM FIRE MELTED THE REGULATOR AND METER BODIES. | CLASS 3 LOCATION | 0 | 0 | 2040 | 2695.0633700394756 | 3117 | 4117.89829628090463 |  | 0 |  |  | 586 | 404.889967637540453074433656957928802589 |  | 0 | 5743 | 3196.271317837277220071197411003236245955 | 7217.851633957920683074433656957928802589 | 0 | 0 | 8 |  |  |  |  | 20 | 20 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | JEFF WEBB | SR. GAS DISTRIBUTION ENGINEER | jeff.webb@avistacorp.com | 509-495-4424 | 509-777-9381 |  |  |  | JODY MOREHOUSE | CHIEF GAS ENGINEER | 509-495-2760 | jody.morehouse@avistacorp.com | THIS REPORT ADDRESSES THE TELEPHONIC REPORT THAT JODY MOREHOUSE MADE TO YOU ON AUGUST 26TH, 2010 AT 20:15. ON THAT DAY AT 17:15, AVISTA WAS NOTIFIED OF A FIRE AT 825 OAK KNOLL DR. IN ASHLAND, OR (JACKSON COUNTY). THIS WAS REPORTED TO DOT BECAUSE OF THE RELEASE OF GAS COMBINED WITH THE TOTAL COST OF THE INCIDENT BEING IN EXCESS OF $50,000. AN AVISTA FIRST RESPONDER ARRIVED ON SITE AT 17:30 BUT WAS UNABLE TO GET TO THE HOMES DUE TO THE FIRE. A TWO INCH STEEL DISTRIBUTION MAIN WAS SQUEEZED TO SHUT OFF GAS TO THE AREA AT 21:37, THIS SHUT OFF GAS SERVICE TO EIGHT HOMES. GAS SERVICE WAS RESTORED TO FIVE OF THE HOMES BY 12:29 ON SEPTEMBER 3RD, 2010. THE OTHER THREE SERVICES WERE NOT RESTORED BECAUSE THE HOMES AND THEIR METER SETS WERE DESTROYED IN THE FIRE. NO FURTHER DAMAGE OCCURRED TO OUR SYSTEM AS A RESULT OF THIS INCIDENT. GAS WAS A CONTRIBUTING FACTOR, BUT NOT THE CAUSE OF THE FIRE. THE CAUSE OF THE BLAZE IS BELIEVED TO BE A GRASS FIRE FROM A NEARBY FIELD. PER THE LOCAL FIRE DEPARTMENT; 30-40 HOMES WERE EVACUATED, 11 HOMES WERE DESTROYED, NO FATALITIES OR HOSPITALIZATIONS. THE TOTAL COST OF THE INCIDENT IS ESTIMATED AT $4,405,743 (11 HOMES LOST, WORTH APPROX $400,000 EACH + AVISTA COSTS OF $5,743 FROM PART D). THE COST OF THE REPLACEMENT OF THE HOMES IS AN ESTIMATE BECAUSE THIS IS PRIVATE INFORMATION BETWEEN THE INSURANCE COMPANIES AND THE HOMEOWNERS.
2025-03-31 10:13 | NO | NO | NO | 20100073 | 15101 | 2010-09-24 18:52 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-08-19 14:17 |  |  | 2010 | 17979 LA BARRANCA RD. | LOS ALTOS | SANTA CLARA | CA | 94022 | 37.3694 | -122.146 | [9 empty] | 2010-09-17 19:29 | 954420 |  | NATURAL GAS |  | 27 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-08-19 14:30 |  |  |  | 2010-08-19 15:21 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 6 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1967 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | THIRD PARTY DIG-IN | CLASS 3 LOCATION | 0 | 0 | 10900 | 14400.093496779551 | 0 | 0 | 50000 | 66055.4747558695 | US MAIL TRUCK AND CONTENTS DESTROYED |  | 100 | 69.09385113268608414239482200647249190939 |  | 0 | 61000 | 33386.1992567325565935275080906148867314 | 80524.6621037817370841423948220064724919 | 0 | 0 | 1 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  | YES | [6 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | WATER | YES | 206708 | USA NORTH |  | UTILITY OWNER | YES | YES | 11 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | LAURENCE DENISTON |  | lcd1@pge.com | 925 974 4313 |  |  |  |  | GLEN CARTER |  |  | No Email Address | AT APPROXIMATELY 14:17 HOURS ON 8/19/10 A 3RD-PARTY CONTRACTOR WORKING FOR THE TOWN OF LOS ALTOS HILLS STRUCK AND CAUSED TO LEAK A 3/4-INCH STEEL GAS SERVICE WHILE USING A CONCRETE SAW TO CUT THROUGH PAVEMENT TO REPAIR A WATER MAIN AT 17979 LA BARRANCHA ROAD. THE CONTRACTOR HAD A VALID USA TICKET, THE AREA WAS PROPERLY DELINEATED AND THE UNDERGROUND FACILITIES WERE CORRECTLY MARKED. THE 3/4-INCH SERVICE, WHICH WAS INSTALLED IN 1967, WAS APPROXIMATELY 6-INCHES BELOW THE SURFACE OF THE PAVEMENT. THE CONTRACTOR HAD PUT TRAFFIC CONES OVER THE AREA OF LEAKING GAS PRIOR TO THE ARRIVAL OF PG&E. AT APPROXIMATELY 15:21 A GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SCENE. SHORTLY THEREAFTER, A US POSTAL SERVICE TRUCK WAS DRIVING TOWARD THE LOCATION OF THE GAS LEAK. PERSONNEL ON SCENE WAIVED TO THE POSTAL WORKER DRIVING THE TRUCK, ATTEMPTING TO WARN THE DRIVER NOT TO PROCEED INTO THE CONNED AREA. THE DRIVER, HOWEVER, PROCEEDED TO PARK THE TRUCK IN THE AREA OF THE LEAK. THE GSR ON SCENE RAN TO THE TRUCK AND PULLED THE POSTAL WORKER FROM THE TRUCK AS THE TRUCK CAUGHT FIRE. THE TTRUCK APPEARS TO BE THE SOURCE OF THE IGNITION AND WAS COMPLETELY DESTROYED. THERE WERE NO INJURIES OR FATALITIES. PG&E GAS CREWS ARRIVED ON SITE AT 16:05 HOURS AND SHUTOFF THE FLOW OF GAS AT 16:21 HOURS. THERE WAS SERVICE INTERRUPTION TO ONE CUSTOMER WHICH WAS RESTORED AT 04:41 HOURS ON 8/20/10. THIS INCIDENT IS REPORTABLE DUE TO DAMAGES EXCEEDING $50,000 AND THE PRESENCE OF MAJOR MEDIA.
2025-03-31 10:13 | YES | NO | NO | 20100074 | 15283 | 2010-09-27 18:02 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-09-01 12:45 |  |  | 2010 | 20992 FIRST STREET | COTTONWOOD | SHASTA | CA | 96022 | 40.386 | -122.2778 | [9 empty] | 2010-09-01 15:00 | 952810 |  | NATURAL GAS |  | 25 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-09-01 13:45 |  |  |  | 2010-09-01 13:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUM METER | [9 empty] | OTHER | [8 empty] | FIRE FIRST. | CLASS 3 LOCATION | 0 | 0 | 4900 | 6473.436526075211 | 0 | 0 | 50000 | 66055.4747558695 | DAMAGES TO HOUSE. |  | 100 | 69.09385113268608414239482200647249190939 |  | 0 | 55000 | 30103.2156706116325935275080906148867314 | 72598.0051330773970841423948220064724919 | 0 | 0 | 3 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | GARY GUERRERO |  | gfg2@pge.com | 925-974-4075 |  |  |  |  | GLEN CARTER |  | 925 270 2158 | No Email Address | A FIRE OCCURRED AT APPROXIMATELY 1245 HOURS ON 9/1/10 AT A RESIDENCE AT 3384 WILLOW STREET AND QUICKLY SPREAD TO THE HOMES AT 3382 WILLOW STREET AND THEN 20992 FIRST STREET. A PG&E GAS CONSTRUCTION CREW HAPPENED TO BE DRIVING BY AND OBSERVED THE SMOKE FROM THE FIRES AT 1345 HOURS. THE CREW DROVE TO THE SCENE AND WAS ABLE TO SHUT OFF THE GAS AT THE SERVICE VALVE AT THE FIRST TWO STRUCTURES ON WILLOW STREET WHERE THE METERS WERE UNAFFECTED BY THE FIRE. THE GAS CREW WAS NOT ABLE TO REACH THE SERVICE VALVE AT THE HOUSE ON FIRST STREET BEFORE THE HEAT FROM FIRE HAD MELTED THE GAS METER SET RELEASING GAS WHICH CONTRIBUTED TO THE FIRE. THE GAS SERVICE FOR THE FIRST STREET HOUSE WAS CUT OFF AT THE MAIN IN THE STREET AT 1450 HOURS. THREE CUSTOMERS LOST GAS SERVICE. THIS INCIDENT BECAME REPORTABLE TO THE CPUC AND DOT WHEN IT WAS DETERMINED THAT DAMAGES WOULD EXCEED $50,000. ONE PERSON RECEIVED MINOR INJURIES AND REFUSED TREATMENT; THERE WERE NO FATALITIES. THE CAUSE OF THIS INCIDENT IS CURRENTLY UNDER INVESTIGATION. GAS SERVICE TO THE CUSTOMERS WILL BE RESTORED UPON COMPLETION OF REPAIRS TO THE HOMES.
2025-03-31 10:13 | NO | NO | NO | 20100075 | 15103 | 2010-09-28 08:23 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2010-09-08 04:46 |  |  | 2010 | 3338 E. BRISTOL RD. | BURTON |  | MI | 48529 | 42.9749 | -83.6393 | [9 empty] | 2010-09-08 11:45 | 953388 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-09-08 04:46 |  |  |  | 2010-09-08 05:43 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1969 | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | RELEASE WAS FROM CUSTOMER OWNED EQUIPMENT | CLASS 3 LOCATION |  | 0 | 2500 | 3302.773737793475 | 1000 | 1321.10949511739 |  | 0 |  |  |  | 0 |  | 0 | 3500 | 1915.073758570539 | 4623.883232910865 | 1 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS NOT CAUSE BY THE CONTROLLER(S) OR CONTROL ROOM ISSUES. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | INCIDENT ORIGINATED ON CUSTOMER OWNED EQUIPMENMT. CAUSE OF INCIDENT UNKNOWN. | [47 empty] | GARY F EWERT | REGULATORY SERVICES ENGINEER | gfewert@cmsenergy.com | 586-665-1142 |  |  |  |  | DAVID M MONTAGUE | DIRECTOR COMPLIANCE PROGRAMS | 517-788-0277 | dmmontague@cmsenergy.com | WIND STORM ON SEPTEMBER 7, 2010 CAUSED POWER FAILURE TO RADIO STATION BUILDING. THE RADIO STATIONS'S GAS FED KOHLER GENERATOR KICKED IN AT APPROXIMATELY 06:02 P.M. SUPPLYING POWER TO THE BUILDING. CONSUMERS ENERGY DISPATCH RECEIVED A CALL FROM THE 911 OPERATOR AT 4:56 A.M. ON SEPTEMBER 8, 2010 THAT ELECTRIC AND GAS WAS NEEDED ON SITE INDICATING THAT THE METER INSTALLATION WAS ON FIRE. FIRST RESPONDER FOUND THAT THE FIRE DEPARTMENT HAD THE GAS TURNED OFF ON ARRIVAL AT THE SERVICE LOCKWING. INVESTIGATION INDICATES THE SOURCE OF THE INCIDENT WAS ON CUSTOMER OWNED EQUIPMENT. INCIDENT CAUSE UNKNOWN.
2025-03-31 10:13 | NO | YES | NO | 20100076 | 15104 | 2010-10-01 09:52 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2010-09-08 11:54 |  |  | 2010 | 3529 - 3531 WALTON WAY EXTENSION | AUGUSTA | RICHMOND | GA | 30909 | 33.4871 | -82.0727 | [9 empty] | 2010-09-10 11:52 | 953622 |  | NATURAL GAS |  | 13082 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 300 | 2010-09-08 11:54 |  |  |  | 2010-09-08 12:23 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 54 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1967 | [5 empty] | 6.625 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 3 | 4 | [7 empty] | CLASS 3 LOCATION | 38594 | 50986.89985456054966 | 3973 | 5248.76802410139047 | 8760 | 11572.9191772283364 |  | 0 |  |  | 65413 | 45196.3608414239482200647249190938511327 |  | 0 | 116740 | 69893.5630227465252641488673139158576052 | 113004.9478973142247500647249190938511327 | 49 | 0 | 72 |  |  |  |  | 277 | 277 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | UTILITY | DIRECTIONAL DRILLING | CABLE TV | YES | 8250301737 | UTILITY PROTECTION CENTER |  | CONTRACT LOCATOR | NO | YES | 8 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | RALPH T. MCCOLLUM | SENIOR COMPLIANCE ENGINEER REGULATORY COMPLIANCE | rmccollu@aglresources.com | (404) 584-3733 | (404) 584-4708 |  |  |  | RICHARD R. LONN | DIRECTOR REGULATORY COMPLIANCE | (404) 584-3552 | rlonn@aglresources.com | UTILITY COMPANY INSTALLING CABLE TV DAMAGED A 6-INCH STEEL NATURAL GAS MAIN BY DIRECTIONAL BORING.
2025-03-31 10:13 | NO | NO | NO | 20100077 | 16332 | 2010-10-04 11:26 | SUPPLEMENTAL FINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2010-10-04 01:00 |  |  | 2010 | 54TH & L | OMAHA | DOUGLAS | NE | 68117 | 41.2126 | -95.9977 | [9 empty] | 2010-10-04 09:30 | 955956 |  | NATURAL GAS |  | 2996 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-10-04 01:00 |  |  |  | 2010-10-04 02:05 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1997 | [5 empty] | 0.621 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | UNKNOWN | OTHER | [8 empty] | DRUNK DRIVER HIT SERVICE AND BENT OVER. | CLASS 1 LOCATION | 0 | 0 | 2000 | 2642.21899023478 | 200 | 264.221899023478 | 0 | 0 |  |  | 20 | 13.81877022653721682847896440129449838188 |  | 0 | 2220 | 1216.543819765374398705501618122977346278 | 2920.259659484795216828478964401294498382 | 0 | 0 | 0 |  |  |  |  | 10 | 10 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | POLICE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGED CAUSED BY DRUNK DRIVER | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MIKE PALMESANO | CLAIMS MANGER | mike_palmesano@mudnebr.com | 402-504-7108 | 402-504-5108 |  |  |  | MIKE PALMESANO | CLAIMS MANGER | 402-504-7108 | mike-palmesano@mudnebr.com | ON MONDAY AT 1AM A DRUNK DRIVER HIT A GAS SERVICE THE PARTY DIED BECAUSE OF THE ACCIDENT. THERE WAS NO IGNITION.
2025-03-31 10:13 | YES | NO | NO | 20100079 | 15107 | 2010-10-04 20:32 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2010-09-05 05:28 |  |  | 2010 | 4905 MINNESOTA AVENUE | WASHINGTON | NE | DC | 20019-3841 | 38.9092 | -76.9321 | [9 empty] | 2010-09-05 08:17 | 953133 |  | NATURAL GAS |  | 5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-09-05 05:28 |  |  |  | 2010-09-05 06:16 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | 1973 | [8 empty] | OTHER | CAST ALUMINUM | [9 empty] | OTHER | [8 empty] | INSIDE METER BUILD-UP CONSUMED BY FIRE. | CLASS 3 LOCATION |  | 0 | 200 | 264.221899023478 | 4200 | 5548.659879493038 |  | 0 | 2E SHOULD BE $350,000 - VALUE OF DAMAGES TO THE HOUSE CAUSED BY THE FIRE. |  | 21 | 14.50970873786407766990291262135922330097 |  | 0 | 4421 | 2420.943626585764978640776699029126213592 | 5827.391487254380077669902912621359223301 | 0 | 0 | 2 |  |  |  |  | 20 | 20 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MICHAEL UPSHAW | SUPERVISOR - DOT PIPELINE SAFETY COMPLIANCE | mupshaw@washgas.com | 703-750-4479 | 703-750-5591 |  |  |  | DAVID W. SPANGLER | MANAGER - DOT PIPELINE SAFETY COMPLIANCE | 703-750-4341 | dspangler@washgas.com | WASHINGTON GAS RESPONDED TO THE SCENE OF A HOUSE FIRE AT 4905 MINNESOTA AVENUE, NE, WASHINGTON, DC ON 9/5/10 AT THE REQUEST OF THE DC FIRE BOARD. UPON ARRIVAL, THE FIRST REPONDER FOUND THAT THE GAS HAD BEEN TURNED OFF AT THE CURB VALVE BY THE FIRE DEPARTMENT. THE INSIDE METER BUILD-UP WAS CONSUMED BY THE FIRE. THE SERVICE LINE WAS CAPPED OFF AT THE CURB VALVE. A GAS MIGRATION SURVEY WAS CONDUCTED AROUND THE HOUSE AND OVER THE SERVICE LINE TO THE MAIN. NO INDICATIONS WERE FOUND. WASHINGTON GAS WORKED CLOSELY WITH THE FIRE INVESTIGATORS ON SITE AND BELIEVE THAT THE FIRE STARTED ON THE FIRST OR SECOND FLOOR AND THEY THEN COLLAPSED INTO THE BASEMENT WHERE THE WASHINGTON GAS FACILITIES WERE LOCATED AND CONSUMED BY THE FIRE.
2025-03-31 10:13 | NO | YES | NO | 20100080 | 15838 | 2010-10-07 19:30 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-09-06 23:30 |  |  | 2010 | CIRBY WAY / RIVERSIDE AVENUE INTERSECTION | ROSEVILLE | PLACER | CA | 95678 | 38.7521 | -121.288 | [9 empty] | 2010-09-07 05:20 | 953351 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2010-09-06 23:38 |  |  |  | 2010-09-07 00:27 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 4 | ALDYL A | UNKNOWN | PLASTIC |  |  |  |  | UNKNOWN |  |  |  | UNKNOWN |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 293600 | 387877.747766465704 | 0 | 0 | 0 | 0 | ACTUAL LN 2.C. IS $293,600. CELL WOULD NOT ACCEPT #S ABOVE FIVE FIGURES. |  | 0 | 0 |  | 0 | 293600 | 160647.3301475172144 | 387877.747766465704 | 0 | 0 | 1200 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [15 empty] | NO | [86 empty] | GARY F. GUERRERO | SENIOR COMPLIANCE ANALYST | [6 empty] | LAURENCE DENISTON | MANAGER | 925-328-5756 | lcd1@pge.com | A LEAK IN A FOUR INCH PLASTIC GAS DISTRIBUTION MAIN WAS REPORTED TO THE FIRE DEPARTMENT AT APPROXIMATELY 2330 HOURS ON SEPTEMBER 6, 2010. THE LEAK WAS AT THE INTERSECTION OF CIRBY WAY AND RIVERSIDE AVENUE IN ROSEVILLE. THE FIRE DEPARTMENT NOTIFIED PG&E AT 2338 HOURS. A PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SCENE AT APPROXIMATELY 0027 HOURS ON SEPTEMBER 7, 2010. THE INTERSECTION WAS BLOCKED OFF BY THE FIRE DEPARTMENT AS A PRECAUTIONARY MEASURE. PG&E CREWS ARRIVED AT APPROXIMETLY 0215 HOURS ON SEPTEMBER 7TH, FOUND A CRACK IN THE PLASTIC MAIN AND BEGAN TO MAKE REPAIRS BY SQUEEZING THE MAIN AT 0758 HOURS. DURING THE REPAIRS, APPROXIMATELY 1,200 CUSTOMERS BEGAN TO LOSE SERVICE STARTING AT 1300 HOURS. PG&E CREWS COMPLETED REPAIRS AT APPROXIMATELY 2030 HOURS. PG&E BEGAN CUSTOMER RE-LIGHTS AT 2100 HOURS. SERVICE WAS RESTORED ON SEPTEMBER 8TH AT 0100 HOURS. THERE WERE NO INJURIES OR FATALITIES. THIS INCIDENT BECAME REPORTABLE TO THE CPUC WHEN SACRAMENTO TV NEWS MEDIA WAS OBSERVED ON SCENE AT APPROXIMATELY 0330 HOURS ON SEPTEMBER 7TH AND REPORTABLE TO THE DOT WHEN AN ESTIMATE OF DAMAGES DUE TO THE LABOR COSTS TO RELIGHT THE CUSTOMERS WOULD EXCEED $50,000.
2025-03-31 10:13 | NO | NO | NO | 20100082 | 15364 | 2010-10-08 15:31 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2010-09-15 12:02 |  |  | 2010 | 113 CRESTRIDGE DR | BURNSVILLE |  | MN | 55337 | 44.7536 | -93.2759 | [9 empty] | 2010-09-15 12:09 | 954124 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2010-09-15 12:02 |  |  |  | 2010-09-15 12:37 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1979 | [8 empty] | OTHER | COPPER RISER | [9 empty] | OTHER | [8 empty] | LIGHTNING STRUCK RISER AND METER | CLASS 3 LOCATION | 0 | 0 | 60 | 79.2665697070434 | 532 | 702.83025140245148 | 50000 | 66055.4747558695 | PROPERTY DAMAGE TO THE HOME. |  | 0 | 0 |  | 0 | 50592 | 27682.117598171631168 | 66837.57157697899488 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DUE TO LIGHNING STRIKE | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | CRYSTAL GELSCHUS | SPECIALIST | crystal.gelschus@centerpointenergy.com | 612-861-8689 | 612-861-8565 |  |  |  | KRIS TANDE | DAMAGE PREVENTION SUPERVISOR | 612-861-8692 | kristine.tande@centerpointenergy.com | LIGHTNING STRUCK METER AND RISER, RESULTING IN A FIRE.
2025-03-31 10:13 | NO | NO | NO | 20100084 | 15115 | 2010-10-19 10:21 | ORIGINAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2010-09-21 20:30 |  |  | 2010 | 116 S. MILTON ST. | PERSHING | WAYNE | IN | 47370 | 39.8126 | -85.1361 | [9 empty] | 2010-09-21 23:08 | 954777 |  | NATURAL GAS |  | 56 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 3 | 2010-09-21 20:35 |  |  |  | 2010-09-21 21:20 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 32 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1988 | [5 empty] | 2 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 25000 | 33027.73737793475 | 3150 | 4161.4949096197785 | 16300 | 21534.084770413457 | 0 | 0 |  |  | 378 | 261.174757281553398058252427184466019417 |  | 0 | 44828 | 24563.0386755934181155339805825242718447 | 58984.4918152495388980582524271844660194 | 0 | 0 | 2 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 1988 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [7 empty] | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | RICHARD SLAGLE | MANAGER QUALITY ASSURANCE | rlslagle@vectren.com | 812-491-4611 | 812-491-4504 |  |  |  | JAMES FRANCIS | DIRECTOR ENGINEERING ASSET MANAGEMENT | 812-491-4369 | jmfrancis@vectren.com | A STRUCTURE LOCATED AT 116 S. MILTON ST. IN PERSHING, IN RECEIVED $25,000 DAMAGE DUE TO WHAT APPEARS TO BE AN EXPLOSION CAUSED BY NATURAL GAS. AFTER MAKING THE SITE SAFE, AN INVESTIGATION OF THE GAS FACILITIES IN THE AREA REVEALED A LEAK AT A BUTT FUSION JOINT DIRECTLY IN FRONT OF THE STRUCTURE ON A 2-INCH PE MAIN OPERATING AT 60 PSIG. THIS MAIN RAN PARALLEL TO MILTON ST. (NORTH TO SOUTH) ON THE EAST EDGE OF THE PAVEMENT OF THE ROADWAY. THE MAIN WAS LOCATED 18 FT. WEST OF THE WEST BUILDING LINE. THE STRUCTURE DID NOT HAVE AN ACTIVE GAS SERVICE. IT APPEARS THE GAS MIGRATED FROM THIS LEAK SOURCE INTO THE HOME AS GAS READINGS WERE OBTAINED AT A LEVEL OF 93% GAS AT THE WEST BUILDING WALL. GAS WAS SHUT-OFF BY SQUEEZING THE PIPE IN AN AREA AWAY FROM THE LEAKAGE. THE DEFECTIVE JOINT WAS REMOVED FROM THE SYSTEM AND APPROPRIATE REPAIRS WERE MADE TO THE MAIN.
2025-03-31 10:13 | NO | YES | YES | 20100085 | 15346 | 2010-10-19 15:50 | SUPPLEMENTAL FINAL | 6720 | ATMOS ENERGY CORPORATION - COLORADO/KANSAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2010-09-22 14:05 |  |  | 2010 | 227TH ST AND EASTON RD | EASTON | LEAVENWORTH | KS | 66020 | 39.3452 | -95.1054 | [9 empty] | 2010-09-22 15:45 | 954860 |  | NATURAL GAS |  | 290 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2010-09-22 14:05 |  |  |  | 2010-09-22 14:05 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1978 | [5 empty] | 3 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 3 | 2 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 68000 | 89835.44566798252 | 10700 | 14135.871597756073 | 0 | 0 |  |  | 1460 | 1008.770226537216828478964401294498381877 |  | 0 | 80160 | 43994.9728923217185055016181229773462783 | 104980.0874922758098284789644012944983819 | 19 | 0 | 93 |  |  |  |  | 45 | 49 | 52 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  | YES |  |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | NO | [50 empty] | DOUGLAS L SHATAS | COMPLIANCE MANAGER | doug.shatas@atmosenergy.com | 9132546363 | 9137684924 |  |  |  | DOUGLAS L SHATAS | COMPLIANCE MANAGER | 9132546363 | doug.shatas@atmosenergy.com | ATMOS EMPLOYEES WERE WORKING ON A PIPE REPLACEMENT PROJECT. DURING THE PROCESS, THE EXISTING PIPE WAS DAMAGED, AND WHILE ATTEMPTING TO STOP THE ESCAPING GAS, ONE EMPLOYEE RECEIVED BURNS THAT REQUIRED HOSPITALIZATION.
2025-03-31 10:13 | NO | NO | NO | 20100086 | 15897 | 2010-10-19 15:55 | SUPPLEMENTAL FINAL | 702 | ASHBURN GAS DEPT, CITY OF | P.O. BOX 766 | ASHBURN | GA | 31714 | 2010-09-24 13:45 |  |  | 2010 | CITY OF ASHBURN | ASHBURN | TURNER | GA | 31714 | 31.7095 | -83.6528 | [9 empty] | 2010-09-24 15:16 | 955047 |  | OTHER GAS | NO GAS WAS RELEASED |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-09-24 13:45 |  |  |  | 2010-09-24 13:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | CUSTOMER FUEL LINE |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OTHER | TOTAL DISTRIBUTION SYSTEM | UNKNOWN | [8 empty] | OTHER | TOTAL SYSTEM | [9 empty] | OTHER | [8 empty] | NO RELEASE OF NATURAL GAS | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 16484 | 21777.16891751505676 | TOTAL COST OF SHUT DOWN AND RESTARTING OF THE SYSTEM. |  | 0 | 0 |  | 0 | 16484 | 9019.450238936218536 | 21777.16891751505676 | 73 | 5 | 593 |  |  |  |  | 28 | 23 | 29 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | PROPANE VAPOR WAS INTRODUCED INTO THE NATURAL GAS SYSTEM THROUGH A CUSTOMER FUEL LINE. | [47 empty] | SAM YARLEY | REGLATORY COMPLIANCE - ANALYST | syarley@gasauthority.com | 2293763027 |  |  |  |  | ROGER GIDDENS | GAS SUPERINTENDENT | 2295673431 | gasman1@mchsi.com | CITY OF ASHBURN PROPANE CONTAMINATION OF NATURAL GAS SYSTEM SEPTEMBER 24, 2010 EVENT SUMMARY THE CITY OF ASHBURN RECEIVED A CALL ON SEPT. 24, 2010 AT CITY HALL FROM KEITH-A-QUE RESTAURANT REPORTING THAT THEY WERE HAVING PROBLEMS WITH THE PILOT LIGHTS ON THEIR APPLIANCES. THE CALL WAS RECEIVED AT APPROXIMATELY 10:30AM BY AMANDA BRIDGES. SHE DISPATCHED THE INFORMATION TO THE GAS DEPARTMENT FOR INVESTIGATION. JAMES YOUNG, BRUCE BURGESS, BUSTER FELTON, AND MARIO BYRD PERFORMED THE INITIAL INVESTIGATION AT KEITH-A-QUE, WHICH IS LOCATED AT 249 EAST WASHINGTON AVE. DURING THEIR INVESTIGATION GAS PERSONNEL DETERMINED THAT ADDITIONAL PERSONNEL WERE NEEDED TO DETERMINE THE CAUSE OF THE PROBLEM. ASHBURN GAS SUPERINTENDENT ROGER GIDDENS REPORTED TO THEIR LOCATION AT APPROXIMATELY 11:00AM TO HELP DETERMINE THE SOURCE OF THE PROBLEM. DURING THE INVESTIGATION OTHER LOCATIONS THROUGHOUT TOWN REPORTED HAVING SIMILAR PROBLEMS. PROPANE ODOR WAS DETERMINED TO BE PRESENT WITHIN THE NATURAL GAS SYSTEM. AT APPROXIMATELY 12:00PM CITY PERSONNEL DETERMINED THAT PROPANE WAS BEING INTRODUCED INTO THE NATURAL GAS SYSTEM FROM FOUR 500 GALLON PROPANE TANKS CONNECTED TO A FUEL LINE AT THE HAT CREEK PEANUT COMPANY INC. LOCATED AT 465 BUSSEY ROAD, SYCAMORE GA. 31790. LATER INVESTIGATION REVEALED THAT THIS METERED SERVICE WAS DELIVERING LINE PRESSURE TO THE HAT CREEK PER AGREEMENT BETWEEN ASHBURN AND HAT CREEK. HAT CREEK CONNECTED THE PROPANE TANKS TO ITS INTERNAL PIPING IN AN ATTEMPT TO SUPPLEMENT ITS NATURAL GAS SUPPLY DURING HIGH DEMAND PERIODS. THE ABSENCE OF A SERVICE REGULATOR AT THE METER ALLOWED THE HIGHER-PRESSURE PROPANE TO FLOW BACKWARD THROUGH THE METER INTO ASHBURN'S NATURAL GAS FACILITIES. GEORGIA PUBLIC SERVICE COMMISSION (GPSC) INSPECTORS JOSH LAIRSEY AND ROB PACER WERE NOTIFIED OF THE EVENT AT APPROXIMATELY 1:45PM ON SEPTEMBER 24, 2010. ASHBURN CITY MANAGER BEN TAYLOR ESTABLISHED A COMMAND CENTER AT CITY HALL TO DEVELOP A PLAN OF ACTION WITH ALL CITY PERSONNEL. DUE TO THE UNKNOWN VOLUME AND EXTENT OF PROPANE IN THE NATURAL GAS SYSTEM, CITY PERSONNEL DECIDED TO BEGIN SHUTTING OFF ALL SERVICES THROUGHOUT THE DISTRIBUTION SYSTEM. MUTUAL ASSISTANCE WAS REQUESTED FROM AND PROVIDED BY THE CITIES OF DOUGLAS, TIFTON, CORDELE, SYLVESTER AND FITZGERALD. ASHBURN CONFIRMED THAT THESE CITIES' PERSONNEL HAVE APPROPRIATE OPERATOR QUALIFICATIONS TO PERFORM THE REQUESTED TASK. THE SHUT OFF PROCESS BEGAN AT APPROXIMATELY 4:00PM ON FRIDAY SEPTEMBER 24TH, 2010. ACTING ON INSTRUCTIONS FROM GPSC TO REPORT THIS EVENT TO THE NATIONAL RESPONSE CENTER (NRC) AS AN INCIDENT PURSUANT TO 49 CFR PART 191, BEN TAYLOR REQUESTED THAT THE SUBSCRIBED REGULATORY COMPLIANCE SERVICE (SRCS) MAKE THE TELEPHONIC REPORT ON BEHALF OF ASHBURN. ON 9/24/2010 AT 3:16PM, SRCS MANAGER BILL DEFOOR CALLED THE NRC AND GAVE THE REQUIRED INFORMATION TO KEVIN WILLIAMS, WHO ASSIGNED CASE #955047 TO THE REPORT.ON 9/24/2010 AT 6:59PM THE VALVE SUPPLYING NATURAL GAS TO THE DISTRIBUTION SYSTEM WAS SHUT OFF. THE SHUTTING OFF AND LOCKING OF ALL SERVICES WAS COMPLETE AT APPROXIMATELY 3:15AM ON 9/25/2010. DURING THE COMPLETION OF THE SHUT-OFF ACTION LINE PRESSURE ON THE DISTRIBUTION SYSTEM DROPPED TO ZERO AS HAT CREEK CONSUMED THE REMAINING CONTAMINATED GAS THROUGH ITS PEANUT DRYERS. ON 9/25/2010 AT 9:00AM THE VALVE CONTROLLING THE GAS FLOW TO THE CITY WAS CUT BACK ON. AS A PRECAUTION, LOCATIONS THROUGHOUT THE SYSTEM WERE MONITORED FOR 100% GAS USING (CGI) COMBUSTIBLE GAS INDICATORS. THE LOCATIONS THAT WERE MONITORED WERE INDUSTRIAL BLVD., CENTRAL PACKING PLANT, AND BRIDGES ROAD. WHEN 100% LEVELS WERE CONFIRMED, CREWS BEGAN CUTTING ON SERVICES AND RELIGHTING APPLIANCES THROUGHOUT THE SYSTEM. THE RELIGHTING PROCESS STARTED AT APPROXIMATELY 10:30AM SATURDAY MORNING. AT APPROXIMATELY 6:00PM A MAJORITY OF THE SERVICES WERE BACK ON. WHERE OCCUPANTS WERE NOT AVAILABLE TO ALLOW ACCESS FOR RELIGHTING, CONTACT INFORMATION AND INSTRUCTIONS WERE PLACED IN A CONSPICUOUS LOCATION. A POST-EMERGENCY
2025-03-31 10:13 | NO | YES | NO | 20100087 | 15877 | 2010-10-21 14:13 | SUPPLEMENTAL FINAL | 11032 | LACLEDE GAS CO | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2010-01-12 11:40 |  |  | 2010 | 1829 DUNN ROAD | SPANISH LAKE | ST LOUIS | MO | 63138 | 38.7711 | -90.2293 | [9 empty] | 2010-01-13 11:55 | 928453 |  | NATURAL GAS |  | 5747 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2010-01-12 12:00 |  |  |  | 2010-01-12 12:25 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | VALVE | 1963 | [8 empty] | OTHER | CAST STEEL | [9 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 93802 | 123922.71286100141678 | 0 | 0 | 0 | 0 |  |  | 36225 | 25029.2475728155339805825242718446601942 |  | 0 | 130027 | 74478.5904750282136633398058252427184466 | 148951.9604338169507605825242718446601942 | 0 | 0 | 0 |  |  |  |  | 200 | 200 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | LOOSE COMPACTION CREATED BY AN EXCAVATION 27 DAYS PRIOR TO FAILURE COMBINED WITH SEVERE WET, THEN COLD WEATHER, LED TO EXTREME FORCE BEING EXERTED ON THE PIPELINE. | [154 empty] | MARK D LAUBER | SUPERINTENDENT OF MAINTENANCE ENGINEERING | mlauber@lacledegas.com | 3146585413 | 3145355075 |  |  |  | CRAIG R HOEFERLIN | ASSISTANT VP ENGINEERING AND FIELD SERVICES | 3146585410 | choeferlin@lacledegas.com | A 2-INCH STEEL NATURAL GAS MAIN WAS EXPOSED IN AN EXCAVATION BY A CONTRACTOR PREPARING TO INSTALL A WATER MAIN ON DECEMBER 16, 2009 . THE 2-INCH LINE WAS CONNECTED TO A 2-INCH VALVE JUST BEYOND THE EXCAVATION. THE EXCAVATION WAS QUICKLY BACKFILLED THE SAME DAY IT WAS EXCAVATED. IN THE DAYS FOLLOWING THE BACKFILL, HEAVY RAIN SATURATED THE AREA AND FILLED THE VOIDS CREATED BY THE RECENT EXCAVATION WITH MOISTURE. THIS WAS QUICKLY FOLLOWED BY EXTREMELY COLD TEMPERATURES. A LEAK WAS REEORTED BY THE PUBLIC IN THE AREA OF THE DECEMBER 16 EXCAVATION, ON JANUARY 12, 2010. DURING REPAIR THE MAIN REMAINED ACTIVE IN ORDER TO MAINTAIN SERVICE TO CUSTOMERS. ON JANUARY 13, 2010, IT WAS ESTIMATED THAT THE COST OF REPAIR AND THE RELEASED NATURAL GAS WOULD EXCEED $50,000. A NOTIFICATION WAS THEN MADE TO THE NATIONAL RESPONSE CENTER WHILE NATURAL GAS WAS STILL BEING BEING RELEASED AND REPAIRS WERE ON-GOING. THE BODY OF THE 2-INCH VALVE AT THE FLANGE WAS FOUND CRACKED ON JANUARY 14, 2010, FROM SOIL STRESS. REPAIR CREWS ESTIMATED THE DEPTH OF FROST IN THE PREVIOUSLY EXCAVATED AREA TO BE 30-INCHES AND THE FROST DEPTH OUTSIDE OF THIS AREA TO BE 12 TO 18 INCHES. APPARENTLY THE FROZEN SOIL EXPANSION CAUSED THE FAILURE AS THE BREAK ORIGINATED FROM PRESSURE PUSHING DOWNWARD ON THE MAIN.
2025-03-31 10:13 | NO | YES | NO | 20100088 | 15143 | 2010-05-05 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS CO | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2010-04-07 16:15 |  |  | 2010 | S.W. 7TH & DEWEY | OKLAHOMA CITY | OKLAHOMA | OK | 73109-5132 | 35.4571 | -97.5233 | [9 empty] | 2010-04-07 22:00 | 936448 |  | NATURAL GAS |  | 4711 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | [6 empty] | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 360 |  | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 2008 | [5 empty] | 12 | API-5L GR A-53-B/X-42 | NATIONAL PIPE CO | STEEL |  | SEAMLESS | SEAMLESS | 0.375 | [6 empty] | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 346838 | 458210.97506752531282 | 5475 | 7233.07448576771025 | 0 | 0 |  |  | 32468 | 22433.3915857605177993527508090614886731 |  | 0 | 384781 | 213525.1666767527071405113268608414239482 | 487877.4411390535408693527508090614886731 | 1 | 0 | 9 |  |  |  |  | 48 | 48 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS SYSTEM IS NOT MONITORED BY CONTROL ROOM FACILITIES. THIS PIPELINE SEGMENT IS A SMALL PORTION OF A LARGER DISTRIBUTION NETWORK WITHIN A CITY GATE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | INTERSTATE HIGHWAY | [5 empty] | YES | [6 empty] | CONTRACTOR | UNKNOWN/OTHER | ROAD WORK | YES | 10032908410443 | NOT APPLICABLE |  | UTILITY OWNER | YES | YES | 8 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | TRACY ROWLETT | REGULATORY SPECIALIST | tracy.rowlett@ong.com | 405-551-6904 |  |  |  |  | BRYAN BREWSTER | DIRECTOR OF OPERATIONS AND COMPLIANCE | 405-551-6653 | bryan.brewster@oneok.com | ADDITIONAL REPORT INFORMATION TO REVISE FINAL PERMANENT REPAIR COST OF OPERATOR'S PROPERTY DAMAGE AND REPAIRS. SEE REVISIONS ON PAGE 2, PART A, NUMBER 13 GAVE THE TIME FOR THE NEW LINE TO BE STARTED BACK UP. ON PAGE 5, PART D, #2. IN ADDITION, THE OKIE ONE CALL TICKET NUMBER WAS CORRECTED ON PAGE 11, PART G3, #9. CONTRACTOR WORKING ON ROADBED FOR THE I-40 RELOCATION PROJECT IN OKLAHOMA CITY DROVE A 12" I-BEAM INTO THE ONG 12" STEEL GAS MAIN, PUNCTURING THE PIPELINE. LINE WAS APPROXIMATELY 30 FEET DEEP AT THE POINT OF THE DAMAGE. THE DEPTH AND THE LOCATION MADE IT TOO DANGEROUS AND IMPRACTICAL TO EXCAVATE TO ATTEMPT A REPAIR OF THE EXISTING PIPELINE. THE PUNCTURE SIZE OF 3" IS AN ESTIMATE NECESSARY DUE TO THE I-BEAM BEING ON TOP OF THE PIPE AND NOT BEING ABLE TO EXPOSE THE PIPE FOR FURTHER EVALUATION AT THAT, DEPTH. THE DAMAGED 12" PIPELINE WILL REMAIN OUT OF SERVICE PENDING PERMIT APPROVAL FROM OKLAHOMA DEPARTMENT OF TRANSPORTATION (ODOT) AND UNION PACIFIC RAILROAD TO REPLACE THE PIPELINE IN A NEW LOCATION BY DIRECTIONAL BORE. DURING THE INITIAL EMERGENCY RESPONSE, A 2" PLASTIC LATERAL LINE TIED TO THE DAMAGED SECTION WAS SHUT OFF. APPROXIMATELY 100 FEET OF 2" PLASTIC PIPE WAS INSTALLED TO RESTORE SERVICE TO THE 10 CUSTOMERS AFFECTED BY THE OUTAGE.
2025-03-31 10:13 | NO | YES | YES | 20100089 | 15229 | 2010-10-22 16:31 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2010-09-28 08:45 |  |  | 2010 | 401 JUBILEE ST. | ANDALE | SEDGWICK | KS | 67001-9669 | 37.79 | -97.629 | [9 empty] | 2010-10-01 15:00 | 955781 |  | NATURAL GAS |  | 4 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2010-09-28 08:55 |  |  |  | 2010-09-28 09:10 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 35 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1994 | [5 empty] | 0.75 | ASTMD2513 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  |  | MECHANICAL PUNCTURE | 1.5 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 200 | 264.221899023478 | 750 | 990.8321213380425 | 0 | 0 |  |  | 11 | 7.60032362459546925566343042071197411003 |  | 0 | 961 | 526.836478805715879288025889967637540453 | 1262.65434398611596925566343042071197411 | 0 | 0 | 1 |  |  |  |  | 44 | 44 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 4 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | CONTRACTOR FAILED TO FOLLOW PROPER PROCEDURE FOR DEALING WITH BLOWING NATURAL GAS. BHE POLICY CLEARLY STATES IN SECTION 74.21.2 OF ITS O&M MANUAL TO 'DIG A SAFE WORK AREA 5-15 FEET UPSTREAM OF THE BLOWING GAS.' |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | BRIAN PETERSON | OPERATIONS MANAGER | brian.peterson@blackhillscorp.com | 316-941-1641 | 402-829-2547 |  |  |  | JERRY A. WATKINS | TECHNICAL SERVICES MANAGER | 316-941-1642 | jerry.watkins@blackhillscorp.com | WHILE DIGGING UP A 2" PE MAIN OUR CONTRACTOR, UNDERGROUND SYSTEMS CONSTRUCTION HIT A 3/4" SERVICE LINE THAT CONTAINED 44PSIG OF PRESSURE. THE LABORER AND OPERATOR PROCEEDED TO DIG UP AND FURTHER EXPOSE THE DAMAGED SERVICE LINE WITH SHOVELS WHEN THE NATURAL GAS SUDDENLY IGNITED CAUSING 2ND DEGREE BURNS TO THEIR HANDS, FACE, AND ARMS. THE CREW FOREMAN IMMEDIATELY EXTINGUISHED THE FIRE AND A 4TH CONTRACT EMPLOYEE SQUEEZED OFF THE LINE, STOPPING THE GAS FLOW. BOTH INJURED EMPLOYEES WERE TAKEN TO THE LOCAL HOSPITAL AND LATER TRANSPORTED TO THE LOCAL BURN UNIT. ONE WAS TREATED AND RELEASED AND THE OTHER WAS KEPT OVERNIGHT FOR OBSERVATION AND RELEASED THE NEXT MORNING.
2025-03-31 10:13 | NO | NO | NO | 20100090 | 15294 | 2010-10-26 07:07 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2010-10-15 07:08 |  |  | 2010 | 1428 CENTER STREET | LANSING |  | MI | 48906-4409 | 42.7505 | -84.5477 | [9 empty] | 2010-10-15 09:35 | 957045 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES |  | 2010-10-15 07:08 |  |  |  | 2010-10-15 07:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1998 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 10 |  |  | 2406 | OTHER | [8 empty] | PLASTIC RISER DAMAGED DUE TO CAR RUNNING INTO THE OUTSIDE METER ASSEMBLY | CLASS 3 LOCATION | 0 | 0 | 500 | 660.554747558695 | 2000 | 2642.21899023478 | 0 | 0 |  |  | 50 | 34.54692556634304207119741100323624595469 |  | 0 | 2550 | 1399.867756352973996763754045307443365696 | 3337.320663359818042071197411003236245955 | 0 | 0 | 19 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY CAR HITTING METER ASSEMBLY | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | THIRD PARTY DAMAGE WAS CAUSED BY RUNNING VEHICLE ROLLING ACROSS STREET AND HITTING AND DAMAGING METER AND RISER. | [47 empty] | GARY F EWERT | REGULATORY SERVICES ENGINEER | gfewert@cmsenergy.com | 586-665-1142 | 517-788-1369 |  |  |  | DAVID M MONTAGUE | DIRECTOR GAM COMPLIANCE PROGRAMS | 517-788-0277 | dmmontague@cmsenergy.com | POLICE REPORTED VEHICLE AT 401 BEAVER ST (ARCROSS THE STREET FROM 1428 CENTER ST.) WAS LEFT RUNNING IN DRIVEWAY, ROLLED ACROSS STREET AND HIT METER AND RISER (FRONT OF HOUSE), CAUSING BLOWING GAS. FIRE DEPT CALLED CONUSMERS ENERGY AND REPORTED GAS METER HIT/BLOWING. THE FIRE DEPT DID NOT INDICATE ON ORIGINAL EMERGENCY ORDER ABOUT FIRE OR EXPLOSION. FIRE DEPT PERFORMED PRECAUTIONARY EVACUATION OF RESIDENTS UPON THEIR ARRIVAL. PER FIRE DEPT APPROXIMATELY 3 MINUTES AFTER HOUSE WAS EVACUATED, HOUSE EXPLODED AND FIRE AT METER. SUPERVISOR DAN RUBLE ARRIVED ONSITE AT 07:40 AND REQUESTED A CREW. CREW DUG UP GAS MAIN ACROSS THE STREET AND SQUEEZED OFF 4" PLASTIC- MEDIUM PRESSURE MAIN, INTERRUPTING GAS SERVICE TO 19 CUSTOMERS.
2025-03-31 10:13 | NO | YES | YES | 20100091 | 15181 | 2010-10-26 12:48 | SUPPLEMENTAL FINAL | 8170 | ALLIANT ENERGY - INTERSTATE POWER AND LIGHT COMPANY | 200 FIRST STREET SE | CEDAR RAPIDS | IA | 52401-1409 | 2010-09-26 08:48 |  |  | 2010 | 1202 DRAKE AVENUE | CENTERVILLE | APPANOOSE | IA | 52544-2920 | 40.7234 | -92.8727 | [9 empty] | 2010-09-27 10:01 | 955252 |  | NATURAL GAS |  | 50 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 3 | 0 | 0 | 3 | YES |  |  |  |  | YES | 0 | 2010-09-26 08:48 |  |  |  | 2010-09-26 09:20 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | IT APPEARS A SQUIRREL MADE CONTACT WITH A GANG OPERATED SWITCH ON A POLE AT THE REAR OF 1202 DRAKE AVENUE, WHICH RESULTED IN A FAULT AND BREAKER OPERATIONS THAT INTRODUCED HIGH VOLTAGE ELECTRICITY ON THE ELECTRIC SERVICE, CAUSING A HIGH VOLTAGE ELECTRICAL ARC BETWEEN THE UNDERGROUND ELECTRIC SERVICE AND THE STEEL GAS SERVICE. HOLES WERE SUBSEQUENTLY BURNED IN BOTH THE STEEL GAS SERVICE AND THE CONDUIT FOR THE ELECTRIC SERVICE. | CLASS 3 LOCATION | 80000 | 105688.7596093912 | 1000 | 1321.10949511739 | 5000 | 6605.54747558695 | 0 | 0 |  |  | 175 | 120.914239482200647249190938511326860841 |  | 0 | 86175 | 47167.9508185423054886731391585760517799 | 113736.3308195777406472491909385113268608 | 0 | 0 | 1 |  |  |  |  | 52 | 52 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | RICHARD A. SUBLETT | SR. MGR. COMPLIANCE AND OPERATIONAL PERFORMANCE | richardsublett@alliantenergy.com | 319-786-4008 | 319-786-4638 |  |  |  | RICHARD A. SUBLETT | SR. MGR. COMPLIANCE AND OPERATIONAL PERFORMANCE | 319-786-4008 | richardsublett@alliantenergy.com | THE FIRE OCCURRED ON SUNDAY, SEPTEMBER 26, 2010 AT 1202 DRAKE AVENUE IN CENTERVILLE, IA. CENTERVILLE IS LOCATED IN APPANOOSE COUNTY. CONDITIONS THAT MORNING WERE CLEAR AND SUNNY WITH TEMPERATURES AROUND 65 DEGREES FAHRENHEIT. AT APPROXIMATELY 8:48 AM CST, INTERSTATE POWER & LIGHT'S (IPL) DISTRIBUTION DISPATCH CENTER IN CEDAR RAPIDS, IA RECEIVED A CALL FROM EMPLOYEES IN IPL'S CENTERVILLE CALL CENTER WITH A REPORT OF AN ELECTRICAL OUTAGE AND A HOUSE FIRE ACROSS THE STREET FROM THE CALL CENTER BUILDING. AN ELECTRIC LINEMAN WAS DISPATCHED TO INVESTIGATE. AT APPROXIMATELY 9:05 AM, A CALL ALSO CAME IN FROM THE CENTERVILLE POLICE/FIRE DISPATCHER REPORTING A HOUSE FIRE. WHEN THE IPL LINEMAN ARRIVED ONSITE AT 9:20 AM, THE VALVE AT THE GAS METER SET HAD BEEN SHUT OFF BY FIRE DEPARTMENT PERSONNEL. AT THIS POINT, THE SITUATION APPEARED TO BE A HOUSE FIRE CAUSED BY A SQUIRREL MAKING CONTACT WITH AN ENERGIZED SWITCH ON A POLE AT THE REAR OF 1202 DRAKE AVENUE, WHICH RESULTED IN A FAULT AND BREAKER OPERATIONS THAT INTRODUCED HIGH VOLTAGE ELECTRICITY INTO THE HOME'S ELECTRICAL WIRING SYSTEM. AT APPROXIMATELY 9:25 AM, DURING FIREFIGHTING ACTIVITIES, A "WHOOSH" OR "FLASH" OCCURRED, INDICATING AN IGNITION OF GAS. AT THIS POINT, FLAMES ALSO APPEARED ALONG THE GROUND NEAR THE HOUSE. GAS EMPLOYEES ARRIVED ON SITE AT 9:32 AM. AT APPROXIMATELY 10:25 AM, GAS TO THE RESIDENCE WAS SHUT OFF BY EXCAVATING OVER THE SERVICE TAP AND OPERATING THE EXISTING SERVICE TEE. SIX FIREFIGHTERS SOUGHT MEDICAL TREATMENT DUE TO THE GAS IGNITION. THREE OF THEM WERE ADMITTED TO THE HOSPITAL FOR OVERNIGHT OBSERVATION AND RELEASED THE NEXT DAY. AN IOWA UTILITIES BOARD INVESTIGATOR, ALONG WITH A STATE FIRE INVESTIGATOR, VISITED THE SITE ON THE AFTERNOON OF MONDAY, SEPTEMBER 27, 2010 AND WITNESSED THE EXCAVATION AND REMOVAL OF A SEGMENT OF THE SERVICE LINE. INITIAL INDICATIONS ARE THAT AN ELECTRICAL ARC BETWEEN THE ELECTRICAL SERVICE LINE CONDUIT AND THE STEEL GAS SERVICE BURNED A HOLE IN BOTH, ALLOWING GAS TO MIGRATE INTO THE ALREADY BURNING STRUCTURE VIA THE CONDUIT AND INTO THE ELECTRIC SERVICE PANEL. THE SOURCE OF IGNITION WOULD APPEAR TO BE THE EXISTING FIRE IN THE STRUCTURE. THE INCIDENT WAS REPORTED TELEPHONICALLY TO KEVIN WILLIAMS OF THE NATIONAL RESPONSE CENTER AT APPROXIMATELY 10:01 CST ON MONDAY, SEPTEMBER 27, 2010 BY JIM HOUSE, MANAGER GAS DISTRIBUTION AND METERING. (CASE #955252) THE INCIDENT WAS NOT REPORTED ON SUNDAY, SEPTEMBER 26, 2010, BECAUSE IT WAS REPORTED TO MR. HOUSE AS A HOUSE FIRE THAT WAS LATER FED BY NATURAL GAS. THERE WERE NO INDICATIONS OF AN EXPLOSIVE OR VIOLENT GAS IGNITION. AFTER READING THE NEWS ACCOUNTS ON MONDAY MORNING, SEPTEMBER 27, 2010 DESCRIBING IT AS A GAS EXPLOSION, MR. HOUSE IMMEDIATELY MADE THE TELEPHONIC NOTIFICATION TO THE NATIONAL RESPONSE CENTER. IN MR. HOUSE'S FOLLOW-UP DISCUSSIONS WITH MR. LOPEZ FROM THE PHMSA OFFICE IN HOUSTON, MR. LOPEZ AGREED THAT IT APPEARED TO BE A "FIRE FIRST, GAS SECOND" SCENARIO. SUPPLEMENTAL REPORT (02/03/2011): NO CHANGES TO INFORMATION PREVIOUSLY PROVIDED. STATUS OF REPORT IS CHANGED TO "FINAL".
2025-03-31 10:13 | NO | NO | NO | 20100092 | 15123 | 2010-10-26 16:23 | ORIGINAL FINAL | 31432 | SEMSTREAM ARIZONA PROPANE LLC | 600 E. LAS COLINAS BLVD SUITE 1650 | IRVING | TX | 75039 | 2010-02-04 14:30 |  |  | 2010 | 910 COPPERMINE RD | PAGE | COCONINO | AZ | 86040 | 36.901 | -111.4533 | [9 empty] | 2010-02-04 20:35 | 930555 |  | PROPANE GAS |  | 354 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 10 | 2010-02-04 14:35 |  |  |  | 2010-02-04 14:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | PETROLEUM GAS DISTRIBUTION |  | MAIN |  | 1982 | [5 empty] | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 2 | 3 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 500 | 660.554747558695 | 25600 | 33820.403075005184 |  | 0 |  |  | 12000 | 8291.262135922330097087378640776699029126 |  | 0 | 38100 | 21950.881512247378623300970873786407767 | 42772.2199584862090970873786407766990291 | 240 | 0 | 936 |  |  |  |  | 28 | 28 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  |  |  | YES |  |  | YES | [6 empty] | UNKNOWN/OTHER | BACKHOE/TRACKHOE | UNKNOWN/OTHER | NO |  |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED | YES | 101 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | FLOYD ELMORE | MANAGER | felmore@semgroupcorp.com | 928-645-2391 | 928-645-3315 |  |  |  | DOUGLASS MANN | PRESIDENT-GENERAL MANAGER | 928-474-2294 | dmann@semgrpoucorp.com
2025-03-31 10:13 | NO | NO | NO | 20100093 | 15125 | 2010-10-27 16:29 | SUPPLEMENTAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2010-10-13 20:30 |  |  | 2010 | US HIGHWAY 95 AND FAIRMONT LOOP | COEUR D'ALENE | KOOTENAI | ID | 83814 | 47.6801 | -116.807 | [9 empty] | 2010-10-13 21:45 | 956918 |  | NATURAL GAS |  | 4.49 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-10-13 20:33 |  |  |  | 2010-10-13 21:12 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2009 | [8 empty] | STEEL |  | SEAMLESS | SEAMLESS | 0.28 | [6 empty] | MECHANICAL PUNCTURE | 0.3 | 0.2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 15000 | 19816.64242676085 | 1000 | 1321.10949511739 | 12000 | 15853.31394140868 | $3000 FOR CAR, $9000 FOR POLICE RESPONSE.(NO EXPENSES NOTED WERE PD BY OPERATOR) |  | 24 | 16.58252427184466019417475728155339805825 |  | 0 | 28024 | 15335.9298743895547184466019417475728155 | 37007.6483875587646601941747572815533981 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | KRIS BUSKO | GAS COMPLIANCE MANAGER | kristen.busko@avistacorp.com | 509-495-8767 | 509-777-6027 |  |  |  | KRIS BUSKO | GAS COMPLIANCE MANAGER | 509-495-8767 | kristen.busko@avistacorp.com | A DRUNK DRIVER HIT A REGULATOR STATION, SEVERELY DAMAGING THE STATION BUT CAUSING ONLY A SMALL HOLE WHERE A FITTING WAS KNOCKED OFF. THE DRIVER WAS TREATED AND RELEASED WITH MINOR INJURIES, AND THE COST OF THE EVENT IS APPROX $28,000. THIS INCIDENT IS REPORTABLE DUE TO HIGHWAY 95 BEING CLOSED FOR APPROXIMATELY 2 HOURS DUE TO THE INCIDENT. THOUGH PART D ASKS FOR COSTS PAID BY THE OPERATOR ONLY, ALL COSTS ARE INCLUDED IN THIS SECTION SINCE THERE IS NOWHERE ELSE ON THE FORM TO PUT THE INFORMATION.
2025-03-31 10:13 | NO | YES | NO | 20100094 | 16314 | 2010-10-29 16:29 | SUPPLEMENTAL FINAL | 3240 | DELMARVA POWER & LIGHT COMPANY | 630 MARTIN LUTHER KING JR. | WILMINGTON | DE | 19801 | 2010-10-01 03:35 |  |  | 2010 | COLONY NORTH & LEA BLVD | WILMINGTON | NEW CASTLE COUNTY | DE | 19802 | 39.7568 | -75.5172 | [9 empty] | 2010-10-01 06:15 | 955699 |  | NATURAL GAS |  | 80 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-10-01 03:35 |  |  |  | 2010-10-01 03:50 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | YES | YES | UNCASED | [9 empty] | PRIVATELY OWNED |  | MAIN |  | 1967 | [5 empty] | 6 | API5L, GRADE B | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.28 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 65000 | 85872.11718263035 | 450 | 594.4992728028255 | 30000 | 39633.2848535217 | BUILT A TEMPORARY ROAD FOR CONSTRUCTION EQUIPMENT AND OPERATOR PERSONNEL ACCESS. |  | 50 | 34.54692556634304207119741100323624595469 |  | 0 | 95500 | 52258.7551446762882967637540453074433657 | 126134.448234521218542071197411003236246 | 8 | 0 | 370 |  |  |  |  | 34 | 35 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | [8 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  | YES | [216 empty] | ROBERT G KITSON | MANAGER GAS ENGINEERING | robert.kitson@delmarva.com | 3024293848 | 3024293207 |  |  |  | ROBERT G KITSON | MANAGER GAS ENGINEERING | 3024293848 | robert.kitson@delmarva.com | THIS IS THE FINAL REPORT. IN THE EARLY MORNING HOURS FRIDAY, OCT. 1, AS REMNANTS OF TROPICAL STORM NICOLE PASSED THROUGH DELAWARE WITH HEAVY RAINS AND HIGH WINDS, COLONY BOULEVARD (A PRIVATE ROAD) OVER THE SHELLPOT CREEK NEAR WILMINGTON, DE BEGAN TO CRUMBLE, WASHING AWAY THE ROAD BASE DOWN TO TWO STEEL CULVERTS, AND EXPOSING A SIX-INCH GAS MAIN BURIED IN THE ROADWAY PRIOR TO THE WASH-OUT. IT IS BELIEVED THE EARTH MOVEMENT DISPLACED THE NOW UNSUPPORTED SIX INCH STEEL GAS MAIN, WHICH THEN DAMAGED A CATHODIC PROTECTION INSULATING JOINT, CAUSING AN UNINTENDED ESCAPE OF NATURAL GAS FROM THE INSULATING JOINT.
2025-03-31 10:13 | NO | NO | NO | 20100095 | 15127 | 2010-11-01 12:21 | ORIGINAL FINAL | 13400 | NEW ULM PUBLIC UTILITIES COMMISSION | 310 FIRST NORTH STREET | NEW ULM | MN | 56073 | 2010-09-28 13:50 |  |  | 2010 | BROADWAY AND COTTON ST | NEW ULM | BROWN | MN | 56073 | 44.2901 | -94.4397 | [9 empty] | 2010-09-28 16:00 | 955425 |  | NATURAL GAS |  | 70 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-09-28 14:00 |  |  |  | 2010-09-28 14:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | TRANSITION AREA | OTHER | UNDER A RIVER |  |  | YES | [6 empty] | YES | UNCASED, BORED/DRILLED | COTTONWOOD RIVER | 10 |  | MUNICIPALLY OWNED |  | MAIN |  | 1998 | [5 empty] | 4 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | LEAK | [9 empty] | CLASS 1 LOCATION | 0 | 0 | 20000 | 26422.1899023478 | 4800 | 6341.325576563472 |  | 0 |  |  | 350 | 241.828478964401294498381877022653721683 |  | 0 | 25150 | 13793.3709909179421773462783171521035599 | 33005.3439578756732944983818770226537217 | 0 | 0 | 25 |  |  |  |  | 18 | 18 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | REPORTED BY EMPLOYEE OF CITY WATER DEPARTMENT |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | LOG JAM | YES |  |  |  | YES | HEAVY RAINS/FLOODS | [213 empty] | GARY PORTNER | GAS SUPERVISOR | gary.portner@ci.new-ulm.mn.us | 507-359-8298 | 507-354-7318 |  |  |  | GARY PORTNER | GAS SUPERVISOR | 507-359-8289 | gary.portner@ci.new-ulm.mn.us | ON 9-28-2010 RECEIVED A CALL AT 1:50 PM FROM MIKE SELVIG, WATER DEPT. EMPLOYEE. HE WAS WORKING IN THE AREA, AND BYSTANDERS TOLD HIM THEY SMELLED GAS. MR. SELVIG RADIOED GARY PORTNER IN THE GAS DEPT. GARY THEN DISPATCHED PAUL MACHO AND DAVE O'BRIEN AND THEY RESPONED TO THIS GAS CALL. DAVE O'BRIEN FOUND GAS LEAKING AT 2:00 PM AND PAUL MACHO CALLED 911. SHUT OFF GAS REGULATING STSTION THAT FEEDS THAT AREA AT 2:15PM SET UP COMMOND POST AND PAUL MACHO WAS NAMED INCIDMENT COMMANDER. GARY PORTNER, GAS DEPT. SUPERVISOR, THEN CALLED THE STATE DUTY OFFICER AT 2:15 PM CASE #11485 CHECKED BOTH SIDES OF THE COTTONWOOD RIVER FOR GAS WITH CGI FOR UNDERGROUND MIGRATION AND FOUND NO GAS. WE ALSO CHECKED ALL HOMES AND BUSINESS IN THE AREA WITH CGI'S. AND FOUND NO GAS. WE CHECKING CHECKING #'S UNTIL THE GAS MAIN WAS BLED OFF. RELEASED FIRE DEPAETMENT AT 2:40 PM. WENT HOUSE TO HOUSE FROM2:30-2:40 PM AND TURNED OFF GAS SERVICES; 25 HOMES WERE TURNED OFF. AT APPROXIMATELY 2:30 PM THE GAS DEPT. CLERICAL ASSISANT STARTED NOTIFYING ALL AFFECTED CUSTOMERS BY PHONE TO LET THEM KNOW THAT THE GAS WAS TURNED OFF TO THEIR HOMES AND THAT EMERGENCY REPAIR WAS BEING CONDUCTED AT 2:41 PM THE GAS DEPT CALLED AN EMERGENCY LOCATE INTO GOPHER STATE ONE CALL TO EXPOSE THE MAIN ON BOTH SIDES OF THE COTTONWOOD RIVER. GAS DEPT. EMPLOYS THEN CAPPED AND TESTED THE MAIN THAT WILL BE PUT INTO SERVICE. GARY PORTNER, GAS DEPT. SUPERVISOR, THEN CALLED THE FEDERAL DUTY OFFICER AT 4:35 PM CASE #99425 ON 9-29-2010 AT 9:00AM THE GAS DEPT. CALLED AN EMERGENCY LOCATE IN TO GOPHER STATE ONE CALL. GAS DEPT. EMPOLYEES THEN RAN A 1" CTS GAS SERVICE THROUGH THE ELECTRIC DEPT. EMPTY 5" CONDUIT LINE 600 FEET WITH THE AID OFF THE ELEC. DEPT. AND STREET DEPT. TEMPORARY GAS SERVICE WAS RESTORED ON COTTONWOOD STREET BY 7:30PM. WHEN THE COTTONWOOD RIVER RECEDS, THE GAS DEPT. WILL INSTALL A NEW 4" MAIN UNDER THE RIVER BED
2025-03-31 10:13 | NO | YES | YES | 20100096 | 15190 | 2010-11-01 19:07 | SUPPLEMENTAL FINAL | 15329 | PEOPLES GAS LIGHT & COKE CO | 200 E RANDOLPH STREET | CHICAGO | IL | 60601 | 2010-03-03 13:28 |  |  | 2010 | 358 WEST JACKSON | CHICAGO | COOK | IL | 60606 | 41.8781 | -87.6369 | [9 empty] | 2010-03-03 13:50 | 932920 |  | OTHER GAS | COMPRESSED AIR |  |  | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO |  |  |  |  | NO |  | 2010-03-03 13:28 |  |  |  | 2010-03-03 13:28 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 20 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | NATURAL GAS WAS NOT RELEASED. COMPRESSED AIR WAS RELEASED FROM THE MAIN DURING A PRESSURE TEST. | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | BOLTED |  | COUPLING |  | UNKNOWN |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | SEE PART H | [7 empty] | YES | 2010 | 100 | [84 empty] | ALFREDO ULANDAY | MANAGER TECHNICAL TRAINING AND STANDARDS | asulanday@integrysgroup.com | 7735427814 | 7735427820 |  |  |  | EDWARD DOERK | VP GAS OPERATIONS | 7733957412 | edoerk@peoplesgasdelivery.com | PERFORMING A 100 POUND AIR PRESSURE TEST ON A 54 FOOT SEGMENT OF 20-INCH DIAMETER STEEL GAS MAIN WHEN AN UNEXPOSED 20-INCH BOLTED - TYPE MECHANICAL COUPLING GAVE WAY PROPELLING A SECTION OF THE 20-INCH DIAMETER GAS MAIN FORWARD. THE TEST WAS PERFORMED AS PART OF UPRATING AN EXISTING STEEL MAIN FROM LOW TO MEDIUM PRESSURE. DATA ENTRY NOTE: I WAS UNABLE TO ENTER 1954 FOR THE ACTUAL YEAR OF INSTALL OF THE PIPE IN PART C, QUESTION 2A. THE PROGRAM WOULD NOT LET ME ENTER A YEAR LESS THAN 1959. THE "UNKNOWN" BOX WAS CHECKED TO ALLOW ELECTRONIC COMPLETION OF THE FORM, BUT THE PIPE WAS INSTALLED IN 1954.
2025-03-31 10:13 | NO | NO | NO | 20100098 | 15554 | 2010-11-02 16:12 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2010-10-07 08:26 |  |  | 2010 | 112 W JEFFERSON | SOUTH BEND | ST. JOESPH | IN | 46601 | 41.6751 | -86.2508 | [9 empty] | 2010-10-07 09:50 | 956272 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 350 | 2010-10-07 08:26 |  |  |  | 2010-10-07 08:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2010 | [5 empty] | 2 | ATSM D3261, D2513, F1055 | CENTRAL PLASTICS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.8 | 6.2 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 900 | 1188.998545605651 | 4500 | 5944.992728028255 | 0 | 0 |  |  | 1404 | 970.077669902912621359223300970873786408 |  | 0 | 6804 | 3852.063868285530629126213592233009708738 | 8104.068943536818621359223300970873786408 | 74 | 0 | 1 |  |  |  |  | 35 | 35 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS THIRD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | NO |  |  |  | CONTRACT LOCATOR | NO | YES | 4 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JOHN CURTIS | MANAGER SYSTEM INTEGRITY AND DESIGN | jlcurtis@nisource.com | 219-962-0425 | 219-962-0404 |  |  |  | JOHN CURTIS | MANAGER SYSTEM INTEGRITY AND DESIGN | 219-962-0425 | jlcurtis@nisource.com | CEMENT CONTRACTOR ENGAGED IN STREET RESTORATION ACTIVITIES FOLLOWING A NATURAL GAS SYSTEM TIE-IN, HIT PIPELINE FACILIITES IN THE PROCESS OF DOING THIS ACTIVITY. ADDITIONAL INFORMATION: RESTORATION CONTRACTOR DID NOT CALL FOR LOCATES AND WAS OPERATING MECHANIZED EQUIPMENT OVER UNMARKED FACILITIES. CONTRACTOR HIT TAP-TEE ON MAIN WITH MECHANIZED EQUIPMENT. THE LAST LEAK SURVEY WAS CONDUCTED ON THIS FACILITY ON 12-29-2009. THERE WERE NO PREVIOUS PRESSURE TESTS ON THE FACILITY OTHER THAN THE ORIGINAL TEST.
2025-03-31 10:13 | NO | YES | YES | 20100099 | 15455 | 2010-11-03 17:23 | SUPPLEMENTAL FINAL | 30839 | WALDEN, TOWN OF | PO BOX 489 513 HARRISON ST | WALDEN | CO | 80480 | 2010-10-04 12:25 |  |  | 2010 | ALLEY BEHIND 505 GARFIELD STREET | WALDEN | JACKSON | CO | 80480 | 40.7294 | -106.279 | [9 empty] | 2010-10-05 22:59 | 956136 |  | NATURAL GAS |  | 100 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2010-10-04 12:25 |  |  |  | 2010-10-04 12:25 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 28 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1956 | [5 empty] | 2 | API 5L | UNKNOWN | STEEL |  | OTHER | ERW | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 3.5 | 0.7 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1000 | 1321.10949511739 | 4900 | 6473.436526075211 | 1000 | 1321.10949511739 | RESPONSE BY FIRE AND SHERIFF DEPTS |  | 400 | 276.375404530744336569579288025889967638 |  | 0 | 7300 | 4031.094554459774574110032362459546925566 | 9392.030920840735336569579288025889967638 | 0 | 0 | 0 |  |  |  |  | 20 | 20 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  | YES |  |  |  | DECOMMISSIONING | NO | [50 empty] | STEVEN SHUTE | PRESIDENT PINEDALE NATL GAS OPERATOR WALDEN GAS | pipeline@rof.net | 970-928-9208 |  |  |  |  | JAMES CAROTHERS | MAYOR TOWN OF WALDEN | 970-723-4344 | waldentownclerk@yahoo.com | ORIGINAL REPORT FILED 11/03/10. FINAL REPORT FILED 5/30/12 AT REQUEST OF PHMSA THROUGH COLORADO PUC. NO NEW INFORMATION TO REPORT.
2025-03-31 10:13 | NO | NO | NO | 20100100 | 15133 | 2010-11-08 11:59 | ORIGINAL FINAL | 13840 | NORTHWEST NATURAL GAS CO | 250 SW TAYLOR ST | PORTLAND | OR | 97204 | 2010-10-30 12:20 |  |  | 2010 | 5408 NE ST. JOHNS ROAD | VANCOUVER | CLARK COUNTY | WA | 98661-2052 | 45.662 | -122.6356 | [9 empty] | 2010-10-30 13:45 | 958522 |  | NATURAL GAS |  | 5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-10-30 12:24 |  |  |  | 2010-10-30 12:42 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1983 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.75 | [6 empty] | OTHER | [8 empty] | VEHICLE INTO METER SET. | CLASS 2 LOCATION | 0 | 0 | 1590 | 2100.5640972366501 | 0 | 0 | 0 | 0 |  |  | 50 | 34.54692556634304207119741100323624595469 |  | 0 | 1640 | 901.948579124633856763754045307443365696 | 2135.111022802993142071197411003236245955 | 1 | 0 | 0 |  |  |  |  | 38 | 38 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSED BY THIRD PARTY. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DARLENE T. MAURER | PIPELINE SAFETY COMPLIANCE SPECIALIST | darlene.maurer@nwnatural.com | 503-226-4211 | 503-273-4822 |  |  |  | JON G. HUDDLESTON | DIRECTOR DELIVER GAS | 503-226-4211 | jon.huddleston@nwnatural.com | AT APPROXIMATELY 12:24 P.M. ON OCTOBER 30, 2010, NW NATURAL WAS NOTIFIED BY A 9-1-1 DISPATCHER THAT A VEHICLE STRUCK A METER SET AT 5408 NE ST. JOHNS ROAD, VANCOUVER, CLARK COUNTY, WASHINGTON, RESULTING IN THE RELEASE OF NATURAL GAS. NW NATURAL PERSONNEL ARRIVED AT APPROXIMATELY 12:42 P.M., AND THE FIRST RESPONDER DISCOVERED THAT AS THE RESULT OF A TWO-CAR ACCIDENT, A VAN CRASHED INTO AND THROUGH THE UNOCCUPIED BUILDING AND STRUCK THE METER SET AND GUARD POSTS ON THE OTHER SIDE. THE RELEASE OF NATURAL GAS WAS CONTROLLED AT 12:52 P.M. SERVICE WAS INTERRUPTED TO ONE CUSTOMER. REPAIRS WERE COMPLETED AT 17:30 P.M. ON OCTOBER 30, 2010. SERVICE TO THE STRUCTURE HAS NOT BEEN RESTORED. THE COST TO REPAIR NW NATURAL'S FACILITIES TOTALLED $1,589.79. THE MAIN WAS OPERATING AT 38 PSIG, WITH A MAOP OF 50 PSIG. NW NATURAL REPORTED THE INCIDENT AS IT BELIEVED PROPERTY DAMAGE COULD APPROACH OR EXCEED $50,000.
2025-03-31 10:13 | NO | NO | NO | 20100101 | 15134 | 2010-11-08 17:12 | ORIGINAL FINAL | 18140 | SCOTTSBORO WATER SEWER & GAS BOARD | P O BOX 550 | SCOTTSBORO | AL | 35768 | 2010-10-20 19:34 |  |  | 2010 | 4623 SOUTH BROAD STREET | SCOTTSBORO |  | AL | 35769 | 34.6118 | -86.0667 | [9 empty] | 2010-10-21 14:00 | 957657 |  | NATURAL GAS |  | 8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2010-10-20 19:37 |  |  |  | 2010-10-20 19:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1985 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | OTHER | [8 empty] | 3/4 " NIPPLE WAS BROKE IN THREADED JOINT DUE TO CAR IMPACT. | CLASS 2 LOCATION | 0 | 0 | 1586 | 2095.27965925618054 | 1097 | 1449.25711614377683 | 0 | 0 |  |  | 100 | 69.09385113268608414239482200647249190939 |  | 0 | 2783 | 1531.956684532251175527508090614886731392 | 3613.630626532643454142394822006472491909 | 1 | 0 | 12 |  |  |  |  | 168 | 175 | 200 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | PAUL D. BUTLER | GAS SUPERINTENDENT | paul@scottsboro.org | 256-574-1744 | 256-574-1965 |  |  |  | ROY E. LIGHT | GENERAL MANAGER | 256-574-1744 | roy@scottsboro.org | THIS INCIDENT OCCURED AT A PRIVATELY OWNED SERVICE STATION/CONVENIENCE STORE ON OCTOBER 20,2010.THE NATURAL GAS METER SET WAS LOCATED IN THE BACK CORNER OF THE PARKING LOT APPROXIMATELY FIVE FEET FROM SIDE OF SERVICE STATION NEXT TO A UTILITY POLE. A PRIVATELY OWNED VEHICLE TRAVELED OFF THE PUBLIC ROADWAY ACROSS THE SERVICE STATION PARKING LOT.THE VEHICLE STRUCK THE NATURAL GAS METER SET BREAKING THE 3/4 INCH NIPPLE BETWEEN THE NATURAL GAS SERVICE LINE RISER VALVE (STOP COCK) AND THE GAS PRESSURE REGULATOR. NATURAL GAS RELEASE OCCURED AT THIS TIME. NATURAL GAS IGNITED ( IGNITION SOURCE UNKNOWN). BURNING VEHICLE AND BURNING NATURAL GAS IGNITED THE WOOD SIDING AND ROOF ON THE SERVICE STATION/CONVENIENCE STORE,AS WELL AS,THE UTILITY POLE. POLICE AND FIRE PERSONNEL WERE THE FIRST TO ARRIVE AT THE SCENE. POLICE REQUESTED ASSISTANCE FROM GAS SYSTEM PERSONNEL WHO IMMEDIATELY REPORTED TO THE SCENE AND CLOSED THE VALVE ON THE NATURAL GAS MAIN LINE STOPPING THE FLOW OF GAS TO THE SERVICE LINE AND BROKEN METER SET. FIREMAN EXTINGUSHED THE FIRE ON THE BURNING VEHICLE AND CONVENIENCE STORE. GAS SYSTEM PERSONNEL ISOLATED THE NATURAL GAS SERVICE LINE FOR THE SERVICE STATION/CONVENIENCE STORE FROM THE REST OF THE NATURAL GAS SYSTEM AND RESTORED SERVICE TO TWELVE RESIDENCES IN THE AREA THE SAME NIGHT. GAS SYSTEM PERSONNEL RESTORED THE SERVICE LINE/METER SET FOR THE CONVENIENCE STORE ON NOVEMBER 3, 2010. NO ONE WAS KILLED OR INJURED. NO ONE WAS HOSPITALIZED. THE ESTIMATED DAMAGE TO THE DRIVER'S VEHICLE WAS $4000. THE ESTIMATED DAMAGE TO THE SERVICE STATION/CONVENIENCE STORE WAS APPROXIMATELY $250,000. POLICE ARRESTED THE DRIVER OF THE VEHICLE FOR DRIVING UNDER THE INFLUENCE AND OBSTRUCTING GOVERNMENTAL OPERATIONS.
2025-03-31 10:13 | NO | NO | NO | 20100102 | 15205 | 2010-11-09 11:22 | SUPPLEMENTAL FINAL | 15350 | DOMINION PEOPLES | 1201 PITT STREET | WILKINSBURG | PA | 15221 | 2010-04-26 12:14 |  |  | 2010 | NEAR 66-277 CREEK ROAD, FROM GOOGLE MAPS | BURGETTSTOWN | WASHINGTON | PA | 15021 | 40.395 | -80.3664 | [9 empty] | 2010-04-26 16:05 | 938250 |  | NATURAL GAS |  | 4971 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-04-26 12:14 |  |  |  | 2010-04-26 12:57 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1969 | [5 empty] | 10.75 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 3 | 2 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 42217 | 55773.27955537085363 | 0 | 0 | 0 | 0 |  |  | 40987 | 28319.4967637540453074433656957928802589 |  | 0 | 83204 | 49296.8122325121456251197411003236245955 | 84092.7763191248989374433656957928802589 | 0 | 0 | 0 |  |  |  |  | 68 | 68 | 82 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE LANDOWNER | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | UNKNOWN/OTHER | NO |  |  |  | CONTRACT LOCATOR | YES |  |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | MAPPING RECORDS ERROR. | [169 empty] | PAUL A. HESS | SUPERVISOR GAS OPERATIONS | paul.a.hess@peoples-gas.com | 412-244-4381 |  |  |  |  | KENNETH M. JOHNSTON | VICE PRESIDENT GAS OPERATIONS | 412-473-4132 | kenneth.m.johnston@peoples-gas.com | THE MINE OPERATOR UNCOVERED THE PIPELINE ON A SATURDAY. HE CALLED PEOPLES DAMAGE PREVENTION HOTLINE AND WAS INSTRUCTED TO MAKE AN EMERGENCY ONE CALL. PHONE RECORDS FROM THE ONE CALL CENTER DO NOT INDICATE THAT HE CALLED. PEOPLES SENT A REPRESENTATIVE TO THE SITE THE SAME DAY, WHICH WAS A SATURDAY, AND TOLD THE OPERATOR TO STAY AWAY FROM IT UNTIL WE CHECK OUR ENGINEERING RECORDS. ON THE FOLOWING MONDAY, THE OPERATOR AND PEOPLES ENGINEERING DEPARTMENT HAD CONVERSATIONS. THE ENGINEERING DEPARTMENT AND OPERATOR MISS-COMMUNICATED. OPERATOR COMMENCED DIGGING AND PUNCTUATED THE PIPE, CAUSING THE RELEASE OF GAS.
2025-03-31 10:13 | YES | NO | NO | 20100103 | 15282 | 2010-11-12 13:35 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2010-10-12 03:55 |  |  | 2010 | 2800 GENTRYTOWN DRIVE | ANTIOCH | CONTRA COSTA | CA | 94509 | 37.9959 | -121.8391 | [9 empty] | 2010-10-12 10:00 | 956728 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2010-10-12 03:58 |  |  |  | 2010-10-12 04:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMININ | [9 empty] | OTHER | [8 empty] | SECONDARY | CLASS 3 LOCATION | 100000 | 132110.949511739 | 5000 | 6605.54747558695 | 2000 | 2642.21899023478 | 0 | 0 |  |  | 0 | 0 |  | 0 | 107000 | 58546.540619156478 | 141358.71597756073 | 6 | 0 | 6 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | GARY F. GUERRERO | SENIOR COMPLIANCE ANALYST | gfg2@pge.com | 925-974-4075 |  |  |  |  | GLEN E. CARTER | SENIOR DIRECTOR GAS ENGINEERING | 925-974-4231 | No Email Address | A FIRE OCCURRED AT AN APARTMENT COMPLEX AT 2800 GENTRYTOWN DRIVE IN ANTIOCH, CALIFORNIA AT APPROXIMATELY 0355 HOURS ON OCTOBER 12, 2010. THE FIRE DEPARTMENT NOTIFIED PG&E OF THIS FIRE AT APPROXIMATELY 0358 HOURS. THE PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED AT APPROXIMATELY 0415 HOURS. THE APARTMENT BUILDING AT 2800 GENTRYTOWN DRIVE HAD COLLAPSED ON THE SERVICE RISER RESULTING IN GAS BEING RELEASED TO THE ATMOSPHERE. A PG&E GAS CREW WAS CALLED AND THEY STOPPED THE FLOW OF GAS AT APPROXIMATELY 0640 HOURS BY SQUEEZING OFF THE 1.25-INCH PLASTIC SERVICE LINE APPROXIMATELY 15-FEET FROM THE BUILDING. THE APARTMENT FIRE DAMAGED A FIVE-METER MANIFOLD AND THE METERS. IN ADDITION, AN EIGHT METER MANIFOLD AND METERS ON THE BUILDING NEXT DOOR WERE SCORCHED AND DAMAGED BY THE FIRE. THE FIRE DAMAGE TO THE APARTMENT BUILDINGS RESULTED IN PROPERTY DAMAGES EXCEEDING $50,000. THE OCCUPANTS OF BOTH APARTMENT BUILDINGS WERE DISPLACED BY THE FIRE. THE CAUSE OF THE FIRE REMAINS OFFICIALLY UNDETERMINED, BUT FIRE INVESTIGATORS INDICATED AT THE SCENE THAT THERE WAS A LARGE PILE OF ROOFING DEBRIS BETWEEN THE BUILDINGS THAT MAY HAVE BEEN THE SOURCE. PG&E HAS REQUESTED A COPY OF THE FIRE DEPARTMENT REPORT. GAS SERVICE TO BOTH APARTMENT BUILDINGS WAS DISRUPTED. SERVICE WILL BE RESTORED WHEN REPAIRS TO THE HOUSE ARE COMPLETED AND THE CUSTOMERS REQUEST SERVICE RESTORATION. THERE WERE NO INJURIES AND NO FATALITIES AS A RESULT OF THIS INCIDENT. MAJOR BAY AREA MEDIA, KTVU CHANNEL 2 AND ABC NEWS CHANNEL 7, WERE PRESENT AT THE SCENE
2025-03-31 10:13 | NO | YES | NO | 20100104 | 15138 | 2010-11-18 14:41 | ORIGINAL FINAL | 30750 | MIDAMERICAN ENERGY COMPANY | 666 GRAND AVENUE, SUITE 500 | DES MOINES | IA | 50309-2580 | 2010-10-18 18:23 |  |  | 2010 | 4040 SOUTHGATE DRIVE | SIOUX CITY | WOODBURY | IA | 51106 | 42.4382 | -96.3693 | [9 empty] | 2010-10-18 20:20 | 957336 |  | PROPANE GAS |  | 38 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2010-10-18 18:23 |  |  |  | 2010-10-18 18:23 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | OTHER | LP-AIR PLANT ABOVE GROUND PIPING |  |  | NO | [11 empty] | OTHER | LIQUID PROPANE PLANT | OTHER | PROPANE PIPE | 1976 | [8 empty] | OTHER | PROPANE | [9 empty] | OTHER | [8 empty] | OPERATOR ERROR - OPENED VALVE. | CLASS 4 LOCATION | 0 | 0 | 1078000 | 1424156.03573654642 | 2400 | 3170.662788281736 |  | 0 |  |  | 1091 | 753.813915857605177993527508090614886731 |  | 0 | 1081491 | 591853.2330806468735093851132686084142395 | 1428080.51244068576117799352750809061489 | 0 | 0 | 0 |  |  |  |  | 90 | 90 | 250 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | INCORRECT OPERATION | INCORRECT VALVE POSITION | [222 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  | OTHER MAINTENANCE | NO | [50 empty] | EDWARD A. DREESMAN | MANAGER GAS ENGINEERING | eadreesman@midamerican.com | 712-277-7750 | 712-252-7360 |  |  |  | EDWARD A. DREESMAN | MANAGER GAS ENGINEERING | 712-277-7750 | eadreesman@midamerican.com | ON OCTOBER 18, 2010, AT 18:23, A FIRE AND EXPLOSION OCCURRED AT THE SIOUX CITY LIQUID PROPANE PLANT IN SIOUX CITY, IOWA. TWO EMPLOYEES WERE ISOLATING AND VENTING THE PLANT SEND-OUT PIPING IN PREPARATION FOR PIPE MODIFICATION. THE PRODUCT BEING VENTED WAS PROPANE. BECAUSE OF THE LOCATION OF THE VENTING, PROPANE LIQUID AND VAPOR ACCUMULATED. THE VAPOR WAS IGNITED BY AN ELECTRICAL SOURCE IN AN UNOCCUPIED ROOM CAUSING AN EXPLOSION AND FIRE. THE EXPLOSION COMPROMISED THE VAPOR BARRIER BETWEEN THE ELECTRONIC EQUIPMENT AND THE MIXER ROOM, AND FIRE IGNITED PROPANE VAPORS THAT HAD ACCUMULATED IN THE MIXER ROOM. THE BUILDING AND ELECTRONIC EQUIPMENT SUSTAINED SIGNIFICANT DAMAGE. THE INCIDENT INVOLVED THE RELEASE OF PROPANE, FIRE, EXPLOSION AND PROPERTY DAMAGE EXCEEDING $50,000. THEREFORE, THE INCIDENT WAS REPORTABLE AS REQUIRED BY PIPELINE HAZARDOUS MATERIAL SAFETY ADMINISTRATION RULES 49 CFR 191.3. THERE WERE NO INJURIES AND NO DEATHS. THE ON-SITE PAINTING CONTRACTOR EMPLOYEES THAT WERE WORKING SEVERAL HUNDRED FEET FROM THE INCIDENT ALSO EVACUATED THE PLANT WITHOUT INJURY. THE LOCAL FIRE DEPARTMENT RESPONDED, AND POLICE BLOCKED THE PUBLIC ROAD PASSING IN FRONT OF THE PLANT. THERE WAS EXTENSIVE MEDIA COVERAGE.
2025-03-31 10:13 | NO | NO | NO | 20100105 | 15139 | 2010-11-19 17:30 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2010-10-20 00:34 |  |  | 2010 | 728 E. CHURCH STREET | SANDWICH | DEKALB | IL | 60548 | 41.6448 | -88.612 | [9 empty] | 2010-10-20 02:35 | 957469 |  | NATURAL GAS |  | 28.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES |  | 2010-10-20 00:34 |  |  |  | 2010-10-20 01:16 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.14 | [6 empty] | OTHER | [8 empty] | 3/4" METER SET RISER SHEARED OFF. | CLASS 3 LOCATION | 45000 | 59449.92728028255 | 3150 | 4161.4949096197785 | 250 | 330.2773737793475 | 0 | 0 | OPERATOR NOT EXPECTED TO PAY FOR ANY PUBLIC OR PRIVATE PROPERTY DAMAGE. |  | 150 | 103.640776699029126213592233009708737864 |  | 0 | 48550 | 26578.6080477832205902912621359223300971 | 64045.3403403807051262135922330097087379 | 1 | 0 | 2 |  |  |  |  | 56 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | lquezad@nicor.com | 630-388-2316 | 630-983-0639 |  |  |  | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | 630-388-2316 | lquezad@nicor.com | DRIVER VEERED OFF THE ROAD, JUMPED A CURB THEN HIT A METAL FENCE BEFORE HITTING A BUILDING AND CAUSING DAMAGE TO THE GAS METER SET THAT WAS ATTACHED TO THE BUILDING.
2025-03-31 10:13 | YES | NO | NO | 20100109 | 15149 | 2010-12-15 16:51 | ORIGINAL FINAL | 32513 | AMEREN ILLINOIS COMPANY | 2125 EAST STATE ROUTE 104 | PAWNEE | IL | 62558 | 2010-11-16 05:40 |  |  | 2010 | 629 BRANDYWINE LANE | JACKSONVILLE | MORGAN | IL | 62650 | 39.7479 | -90.2475 | [9 empty] | 2010-11-16 15:00 | 960009 |  | NATURAL GAS |  | 3 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-11-16 05:40 |  |  |  | 2010-11-16 05:51 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | STRUCTURE "FIRE FIRST" MELTED RISER |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 2003 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 7 |  |  | 2406 | OTHER | [8 empty] | FIRE FIRST" - STRUCTURE FIRE CAUSED BY ELECTRIC SPACE HEATER MELTED A PORTION OF THE PE RISER CAUSING A SUBSEQUENT SMALL GAS FIRE AT THE BASE OF THE RISER. | CLASS 3 LOCATION | 0 | 0 | 118 | 155.89092042385202 | 312 | 412.18616247662568 | 0 | 0 |  |  | 21 | 14.50970873786407766990291262135922330097 |  | 0 | 451 | 248.702820435753598640776699029126213592 | 582.586791638341777669902912621359223301 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CHARLES RAYOT | SUPERVISING ENGINEER | crayot@ameren.com | 217-625-6802 | 217-625-6803 |  |  |  | JEROME THEMIG | MANAGER GAS COMPLIANCE | 217-625-6804 | jthemig@ameren.com | AMEREN ILLINOIS RECEIVED AN INITIAL CALL FROM THE FIRE DEPARTMENT ON 11/16/2010 AT 05:40 OF A STRUCTURE FIRE AT 629 BRANDYWINE LANE IN JACKSONVILLE, ILLINOIS. FIRE DEPARTMENT REQUESTED GAS AND ELECTRIC TO BE DISCONNECTED DUE TO HOUSE FIRE. AMEREN ILLINOIS FIRST RESPONDER ARRIVED ON SITE AT 05:51. HEAT OF STRUCTURE FIRE HAD SUBSEQUENTLY CAUSED THE POLYETHYLENE PIPE IN THE RISER TO MELT AT THE AREA OF THE CRIMP JUST ABOVE GROUND LEVEL. A SMALL AMOUNT OF GAS WAS RELEASED WHICH THEN IGNITED RESULTING IN A SMALL GAS FIRE ABOUT SIX INCHES IN DIAMETER AND FOUR INCHES IN HEIGHT. THE RISER WAS EXCAVATED AND SQUEEZED OFF AT 06:10 STOPPING THE FLOW OF GAS. THE SERVICE WAS CUT AND CAPPED AND REMAINS CAPPED OFF. IT IS NOT KNOWN AT THIS TIME WHETHER OR NOT SERVICE WILL BE REINSTATED AT THIS LOCATION. PROPERTY DAMAGE TO THE TRAILER WAS ESTIMATED TO BE NO MORE THAN $15,000 AT THAT TIME AND THE EVENT WAS CONSIDERED A "FIRE FIRST" AND NOT A REPORTABLE INCIDENT AS PROPERTY DAMAGE WAS ESTIMATED TO BE LESS THAN $50,000. AFTER THE SCENE WAS SECURED AND FIRE EXTINGUISHED, INVESTIGATION INTO THE CAUSE OF THE FIRE ENSUED. THE ILLINOIS STATE FIRE MARSHAL INVESTIGATOR INFORMED THE AMEREN ILLINOIS SUPERVISOR GAS OPERATIONS THAT HIS INITIAL INVESTIGATION REVEALED THAT THE FIRE STARTED IN THE KITCHEN/DINING AREA. THE TRASH AND CLUTTER IN THIS AREA WAS IGNITED BY ONE OF THE THREE ELECTRIC SPACE HEATERS THAT WERE IN THE AREA. IT WAS ALSO STATED THAT THERE HAD BEEN ONE FATALITY DUE TO BURNS AND SMOKE INHALATION. THE SUPERVISOR MADE NECESSARY CONTACTS AFTER LEARNING THIS FACT AND AMEREN ILLINOIS THEN DETERMINED THIS TO BE A REPORTABLE INCIDENT AT 13:10. NECESSARY INFORMATION WAS GATHERED AND THE INCIDENT WAS REPORTED TO THE NRC AT 15:00. PLEASE NOTE: IN PART A OF THIS REPORT, 17 A. LOCAL TIME OPERATOR IDENTIFIED INCIDENT IS LISTED AS 05:40 WHICH IS THE TIME THE EMERGENCY CALL WAS RECEIVED AND NOT THE TIME AMEREN ILLINOIS DETERMINED THIS TO BE A REPORTABLE INCIDENT SINCE THE LOGIC BUILT INTO THIS DATA ENTRY FORM REQUIRES THE DATE AND TIME IN 17 B. LOCAL TIME OPERATOR RESOURCES ARRIVED ON SITE TO BE GREATER THAN OR EQUAL TO OPERATOR IDENTIFIED DATE AND TIME IN 17 A. A COPY OF THE JACKSONVILLE FIRE DEPARTMENT REPORT WAS OBTAINED AND FORWARDED ON TO THE ILLINOIS COMMERCE COMMISSION CONFIRMING THE AREA OF ORIGIN TO BE IN THE KITCHEN/DINING AREA AND THAT THE POSSIBLE CAUSE IS SUSPECTED TO BE A "SPACE HEATER FOUND HEAVILY DAMAGED IN THAT LOCATION".
2025-03-31 10:13 | NO | YES | NO | 20100110 | 15215 | 2010-12-16 16:16 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 200 CIVIC CENTER DR, P.O. BOX 117 | COLUMBUS | OH | 43215 | 2010-11-16 17:21 |  |  | 2010 | DISTRICT REGULATOR STATION, R-316, MANHATTAN BLVD & SUDER AVE. | TOLEDO | LUCAS | OH | 43611 | 41.688 | -83.4983 | [9 empty] | 2010-11-16 19:28 | 960035 |  | NATURAL GAS |  | 862 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2010-11-16 17:21 |  |  |  | 2010-11-16 17:30 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1964 | [8 empty] | OTHER | RTU STAINLESS STEEL TUBING, FLANGEGASKET | [9 empty] | OTHER | [8 empty] | ARC BURN ON STAINLESS STEEL TUBING | CLASS 3 LOCATION | 0 | 0 | 514417 | 679601.18314980241163 | 8800 | 11625.763557033032 | 64000 | 84551.00768751296 | INSTALLED TEMPORARY REGULATOR STATION |  | 7400 | 5112.944983818770226537216828478964401294 |  | 0 | 594617 | 326033.735544644942939035598705501618123 | 780890.8993781671738565372168284789644013 | 0 | 1 | 0 |  |  |  |  | 131 | 131 | 145 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 2 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | ROB SMITH | OPERATION COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB R. SMITH | OPERATION COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | ON 11-16-10 A FIRE WAS REPORTED TO COLUMBIA GAS OF OHIO (COLUMBIA) BY THE TOLEDO FIRE DEPARTMENT. COLUMBIA PERSONNEL ARRIVED AND FOUND COLUMBIA'S DISTRICT REGULATOR STATION, R-316, MANHATTAN BLVD & SUDER AV., ON FIRE. COLUMBIA CREWS OPERATED VALVES TO SHUT IN THE STATION FOR SAFETY. DISTRICT STATION, R-316, CONTINUES TO BE OUT OF COMMISSION. A TEMPORARY REGULATOR STATION HAS BEEN INSTALLED TO ENSURE SAFE, RELIABLE SERVICE TO CUSTOMERS DURING WINTER OPERATIONS. CURRENTLY SERVICE HAS BEEN RESTORED TO ALL CUSTOMERS. COLUMBIA'S CAUSE AND ORIGIN INVESTIGATORS HAVE CONCLUDED THAT THE CAUSE OF THIS FIRE WAS THE RESULT OF A CROSS ARM FAILURE FROM OUR ELECTRICAL PROVIDER'S NEARBY POWER POLE. THE HIGH VOLTAGE PRIMARY CONDUCTORS (LINES) FELL INTO THE SECONDARY ELECTRICAL DROP SERVING COLUMBIA'S REGULATOR STATION BUILDING AND ENERGIZED THE NEUTRAL TO 7200 VOLTS. THIS RESULTED IN A FAULT CURRENT THAT TRAVELED VIA ALL AVAILABLE GROUND PATHS TO STAINLESS STEEL CONTROL LINES LOCATED INSIDE THE STATION. THE SUBSEQUENT ELECTRICAL ARCING RESULTED IN HOLES BEING BURNED IN THE STAINLESS STEEL CONTROL LINES WHICH RELEASED GAS THAT WAS IGNITED BY THE ELECTRICAL ARCING, RESULTING IN THE INITIAL PHASE OF THIS FIRE. ONCE THE GAS-FED FIRE IGNITED WITHIN THE REGULATOR STATION FROM THE ELECTRICALLY DAMAGED STAINLESS STEEL CONTROL LINES AND CONTROL BOX, THE FIRE FROM THE CONTROL LINES BURNED THE GASKETS OUT OF THE LARGE DIAMETER PIPE FLANGES AND A MUCH LARGER FIRE ENSUED FED BY THE 130 PSIG GAS. THIS IS CONSISTENT WITH EYE WITNESS ACCOUNTS THAT THE FIRE THAT DAMAGED THE REGULATOR BUILDING DID NOT START UNTIL 20 TO 30 MINUTES AFTER THE POWER LINES CAME DOWN
2025-03-31 10:13 | NO | YES | NO | 20100111 | 15850 | 2010-12-22 14:42 | SUPPLEMENTAL | 2652 | NSTAR GAS COMPANY | ONE NSTAR WAY | WESTWOOD | MA | 02090 | 2010-11-03 08:52 |  |  | 2010 | 17 DANNY ROAD | HYDE PARK | SUFFOLK | MA | 02136 | 42.2411 | -71.1369 | [9 empty] | 2010-11-03 15:37 | 958866 |  | NATURAL GAS |  | 4 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES |  | 2010-11-03 08:52 |  |  |  | 2010-11-03 09:10 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1960 | [5 empty] | 1 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.133 | [6 empty] | OTHER | [8 empty] | KOMATSU PC240LC BACKHOE EXCAVATOR OPERATED BY A THIRD PARTY CONTRACTOR PULLED GAS LINE CAUSING BREAK | CLASS 3 LOCATION | 500000 | 660554.747558695 | 0 | 0 | 0 | 0 | 0 | 0 | COSTS ORIGINALLY UNKNOWN. ESTIMATE OF PROPERTY DAMAGE ADDED 4/21/14. |  | 240 | 165.825242718446601941747572815533980583 |  | 0 | 500240 | 273735.3635683294271844660194174757281553 | 660720.5728014134466019417475728155339806 | 0 | 0 | 1 |  |  |  |  | 22 | 22 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY CONTRACTORS DAMAGE TO THE GAS SERVICE LINE DID NOT CAUSE SUFFICIENT REDUCTION OF PRESSURE ON THE SYSTEM TO TRIGGER ANY SCADA ALARMS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER |  |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | KEVIN KELLEY | MANAGER - GAS DISTRIBUTION | kevin.kelley@nstar.com | (339) 987-8222 | (617) 369-5496 |  |  |  | WILLIAM MCCABE | DIRECTOR - GAS DISTRIBUTION | (508) 305-6950 | william.mccabe@nstar.com | ON NOVEMBER 3, 2010, A THIRD PARTY CONTRACTOR WAS INSTALLING NEW WATER MAINS IN THE PUBLIC WAY IN HYDE PARK, MASSACHUSETTS. WHILE EXCAVATING IN THE PUBLIC WAY, THE CONTRACTOR STRUCK AND PULLED UP A 1" IP STEEL GAS SERVICE TO 17 DANNY ROAD, HYDE PARK CAUSING AN UNINTENTIONAL RELEASE OF NATURAL GAS INTO THE HOME LOCATED AT 17 DANNY ROAD, HYDE PARK AND RESULTING EXPLOSION. THE 1" IP STEEL GAS SERVICE HAD BEEN INSTALLED WITH THE COVER OF 36 INCHES.THE CONTRACTOR HAD FAILED TO REQUEST A MARK-OUT OF UNDERGROUND FACILITIES IN DANNY ROAD AS REQUIRED BY MASSACHUSETTS DIG SAFE LAWS AND REGULATIONS. AS A RESULT OF THE EXPLOSION AND AS A PRECAUTION, EMERGENCY PERSONNEL AT THE SCENE EVACUATED SEVERAL ADJACENT RESIDENCES; THE NUMBER OF GENERAL PUBLIC EVACUATED IS NOT KNOWN.
2025-03-31 10:13 | NO | YES | YES | 20100112 | 15191 | 2010-12-22 16:45 | SUPPLEMENTAL FINAL | 15329 | PEOPLES GAS LIGHT & COKE CO | 200 E RANDOLPH STREET | CHICAGO | IL | 60601 | 2010-11-28 19:27 |  |  | 2010 | 12245 SOUTH ADA STREET | CHICAGO | COOK | IL | 60643-5405 | 41.6708 | -87.6547 | [9 empty] | 2010-11-28 20:48 | 960900 |  | NATURAL GAS |  | 1.3 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES |  |  |  |  | YES |  | 2010-11-28 19:34 |  |  |  | 2010-11-28 20:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | OTHER | CUSTOMER PIPING - SEE PART H NARRATIVE | OTHER | CUSTOMER PIPING - SEE PART H NARRATIVE | UNKNOWN | [8 empty] | OTHER | CUSTOMER PIPING - SEE PART H NARRATIVE | [9 empty] | OTHER | [8 empty] | SEE PART H NARRATIVE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 3724 | 4919.81175981716036 | 0 | 0 |  |  | 7 | 4.83656957928802588996763754045307443366 |  | 0 | 3731 | 2042.112589151415955546925566343042071197 | 4924.648329396448385889967637540453074434 | 0 | 0 | 3 |  |  |  |  | 0.21 | 0.21 | 0.43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT OCCURRED ON CUSTOMER PIPING - SEE PART H NARRATIVE | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | INCIDENT OCCURRED ON CUSTOMER PIPING - SEE PART H NARRATIVE | [47 empty] | ALFREDO ULANDAY | MANAGER TECHNICAL TRAINING AND STANDARDS | asulanday@integrysgroup.com | 7735427814 | 7735427820 |  |  |  | EDWARD DOERK | VP GAS OPERATIONS | 7733957412 | edoerk@peoplesgasdelivery.com | AT APPROXIMATELY 19:27 HOURS ON NOVEMBER 28, 2010, THERE WAS AN EXPLOSION AT A SINGLE-FAMILY RESIDENCE LOCATED AT 12245 SOUTH ADA STREET, CHICAGO, ILLINOIS ("PREMISES"). THE EXPLOSION DESTROYED THE PREMISES AND DAMAGED THE HOUSES ON EITHER SIDE (RESPECTIVELY, 12241 AD 12249 SOUTH ADA). PEOPLES GAS' RECORDS FOR THE PREMISES SHOW THAT THE NATURAL GAS SERVICE TO THE PREMISES WAS SHUT-OFF AT THE BUFFALO BOX (VALVE BOX) OUTSIDE THE PREMISES IN JUNE OF 2009, AND THAT THE NATURAL GAS SERVICE HAD NOT BEEN RESTORED BY PEOPLES GAS BETWEEN THE JUNE 2009 SHUT-OFF AND THE DATE OF THIS OCCURRENCE. PEOPLES GAS EMPLOYEES RESPONDING TO THE NOTICE OF THE EXPLOSION FROM THE CHICAGO FIRE DEPARTMENT FOUND THE SERVICE VALVE IN THE BUFFALO BOX IN THE "ON" POSITION. IN THE BASEMENT OF THE PREMISES, THERE WAS AN UNCAPPED, OPEN SECTION OF 1/2 INCH CUSTOMER PIPING THAT APPEARS TO BE THE SOURCE OF A GAS LEAK INSIDE THE PREMISES. NO LEAKS FROM ANY NATURAL GAS FACILITIES OF PEOPLES GAS WERE FOUND. POLICE AND FIRE DEPARTMENT REPORTS WHICH PEOPLES GAS HAS BEEN ABLE TO OBTAIN DO NOT INDICATE THAT ANY PERSON WAS EVACUATED. PEOPLES GAS DID NOT EVACUATE ANYONE. ON THE EVENING OF THE INCIDENT, PEOPLES GAS WAS ADVISED THAT 3 INDIVIDUALS WERE REMOVED FROM THE SCENE BY AMBULANCE AND WERE HOSPITALIZED. THE POLICE REPORT INDICATES THAT 4 OCCUPANTS OF A RESIDENCE IN THE 12200 BLOCK OF SOUTH ADA (ADDRESS REDACTED IN REPORT) WITH MINOR INJURIES WERE REMOVED FROM THE SCENE BY AMBULANCE. PEOPLES GAS WAS ALSO ADVISED THAT OCCUPANTS (UNKNOWN NUMBER) OF THE PREMISES OF 12241 S. ADA AND 12249 S. ADA SPENT THE NIGHT OF NOVEMBER 28, 2010 IN A MOTEL.
2025-03-31 10:13 | YES | NO | NO | 20100113 | 15153 | 2010-12-23 21:18 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2010-11-25 02:34 |  |  | 2010 | 3105 MADISON STREET | HYATTSVILLE | PRINCE GEORGE'S | MD | 20782 | 38.9618 | -76.9648 | [9 empty] | 2010-11-25 05:17 | 960729 |  | NATURAL GAS |  | 5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-11-25 02:34 |  |  |  | 2010-11-25 03:06 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | 2009 | [8 empty] | OTHER | CAST ALUMINUM | [9 empty] | OTHER | [8 empty] | FIRE DAMAGE TO METER BUILD-UP. | CLASS 3 LOCATION | 0 | 0 | 200 | 264.221899023478 | 2200 | 2906.440889258258 | 100000 | 132110.949511739 | DAMAGE TO THE HOUSE CAUSED BY THE FIRE AND EXTINGUISHING EFFORTS. |  | 20 | 13.81877022653721682847896440129449838188 |  | 0 | 102420 | 56042.3697079848051987055016181229773463 | 135295.4310702472732168284789644012944984 | 0 | 0 | 1 |  |  |  |  | 20 | 20 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MICHAEL UPSHAW | SUPERVISOR - DOT PIPELINE SAFETY COMPLIANCE | mupshaw@washgas.com | 703-750-4479 | 703-750-5591 |  |  |  | DAVID W. SPANGLER | MANAGER - DOT PIPELINE SAFETY COMPLIANCE | 703-750-4341 | dspangler@washgas.com | WASHINGTON GAS WAS CALLED BY THE PRINCE GEORGES FIRE BOARD FOR A HOUSE FIRE AT 3105 MADISON STREET IN HYATTSVILLE MD. THIS WAS ON THURSDAY, NOVEMBER 25, 2010, AT 2:34AM. CREW 358, HELEN ANDERSON ARRIVED AT 3:06AM AND FOUND THE INSIDE GAS METER VALVE WAS TURNED OFF BY THE FIRE DEPARTMENT. WASHINGTON GAS HAD CREW 343 PERFORM A 360 DEGREE BAR AND TEST UNDERGROUND MIGRATION SURVEY OVER THE SERVICE LINE AND AROUND THE HOUSE. NO INDICATIONS WERE FOUND. THEY ALSO TURNED OFF THE CURB VALVE LOCATED ON THE SERVICE LINE. AN ODORANT SAMPLE WAS TAKEN AND THE LEVEL OF ODORANT WAS DETERMINED TO BE ADEQUATE. WASHINGTON GAS CAME BACK ON 12/2/10 AND CAPPED THE SERVICE OFF AND CONDUCTED A PRESSURE TEST. AGAIN, NO LEAK INDICATIONS WERE FOUND. THE FIRE IS BELIEVED TO HAVE STARTED AROUND THE ELECTRICAL PANEL AND SPREAD FROM THERE LATER ENCOMPASSING WASHINGTON GAS FACILITIES.
2025-03-31 10:13 | NO | NO | NO | 20110003 | 15652 | 2011-01-06 13:15 | SUPPLEMENTAL FINAL | 5340 | FOLEY UTILITY BOARD, CITY OF (RIVIERA UTIL) | 413 EAST LAUREL AVE. | FOLEY | AL | 36535 | 2010-11-22 15:10 |  |  | 2010 | 226 EAST CANAL DRIVE | GULF SHORES | BALDWIN | AL | 36542 | 30.2792 | -87.6842 | [9 empty] | 2010-11-22 17:22 | 960532 |  | NATURAL GAS |  | 250 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 100 | 2010-11-22 15:15 |  |  |  | 2010-11-22 15:30 |  | NO | PUBLIC PROPERTY | TRANSITION AREA | OTHER | INTRACOASTAL WATERWAY CROSSING |  |  | YES | [6 empty] | YES | UNCASED | INTRACOASTAL WATERWAY | 3 |  | MUNICIPALLY OWNED |  | MAIN |  | 1960 | [5 empty] | 2.5 | UNKNOWN | CRANE COMPANY | STEEL |  | OTHER | UNKNOWN | 0.203 | [6 empty] | MECHANICAL PUNCTURE | 2.5 | [8 empty] | CLASS 3 LOCATION | 12500 | 16513.868688967375 | 60000 | 79266.5697070434 | 5000 | 6605.54747558695 | 0 | 0 |  |  | 2640 | 1824.077669902912621359223300970873786408 |  | 0 | 80140 | 44092.5832948386340291262135922330097087 | 104210.0635415006376213592233009708737864 | 1 | 0 | 0 |  |  |  |  | 214 | 214 | 297 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SCADA SYSTEM RECORDED THE PRESSURE DROP DUE TO THE DAMAGE. A LOW PRESSURE ALARM AT THE GULF SHORES REGULATOR STATION OCCURRED APPROXIMATELY 5 MINUTES FROM THE TIME WE WERE NOTIFIED BY THE THIRD PARTY WHO DAMAGED THE MAIN. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SITE DEVELOPMENT | NO |  |  |  | DATA NOT COLLECTED | YES | YES | 2 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | RICHARD PETERSON | MANAGER GAS DEPARTMENT | rpeterson@rivierautilities.com | 251.970.4146 | 251.955.6291 |  |  |  | RICHARD PETERSON | MANAGER GAS DEPARTMENT | 251.970.4146 | rpeterson@rivierautilities.com | THE DAMAGE TO THE PIPELINE WAS APPROXIMATELY TWO FEET UNDER WATER WITHIN THE INTRACOASTAL WATERWAY. WE MAINTAINED SERVICE TO THE ISLAND WITH A REDUNDANT FEE 3/4 MILE WEST OF THIS LOCATION. THE ONE SERVICE THAT WAS INTERUPPTED WAS RELOCATED TO THE BACK SIDE OF THE ISOLATION VALVE USED TO SHUT OFF THE SECTION OF MAIN THAT WAS DAMAGED. WE DID NOT CONSIDER THE REPAIR OR REPLACEMENT OF THIS MAIN AS AN EMERGENCY. WE COORDINATED THE INVESTIGATION OF OPTIONS WITH THE CONTRACTOR'S INSURANCE CARRIER ADN EVENTUALLY BID A REPLACEMENT BORE AFTER OBTAINING A CORP OF ENGINEERS PERMIT AND WAITING FOR THE SUMMER TOURIST SEASON TO END. THE MAIN WAS REPLACED AND BACK IN SERVICE BY LATE OCTOBER, 2011.
2025-03-31 10:13 | NO | YES | YES | 20110004 | 15264 | 2011-01-07 12:31 | SUPPLEMENTAL FINAL | 2364 | DUKE ENERGY OHIO | 139 EAST FOURTH STREET PO BOX 960 - ROOM 460-ANNEX | CINCINNATI | OH | 45202 | 2010-11-02 21:46 |  |  | 2010 | 800 FRANKLIN RD - APT #33 | LEBANON | WARREN | OH | 45036 | 39.441 | -84.2193 | [9 empty] | 2010-12-08 08:25 | 961668 |  | NATURAL GAS |  | 1500 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 7 | 7 | YES |  |  |  |  | YES | 30 | 2010-11-02 21:46 |  |  |  | 2010-11-02 22:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | HOUSELINE PIPING |  |  | NO | [11 empty] | OTHER | NATURAL GAS DISTRIBUTION, PUBLICLY OWNED | OTHER | HOUSELINE PIPING | 1973 | [8 empty] | OTHER | 1/2" FLEXIBLE GAS LINE | [9 empty] | OTHER | [8 empty] | UNKNOWN | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 30 |  |  |  |  | 251 | 251 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL WAS NOTIFIED BY PDWC DISPATCH @ 9:30PM - THEY WERE IN CONTACT WITH GAS OPERATIONS' PERSONNEL, GAS FIELD OPERATIONS PERSONNEL AND SERVICE DELIVERY PERSONNEL THROUGHOUT THE INCIDENT. | [12 empty] | NO |  |  | YES | 2 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | CONTRACTOR PERFORMING GAS METER TURN ON ACTIVITY DID NOT FOLLOW GAS PROCEDURE PROPERLY. |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | JAMES T CALLAHAN | LEAD REGULATORY COMPLIANCE SPECIALIST - GAS OPS | jim.callahan@duke-energy.com | 513-287-2824 | 513-651-5229 |  |  |  | JAMES E MEHRING | VICE PRESIDENT GAS OPERATIONS | 513-287-2535 | jim.mehring@duke-energy.com | REFER TO THE ATTACHED OHIO STATE FIRE MARSHAL - FIRE AND EXPLOSION INVESTIGATION BUREAU INCIDENT REPORT FOR THE "INITIAL REPORT". NOTE: THIS REPORT WAS INITIALLLY FILED AS "OTHER INCIDENT CAUSE" BASED ON THE INVESTIGATION BY THE OHIO STATE FIRE MARSHAL. IT WAS DETERMINED AFTER FURTHER INVESTIGATION BY THE PUBLIC UTILITIES COMMISION OF OHIO (PUCO), THAT A SUPPLEMENTAL REPORT BE SUBMITTED UNDER "INCORRECT OPERATIONS". IT SHOULD BE NOTED THAT WHEN THIS INCIDENT OCCURRED ON NOVEMBER 2, 2010, A COURTESY CALL WAS MADE TO THE PUCO HOTLINE TO INFORM THEM OF THE INCIDENT. BASED ON THE INFORMATION KNOWN AT THE TIME, PUCO STAFF INSTRUCTED DUKE ENERGY THAT THIS OCCURRED ON NON-JURISDICTIONAL PIPELINE AND WAS NOT REPORTABLE. AFTER AN ON-SITE INVESTIGATION MEETING WITH VARIOUS DUKE ENERGY REPRESENTATIVES AND PUCO INVESTIGATORS ON DECEMBER 2, 2010, THE PUCO STAFF INSTRUCTED DUKE ENERGY TO FILE AN INCIDENT REPORT (INITIAL REPORT), AFTER THEIR CONVERSATION WITH PHMSA (PIPELINE AND HAZARDOUS MATERIALS SAFETY ADMINISTRATION) STAFF. DUKE ENERGY RELIED ON THE OHIO STATE FIRE MARSHAL'S INCIDENT REPORT AND USED THAT AS THE EXPLANATION TO THE INCIDENT. AFTER PUCO FOLLOWED UP WITH ADDITIONAL INVESTIGATION OF THIS INCIDENT, PUCO RECOMMENDED BY LETTER DATED FEBRUARY 17, 2011, THAT DUKE ENERGY SUBMIT A SUPPLEMENTAL REPORT TO INDICATE THE INCIDENT WAS CAUSED DUE TO "INCORRECT OPERATIONS".
2025-03-31 10:13 | NO | NO | NO | 20110005 | 15180 | 2011-01-10 11:15 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2010-12-13 09:56 |  |  | 2010 | 3978 WHITE PLAINS ROAD | NEW YORK | BRONX | NY | 10466-3002 | 40.888 | -73.8604 | [9 empty] | 2010-12-13 16:42 | 962144 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | YES | 8 | 2010-12-13 09:56 |  |  |  | 2010-12-13 10:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | CUSTOMER-OWNED PIPING/EQUIPMENT | UNKNOWN | [8 empty] | OTHER | COMMERCIAL OVEN | [9 empty] | OTHER | [8 empty] | FDNY REPORTS COMMERCIAL OVEN CAUSE OF EXPLOSION. | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 4149 | 5481.28329524205111 | 50000 | 66055.4747558695 | EXCESS OF $50,000 IN DAMAGE TO BUILDING INTERIOR/CUSTOMER EQUIPMENT PER NYC DOB |  | 10 | 6.90938511326860841423948220064724919094 |  | 0 | 54159 | 29634.7712865708367453527508090614886731 | 71543.6674362248197184142394822006472492 | 1 | 0 | 0 |  |  |  |  | 0.25 | 0.5 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | FDNY INVESTIGATION DETERMINED CUSTOMER-OWNED COMMERCIAL STOVE, RECENTLY REPAIRED, WAS THE CAUSE OF THE EXPLOSION. | [47 empty] | KEVIN FAGAN | MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4989 |  |  |  | VICTOR DADARIO | DEPT. MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON MONDAY, 12/13/10, THE NYC FIRE DEPARTMENT (FDNY) REPORTED AN EXPLOSION IN A BAKERY TO THE GAS EMERGENCY RESPONSE CENTER (GERC). GAS DISTRIBUTION SERVICES (GDS) CREWS WERE DISPATCHED AND UPON ARRIVAL GDS FOUND THE FDNY HAD EVACUATED 4 BUILDINGS TOTALING 8 PEOPLE. FIVE OF THE EVACUEES WERE TAKEN TO AN UNKNOWN AREA HOSPITAL WITH MINOR INJURIES. THE FDNY HAD TURNED OFF 8 GAS METERS IN 3 BUILDINGS (# 3974, 3976 & 3978 WHITE PLAINS ROAD). THE EXPLOSION INVOLVED AN INDUSTRIAL OVEN IN THE BAKERY(# 3978 WHITE PLAINS ROAD) WHICH SUSTAINED SEVERE DAMAGE. THERE WAS NO STRUCTURAL DAMAGE BUT THERE WAS EXTENSIVE INTERIOR, AND SOME EXTERIOR DAMAGE TO THE BAKERY. THE ADJACENT BUILDINGS WERE NOT AFFECTED. GDS CHECKED THE GAS PRESSURE IN THE BAKERY AND FOUND 8.8" WC WITH NO LOAD. THERE WERE NO NATURAL GAS READINGS INSIDE ANY OF THE CONNECTED BUILDINGS. THE FDNY'S INVESTIGATION DETERMINED THE CUSTOMER-OWNED EQUIPMENT (COMMERCIAL OVEN) WAS THE SOURCE OF THE EXPLOSION. THE CUSTOMER HAD TROUBLE WITH THE OVEN ON THURSDAY 12/9/10 AND HAD IT SERVICED THAT DAY. THE OVEN WAS USED WITHOUT PROBLEMS ON FRIDAY 12/10/10 AND SATURDAY 12/11/10. ON MONDAY 12/13/10, WHEN BAKERY PERSONNEL ATTEMPTED TO LIGHT THE OVEN IT EXPLODED.
2025-03-31 10:13 | NO | YES | YES | 20110006 | 30953 | 2010-06-21 | SUPPLEMENTAL FINAL | 12642 | MOBILE GAS SERVICE CORP | 2828 DAUPHIN STREET | MOBILE | AL | 36606 | 2010-04-29 17:09 |  |  | 2010 | 4710 MOFFETT ROAD | MOBILE | MOBILE | AL | 36618 | 30.72 | -88.1511 | [9 empty] | 2010-05-05 08:25 | 939174 |  | NATURAL GAS |  | 0.5 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2010-04-29 17:09 |  |  |  | 2010-04-29 17:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  |  |  | NO | [11 empty] | OTHER | PRIVATELY OWNED DISTRIBUTION | MAIN |  | 1950 | [5 empty] | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 1321.10949511739 | REMOVAL OF SEGMENT OF PIPE FOR TESTING. |  | 10 | 6.90938511326860841423948220064724919094 |  | 0 | 1010 | 553.555516780671799352750809061488673139 | 1328.018880230658608414239482200647249191 | 0 | 0 | 0 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LOW VOLUME OF GAS RELEASED WOULD NOT HAVE BEEN DETECTED ON THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | CRACK WAS LIKELY CAUSED BY EXCESSIVE EXTERNAL WEIGHT OF VEHICLES PASSING OVER OR IN THE VICINITY OF THE PIPE. | [154 empty] | SHAUN SLADE | MANAGER PIPELINE SAFETY DISTRIBUTION | shaun.slade@spireenergy.com | 334-207-3090 |  |  |  |  | CRAIG HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | ON 4/29/2010, A SUBCONTRACTOR FOR AT&T ENTERED AN AT&T MANHOLE LOCATED AT MOFFETT ROAD AND SHELTON BEACH ROAD, IN MOBILE, ALABAMA, WHILE SMOKING A CIGARETTE. IT IS OUR BELIEF THAT THE AT&T SUBCONTRACTOR DID NOT FOLLOW PROPER AT&T PROCEDURES FOR AIRING OUT THE CONFINED SPACE AND EXTINGUISHING HIS CIGARETTE BEFORE ENTERING. ONCE THE SUBCONTRACTOR HAD ENTERED, A FLAMMABLE SUBSTANCE IN THE MANHOLE IGNITED AND BURNED THE SUBCONTRACTOR, REQUIRING MEDICAL TREATMENT. THE INVESTIGATION DETERMINED THAT NATURAL GAS MAY HAVE MIGRATED FROM AN NEARBY LEAK AND POSSIBLY COLLECTED IN THE MANHOLE. THE 4" CAST IRON MAIN IN THE VICINITY OF THE MANHOLE WAS REMOVED AND SENT TO A LAB FOR TESTING AND INSPECTION. THE TESTS DISCOVERED A CRACK IN THE PIPE APPROXIMATELY A HALF-BLOCK AWAY FROM THE MANHOLE. THE CRACK WAS LIKELY CAUSED BY EXCESSIVE EXTERNAL LOADING FROM PASSING VEHICLES. WHILE THE TYPE OF FLAMMABLE SUBSTANCE COULD NOT BE CONFIRMED, IT IS PRESUMED THAT THE INCIDENT WAS CAUSED BY LEAKING NATURAL GAS FROM THE CRACK IN THE PIPE THAT HAD MIGRATED TO AND COLLECTED IN THE AT&T MANHOLE. .
2025-03-31 10:13 | NO | NO | NO | 20110007 | 15168 | 2011-01-14 14:53 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2010-12-17 11:28 |  |  | 2010 | 554 W 113 STREET | NEW YORK | MANHATTAN | NY | 10025-8001 | 40.8057 | -73.9644 | [9 empty] | 2010-12-17 12:16 | 962522 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-12-17 11:28 |  |  |  | 2010-12-17 11:28 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | CUSTOMER PIPING | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | FAILED INTEGRITY TEST AT THREA | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 5000 | 6605.54747558695 | 0 | 0 |  |  | 100 | 69.09385113268608414239482200647249190939 |  | 0 | 5100 | 2799.735512705947993527508090614886731392 | 6674.641326719636084142394822006472491909 | 0 | 0 | 8 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | WHILE PERFORMING GAS METER EXCHANGE, COMPANY CONTRACTOR FOUND DEAD BODY IN APT. 1-R. THE HOUSE PIPIPING INTEGRITY TEST FAILED INTEGRITY. THE NYC MEDICAL EXAMINER RULED NATURAL GAS NOT INVOLVED. PERSON DIED FROM NATURAL CAUSES. GAS NOT INVOLVED. | [47 empty] | KEVIN FAGAN | MANAGER--GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER--GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON DECEMBER 17, 2010 GAS DISTRIBUTION SERVICES SUPERVISOR PAUL SMITH REPORTED TO THE GAS EMERGENCY RESPONSE CENTER THAT PRESICION PIPELINE SERVICES CONTRACTOR DAN SCHWEIGERT FOUND A DEAD BODY IN APARTMENT 1-R AT 554 W 113 STREET WHILE PERFORMING A METER EXCHANGE. SUPERVISOR SMITH REPORTED THAT AFTER EXCHANGING THE GAS METER SUPPLYING COOKING GAS TO THIS APARTMENT, SCHWEIGART ENTERED THE APARTMENT WITH ACCESS PROVIDED BY THE BUILDING'S SUPERINTENDENT AND FOUND THE RESIDENT HAD PASSED AWAY. BECAUSE THE INTEGRITY TEST HAD FAILED AND NO INFORMATION WAS AVAILABLE AS TO THE CAUSE OF DEATH AT THE TIME OF DISCOVERY, IT WAS DETERMINED TO REPORT THIS CONDITION AS "GAS MAY BE INVOLVED" . UPON COMPLETION OF THE N.Y.C MEDICAL EXAMINER DUNN'S EXAMINATION AT THE SCENE, IT WAS DETERMINED GAS WAS NOT INVOLVED AND DEATH WAS FROM NATURAL CAUSES. THE 82 YEAR OLD OCCUPANT OF APT. 1-R WAS RULED TO HAVE DECEASED APPROXIMATELY ONE (1) WEEK EARLIER. EMERGENCY RESPONSE GROUP PALMER REPORTED THE COOKING LINE SUPPLYING 8 APARTMENTS FAILED THE INTEGRITY TEST AND AS A RESULT THE METER WAS LEFT OFF, LOCKED, TAGGED AND HOLDING. THIS REPORT IS FOR RECORD PURPOSES ONLY. NATURAL GAS WAS NOT INVOLVED.
2025-03-31 10:13 | NO | YES | NO | 20110009 | 33412 | 2011-01-18 17:12 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2010-12-19 20:57 |  |  | 2010 | 4303 LEES CORNER ROAD | CHANTILLY | FAIRFAX | VA | 20151 | 38.8807 | -77.4205 | [9 empty] | 2010-12-19 22:20 | 962692 |  | NATURAL GAS |  | 6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-12-19 20:57 |  |  |  | 2010-12-19 21:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1966 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | DAMAGE TO THE METER BUILD-UP AS A RESULT OF AN EXPLOSION AND RESULTING FIRE. | CLASS 3 LOCATION | 0 | 0 | 15000 | 19816.64242676085 | 12000 | 15853.31394140868 | 420000 | 554865.9879493038 | APPROXIMATE VALUE OF THE BUILDINGS DAMAGED BY THE EXPLOSION AND RESULTING FIRE. |  | 35 | 24.18284789644012944983818770226537216828 |  | 0 | 447035 | 244604.647716170650297734627831715210356 | 590560.1271653697701294498381877022653722 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | RICHARD FITZPATRICK | DOT PIPELINE SAFETY SUPERVISOR | richardfitzpatrick@washgas.com | 7037505921 |  |  |  |  | STEPHEN PRICE | AVP SAFETY QUALITY SYSTEM PROTECTION | 7037504586 | sprice@washgas.com | WASHINGTON GAS WAS TOLD BY THE FIRE DEPARTMENT THAT THE METER VALVE WAS TURNED OFF BY THEM AT APPROXIMATELY 22:00. UPON GAINING ACCESS TO THE METER ON DECEMBER 20TH, WASHINGTON GAS CONDUCTED A PRESSURE TEST ON THE SERVICE LINE FROM THE METER VALVE TO THE CAPPED OFF LOCATION AT THE MAIN. THE SERVICE WAS TESTED AT THE OPERATING PRESSURE FOR 15 MINUTES. THE SERVICE LINE HELD THE PRESSURE TEST. AN ODORANT SAMPLE WAS TAKEN AND THE LEVEL OF ODORANT WAS DETERMINED TO BE ACCEPTABLE. WASHINGTON GAS HAS CONDUCTED ALL THE NECESSARY TESTS AND ACTIVITIES ON THE SYSTEM. ALTHOUGH POST INCIDENT INVESTIGATION FOUND CORROSION AT THE CONNECTION AT THE SERVICE TEE, ON THE STEEL MAIN, NEITHER WASHINGTON GAS NOR THE FIRE DEPARTMENT INVESTIGATION ESTABLISHED MIGRATION OF GAS FROM THE WASHINGTON GAS FACILITY TO THE STRUCTURE PRIOR TO THE INCIDENT. ADDITIONALLY, AN OPEN-ENDED SECTION OF THE CUSTOMER FUEL LINE TERMINATING ON THE SECOND FLOOR WAS FOUND. AS THE INTERIOR FUEL LINE OPERATED AT APPROXIMATELY .25 PSIG, GAS WOULD BE ESCAPING FROM THIS OPENING AT THAT PRESSURE UNTIL THE SERVICE REGULATOR CEASED TO FUNCTION PROPERLY AS A RESULT OF THE DAMAGE FROM THIS INCIDENT. THE ROOT CAUSE OF THIS INCIDENT REMAINS UNDETERMINED; THEREFORE, THE ANSWERS TO QUESTIONS NUMBERS 14 & 15 REMAIN "NO". WHILE THE FAIRFAX COUNTY FIRE DEPARTMENT MAY HAVE CONCLUDED, ON DECEMBER 31, 2010, THAT NATURAL GAS CONTRIBUTED TO THE INCIDENT, IT HAS YET TO BE DETERMINED WHO OR WHAT WAS AT FAULT. BASED UPON ALL KNOWN INFORMATION, THE CAUSE IS UNDETERMINED.
2025-03-31 10:13 | NO | YES | YES | 20110010 | 15558 | 2011-01-19 11:06 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2010-12-29 09:05 |  |  | 2010 | 2945 S. WAYNE ROAD | WAYNE | WAYNE | MI | 48184 | 42.2878 | -83.3841 | [9 empty] | 2010-12-29 10:29 | 963278 |  | NATURAL GAS |  | 600 |  | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | YES | 600 | 2010-12-29 09:05 |  |  |  | 2010-12-29 09:12 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1940 | [5 empty] | 2 | API 5L | UNKNOWN | STEEL |  | OTHER | WELDED | 0.15 | [6 empty] | OTHER | [8 empty] | 2 INCH MAIN SEPARATED AT THREADED JOINT (SEE PART H FOR FURTHER DETAILS) | CLASS 3 LOCATION | 2500000 | 3302773.737793475 | 40000 | 52844.3798046956 | 30000 | 39633.2848535217 | 0 | 0 |  |  | 3000 | 2072.815533980582524271844660194174757282 |  | 0 | 2573000 | 1408128.77844995111980582524271844660194 | 3397324.21798567288252427184466019417476 | 8 | 0 | 9 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 | 517-788-1369 |  |  |  | TRACY A. GOBLE | REGULATORY COMPLIANCE MANAGER | 517-768-3187 | tracy.goble@cmseneregy.com | AN EXPLOSION OCCURRED AT 2945 S. WAYNE RD., WAYNE MI AT 09:05 AM. THE INCIDENT LOCATION WAS THE WM. C. FRANKS FURNITURE STORE. OTHER NEARBY BUILDINGS WERE ALSO AFFECTED. THERE WERE TWO FATALITIES. ADDITIONALLY, TWO OTHER PEOPLE WERE INJURED REQUIRING HOSPITALIZATION. AN INVESTIGATION INTO THE CAUSE OF THE EXPLOSION WAS CONDUCTED. THE CAUSE OF THE INCIDENT REMAINS UNCERTAIN AND THE RESULTS OF THE INVESTIGATION ARE INCONCLUSIVE. A LEAK INSIDE THE FURNITURE STORE PRIOR TO THE EXPLOSION CANNOT BE RULED OUT. FROM THE INVESTIGATION TEAM'S REPORT, UNDER CERTAIN CIRCUMSTANCES A PLAUSIBLE GAS MIGRATION ROUTE INTO THE BUILDING FROM THE 2 INCH MAIN SEPARATION WOULD HAVE BEEN BY WAY OF THE SANITARY SEWER PIPE THROUGH A SEWER CROCK.
2025-03-31 10:13 | NO | YES | YES | 20110012 | 15249 | 2011-01-24 14:54 | SUPPLEMENTAL FINAL | 6510 | GRAND ISLE, TOWN OF | PO BOX 200 | GRAND ISLE | LA | 70358 | 2010-12-23 09:18 |  |  | 2010 | LA 1 & CENTRAL | GRAND ISLE | JEFFERSON PARISH | LA | 70356 | 29.2101 | -90.0501 | [9 empty] | 2010-12-28 13:00 |  |  | NATURAL GAS |  | 139 |  | NO | [5 empty] | 0 | YES | 0 | 2 | 0 | 0 | 0 | 2 | YES |  |  |  |  | NO | 0 | 2010-12-23 09:18 |  |  |  | 2010-12-23 09:18 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1974 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | 2" PIPE CUT TO INSTALL VALVE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 1000 | 1321.10949511739 | 0 | 0 |  |  | 695 | 480.20226537216828478964401294498381877 |  | 0 | 1695 | 991.379141376141055016181229773462783172 | 1801.31176048955828478964401294498381877 | 0 | 0 | 100 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | PREVENTION OF ACCIDENTIAL IGNITION |  |  |  | YES | FAILURE TO SECURE WET RAG TO PE PIPE | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | GEORGE MOULEDOUX JR | [7 empty] | GEORGE MOULEDOUX JR |  | 504-891-4711 |  | WHILE INSTALLING A POLY VALVE ASSENBLY ON A 2" FLANGED STEEL PIPE STATIC ELECTRICITY IGNITED THE ESCAPING GAS.
2025-03-31 10:13 | NO | YES | NO | 20110013 | 15175 | 2011-01-28 14:34 | ORIGINAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2010-12-30 13:51 |  |  | 2010 | 2057 ROUTE 208 | MONTGOMERY | ORANGE | NY | 12549 | 41.5095 | -74.2071 | [9 empty] | 2010-12-30 16:45 | 963400 |  | NATURAL GAS |  | 584 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-12-30 13:51 |  |  |  | 2010-12-30 14:05 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 72 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1990 | [5 empty] | 8 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 6.5 | 2.5 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 30000 | 39633.2848535217 | 155000 | 204771.97174319545 | 0 | 0 |  |  | 2844 | 1965.029126213592233009708737864077669903 |  | 0 | 187844 | 103043.0942290197521359223300970873786408 | 246370.2857229307422330097087378640776699 | 44 | 0 | 631 |  |  |  |  | 111 | 111 | 120 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | WATER | NO |  |  |  | CONTRACT LOCATOR | YES | YES | 24 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | DAVID W. MERTE | SECTION LEADER-GAS SYSTEM SAFETY AND INTEGRITY | dmerte@cenhud.com | 8454865521 | 8454865894 |  |  |  | ERIC J. KISZKIEL | MANAGER - GAS AND MECHANICAL ENGINEERING | 8454865472 | ekiszkiel@cenhud.com | DRILLING TECHNOLOGIES, INC. WAS CONDUCTING A HORIZONTAL DIRECTIONAL BORE FOR THE INSTALLATION OF A WATER MAIN. THE CONTRACTOR FAILED TO NOTIFY THE ONE CALL CENTER AND FAILED TO MAINTAIN 4" OF CLEARANCE FROM THE PIPELINE WITH MECHANIZED DIRECTIONAL DRILLING EQUIPMENT. THE EXCAVATOR WAS WORKING UNDER ANOTHER EXCAVATOR'S MARK-OUT REQUEST WHICH WAS NOT FOR DIRECTIONAL DRILLING.
2025-03-31 10:13 | YES | NO | NO | 20110014 | 15176 | 2011-01-28 15:55 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2010-12-29 17:07 |  |  | 2010 | 6010 COLUMBIA PIKE | FALLS CHURCH | FAIRFAX | VA | 22041-1911 | 38.8461 | -77.1399 | [9 empty] | 2010-12-29 19:15 | 963329 |  | NATURAL GAS |  | 5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-12-29 17:07 |  |  |  | 2010-12-29 17:31 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | 1955 | [8 empty] | OTHER | CAST ALUMINUM | [9 empty] | OTHER | [8 empty] | DAMAGE TO AN INSIDE METER BUILD-UP AS A RESULT OF A HOUSE FIRE. | CLASS 3 LOCATION | 0 | 0 | 150 | 198.1664242676085 | 2700 | 3566.995636816953 | 75000 | 99083.21213380425 | DAMAGE ESTIMATE TO THE STRUCTURE AS A RESULT OF A HOUSE FIRE. |  | 26 | 17.96440129449838187702265372168284789644 |  | 0 | 77876 | 42613.3301528963351783171521035598705502 | 102866.3385961833098818770226537216828479 | 0 | 0 | 1 |  |  |  |  | 20 | 20 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MICHAEL UPSHAW | SUPERVISOR - DOT PIPELINE SAFETY COMPLIANCE | mupshaw@washgas.com | 703-750-4479 | 703-750-5591 |  |  |  | DAVID W. SPANGLER | MANAGER - DOT PIPELINE SAFETY COMPLIANCE | 703-750-4341 | dspangler@washgas.com | WASHINGTON GAS RESPONDED TO THE SCENE OF A HOUSE FIRE AT 6010 COLUMBIA PIKE IN FALLS CHURCH, VA ON WEDNESDAY, DECEMBER 29, 2010, AT THE REQUEST OF THE FAIRFAX COUNTY FIRE BOARD. UPON ARRIVAL, WASHINGTON GAS FOUND THE GAS OFF BY THE FIRE DEPARTMENT AT THE INSIDE METER VALVE. A WASHINGTON GAS CREW ALSO TURNED THE GAS OFF AT THE CURB VALVE. A 360-DEGREE UNDERGROUND MIGRATION SURVEY WAS CONDUCTED AND NO LEAK INDICATIONS WERE FOUND. THE SERVICE WAS EXCAVATED AND CAPPED OFF AT THE CURB VALVE. A PRESSURE TEST WAS CONDUCTED ON THE SERVICE FROM THE CAPPED OFF LOCATION TO THE INSIDE METER VALVE AND NO LEAK INDICATIONS WERE FOUND. AN ODORANT SAMPLE WAS TAKEN AND THE LEVEL OF ODORANT WAS FOUND TO BE ACCEPTABLE. WASHINGTON GAS HAD DISCUSSIONS WITH THE FAIRFAX FIRE DEPARTMENT AND FOUND THAT THE FIRE WAS STARTED BY A CANDLE ON A BED IN THE BASEMENT. DAMAGE TO WASHINGTON GAS FACILITIES WAS SECONDARY.
2025-03-31 10:13 | YES | NO | NO | 20110015 | 15177 | 2011-01-28 15:57 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2011-01-01 19:38 |  |  | 2011 | 1307 DUNWOODY AVENUE | OXON HILL | PRINCE GEORGE'S | MD | 20745 | 38.8094 | -76.9881 | [9 empty] | 2011-01-01 21:39 | 963487 |  | NATURAL GAS |  | 0.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2011-01-01 19:38 |  |  |  | 2011-01-01 19:42 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | 2006 | [8 empty] | OTHER | CAST ALUMINUM | [9 empty] | OTHER | [8 empty] | DAMAGE TO AN INSIDE METER BUILD-UP AS A RESULT OF A HOUSE FIRE. | CLASS 3 LOCATION | 0 | 0 | 150 | 194.25152749490835 | 1800 | 2331.0183299389002 | 75000 | 97125.763747454175 | DAMAGE ESTIMATE TO THE STRUCTURE AS A RESULT OF A HOUSE FIRE. |  | 2 | 1.51687388987566607460035523978685612789 |  | 0 | 76952 | 41273.8726472598938551509769094138543517 | 99652.5504787778592160746003552397868561 | 0 | 0 | 1 |  |  |  |  | 20 | 20 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MICHAEL UPSHAW | SUPERVISOR - DOT PIPELINE SAFETY COMPLIANCE | mupshaw@washgas.com | 703-750-4479 | 703-750-5591 |  |  |  | DAVID W. SPANGLER | MANAGER - DOT PIPELINE SAFETY COMPLIANCE | 703-750-4341 | dspangler@washgas.com | WASHINGTON GAS RESPONDED TO THE SCENE OF A HOUSE FIRE AT 1307 DUNWOODY AVENUE ON SATURDAY, JANUARY 1, 2011, AT THE REQUEST OF THE PRINCE GEORGE'S COUNTY FIRE BOARD. UPON ARRIVAL, WASHINGTON GAS FOUND THE GAS OFF BY THE FIRE DEPARTMENT AT THE INSIDE METER VALVE. A 360-DEGREE UNDERGROUND MIGRATION SURVEY WAS CONDUCTED AND NO LEAK INDICATIONS WERE FOUND. THE SERVICE WAS EXCAVATED AND CAPPED OFF AT THE CURB. AN ODORANT SAMPLE WAS TAKEN AND THE LEVEL OF ODORANT WAS FOUND TO BE ACCEPTABLE. WASHINGTON GAS HAD DISCUSSIONS WITH THE PRINCE GEORGE'S FIRE DEPARTMENT AND FOUND THAT THE FIRE WAS ELECTRICAL. DAMAGE TO WASHINGTON GAS FACILITIES WAS SECONDARY.
2025-03-31 10:13 | NO | YES | NO | 20110016 | 16174 | 2011-01-28 17:40 | SUPPLEMENTAL FINAL | 180 | ALABAMA GAS CORPORATION | 605 RICHARD ARRINGTON JR BLVD N | BIRMINGHAM | AL | 35203 | 2011-01-01 04:42 |  |  | 2011 | 301 REACH COURT | BIRMINGHAM | SHELBY | AL | 35242 | 33.3712 | -86.668 | [9 empty] | 2011-01-01 09:25 | 963465 |  | NATURAL GAS |  | 6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 5 | 2011-01-01 04:55 |  |  |  | 2011-01-01 05:27 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | SERVICE TAP | 2002 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 731160 | 946859.64562118126124 | 530 | 686.35539714867617 | 1500 | 1942.5152749490835 | 15617 | 20224.174032586558013 | INVESTIGATIVE COSTS |  | 80 | 60.67495559502664298401420959147424511545 |  | 0 | 748887 | 401682.0412264452649650390763765541740675 | 969773.3652814606055659840142095914742451 | 0 | 0 | 10 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VOLUME OF LOST GAS WAS NOT ENOUGH TO DISTINGUISH A PROBLEM. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | BOLTED |  | SERVICE OR MAIN TEE |  | PERFECTION |  | OTHER | MATERIALS JOINED: 1ST PLASTIC, 2ND PLASTIC | [22 empty] | YES | THE OPERATOR'S ONGOING ANALYSIS CONCLUDES THAT THE MANUFACTURER'S DESIGN CONTRIBUTED TO THIS INCIDENT. | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | RANDY A. WILSON | MANAGER-REGULATORY COMPLIANCE | randy.wilson@alagasco.com | 205-326-2987 | 205-326-8483 |  |  |  | ROBERT N. GARDNER | DIRECTOR-QUALITY ASSURANCE AND COMPLIANCE | 205-326-2584 | bob.gardner@alagasco.com | A LEAK AT THE MECHANICAL SERVICE TEE RESULTED IN THE MIGRATION OF NATURAL GAS INTO THE GARAGE AREA, CAUSING AN EXPLOSION. PORTIONS OF THE FOUR-UNIT TOWNHOME COMPLEX EXPERIENCED EXTENSIVE DAMAGE. THE EVENT WAS DETERMINED TO MEET THE REQUIREMENTS OF A REPORTABLE INCIDENT AT APPROXIMATELY 9:00 A.M. IN ADDITION TO THE FIGURES PROVIDED IN PART D OF THIS REPORT, THE INCIDENT HAS FORCED ALABAMA GAS TO UNDERGO INSPECTION AND REMEDIATION EFFORTS FOR SIMILARLY DEFECTIVE AND MIS-INSTALLED TAPPING TEES THROUGHOUT THE NARROWS AND OTHER SUBDIVISIONS. THESE EFFORTS ARE CURRENTLY UNDERWAY, AND THEY ARE EXPECTED TO TAKE ANOTHER 8 YEARS TO COMPLETE. ALABAMA GAS SPENT APPROXIMATELY $854,669.00 AS PART OF ITS INSPECTION AND REMEDIATION EFFORTS AT THE NARROWS, AND COSTS ASSOCIATED WITH THE ENTIRE INSPECTION AND REMEDIATION PROJECT ARE ESTIMATED TO BE APPROXIMATELY $20 MILLION.
2025-03-31 10:13 | NO | NO | NO | 20110017 | 15179 | 2011-02-01 15:34 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-01-18 15:07 |  |  | 2011 | 60 KNOLLS CRESCENT | NEW YORK | BRONX | NY | 10463-6319 | 40.8794 | -73.9175 | [9 empty] | 2011-01-18 16:08 | 965040 |  | NATURAL GAS |  | 0.15 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2011-01-18 15:56 |  |  |  | 2011-01-18 15:56 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | OTHER | CUSTOMER-OWNED PIPING | SERVICE |  | 1951 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 500 | 647.5050916496945 | 5683 | 7359.542871690427687 | CONSTRUCTION REPAIRS |  | 10 | 7.58436944937833037300177619893428063943 |  | 0 | 6193 | 3323.295110026659396754884547069271758437 | 8014.632332789500517373001776198934280639 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | NO | NONE | [22 empty] | NO | [227 empty] | KEVIN FAGAN | MANAGER--GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER--GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | THIS IS NOT DOT REPORTABLE! THIS REPORT IS FOR RECORD PURPOSES ONLY. ON JANUARY 18, 2011 THE NEW YORK FIRE DEPARTMENT (FDNY) REPORTED A BUILDING FIRE AND A HIGH CO CONDITION AT 60 KNOLLS CRESCENT, BRONX, NEW YORK TO THE GAS EMERGENCY RESPONSE CENTER (GERC). GAS DISTRIBUTION SERVICES (GDS) RESPONDED AND REPORTED THAT THERE WAS A CON EDISON ELECTRIC EMERGENCY RESPONDER ON LOCATION. GDS INVESTIGATED AND REPORTED THAT THERE WAS AN ACTIVE GAS FED FIRE OUTSIDE THE BUILDING IN THE GRASS AREA WHERE THE CUSTOMER-OWNED GAS AND ELECTRIC SERVICES CROSS (INSIDE THE PROPERTY LINE). GDS AND THE FDNY LOCATED AND SHUT THE CURB VALVE ON THE SERVICE AT 16:09 AND THE FIRE WAS EXTINGUISHED. COOKING GAS SUPPLYING 120 APARTMENTS WAS INTERRUPTED BUT THE GAS BOILER WAS NOT AFFECTED AS IT IS SUPPLIED FROM A SEPARATE SERVICE. AT 18:17 THE ELECTRIC SERVICE TO BUILDING WAS CUT AND THE ELECTRIC RELATED EVACUATION ENDED. GDS REPORTED THAT THE FIRE APPEARED TO HAVE BEEN WHERE THE CUSTOMER-OWNED ELECTRIC CABLE CROSSED OVER THE CUSTOMER-OWNED 4" LOW PRESSURE STEEL GAS SERVICE (INSIDE THE PROPERTY LINE). BRONX GAS CONSTRUCTION EXCAVATED OVER THE MAIN AND CUT THE GAS SERVICE OFF FOR SAFETY. ON JANUARY 19, 2011 A NEW SERVICE TO THE BUILDING WAS INSTALLED AND SERVICE WAS RESTORED. THERE WAS LESS THAN $50,000.00 IN DAMAGES (SMALL PATCH OF GRASS ONLY) AND UPON CONSULTATION WITH USDOT REPRESENTATIVE WAYNE CHAN, THIS IS NOT DOT REPORTABLE. THERE WERE NO INJURIES AND THIS IS AN UPGRADED LEVEL INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20110018 | 34481 | 2011-02-04 11:43 | SUPPLEMENTAL FINAL | 1209 | BAY STATE GAS CO | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2011-01-23 17:26 |  |  | 2011 | 92 FRONT STREET | WEST SPRINGFIELD | HAMPDEN | MA | 01089 | 42.6 | -72.38 | [10 empty] | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 20 | 2011-01-23 17:26 |  |  |  | 2011-01-23 18:38 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | OVERPRESSURIZATION OF SERVICE REGULATOR ON MULTI METER SET | CLASS 3 LOCATION | 300000 | 388503.0549898167 | 1500 | 1942.5152749490835 | 1200 | 1554.0122199592668 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 302700 | 162354.4704684316899 | 391999.5824847250503 | 11 | 3 | 8 |  |  |  |  | 0.5 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | SERVICE REGULATOR VENT PIPING WAS OBSTRUCTED DUE TO TAMPERING. THE PIPING WAS FOUND TO HAVE COMMON TRASH ITEMS INSERTED AND INSECT SCREEN REMOVED. INOPERABLE VENT CAUSED AN OVER PRESSURE TO APPLIANCES. STATE INVESTIGATOR DETERMINED THE CAUSE TO BE ACCIDENTAL IN NATURE. | [47 empty] | MEGGAN BIRMINGHAM | MANAGER COMPLIANCE GAS OPERATIONS | meggan.pena@eversource.com | 508.468.9956 |  |  |  |  | MEGGAN BIRMINGHAM | MANAGER COMPLIANCE GAS OPERATIONS | 508.468.9956 | meggan.pena@eversource.com | FIRE AT 92 FRONT STREET, WEST SPRINGFIELD, MA REPORTED TO COLUMBIA GAS OF MASSACHUSETTS BY WEST SPFLD FIRE DEPT. GAS SERVICE SHUTOFF TO BLDG, AND INITIAL INVESTIGATION DID NOT FIND NATURAL GAS TO BE INVOLVED IN THE CAUSE OF FIRE. 2 DAYS LATER ON TUESDAY 1/25/2011, INVESTIGATORS FROM FIRE MARSHAL'S OFFICE SUSPECTED A POSSIBLE OVER PRESSURIZATION BASED ON SOME MARKS ON WATER HEATING EQUIPMENT, AND THE REGULATOR VENT PIPING PARTIALLY OBSTRUCTED. SERVICE REGULATOR VENT PIPING WAS OBSTRUCTED DUE TO TAMPERING. THE PIPING WAS FOUND TO HAVE COMMON TRASH ITEMS INSERTED AND INSECT SCREEN REMOVED. INOPERABLE VENT CAUSED AN OVER PRESSURE TO APPLIANCES. STATE INVESTIGATOR DETERMINED THE CAUSE TO BE ACCIDENTAL IN NATURE. THERE WAS A BREAKDOWN IN THE NOTIFICATION PROCESS WHICH RESULTED IN AN NRC CALL NOT BEING MADE.
2025-03-31 10:13 | NO | NO | NO | 20110019 | 15452 | 2011-02-04 22:16 | SUPPLEMENTAL FINAL | 18308 | NV ENERGY | PO BOX 10100 | RENO WASHOE | NV | 89520 | 2010-12-27 07:48 |  |  | 2010 | 710 SOUTH MEADOWS PARKWAY | RENO | WASHOE COUNTY | NV | 89521-4877 | 39.4385 | -119.7577 | [9 empty] | 2011-01-06 13:50 | 963949 |  | NATURAL GAS |  | 14 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-12-27 07:48 |  |  |  | 2010-12-27 11:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | VALVE | 1996 | [8 empty] | OTHER | VALVE BONNET AND BOLTS | [9 empty] | LEAK |  |  | CONNECTION FAILURE | VALVE BONNET TO BODY LEAK | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 8037 | 10617.75701225846343 | 67397 | 89038.81664242673383 | 0 | 0 |  |  | 60 | 41.45631067961165048543689320388349514563 |  | 0 | 75494 | 41313.1134871374036321165048543689320388 | 99698.0299653648089104854368932038834951 | 0 | 0 | 0 |  |  |  |  | 85 | 85 | 90 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA SYSTEM IS USED FOR SYSTEM PRESSURE MONITORING. THIS GAS LEAK DID NOT IMPACT SYSTEM PRESSURES. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | BONNET ON VALVE BECAME LOOSE AND LEAKED DUE TO FAILURE OF BOLTS. | [5 empty] | YES | STRESS CORROSION CRACKING |  |  | YES |  | YES | KEROTEST VALVE LETTER DATED JULY 17, 2002 (SEE SECTION H BELOW) | YES | YES | 1996 | NO | YES | YES |  |  | 2010 |  |  |  |  | NO | [251 empty] | JAY WIGGINS | SUPERVISOR GAS COMPLIANCE OPERATIONS | jwiggins@nvenergy.com | 775-834-7850 | 775-834-1225 |  |  |  | JOHN OWENS | DIRECTOR GAS BUSINESS | 775-834-5644 | jowens@nvenergy.com | ON 12/27/2010 AT 0748 HRS. CITY OF RENO INFORMS NV ENERGY DISPATCH THAT A PHONE MESSAGE WAS LEFT ON 12/25/2010 REPORTING A GAS ODOR ON SOUTH MEADOWS PARKWAY BETWEEN DOUBLE R BLVD. AND DOUBLE DIAMOND PARKWAY. NV ENERGY DISPATCH CREATES WORK ORDER. AT 0953 HRS A PASSERBY REPORTS A GAS ODOR AT SOUTH MEADOWS PARKWAY AND DOUBLE R BLVD. TO NV ENERGY DISPATCH. NV ENERGY PERSONNEL ARRIVE ON SCENE AT 1100 HRS. TO BEGIN LEAK INVESTIGATION. AT 1223 HRS. NV ENERGY PERSONNEL DISCOVER A GRADE 1 GAS LEAK AND REQUEST ADDITIONAL PERSONNEL FOR PINPOINTING AND REPAIRS. AREA IS MADE SAFE BY NV ENERGY PERSONNEL AND NO EVACUATIONS ARE REQUIRED. LEAK IS DETERMINED TO BE ORIGINATING FROM A 2' VALVE FACING NORTH. NV ENERGY BEGINS AERATING THE SOIL DUE TO UNDERGROUND GAS MIGRATION. TRAFFIC CONTROL AND LOCATES ARE REQUESTED. REPAIRS ARE STARTED AT 1500 HRS. GAS LEAK IS STOPPED AT 1910 HRS. REPAIRS ARE COMPLETED AT 2040 HRS. NV ENERGY CONTINUES AERATING SOIL 24 HOURS PER DAY FROM 12/27/2010 TO 1/8/2011 AT 830 HRS. SOIL AERATION COSTS PUSH THE INCIDENT COSTS ABOVE THE $50,000 THRESHOLD. BASED ON A LETTER FROM KEROTEST, THE VALVE MANUFACTURER, DATED JULY 17, 2002, NV ENERGY BELIEVES THE FAILURE OF THE VALVE BONNET BOLTS IS DUE TO STRESS CORROSION CRACKING. THE AFFECTED YEARS OF MANUFACTURE ARE 1986-1996 AS IDENTIFIED BY KEROTEST. A POSSIBLE CONTRIBUTING FACTOR WAS A LACK OF COATING ON THE BONNET BOLT. ATTACHMENT: KEROTEST LETTER DATED JULY 17, 2002
2025-03-31 10:13 | NO | YES | NO | 20110020 | 15339 | 2011-02-07 18:32 | SUPPLEMENTAL FINAL | 11032 | LACLEDE GAS CO | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2011-01-08 12:00 |  |  | 2011 | 3810 COUNCIL GROVE AVENUE | PINE LAWN | ST. LOUIS | MO | 63121 | 38.6918 | -90.275 | [9 empty] | 2011-01-08 14:32 | 964078 |  | NATURAL GAS |  | 140 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 134 | 2011-01-08 12:07 |  |  |  | 2011-01-08 12:23 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1953 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 25446 | 32952.829124236252494 | 0 | 0 | 90000 | 116550.91649694501 | HOUSE AND CONTENTS |  | 898 | 681.076376554174067495559502664298401421 |  | 0 | 116344 | 62550.0031410865973147886323268206039076 | 150184.8219977354365614955595026642984014 | 0 | 0 | 10 |  |  |  |  | 18 | 18 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM PRESSURE WAS WITHIN NORMAL OPERATING RANGE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE NOT RELATED TO EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [112 empty] | PREVIOUS MECHANICAL DAMAGE NOT RELATED TO EXCAVATION | [7 empty] | 2009-09-03 | NO | [159 empty] | MARK D. LAUBER | SUPERINTENDENT OF MAINTENANCE ENGINEERING | mlauber@lacledegas.com | 314-658-5413 | 314-535-5075 |  |  |  | CRAIG R. HOEFERLIN | ASSISTANT VP ENGINEERING AND FIELD SERVICES | 314-658-5410 | choeferlin@lacledegas.com | THE 2-INCH STEEL NATURAL GAS MAIN IN FRONT OF 3810 COUNCIL GROVE AVENUE WAS EXCAVATED TO REVEAL A CIRCUMFRENTIAL CRACK IN THE BODY OF THE PIPE FROM THE 1 O'CLOCK TO 11 O'CLOCK POSITION. THE CRACK WAS LOCATED AT A DENT AND DEFLECTION OF THE GAS MAIN THAT APPEARED TO HAVE BEEN CASUED BY PRIOR EXCAVATION ACTIVITY. THE DAMAGE WAS DIRECTLY OVER A SEWER LATERAL THAT HAD BEEN INSTALLED PRESUMABLY WHEN THE HOUSE WAS BUILT IN 2000.
2025-03-31 10:13 | NO | YES | NO | 20110021 | 15187 | 2011-02-07 18:48 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2010-12-21 11:16 |  |  | 2010 | 1011 E RTE 34 | EARLVILLE | LASALLE | IL | 60518 | 41.5832 | -88.9081 | [9 empty] | 2010-12-21 13:41 | 962831 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2010-12-21 11:16 |  |  |  | 2010-12-21 11:59 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2006 | [8 empty] | OTHER | MIXED MATERIAL REGULATOR | [9 empty] | OTHER | [8 empty] | ADJUSTMENT SCREW HEAD SHEARED OFF THE REGULATOR HEAD | CLASS 3 LOCATION | 120000 | 158533.1394140868 | 1500 | 1981.664242676085 | 800 | 1056.887596093912 | 0 | 0 |  |  | 100 | 69.09385113268608414239482200647249190939 |  | 0 | 122400 | 66982.0646213700121935275080906148867314 | 161640.7851039894830841423948220064724919 | 1 | 0 | 0 |  |  |  |  | 56 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | lquezad@nicor.com | 630-388-2316 |  |  |  |  | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | 630-388-2316 | lquezad@nicor.com | CUSTOMER WAS REMOVING SNOW USING A BOBCAT. HE HAD LOADED SNOW IN THE BUCKET AND WAS BACKING OUT WHEN THE BOBCAT SLID ON ICE AND STRUCK THE GAS REGULATOR. THE DJUSTMENT SCREW ON THE REGULATOR HEAD WAS SHEARED OFF CAUSING AN OVERPRESSURE CONDITION TO THE FURNACE WHICH CAUSED THE FIRE INSIDE.
2025-03-31 10:13 | NO | YES | NO | 20110022 | 15280 | 2011-02-07 21:11 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2011-01-08 00:50 |  |  | 2011 | 4309 PRAIRIE WAY | MODESTO | STANISLAUS | CA | 93555 | 37.6659 | -120.9157 | [9 empty] | 2011-01-08 03:45 | 96407 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | [7 empty] | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMININ | [9 empty] | OTHER | [8 empty] | FIREPLACE ASHES FROM CONTAINER STARTED A FIRE (SECONDARY IGNITION) | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 2000 | 2590.020366598778 | 100000 | 129501.0183299389 | VALUE OF DAMAGE TO HOME. |  | 1 | 0.7584369449378330373001776198934280639432 |  | 0 | 102001 | 54708.8482380902148525754884547069271758 | 132091.7971334826158330373001776198934281 | 0 | 0 | 1 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | SECONDARY IGNITION FROM ASHES LEFT IN A CONTAINER NEXT TO HOME | [154 empty] | GARY F. GUERRERO | SENIOR COMPLIANCE ANALYST | gfg2@pge.com | 925-974-4075 |  |  |  |  | BRIAN DAUBIN | MANAGER GAS ENGINEERING | 925-9744210 | bmd5@pge.com | AT APPROXIMATELY 0050 HOURS ON JANUARY 8, 2011 THERE WAS A STRUCTURE FIRE AT 4309 PRAIRIE CREEK WAY, MODESTO. ACCORDING TO THE FIRE DEPARTMENT PRELIMINARY ON-SITE REPORT, THE RESIDENT AT THIS ADDRESS HAD CLEANED OUT A FIREPLACE AND PLACED ASHES IN A CONTAINER NEAR THE GARAGE AND GAS METER. THE ASHES STARTED A FIRE IN THE CONTAINER THAT SPREAD TO THE GARAGE AND GAS METER. AS A RESULT, PART OF THE HOME WAS DAMAGED AND THE GAS METER SET MELTED RELEASING NATURAL GAS INTO THE ATMOSPHERE. THE FIRE DEPARTMENT NOTIFIED PG&E OF THIS INCIDENT AT APPROXIMATELY 0050 HOURS. PG&E'S GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON-SITE AT APPROXIMATELY 0143 HOURS. THE FIRE DEPARTMENT HAD BEEN ABLE TO PUT OUT THE FIRE PRIOR TO PG&E'S ARRIVAL AND HAD TURNED OFF GAS AT THE RISER VALVE: HOWEVER, HEAT FROM THE FIRE HAD DAMAGED THE SHUT OFF VALVE. A CREW WAS DISPATCHED AND SQUEEZED OFF THE SERVICE, STOPPING THE FLOW OF GAS AT APPROXIMATELY 0345 HOURS. THE INCIDENT WAS DEEMED TO BE REPORTABLE AT 0308 HOURS DUE TO AN ESTIMATE OF THE DAMAGES TO THE HOME EXCEEDING $50,000. THERE WERE NO INJURIES, NO FATALITIES, AND NO MEDIA AS A RESULT OF THIS INCIDENT. PG&E NOTIFIED THE DOT AT 0336 HOURS AND THE CPUC AT 0341 HOURS. THE CAUSE OF THE FIRE REMAINS OFFICIALLY UNDETERMINED. SERVICE WILL BE RESTORED ONCE REPAIRS ARE MADE TO THE HOME.
2025-03-31 10:13 | NO | NO | NO | 20110023 | 15193 | 2011-02-10 23:40 | ORIGINAL | 3240 | DELMARVA POWER & LIGHT COMPANY | 630 MARTIN LUTHER KING JR. | WILMINGTON | DE | 19801 | 2011-01-07 11:18 |  |  | 2011 | 101 CLIFTON AVE | ELESMERE |  | DE | 19805 | 39.7405 | -75.6133 | [9 empty] | 2011-01-10 11:31 | 964171 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | [6 empty] | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1978 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | CAR HIT MEER SET | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 1579 | 2044.821079429735231 | 0 | 0 | 0 | 0 |  |  | 3 | 2.27531083481349911190053285968028419183 |  | 0 | 1582 | 849.008359891908280726465364120781527531 | 2047.096390264548730111900532859680284192 | 0 | 0 | 1 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ROBERT G KITSON | MANAGER OF GAS ENGINEERING | robert.kitson@delmarva.com | 3024293848 | 3024293207 |  |  |  | ROBERT G KITSON | MANAGER OF GAS ENGINEERING | 3024293848 | robert.kitson@delmarva.com | AROUND 11:18 ON 1/7/11 IT WAS REPORTED THAT A PRIVATE VEHICLE HIT A GAS METER, RESULTING IN A FIRE. FROM WHAT I HAVE BEEN TOLD, THE PRIVATE VEHICLE WAS UNABLE TO STOP DUE TO ICY CONDITIONS, AND RAN OVER A FENCE AND HIT CORNER OF A HOUSE AND THE GAS METER SET. THIS FORCE BROKE THE PIPING AFTER LOCKWING VALVE, AND THEN THE LEAKING GAS IGNITED. GAS WAS SHUTOFF AT THE LOCKWING TO MAKE SAFE, THEN REPAIRS WERE MADE. NO ONE WAS TAKEN TO HOSPITAL FOR INJURIES, AND DAMAGE TO THE BRICK HOUSE WAS RELATIVELY MINOR BASED ON PHOTOS. THE COST ESTIMATE IS LESS THAN $50K, BUT WERE ADVISED TO REPORT IN CASE THE ACTUAL COST EXCEEDS $50K ELESMERE FIRE COMPANY REPORT ESTIAMTES NO DMAMGE DUE TO FIRE. THUS THIS WAS NOT AN INCIDENT AS PER THE NEW DEFINITION, BUT BELIEVED A REPORT HAD TO BE SUBMITED SINCE THE NRC WAS NOTIFIED. I WOULD LIKE TO RECEIND THE NRC REPPORT AND THIS INCIDENT REPORT.
2025-03-31 10:13 | NO | YES | YES | 20110024 | 15657 | 2011-02-11 14:40 | SUPPLEMENTAL FINAL | 2060 | CANTON MUNICIPAL UTILITY | 226 HARGON STREET | CANTON | MS | 39046 | 2011-01-17 18:40 |  |  | 2011 | 392 FROST STREET | CANTON | MADISON | MS | 39046 | 32.6184 | -90.0409 | [9 empty] | 2011-01-17 19:52 | 964967 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | YES | 28 | 2011-01-17 18:40 |  |  |  | 2011-01-17 18:45 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 25000 | 32375.254582484725 | 3000 | 3885.030549898167 | 5000 | 6475.050916496945 | 0 | 0 |  |  | 1000 | 758.436944937833037300177619893428063943 |  | 0 | 34000 | 18401.2930800591735754884547069271758437 | 43493.7729938176700373001776198934280639 | 0 | 0 | 1 |  |  |  |  | 15 | 15 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CALL WAS RECEIVED FROM POLICE DEPT. AND IMMEDIATELY DISPATCHED TO ON CALL EMPLOYEE. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | NO | NONE | [21 empty] | 2009-08-13 | NO | [227 empty] | KYLE CANOY | TECHNICAL SERVICES MANAGER | k.canoy@cmu.com | 601-855-5462 | 601-855-5441 |  |  |  | JOHN WALLACE | GENERAL MANAGER | 601-859-2474 | j.wallace@cmu.com
2025-03-31 10:13 | YES | NO | NO | 20110025 | 15230 | 2011-02-15 14:56 | SUPPLEMENTAL FINAL | 2309 | CHESAPEAKE UTILITY CORP | 32145 BEAVER RUN DR | SALISBURY | MD | 21804 | 2011-01-31 02:20 |  |  | 2011 | 200 SHADY LANE | FRUITLAND | WICOMICO | MD | 21826-0000 | 38.3335 | -75.6322 | [12 empty] | NATURAL GAS |  | 0.01 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2011-01-31 02:29 |  |  |  | 2011-01-31 02:45 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 2003 | [8 empty] | DUCTILE IRON | [10 empty] | OTHER | [8 empty] | THE GREASE MELTED OUT OF SERVICE RISER VALVE PACKING DUE TO HEAT FROM FIRE. A SMALL AMOUNT OF GAS WAS RELEASED AND IGNITED. | CLASS 3 LOCATION | 0 | 0 | 219 | 283.607230142566191 | 2041 | 2643.115784114052949 | 375000 | 485628.818737270875 | DAMAGE TO POLE SHED LEAN-TO BUILDING AND STORED EQUIPMENT CAUSED BY THE FIRE. |  | 1 | 0.7584369449378330373001776198934280639432 |  | 0 | 377261 | 202345.7545517357614725754884547069271758 | 488556.3001884724319730373001776198934281 | 0 | 0 | 0 |  |  |  |  | 28 | 32 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CHARLES RUSSELL | ENGINEERING AND INTEGRITY MANAGER | crussell@chpk.com | 410-548-5515 | 410-548-3245 |  |  |  | CHARLES RUSSELL | ENGINEERING AND INTEGRITY MANAGER | 410-548-5515 | crussell@chpk.com | A FRUITLAND POLICE OFFICER WENT INTO THE FRUITLAND PUBLIC WORKS COMPOUND LOCATED AT 200 SHADY LANE AROUND 2:00 AM ON JANUARY 31, 2011 TO FUEL HIS POLICE CRUISER AND NOTICED SOME SMOKE AND SMOULDERING DEBRIS. HE NOTIFIED THE FRUITLAND FIRE DEPARTMENT WHO RESPONDED TO THE SCENE AND PUT OUT THE REMAINING HOT SPOTS AND COOL DOWN THE STRUCTURE AND EQUIPMENT. FIRE WAS DETECTED AROUND THE SERVICE RISER TO THE BUILDING AND WE WERE NOTIFIED BY WICOMICO COUNTY 911 CENTER. OUR ON-CALL METER TECH RESPONDED AND NOTED THAT THE GREASE HAD MELTED OUT OF THE 3/4" SERVICE STOP AND DETECTED THE SMELL OF GAS. HE NOTICED THAT SOME GAS WAS BUBBLING THROUGH THE WATER FROM THE SERVICE RISER NEAR THE FENCE. HE CALLED OUT OUR ON-CALL CONSTRUCTION CREW WHO HAND DUG AROUND THE RISER AND SQUEEZED OFF THE 3/4" PE SERVICE AND CAPPED IT OFF. THEY DUG THE RISER OUT AND BROUGHT IT BACK TO THE SHOP FOR FURTHER INVESTIGATION. THE INSERTED TUBE WAS CUT OFF THE RISER AND SHOWED A SMALL PINHOLE THAT HAD FORMED DUE TO THE HEAT. THE GAS FROM THE PINHOLE TRAVELLED DOWN THE CASING PIPE AND OUT THE BOOT AND VENTED THROUGH THE GROUND AND WATER PUDDLES BUT DID NOT IGNITE. MARYLAND STATE FIRE MARSHALL S. P. MASON INVESTIGATED THE INCIDENT AND CONCLUDED THAT THE ORIGIN OF THE FIRE WAS AN EXTENSION CORD GOING TO A BATTERY TRICKLE CHARGER ON A PIECE OF EQUIPMENT IN THE STRUCTURE AND THAT NATURAL GAS WAS NOT A CAUSE. THE BUILDING CONTAINED A BACKHOE, SEVERAL TRACTORS, COMPRESSORS, ZERO-TURN LAWN MOWERS, ETC. WHICH WERE DESTROYED IN THE FIRE. THE INCIDENT WAS REALIZED AT 11:06 AS A RESULT OF OUR INVESTIGATION INTO THE DAMAGES BY THE FIELD OPERATIONS MANAGER AND WAS REPORTED TO THE NATIONAL CALL CENTER AT 11:16. THE MARYLAND PSC WAS NOTIFIED AT 11:24.
2025-03-31 10:13 | NO | YES | YES | 20110026 | 15196 | 2011-02-15 17:00 | ORIGINAL | 15469 | PHILADELPHIA GAS WORKS | 800 W. MONTGOMERY AVENUE | PHILADELPHIA | PA | 19122 | 2011-01-18 19:28 |  |  | 2011 | 6932 TORRESDALE AVENUE | PHILADELPHIA | PHILADELPHIA | PA | 19135-1906 | 40.0266 | -75.0424 | [9 empty] | 2011-01-19 00:45 | 965075 |  | NATURAL GAS |  | 2923 |  | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 3 | 0 | 0 | 0 | 0 | 3 | YES |  |  |  |  | YES | 30 | 2011-01-18 19:28 |  |  |  | 2011-01-18 19:38 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 37 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1942 | [5 empty] | 12.75 | ASA A21.1 | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 300000 | 388503.0549898167 | 40000 | 51800.40733197556 | 17500 | 22662.6782077393075 | 0 | 0 |  |  | 15350 | 11642.0071047957371225577264653641207815 |  | 0 | 372850 | 202516.2286159755645337477797513321492007 | 474608.1476343273046225577264653641207815 | 2 | 0 | 18 |  |  |  |  | 18 | 18 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [15 empty] | NO | [86 empty] | JOHN J. JOLLY | MANAGER DISTRIBUTION DEPARTMENT | john.jolly@pgworks.com | 215-684-6386 | 215-684-6388 |  |  |  | PAUL A. MONDIMORE | VICE PRESIDENT FIELD OPERATIONS | 215-684-6372 | paul.mondimore@pgworks.com | ON JANUARY 18TH, 2011 PGW RECEIVED A PHONE CALL AT 19:28 FROM THE PHILADELPHIA FIRE DEPARTMENT REPORTING A STRONG ODOR OF GAS IN THE INTERSECTION OF TORRESDALE (6900 BLOCK) AVENUE AND DISSTON (4600 BLOCK) STREET. PGW DISPATCHED FIRST RESPONDERS AT 19:29, WITH THE FIRST PGW EMPLOYEE ARRIVING ON LOCATION AT 19:38. UPON ARRIVAL, PGW PRELIMINARILY IDENTIFIED A SIGNIFICANT LEAK ON A DISTRIBUTION MAIN OPERATING AT 18 PSIG (10-35 PSIG MAOP). AT 20:00, PGW CALLED IN RESOURCES TO START AN EMERGENCY SHUT DOWN. ADDITIONAL RESOURCES CONTINUED TO ARRIVE AND STARTED LEAK MIGRATION AND HOUSE CHECKS ALONG THE 6900 BLOCK OF TORRESDALE. WITH THE ASSISTANCE OF THE PFD, PGW BEGAN FORCED ENTRY PROCEDURES AND EVACUATIONS OF RESIDENTS. PGW RECORDED ATMOSPHERIC READINGS IN SEVERAL HOUSES DURING THE HOUSE CHECKS. WHEN THE FIRST DISTRIBUTION CREW ARRIVED (20:10), PGW MADE BAR HOLES TO VENTILATE THE GAS AND LOCATE THE LEAK. AT 20:35, A PGW SUPERVISOR REPORTED AN EXPLOSION AND FIRE AT 6932 TORRESDALE AVENUE. AFTER CLOSURE OF THE ISOLATION VALVES THE GAS FIRE SUBSIDED. THE PFD EXTINGUISHED THE REMAINING FIRES. PGW ALSO GREASED OFF THE 6" LP CI MAIN ON TORRESDALE CROSSING THE INTERSECTION OF DISSTON STREET. THE SOUTH END WAS GREASED OFF THRU THE SERVICE AT 6924 TORRESDALE; AND THE NORTH END WAS GREASED OFF THROUGH THE MAIN. FSD PULLED A HEAD OF SERVICE PLUG ON BUILDING 6926 TO CONFIRM THE LINE WAS DEACTIVATED. WITH THE 6" MAIN (1/4 PSIG) MAIN DEACTIVATED AND THE 12" (10-35 PSIG) MAIN DEACTIVATED, HOUSES VENTILATED, THE JOB WAS DECLARED 'MADE SAFE' AT 22:40. PGW MADE EXCAVATIONS TO PHYSICALLY CUT AND CAP THE 12" MAIN AND 6' MAIN. THE 6" MAIN WAS CUT AND CAPPED ON 1/19/11 AT 03:25. THE 12" MAIN WAS CUT AND CAPPED ON AT 05:30. ON 01/19/11 PGW INSERTED A CAMERA INSIDE THE CUT & CAPPED 12" CI MAIN FROM 25' EEC MARSDEN ST TO 35' WWC TORRESDALE AVENUE. THE MAIN WAS CLEAN, NO SIGNS OF PITTING AND THE MECHANICAL JOINTS WERE INTACT. WITH THE CAMERA THE BROKEN MAIN WAS LOCATED AT 29' 4" WWC TORRESDALE AVENUE & 3'6" NSC DISSTON STREET PGW EXCAVATED THE AREA WHERE THE BROKEN MAIN WAS LOCATED. THE GROUND WAS SOLID CLAY IN THE ROADWAY, NO SIGNS OF ANY VOIDS. THE BREAK WAS CIRCUMFERENTIAL AND APPEARED TO BE A COMPLETE BREAK, AND THE MAIN WAS STILL IN ALIGNMENT, NO INDICATION THAT THE MAIN HAD DROPPED. PGW EXCAVATED THE AREA WHERE THE BROKEN MAIN WAS LOCATED. THE GROUND WAS SOLID CLAY IN THE ROADWAY, NO SIGNS OF ANY VOIDS. THE BREAK WAS CIRCUMFERENTIAL AND APPEARED TO BE A COMPLETE BREAK, AND THE MAIN WAS STILL IN ALIGNMENT, NO INDICATION THAT THE MAIN HAD DROPPED. THE AREA EXCAVATED CONSISTED OF MACADAM WITH AN OVERLAY OF ASPHALT WITH A STONE BASE. THERE WAS NO CONCRETE BASE IN THE ROADWAY. THE DIRT WAS SOLID CLAY AND NO FROST WAS DETECTED IN THIS OPENING. THE SOIL AROUND THE PIPE WAS UNDISTURBED CLAY, VERY MOIST. THE GROUND WAS SOLID WITH NO SIGNS OF CAVITY, VOID OR UNDERMINING CONDITIONS OR DEPRESSIONS SUPPORTING THE PIPE. THE DIRT AROUND THE BREAK HAD EQUAL MOISTURE AS THE SURROUNDING SOIL. PGW EXCAVATED ALONG BOTH SIDES OF THE MAIN AND LEFT THE DIRT UNDER THE MAIN, NOT TO DISTURB IT. THERE WERE NO OBVIOUS SIGNS OF ANY GRAPHITIZATION, PITS, PLUGS, OR HOLES. THERE WERE NO OTHER TYPES OF FITTINGS IN THIS OPENING. THE EXCAVATION WAS PREPARED TO ALLOW A 6' SECTION TO BE REMOVED WITH THE BREAK IN THE MIDDLE. THE MAIN WAS HAND DUG AND SCALED. THE PIPE WAS SCALED ONLY IN THE AREAS OF THE CUT. THE REMAINDER OF THE REMOVED SECTION WAS ONLY CLEANED, NOT SCALED. A STAINLESS STEEL SLEEVE WAS INSTALLED ON THE BREAK AREA; IT WAS A COMPLETE CIRCUMFERENTIAL BREAK. THE MAIN WAS MARKED EAST, WEST AND TOP. PICTURES WERE TAKEN DURING THE REMOVAL. THE REMOVED MAIN IS SCHEDULED TO BE TRANSPORTED TO A LABORATORY FOR A COMPLETE METALLURGICAL EXAMINATION.
2025-03-31 10:13 | YES | NO | NO | 20110028 | 15200 | 2011-02-17 23:51 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2011-01-19 04:06 |  |  | 2011 | 4709 40TH AVENUE | HYATTSVILLE | PRINCE GEORGE'S | MD | 20781-2102 | 38.9487 | -76.9481 | [9 empty] | 2011-01-19 06:06 | 965079 |  | NATURAL GAS |  | 56 |  | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 0 | 0 | 0 | 0 | 4 | 4 | NO |  |  |  |  | NO | 7 | 2011-01-19 04:06 |  |  |  | 2011-01-19 04:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 2007 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | OTHER | [8 empty] | DAMAGE TO AN OUTSIDE RISER AS A RESULT OF A HOUSE FIRE. | CLASS 3 LOCATION | 0 | 0 | 200 | 259.0020366598778 | 7000 | 9065.071283095723 | 270000 | 349652.74949083503 | APPROXIMATE DAMAGE TO THE STRUCTURE AS A RESULT OF A HOUSE FIRE. |  | 240 | 182.024866785079928952042628774422735346 |  | 0 | 277440 | 148845.8174675237010181172291296625222025 | 359158.8476773757107289520426287744227353 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MICHAEL UPSHAW | SUPERVISOR - DOT PIPELINE SAFETY COMPLIANCE | mupshaw@washgas.com | 703-750-4479 | 703-750-5591 |  |  |  | DAVID W. SPANGLER | MANAGER - DOT PIPELINE SAFETY COMPLIANCE | 703-750-4341 | dspangler@washgas.com | WASHINGTON GAS WAS NOTIFIED BY THE PRINCE GEORGE'S COUNTY FIRE BOARD OF A HOUSE FIRE AT 4709 40TH AVENUE, HYATTSVILLE, MD, ON WEDNESDAY, JANUARY 19, 2011 AT 4:06 AM. WASHINGTON GAS PERSONNEL ARRIVED AT 4:30 AM. CREWS FOUND GAS TURNED OFF AT THE OUTSIDE METER VALVE BY THE FIRE DEPARTMENT. GAS WAS NOTED AT THE FRONT BUILDING WALL OVER SERVICE LINE DUE HEAT EXPOSURE TO RISER FROM HOUSE FIRE. WASHINGTON GAS SQUEEZED-OFF THE GAS SERVICE APPROXIMATELY 5 FEET FROM FRONT BUILDING WALL. NO GAS IGNITION OCCURRED. A 360 DEGREE BAR AND TEST SURVEY WAS CONDUCTED AROUND THE STRUCTURE AND OVER THE SERVICE LINE AND MAIN. NO LEAK INDICATIONS WERE FOUND. AN ODORANT SAMPLE WAS TAKEN AND THE LEVEL OF ODORANT WAS FOUND TO BE ACCEPTABLE. THE SERVICE WAS CAPPED OFF AT THE MAIN AND THE SERVICE LINE WAS PRESSURE TESTED ON JANUARY 24, 2011. NO LEAK INDICATIONS WERE FOUND. DISCUSSIONS ON SITE WITH FIRE PERSONNEL ON DAY OF INCIDENT INDICATED PRELIMINARY FINDINGS WERE SUGGESTING POSSIBLE ELECTRICAL INVOLVEMENT IN THE CAUSE OF THE FIRE. WASHINGTON GAS FACILITY INVOLVEMENT WAS SECONDARY.
2025-03-31 10:13 | NO | NO | NO | 20110030 | 15232 | 2011-02-19 08:09 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-01-26 18:41 |  |  | 2011 | 28-29 209 STREET | NEW YORK | QUEENS | NY | 11360-2829 | 40.7203 | -73.7555 | [9 empty] | 2011-01-26 19:11 | 965787 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2011-01-26 18:41 |  |  |  | 2011-01-26 18:46 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1957 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 1325 | 1715.888492871690425 | 41927 | 54295.891955193482603 | REPAIRS |  | 15 | 11.37655417406749555950266429840142095915 |  | 0 | 43267 | 23208.9235713536255126323268206039076377 | 56023.157002239240523559502664298401421 | 0 | 0 | 0 |  |  |  |  | 62 | 62 | 80 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM WAS OPERATING NORMALLY AND FLASH WAS CAUSED BY MIGRATION FROM A COMPRESSION COUPLING LEAK IN THE STREET COMBINATION WITH AN OVERLOADED CIRCUIT BREAKER IN THE ELECTRIC PANEL. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | OTHER COMPRESSION TYPE FITTING | COUPLING-- TEE COMPRESSION |  |  | DRESSER |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | SEAL LEAK ON COMPRESSION FITTING |  | YES |  |  |  | OTHER | SEAL LEAK | NO | [86 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | AT 18:41 ON JANUARY 26,2011 THE NEW YORK CITY FIRE DEPARTMENT (FDNY) REPORTED A SMALL EXPLOSION IN THE BASEMENT OF 28-29 209 PLACE, BAYSIDE, NEW YORK TO THE GAS EMERGENCY RESPONSE CENTER (GERC). THE GERC CALLED THE CUSTOMER AS WELL AS WITH THE FDNY WHO STATED THE RESIDENT WAS INJURED WHILE ATTEMPTING TO EXTINGUISH A FIRE IN A UTILITY CLOSET IN THE BASEMENT. THE FDNY REPORTED THE CUSTOMER WAS TREATED AT THE SCENE. A CODE MURRE (MULTIPLE RESOURCE RESPONSE EVENT) WAS INITIATED AND THE GERC DISPATCHED (4) GAS DISTRIBUTION SERVICES (GDS)CREWS, (3) GDS SUPERVISORS, GDS PLANNER AND (2) CONSTRUCTION CREWS. A GDS SUPERVISOR REPORTED AT 18:53 THAT THEY RECEIVED A 15% GAS READING AT THE INSIDE SEWER TRAP IN THE UTILITY CLOSET OF THIS PRIVATE HOME. THE STEEL PLATE OVER THE TRAP WAS OPENED AND THE TWO SCREW CAPS WERE IN PLACE BUT NOT TIGHT. THE CUSTOMER, MICHAEL SCUDERI 28 YEARS OLD, STATED THAT HE WAS NOT INJURED, WAS NOT TREATED BY EMS AND REFUSED TO GO TO THE HOSPITAL. THE CUSTOMER STATED THAT HE SAW SMOKE COMING FROM UNDERNEATH THE UTILITY ROOM DOOR, SAW A FLASH, THE DOOR BLEW OPEN AND HE SPRAYED THE AREA WITH HIS PERSONAL FIRE EXTINGUISHER. GDS INVESTIGATED AND REPORTED RECEIVING READINGS INSIDE (7) PRIVATE HOMES (AT SEWER TRAPS) (2) ELECTRIC MANHOLES IN THE STREET AND (3) SEWER MANHOLES. INTERNAL AND EXTERNAL NOTIFICATIONS WERE MADE AS REQUIRED. AN FDNY FIRE MARSHAL RESPONDED AND ATTRIBUTED THE INCIDENT TO NATURAL GAS. THE LEAK WAS INVESTIGATED, EXCAVATED AND CREWS SECURED A LEAKING 2" X 2" X 2" COMPRESSION TEE ON THE 2" STEEL MAIN IN THE STREET. THIS WAS AN UPGRADED LEVEL INCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20110031 | 15202 | 2011-02-22 10:45 | ORIGINAL | 17570 | ROCHESTER GAS & ELECTRIC CORP | 180 SOUTH CLINTON AVENUE | ROCHESTER | NY | 14607 | 2010-10-15 10:22 |  |  | 2010 | 219 EVERCLAY DRIVE | GREECE | MONROE | NY | 14616 | 43.1321 | -77.391 | [9 empty] | 2010-10-15 11:07 | 957058 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | YES | 5 | 2010-10-15 10:25 |  |  |  | 2010-10-15 10:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | CUSTOMER OWNED FLEXIBLE CONNECTOR | UNKNOWN | [8 empty] | OTHER | FLEXIBLE CONNECTOR | [9 empty] | OTHER | [8 empty] | CRACK IN CUSTOMER OWNED FLEXIBLE CONNECTOR TO THE GAS DRYER. | CLASS 3 LOCATION | 0 | 0 | 1000 | 1321.10949511739 | 50000 | 66055.4747558695 | 0 | 0 |  |  | 0 | 0 |  | 0 | 51000 | 27905.360482027854 | 67376.58425098689 | 0 | 0 | 1 |  |  |  |  | 12 | 12 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EXPLOSION WAS THE RESULT OF A CRACKED CUSTOMER OWNED FLEX CONNECTOR IN THE INTERIOR HOUSE PIPING. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | THE APPARENT CAUSE WAS A CRACKED FLEX CONNECTOR ON THE FUEL LINE TO THE GAS DRYER. | [47 empty] | MICHAEL D. EASTMAN | V P GAS OPERATIONS | mdeastman@nyseg.com | 585-724-8253 |  |  |  |  | MICHAEL D. EASTMAN | V P GAS OPERATIONS | 585-724-8253 | mdeastman@nyseg.com | THE APPARENT CAUSE OF THE EXPLOSION WAS A CRACK IN THE FLEX CONNECTOR ON THE CUSTOMER OWNED FUEL LINE TO THE NATURAL GAS DRYER LOCATED IN THE BASEMENT OT THE SINGLE FAMILY HOME. AS A FOLLOW UP TO OUR OCTOBER TELEPHONE CONVERSATION REGARDING THE EXPLOSION AT 219 EVERCLAY DRIVE IN GREECE, NEW YORK, RG&E IS FILING THIS REPORT FOR INFORMATIONAL PURPOSES AND IN THE INTEREST OF CAUTION BECAUSE OF THE EXPLOSION, SIGNIFICANT FIRE, PROPERTY DAMAGE AND PERSONAL INJURY THAT OCCURED. THIS EVENT WAS NOT CAUSED BY THE RG&E GAS DISTRIBUTION SYSTEM, IT WAS THE FAILURE OF CUSTOMER OWNED INTERNAL HOUSE PIPING.
2025-03-31 10:13 | NO | YES | YES | 20110032 | 33579 | 2011-02-22 12:29 | SUPPLEMENTAL FINAL | 13420 | NEW YORK STATE ELECTRIC & GAS CORP | 18 LINK DRIVE | BINGHAMTON | NY | 13904 | 2011-01-26 09:18 |  |  | 2011 | 198 JOSEPH STREET | HORSEHEADS | CHEMUNG | NY | 14845 | 42.913 | -76.4933 | [9 empty] | 2011-01-26 10:11 | 765720 |  | NATURAL GAS |  | 3 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | YES | 9 | 2011-01-26 09:18 |  |  |  | 2011-01-26 09:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1955 | [5 empty] | 1 | UNKNOWN | UNKNOWN | OTHER | COATED STEEL | [9 empty] | OTHER | [8 empty] | THIRD PARTY DAMAGE TO THE SERVICE PIPING | CLASS 3 LOCATION | 0 | 0 | 500 | 647.5050916496945 | 225000 | 291377.291242362525 | 0 | 0 |  |  | 100 | 75.84369449378330373001776198934280639432 |  | 0 | 225600 | 121018.0722815292787575488454706927175844 | 292100.6400285060028037300177619893428064 | 0 | 0 | 5 |  |  |  |  | 52 | 52 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS ATTRIBUTED TO THIRD PARTY DAMAGE TO THE SERVICE PIPING. | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | CITY STREET | [12 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | WATER | NO | [5 empty] | YES | 122 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | BARRY J. KACHMARYK | MANAGER GAS ENGINEERING | barry_kachmaryk@rge.com | 585-315-1227 |  |  |  |  | MICHAEL D. EASTMAN | VP GAS OPERATIONS | 585-724-8253 | mdeastman@nyseg.com | THE COMPANY RECEIVED A REPORT OF A HOUSE EXPLOSION AND RESPONDED TO ASSIST THE FIRE DEPARTMENT AND LAW ENFORCEMENT. THE INCIDENT WAS ATTRIBUTED TO THIRD PARTY DAMAGE TO THE SERVICE LINE PIPING.
2025-03-31 10:13 | NO | YES | NO | 20110034 | 15469 | 2011-02-23 15:00 | SUPPLEMENTAL FINAL | 4060 | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2011-01-24 06:37 |  |  | 2011 | HIGH STREET DISTRICT REGULATOR STATION | FAIRPORT HARBOR | LAKE | OH | 44077-5521 | 41.7431 | -81.2744 | [9 empty] | 2011-01-24 09:29 | 965512 |  | NATURAL GAS |  | 86 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1505 | 2011-01-24 06:37 |  |  |  | 2011-01-24 07:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1999 | [8 empty] | OTHER | REGULATOR STATION | [9 empty] | OTHER | [8 empty] | OPERATING PRESSURE EXCEEDED MAOP, WARNING DEVICE RELIEF RELEASED GAS | CLASS 3 LOCATION | 1220000 | 1579912.42362525458 | 0 | 0 | 73000 | 94535.743380855397 | 0 | 0 |  |  | 413 | 313.234458259325044404973357015985790409 |  | 0 | 1293413 | 693795.9720257708131136767317939609236234 | 1674761.40146436930204440497335701598579 | 100 | 0 | 1200 |  |  |  |  | 8.5 | 0.5 | 1 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | OTHER | SYSTEM IS MONITORED BY HI- LOW PRESSURE ALARMS |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | STEVEN W. BUCK | TECHNICAL CONSULTANT | steven.w.buck@dom.com | 330-401-8033 | 866-521-4877 |  |  |  | AARON MCCOY | TECHNICAL SPECIALIST | 330-458-9186 | aaron.m.mccoy@dom.com | THE DOMINION NETWORK THAT IS UTILIZED TO SERVE FAIRPORT HARBOR CONSISTS OF STEEL AND PLASTIC LOW PRESSURE DISTRIBUTION PIPING. GAS IS SUPPLIED THROUGH THREE DISTRICT REGULATOR STATIONS FROM THE NORTHEAST, EAST AND SOUTHWEST AREAS OF THE VILLAGE. THESE THREE STATIONS CONTAIN TWO CONTROL/MONITOR REGULATORS SET AT 6.5 OUNCES (OZ) AND 8.5 OUNCES PER SQUARE INCH GAUGE RESPECTIVELY. THE NORTHEAST STATION IS EQUIPPED WITH A HI-LO FOR MONITORING SYSTEM PRESSURE THAT IS SET AT 8.5 OZ AND 4.5 OZ RESPECTIVELY. THE EAST STATION ALSO CONTAINS A RELIEF DEVICE FOR AUDIBLE WARNING SET AT 12OZ. AT APPROXIMATELY 6:37 A.M. ON 01/24/2011, DOMINION RECEIVED A HIGH ALARM FROM THE HI-LO MONITOR AT THE NORTHEAST STATION. A TECHNICIAN WAS IMMEDIATELY DISPATCHED TO THE AREA. THE TECHNICIAN NOTED THE RELIEF BLOWING AS HE PASSED THE EAST STATION AND NOTIFIED SUPERVISION. THE TECHNICIAN ARRIVED AT THE NORTHEAST STATION AT 7:15 A.M., AND SHUT THE INLET VALVE TO THE NORTHEAST STATION. HE PROCEEDED TO THE EAST STATION, SHUT THE INLET VALVE AND OBTAINED A SYSTEM PRESSURE READING OF 8.5 PSIG. SUPERVISION WAS UPDATED THAT THE NORTHEAST AND EAST STATIONS WERE NOT SUPPLYING GAS, AND BOTH STATIONS HAD BEEN SHUT-IN. SUPERVISION ADVISED THE TECHNICIAN TO OPEN THE INLET TO THE EAST STATION AND PROCEED TO THE SOUTHWEST STATION. UPON ARRIVAL HE NOTED THE SOUTHWEST STATION WAS SUPPLYING GAS AND SHUT THE INLET VALVE. SUPERVISION ADVISED HIM TO RETURN TO THE EAST STATION AND MONITOR THE SYSTEM PRESSURE. AT 8:05 A.M. THE TECHNICIAN RETURNED TO THE EAST STATION AND NOTED THE RELIEF HAD STOPPED BLOWING. HE VERIFIED THAT SYSTEM PRESSURE HAD RETURNED TO 6.5OZ. LEAK SURVEY OF THE FAIRPORT HARBOR SYSTEM WAS CONDUCTED ON 01/24/2011 AND REPEATED ON 01/25/2011. CONSTRUCTION AND MAINTENANCE CREWS REPAIRED ALL HAZARDOUS LEAKS UPON DISCOVERY AND CONTINUE TO WORK ON REPAIR OF NON-HAZARDOUS LEAKS. DOMINION FIELD PERSONNEL REMAINED IN THE AREA OVER THE NEXT THREE DAYS, RESTORING SERVICE TO 1300 AFFECTED CUSTOMERS. DOMINION HAS WORKED WITH FAIRPORT HARBOR VILLAGE OFFICIALS AND THE AMERICAN RED CROSS PROVIDING HOUSING AND SHORT-TERM FINANCIAL SUPPORT FOR THOSE IN NEED UNTIL SERVICE RESTORATION. ELEVEN HOMES RECEIVED SEVERE DAMAGE FROM FIRE AND 150 HOMES REQUIRED APPLIANCE REPAIR OR REPLACEMENT. DOMINION AND ITS CONTRACTORS HAVE PROVIDED ALL NECESSARY HOUSE LINE REPAIRS, APPLIANCE REPAIRS AND REPLACEMENT. FOR NINE STRUCTURES CONSIDERED TO BE UNINHABITABLE, DOMINION CONTINUES TO WORK THROUGH THE PROCESS OF RESOLVING CUSTOMER CLAIMS. DOMINION WORKED WITH THE PUBLIC UTILITIES COMMISSION OF OHIO, FAIRPORT HARBOR FIRE DEPARTMENT INVESTIGATORS AND THE STATE FIRE MARSHAL IN REMOVING THE REGULATORS AND OTHER ASSOCIATED EQUIPMENT FROM THE SOUTHWEST STATION. THE STATION EQUIPMENT HAS BEEN TAKEN TO THE GAS TECHNOLOGY INSTITUTE (GTI) FOR FURTHER EXAMINATION AND INVESTIGATION. AFTER GTI REMOVED AN OILY SUBSTANCE AND CLEANED THE COMPONENTS WITH ISOPROPYL ALCOHOL, THE REGULATORS INVOLVED IN THE INCIDENT WERE TESTED IN JUNE AND AUGUST WITH ALL OTHER INTERESTED PARTIES PRESENT. THE REGULATING EQUIPMENT WAS DETERMINED TO FUNCTION AS DESIGNED DURING INCREASING AND DECREASING FLOW AND PRESSURE CONDITIONS. THE REGULATING EQUIPMENT WAS FOUND TO OPERATE PROPERLY WITH THE FLUIDS REMOVED. IT IS CURRENTLY BELIEVED THAT THE PRESENCE OF PIPELINE FLUIDS AND GAS TEMPERATURE DROP ACROSS THE REGULATORS CAUSED THE REGULATORS TO MALFUNCTION.
2025-03-31 10:13 | NO | YES | YES | 20110035 | 15876 | 2011-02-25 13:33 | SUPPLEMENTAL FINAL | 2012 | CAIRO GAS SYSTEMS, CITY OF | P.O. BOX 29 | CAIRO | GA | 39828 | 2010-09-28 11:25 |  |  | 2010 | 4TH. AVE @ 4TH. ST. SW | CAIRO | GRADY | GA | 31728 | 30.5276 | -84.1282 | [9 empty] | 2010-09-28 12:00 | 955372 |  | NATURAL GAS |  | 25000 |  | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2010-09-28 11:25 |  |  |  | 2010-09-28 11:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | MUNICIPALLY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | OPERATOR HAD CUT OUT A OF SHORT SECTION THAT WAS FOUND TO HAVE CORROSION DAMAGE AND WAS IN THE PROCESS OF REPLACEING THAT SECTION OF PIPE WITH A SECTION OF PE 2406 PLASTIC AND WAS HANDLING THE PIPE WITHOUT TURNING OFF THE GAS FLOW AND THE GAS IGNITED. | CLASS 3 LOCATION | 0 | 0 | 25000 | 33027.73737793475 | 0 | 0 | 0 | 0 |  |  | 115 | 79.45792880258899676375404530744336569579 |  | 0 | 25115 | 13752.6015117498046925566343042071197411 | 33107.1953067373389967637540453074433657 | 0 | 0 | 3 |  |  |  |  | 20 | 20 | 26 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 4 | 1 | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  | YES |  |  |  | ROUTINE MAINTENANCE | NO | [50 empty] | BILLY DONALDSON | REGULATORY COMPLIANCE CONSULTANT | bdonaldson01@windstream.net | 912-309-2402 | 912-384-6106 |  |  |  | BILLY DONALDSON | REGULATORY COMPLIANCE CONSULTANT | 912-309-2402 | bdonaldson01@windstream.net | ON TUESDAY, SEPTEMBER 28, 2010, AT APPROXIMATELY 1100 HRS. THE CITY OF CAIRO GAS DEPARTMENT PERSONNEL WERE AT THE INTERSECTION OF 4TH AVE & 4TH ST NW WHERE THEY WERE IN THE PROCESS OF REPLACING A SECTION OF 2" COATED AND WRAPPED STEEL GAS MAIN THAT WAS LEAKING DUE TO CORROSION. THE CREW HAD EARLIER DETECTED AND REPAIRED A LEAK IN THIS AREA CAUSED BY CORROSION. WHEN THE SECOND LEAK WAS DETECTED, THE GAS CREW DECIDED TO REPLACE THE SECTION OF PIPE INSTEAD OF MAKING A SECOND REPAIR IN THE SAME AREA. THE CREW EXCAVATED THE PIPE AND DECIDED THAT THE CORRECTIONS WOULD BE MADE WITHOUT TURNING OFF THE GAS SOURCE TO THE PIPE BEING REPLACED. AFTER CUTTING OUT APPROXIMATELY ELEVEN (11) FEET OF THE DAMAGED PIPE, THE CREW WAS ATTEMPTING TO INSTALL A PIECE OF 2" PE 2406 PLASTIC USING TWO (2) DRESSER STYLE COUPLINGS. WHILE ATTEMPTING TO MAKE THE CONNECTION, THE GAS WAS IGNITED BY AN UNKNOWN SOURCE WHICH RESULTED IN 1 DEATH AND 3 INJURIES TO GAS DEPARTMENT EMPLOYEES. AFTER EMERGENCY CREWS RESPONDED TO THE SITE, THE GAS WAS TURNED OFF AND PERMANENT REPAIRS WERE MADE BY GAS PERSONNEL FROM A "MUTUAL AID" ASSISTANCE CITY THAT RESPONDED TO THE CALL FOR ASSISSTANCE.
2025-03-31 10:13 | NO | NO | NO | 20110036 | 15338 | 2011-02-25 17:33 | SUPPLEMENTAL FINAL | 11032 | LACLEDE GAS CO | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2011-01-27 02:43 |  |  | 2011 | WEST FLORISSANT AND LUCAS & HUNT RD | COUNTRY CLUB HILLS | ST. LOUIS | MO | 63136 | 38.7252 | -90.2752 | [9 empty] | 2011-01-27 05:00 | 965805 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-01-27 02:43 |  |  |  | 2011-01-27 03:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1967 | [8 empty] | OTHER | STAINLESS STEEL TUBING | [9 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 0.4 | 0.4 |  | CLASS 3 LOCATION | 0 | 0 | 63000 | 81585.641547861507 | 640 | 828.80651731160896 | 1000 | 1295.010183299389 | TOTALED VEHICLE |  | 0 | 0 |  | 0 | 64640 | 34669.94704684315968 | 83709.45824847250496 | 0 | 0 | 0 |  |  |  |  | 31 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAR INVOLVED IN A POLICE CHASE LOST CONTROL AND RAN INTO THE REGULATOR STATION CONTROL BOX. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MARK D. LAUBER | SUPERINTENDENT MAINTENANCE ENGINEERING | mlauber@lacledegas.com | 314-658-5413 | 314-535-5075 |  |  |  | CRAIG R. HOEFERLIN | ASSISTANT VP ENGINEERING AND FIELD SERVICES | 314-658-5410 | choeferlin@lacledegas.com | IN THE MORNING OF JANUARY 27, 2011 A PRIVATELY OWNED/OPERATED VEHICLE INVOLVED IN A POLICE CHASE LOST CONTROL, RAN OFF THE ROAD, AND CRASHED INTO THE ABOVE GROUND EQUIPMENT BOX OF A REGULATOR STATION.
2025-03-31 10:13 | NO | NO | NO | 20110038 | 15378 | 2010-08-16 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2010-07-11 06:40 |  |  | 2010 | FIRST STREET AND COOLIDGE AVENUE | LAS VEGAS | CLARK | NV | 89101 | 36.1613 | -115.1518 | [9 empty] | 2010-07-11 11:37 | 947326 |  | NATURAL GAS |  | 215 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-07-11 06:40 |  |  |  | 2010-07-11 07:14 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1964 | [5 empty] | 2 | PVC 2110 | KRALOY | PLASTIC |  |  |  |  | POLYVINYL CLORIDE (PVC) |  |  | 0.1 |  |  | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 8009 | 10580.76594639517651 | 0 | 0 |  |  | 945 | 652.936893203883495145631067961165048544 |  | 0 | 8954 | 4986.24077790934542483495145631067961165 | 11233.7028395990600051456310679611650485 | 2 | 0 | 0 |  |  |  |  | 39 | 39 | 43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2010-07-02 | NO | [12 empty] | NO | YES | CITY STREET | [12 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO PROTECT/SHORE/SUPPORT FACILITIES | [170 empty] | KELLY EVERSON | ADMINISTRATOR-COMPLIANCE | kelly.everson@swgas.com | (702) 365-2324 | (702) 221-4116 |  |  |  | PHIL ANDREW | DIRECTOR-GAS OPERATIONS | (702) 365-2207 | phil.andrew@swgas.com | SOUTHWEST GAS EMERGENCY DISPATCH WAS NOTIFIED OF AN EXPLOSION AND POSSIBLE GAS LEAK IN THE AREA OF FIRST STREET AND COOLIDGE AVENUE BY A REPRESENTATIVE OF THE CITY OF LAS VEGAS FIRE DEPARTMENT AT 0640 ON THE MORNING OF JULY 11, 2010. MULTIPLE COMPANY EMERGENCY PERSONNEL RESPONDED TO THE SCENE AND DISCOVERED A GAS MAIN LEAK ON A TWO INCH PVC MAIN IN THE RIGHT OF WAY FOR THE PUBLIC STREET ON FIRST STREET BEHIND 921 SOUTH MAIN STREET. RESPONDING PERSONNEL HAD THE GAS MAIN LEAK UNDER CONTROL BY 0929. JANUARY 2012 SUPPLEMENT: BASED UPON THE RESULTS OF A THIRD PARTY ANALYSIS OF THE FAILED SEGMENT OF PIPE, THE CAUSE OF THE TWO-INCH PVC MAIN PIPE LEAK DISCOVERED ON FIRST STREET ON JULY 11, 2010 WAS A PREVIOUS THIRD PARTY'S FAILURE TO EMPLOY PROPER EXCAVATION PRACTICES. SPECIFICALLY, IT IS LIKELY THAT THE PIPE HAD BEEN UNCOVERED DURING A PREVIOUS EXCAVATION AND THAT THE BACKFILL WAS UNLAWFULLY AND INPROPERLY DUMPED BACK IN THE HOLE WITHOUT COMPACTION. THIS LEFT THE PIPE WITHOUT LATERAL SUPPORT FROM THE DOWNWARD LOADING CAUSED BY THE WEIGHT OF THE NON-COMPACTED BACKFILL, AND FROM OTHER POSSIBLE LOADINGS. THIS LED TO EXCESSIVE LONG-TERM DEFORMATION OF THE PIPE, CAUSING PREMATURE FAILURE.
2025-03-31 10:13 | NO | NO | NO | 20110039 | 15192 | 2011-01-06 09:53 | SUPPLEMENTAL FINAL | 32282 | JO-CARROLL ENERGY | 793 US HWY 20 WEST | ELIZABETH | IL | 61028 | 2010-12-16 17:45 |  |  | 2010 | 17360 DIAMOND RD | FULTON | WHITESIDE | IL | 61252 | 41.8349 | -90.1683 | [9 empty] | 2010-12-17 14:50 | 962550 |  | NATURAL GAS |  | 3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2010-12-16 17:46 |  |  |  | 2010-12-16 18:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | OTHER | NATURAL GAS COOPERTIVE OWNED | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | WELDED | 0.113 | [6 empty] | OTHER | [8 empty] | NIPPLE SHEARED OFF UNDER REGULATOR | CLASS 1 LOCATION | 0 | 0 | 300 | 396.332848535217 | 200 | 264.221899023478 | 75000 | 99083.21213380425 | DAMAGE TO MEMBERS HOME |  | 30 | 20.72815533980582524271844660194174757282 |  | 0 | 75530 | 41330.0515493031803980582524271844660194 | 99764.4950367027508252427184466019417476 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JAMES B. MCCASKEY | MANAGER OF GAS OPERATIONS | bmccaskey@jocarroll.com | 815-858-4103 | 815-273-2612 |  |  |  | JAMES B. MCCASKEY | MANAGER OF GAS OPERATIONS | 815-858-4103 | bmccaskey@jocarroll.com | WEATHER CONDITIONS WERE AS FOLLOWS; COLD, SNOWY TEMP AROUND -2 DEGREES F. MEMBER NAME: KENNETH AND JODI HOUSENGA 563-613-2232 REPORTED THAT SON OF MEMBER WAS BACKING OUT CAR, CAR SLID INTO METER SET. SON WENT INTO HOME TO TELL MOM WHAT HAD HAPPENED AND THAT IT SOUNDED LIKE GAS WAS ESCAPING. MOM IN TURN CALLED HUSBAND, HUSBAND HAD FAMILY LEAVE HOUSE AND CALL FIRE DEPARTMENT. THE CAR WAS LEFT RUNNING AND IT IGNITED THE ESCAPING NATURAL GAS FROM THE METER SET. NIPPLE JUST BELOW REGULATOR WAS SNAPPED OFF, RELEASE WAS AT 55PSIG. THIS WAS A STEEL SERVICE WITHOUT A EFV. FIRE ENGULFED HOME. OUR LOCAL GAS TECH RECEIVED FIRST CALL DIRECTLY FROM THE FULTON FIRE DEPARTMENT AT 5:46PM AND HE WAS UNABLE TO RESPOND AND A SECOND GAS TECH WAS DISPATCHED AT 5:49PM. HE ARRIVED ON SCENE AT 6:15PM TRAVELING FROM ERIE ,IL. CONDITION WAS MADE SAFE AND THE FIRE EXTINGUISHED AT 7:49PM.
2025-03-31 10:13 | NO | YES | NO | 20110040 | 15337 | 2011-01-14 11:59 | SUPPLEMENTAL FINAL | 11032 | LACLEDE GAS CO | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2010-12-15 19:30 |  |  | 2010 | 1721 HWY 61/67 | CRYSTAL CITY | JEFFERSON | MO | 63028 | 38.21 | -90.3903 | [9 empty] | 2010-12-15 21:20 | 962365 |  | NATURAL GAS |  | 13 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 20 | 2010-12-15 19:45 |  |  |  | 2010-12-15 20:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1995 | [8 empty] | STEEL |  | OTHER | ERW | 0.14 | [6 empty] | MECHANICAL PUNCTURE | 1 | 1.3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1279 | 1689.69904425514181 | 168 | 221.94639517972152 | 200000 | 264221.899023478 | ESTIMATED COST OF ELKS LODGE - TOTAL LOSS |  | 45 | 31.09223300970873786407766990291262135922 |  | 0 | 201492 | 110253.2945481392929350873786407766990291 | 266164.6366959225720678640776699029126214 | 1 | 0 | 0 |  |  |  |  | 22 | 22 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MARK D. LAUBER | SUPERINTENDENT MAINTENANCE ENGINEERING | mlauber@lacledegas.com | 314-658-5413 | 314-535-5075 |  |  |  | CRAIG R. HOEFERLIN |  | 314-658-5410 | choeferlin@lacledegas.com | ON THE NIGHT OF DECEMBER 15, 2010 A PRIVATELY OWNED/OPERATED FULL - SIZED PICKUP TRUCK SLID ON THE ICE COVERED PARKING LOT AND GLANCED OFF THE PROTECTIVE BOLLARD INTO THE GAS METER SET ON THE SIDE OF THE BUILDING. THE IMPACT SEVERED THE STEEL OUTLET PIPING OF THE METER SET. IGNITION SOURCE IS UNKNOWN BUT MAY HAVE BEEN FROM NEARBY ELECTRICAL EQUIPMENT.
2025-03-31 10:13 | NO | NO | NO | 20110041 | 15209 | 2011-03-04 14:31 | ORIGINAL FINAL | 1088 | BALTIMORE GAS & ELECTRIC CO | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2011-02-05 02:01 |  |  | 2011 | 3346 YELLOW-FLOWER RD | LAUREL | ANNE ARUNDEL | MD | 20724-3200 | 39.102 | -76.8164 | [9 empty] | 2011-02-05 05:46 | 966614 |  | NATURAL GAS |  | 18.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2011-02-05 02:16 |  |  |  | 2011-02-05 02:53 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2000 | [8 empty] | CAST/WROUGHT IRON | [10 empty] | OTHER | [8 empty] | VEHICLE WAS DRIVEN INTO OUTSIDE METER INSTALLATION | CLASS 4 LOCATION | 0 | 0 | 200 | 259.0020366598778 | 2000 | 2590.020366598778 | 0 | 0 |  |  | 313 | 237.390763765541740674955595026642984014 |  | 0 | 2513 | 1399.579988641008256127886323268206039076 | 3086.413167024197540674955595026642984014 | 37 | 0 | 37 |  |  |  |  | 85 | 85 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MICHAEL DENNIS BOWLING | GAS SERVICE SUPERVISOR | michael.bowling@bge.com | 410-470-7104 | 410-470-7103 |  |  |  | WILLIAM H. BROWN | MANAGER GAS SERVICE | 410-470-7105 | william.h.brown@bge.com | THE TIME OF DETERMINATION FOR THE REPORTABLE INCIDENT WAS 05:19 AM. THIRD PARTY (LOYCE ATIN) BEING INTOXICATED JUMPED THE CURB AND DROVE HER VEHICLE 35 FEET ACROSS THE YARD INTO THE RESIDENCE OF 3346 YELLOW-FLOWER RD ON THE EARLY MORNING OF FEBRUARY 5, 2011. THIRD PARTY DROVE INTO THE CORNER OF THE RESIDENCE RIGHT WHERE THE OUTSIDE GAS AND ELECTRIC METERS WERE LOCATED, CAUSING NATURAL GAS TO IGNITE. THE IGNITION CAUSED FIRE DAMAGE TO THE VEHICLE AND THE RESIDENCE OF 3346 YELLOW-FLOWER RD. THE OPERATOR HAD TO OPERATE A MAIN LINE VALVE TO STOP THE FLOW OF NATURAL GAS TO EXTINGUISH THE FIRE AT THE GAS METER INSTALLATION THAT AFFECTED 37 HOMES. AFTER THE FIRE WAS EXTINGUISHED, THE VEHICLE WAS REMOVED AND THE NATURAL GAS SERVICE WAS TERMINATED FOR SAFETY AND NATURAL GAS WAS RESTORED TO THE COMMUNITY.
2025-03-31 10:13 | NO | NO | NO | 20110042 | 15210 | 2011-03-04 16:57 | ORIGINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2011-02-09 06:51 |  |  | 2011 | 38 S. 5TH STREET | FULTON | OSWEGO | NY | 13069 | 43.3249 | -76.411 | [9 empty] | 2011-02-09 10:50 | 966946 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2011-02-09 07:01 |  |  |  | 2011-02-09 07:01 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1985 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 25700 | 33281.7617107942973 | 3503 | 4536.420672097759667 | 621 | 804.201323828920569 | 5000 | 6475.050916496945 | DAMAGE TO ADJACENT BUILDING |  | 64 | 48.53996447602131438721136767317939609236 |  | 0 | 34888 | 18722.907197042311852831261101243339254 | 45145.9745876939438503872113676731793961 | 0 | 0 | 2 |  |  |  |  | 22 | 22 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ABOVE GROUND LEAK DUE TO A CRACKED NIPPLE FROM FALLEN ICE. NOT DETECTABLE BY SCADA. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | ICE SLID OFF STEEL ROOF ONTO OUTSIDE METER SET AND CRACKED THE NIPPLE. | YES |  |  |  | YES | ICE SLID OFF STEEL ROOF AND DAMAGED EQUIPMENT. | [213 empty] | DEBORAH DEBERGALIS | MANAGER UPSTATE DISPATCH AND SCHEDULING | deborah.debergalis@us.ngrid.com | 315 460-2615 | 315 460-2762 |  |  |  | DEBORAH DEBERGALIS |  | 315 460-2615 | deborah.debergalis@us.ngrid.com | INCIDENT TIMELINE: 06:56 GAS ODOR CALLED IN FROM 425 CAYUGA ST, FULTON. DISPATCHED TO SERVICE REP. SEE ATTACHED MWORK ORDER. 07:01 SERVICE MAN (ANDY HECKATHORN) ARRIVED AT COMPLAINT ADDRESS. COULD SMELL STRONG ODOR OF GAS AND BEGAN TO INVESTIGATE THE SOURCE. 07:15 WHILE IN FRONT OF 425 CAYUGA ST, SERVICE MAN HEAR A LOUD 'WOOSH' ACROSS THE STREET AND THOUGHT THE BUILDING MAY HAVE CAVED IN. WHEN INVESTIGATING THE NOISE, HE SAW SMOKE FROM A HOUSE AROUND THE CORNER AT 38 S 5TH ST, FULTON. HE CALLED 911 AND WENT TO ADDRESS AND SAW FRONT WALL HAD BEEN BLOWN OUT AND FLAMES COMING FROM INSIDE HOUSE. HE SAW TWO PEOPLE ESCAPE THE HOUSE AND THEY SAID NO ONE ELSE WAS INSIDE. HE CONTACTED SUPERVISOR AND CUT ELECTRIC SERVICE AT POLE AT STREET. UNABLE TO GET TO OUTSIDE GAS METER BECAUSE OF FIRE. 07:20 DISPATCHED GAS OPERATIONS CREW (JAMES TUTTLE, MICHAEL KENYON, JAMIESON BOONZHA) TO 38 S 5TH ST. 07:30 GAS OPS CREW ARRIVED ON SITE. FIRE DEPARTMENT WAS AT SCENE. HOUSE WAS IN FLAMES AND FIRE DEPARTMENT WAS USING HOSES TO CONTROL FIRE. WHEN IT WAS SAFE, CREW APPROACHED OUTSIDE RISER TO DETERMINE WHETHER IT WAS BROKEN ABOVE OR BELOW THE SHUT OFF VALVE. THE ENTIRE METER ASSEMBLY WAS BURIED WITH SNOW, ICE AND ASH WHEN THEY APPROACHED. 07:45 GAS WAS SHUT OFF AT RISER USING A LONG HANDLED VALVE KEY. THIS SIGNIFICANTLY REDUCED THE FLAMES HOWEVER DID NOT STOP THE FIRE. IT WAS DETERMINED THAT GAS WAS LEAKING BY SHUTOFF ON RISER. 07:50 SERVICE DEPARTMENT BEGAN WALL CHECKS AT ALL THE NEIGHBORING HOUSES. ALL WALL CHECKS WERE CLEAR. 08:00 GAS CREW BEGAN DIGGING SERVICE AT MAIN TO SHUT OFF GAS. 08:42 GAS SERVICE WAS SHUT OFF AT TEE. UPON SHUT DOWN, FIRE IMMEDIATELY EXTINGUISHED. FOLLOW-UP INVESTIGATION: IMMEDIATELY FOLLOWING THIS INCIDENT THE SUBSEQUENT ACTION WAS TAKEN: - A GAS SAMPLE WAS TAKEN AT THE NEIGHBORING HOUSE (501 CAYUGA ST) TO CHECK MERCAPTIN LEVELS. TWO TESTS WERE COMPLETED USING BACKARACH ODOROMETER (ID# AIS367). THE RESULTS WERE: - .15 (TESTED BY ANDY HECKATHORN) - .25 (TESTED PHILIP NATOLI) - ABOVE GROUND SERVICE PIPING, INCLUDING CUSTOMER FUEL LINE, WAS INSPECTED FOR DAMAGE. THE ENTIRE METER ASSEMBLY WAS SIGNIFICANTLY BENT FORWARD. THERE WAS SIGNIFICANT DAMAGE TO THE REGULATOR, AND METER DUE TO THE FIRE. CUSTOMER FUEL LINE WAS VERY LOOSE BUT STILL INTACT. A CRACK WAS FOUND ON THE NIPPLE BETWEEN THE REDUCER AND THE BOTTOM OF THE SHUT OFF VALVE. - SERVICE RISER WAS CAPPED, AND LINE WAS RE-ENERGIZED. AN UNDERGROUND LEAK SURVEY WAS COMPLETED USING TWO CALIBRATED COMBUSTIBLE GAS INDICATORS (ID #052010 AND #052010). ZERO GAS READINGS WERE FOUND. - THE SERVICE LINE WAS PRESSURE TESTED WITH AIR AT 22PSI FOR 15 MINUTES, WITH NO DROP IN LINE PRESSURE. - AFTER TESTING WAS COMPLETED, THE SERVICE LINE WAS PERMANENTLY RETIRED AT THE MAIN. - JIM CLARY FROM THE NG CLAIMS DEPARTMENT AS WELL AS DENNIS WARE FROM WARE INVESTIGATIONS ARRIVED TO INVESTIGATE AND DOCUMENT THE EVENT. PRELIMINARY REPORT: CONSENSUS WITH THE LOCAL FIRE AND POLICE INVESTIGATORS AS WELL AS NG PERSONNEL DETERMINED THAT ICE AND SNOW SHED FROM THE ROOF OF THE RESIDENCE CAUSED THE DAMAGE TO THE SERVICE PIPING RESULTING IN THE LEAK. THE MOST LIKELY IGNITION SOURCE OCCURRED FROM THE FURNACE WHICH WAS LOCATED APPROXIMATELY 5 FEET FROM THE SERVICE RISER.
2025-03-31 10:13 | NO | NO | NO | 20110043 | 15211 | 2011-03-08 10:10 | ORIGINAL FINAL | 5410 | FORT HILL NATURAL GAS AUTH | 311 S. PENDLETON STREET | EASLEY | SC | 29640 | 2011-02-02 09:16 |  |  | 2011 | ROCHESTER HWY. | SENECA | OCONEE | SC | 29678 | 34 | -82 | [9 empty] | 2011-02-02 16:37 | 966394 |  | NATURAL GAS |  | 964 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 12 | 2011-02-02 09:16 |  |  |  | 2011-02-02 09:25 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1952 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | SERVICE TEE WAS PULLED OFF OF MAIN BY EXCAVATOR. | CLASS 2 LOCATION | 0 | 0 | 355 | 459.728615071283095 | 15800 | 20461.1608961303462 | 250 | 323.75254582484725 | REPLACE SERVICE TEE AND HIGH PRESSURE STAND TO RESIDENT. |  | 8317 | 6307.920071047957371225577264653641207815 |  | 0 | 24722 | 14634.088966404151355337477797513321492 | 27552.5621280744339162255772646536412078 | 0 | 0 | 305 |  |  |  |  | 360 | 360 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PRESSURE DID NOT DECREASE IN THE CONTROL ROOM AND THE CAUSE WAS OBVIOUS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 1101310909 | SC 811 |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | LINK SARGENT | REGULATORY COMPLIANCE OFFICER | link.sargent@fhnga.com | 864 859 6375 | 864 850 7360 |  |  |  | MICHAEL L. HAGGARD | EXECUTIVE V.P. AND C.O.O. | 864 859 6375 | mike.haggard@fhnga.com
2025-03-31 10:13 | NO | NO | NO | 20110044 | 15212 | 2011-03-08 15:08 | ORIGINAL FINAL | 6920 | ENTERGY GULF STATES | 5755 CHOCTAW DRIVE | BATON ROUGE | LA | 70805 | 2011-02-12 22:30 |  |  | 2011 | 2415 BOYD AVE. | BATON ROUGE | EAST BATON ROUGE PARISH | LA | 70802 | 30.4557 | -91.1638 | [9 empty] | 2011-02-14 09:45 | 967390 |  | NATURAL GAS |  | 23.64 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 6 | 2011-02-12 22:42 |  |  |  | 2011-02-12 22:55 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | CAR HIT GAS METER & REGULATOR SET. | CLASS 2 LOCATION | 0 | 0 | 200 | 259.0020366598778 | 500 | 647.5050916496945 | 0 | 0 |  |  | 131 | 99.35523978685612788632326820603907637655 |  | 0 | 831 | 467.357479027467587388987566607460035524 | 1005.862368096428427886323268206039076377 | 0 | 0 | 1 |  |  |  |  | 55 | 60 | 100 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | CAR HIT METER | [47 empty] | ROBERT A. BORNE | COMPLIANCE COORDINATOR | rborne@entergy.com | 225 354-3289 | 225 354-3061 |  |  |  | DONALD W. VINCI | VP GAS DISTRIBUTION BUSINESS | 504 593-3434 | dvinci@entergy.com | AT APPROXIMATELY 22:30 HOURS ON FEBRUARY 12, 2011 BATON ROUGE CITY POLICE WERE INVOLVED IN A VEHICLE PURSUIT WITH AN UNKNOWN SUBJECT. AS THE SUBJECTS CAR TURNED ON BOYD AVE THE SUBJECT JUMPED FROM THE MOVING VEHICLE ALLOWING THE VEHICLE TO CONTINUE MOVING UNTIL IT HIT THE HOUSE AT 2242 BOYD AVE. THE CAR HIT THE HOUSE AT THE LOCATION OF THE GAS METER AND REGULATOR. THIS SHEERED THE METER AND REGULATOR FROM THE GAS SERVICE RISER CREATING AN OPEN SERVICE LINE WITH 55LBS PRESSURE. ACCORDING TO WITNESSES THE GAS IGNITED IMMEDIATELY CAUSING THE VEHICLE AND HOUSE TO CATCH FIRE. GAS CREWS WERE ABLE TO SHUT OFF THE SUPPLY TO 2242 BOYD AT APPROXIMATELY 02:16 HOURS ON FEBRUARY 13, 2011. INVESTIGATION PENDING TO DETERMINE VALUE OF DAMAGED PROPERTY.
2025-03-31 10:13 | NO | YES | NO | 20110045 | 15213 | 2011-03-09 17:10 | ORIGINAL | 24015 | YANKEE GAS SERVICES CO | 107 SELDEN STREET | BERLIN | CT | 06037 | 2011-02-07 06:38 |  |  | 2011 | 75 KIMBERLY DRIVE | SOUTH WINDSOR | HARTFORD | CT | 06074-1031 | 41.8481 | -72.6032 | [9 empty] | 2011-02-09 14:30 | 966975 |  | NATURAL GAS |  | 26 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2011-02-07 06:38 |  |  |  | 2011-02-07 06:58 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2005 | [8 empty] | STEEL |  |  |  | 0.113 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 1333 | 1726.248574338085537 | 378 | 489.513849287169042 | 500000 | 647505.0916496945 | DAMAGE TO STRUCTURE |  | 209 | 158.513321492007104795737122557726465364 |  | 0 | 501920 | 269241.5258545468971952770870337477797513 | 649879.3673948117616837957371225577264654 | 2 | 0 | 0 |  |  |  |  | 85 | 85 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF GAS FLOWING FROM THE DAMAGE WAS TOO LOW FOR DETECTION FROM SCADA. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | CUSTOMER DEPOSITED LARGE AMOUNT OF SNOWFALL FROM ROOF OF COMMERCIAL BUILDING ONTO OUTSIDE METER SET. | [47 empty] | GARRY DAIGLE | PRINCIPAL ENGINEER | daiglgj@nu.com | 203-596-3149 | 203-596-3130 |  |  |  | BRET FACTORA | GAS ENGINEERING MANAGER | 203-596-3071 | factobp@nu.com | THE STATE HAS EXPERIENCED A LARGE AMOUNT OF ACCUMULATED SNOW THIS SEASON. THE CUSTOMER AT THIS FACILITY HAD REMOVED SNOW ACCUMULATED ON THE ROOF OUT OF CONCERN THAT THE SNOW LOAD WOULD COLLAPSE THE ROOF. THE SNOW WAS REMOVED FROM THE ROOF AND DEPOSITED ON THE GROUND SURROUNDING THE BUILDING INCLUDING THE METER LOCATION. WHEN COMPANY PERSONNEL ARRIVED ONSITE THE SNOW AT THE METER SET WAS 10 FEET HIGH. THE FORCE OF THE SNOW BEING DROPPED FROM THE ROOF STRESSED THE PIPING FROM THE METER VALVE AT THE TOP OF THE SERVICE RISER TO THE REGULATOR CAUSING THE THREADED NIPPLE TO CRACK AT THE THREADS.
2025-03-31 10:13 | NO | YES | YES | 20110046 | 16729 | 2011-03-10 16:43 | SUPPLEMENTAL FINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2011-02-09 22:45 |  |  | 2011 | N. 13TH & W. ALLEN STREETS | ALLENTOWN | LEHIGH | PA | 18102-2104 | 40.6071 | -75.4879 | [9 empty] | 2011-02-10 00:19 | 967026 |  | NATURAL GAS |  | 25 |  | YES | 0 | 0 | 0 | 0 | 5 | 5 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES |  |  |  |  | YES | 500 | 2011-02-09 22:59 |  |  |  | 2011-02-09 23:18 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 52 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1928 | [5 empty] | 12 | ASA SPECIFICATION A-21.3 | FRANCE | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 1575000 | 2039641.038696537675 | 49632 | 64273.945417515274848 | 33088 | 42849.296945010183232 | 8272 | 10712.324236252545808 | COST TO RELIGHT CUSTOMERS ADJACENT TO INCIDENT AREA. SEE SECTION H- NARRATIVE |  | 155 | 117.557726465364120781527531083481349911 |  | 0 | 1666147 | 893670.8520567366242532007104795737122558 | 2157594.16302178104300878152753108348135 | 2 | 0 | 6 |  |  |  |  | 0.36 | 0.36 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | NO | [218 empty] | FRANK BENNETT | DIRECTOR ENGINEERING AND TECHNICAL SERVICES | fbennett@ugi.com | 610-796-3567 |  |  |  |  | FRANK BENNETT | DIRECTOR ENGINEERING AND TECHNICAL SERVICES | 610.796.3567 | fbennett@ugi.com | ON FEBRUARY 9TH, AN EXPLOSION OCCURRED AT N. 13TH AND W. ALLEN STREETS IN ALLENTOWN, PA. DESTROYING 544 AND 542 N. 13TH STREET RESIDENCES. SUBSEQUENT FIRE DAMAGE DESTROYED (6) ADDITIONAL ROW HOMES, 530-540. THE LIKELY SOURCE OF THE GAS IGNITED IN THE EXPLOSION WAS A CIRCUMFERENTIAL SEPARATION/FRACTURE ON A 12" CAST IRON MAIN LOCATED ON W. ALLEN STREET. GAS FROM THE CRACK APPEARS TO HAVE MIGRATED TO 544 N. 13TH STREET AND IGNITED.. ** IN PART D #2E DOES NOT INCLUDE "'CONFIDENTIAL SETTLEMENTS" RELATED TO PERSONAL INJURY OR WRONGFUL DEATH CLAIMS. 12/15/2017 SUPPLEMENTAL REPORT SUBMITTED TO UPDATE THE FOLLOWING: NCR REPORT NUMBER CORRECTED. THE CAST IRON PIPE THAT FAILED WAS REPLACED WITH POLYETHYLENE PIPE AND THE SYSTEM WAS RESTARTED ON 3/11/2011. THE CAST IRON PIPE FAILED DUE TO A COMBINATION OF FACTORS. FROST AND FROZEN GROUND LIKELY CRACKED THE ROAD SURFACE. THE COMPROMISED ROAD SURFACE, AND FROZEN GROUND, ALLOWED VEHICULAR TRAFFIC LOADS TO BE TRANSFERRED TO THE PIPE WHICH EVENTUALLY CAUSED CRACKING IN A PARTIALLY GRAPHITIZED SECTION OF THE MAIN. MATERIALS ANALYSIS INDICATES THAT ABSENT THE CONFLUENCE OF THE FROST HEAVE AND EXTERNAL LOADING, THE PIPE LIKELY WOULD NOT HAVE OTHERWISE FRACTURED..
2025-03-31 10:13 | NO | NO | NO | 20110047 | 15216 | 2011-03-16 12:20 | ORIGINAL FINAL | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2011-02-15 06:05 |  |  | 2011 | 2400 S BEATRICE | DETROIT | WAYNE | MI | 48217 | 42.2697 | -83.1541 | [9 empty] | 2011-02-15 08:06 | 967487 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | YES |  | 2011-02-15 06:05 |  |  |  | 2011-02-15 06:22 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1930 | [5 empty] | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 61000 | 78995.621181262729 | 5558 | 7197.666598778004062 | 6102 | 7902.152138492871678 | 0 | 0 |  |  | 0 | 0 |  | 0 | 72660 | 38971.50916496943042 | 94095.43991853360474 | 0 | 0 | 0 |  |  |  |  | 5 | 5 | 5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | NO | [218 empty] | ROBERT FRECKELTON | MANAGER | freckeltonr@dteenergy.com | 313-389-7755 | 313-389-7757 |  |  |  | ROBERT FRECKELTON | MANAGER | 313-389-7755 | freckeltonr@dteenergy.com | AT 06:05, ON FEBRUARY 15, 2011, MICHCON RESPONDED TO A REPORTED EXPLOSION AT 2400 S. BEATRICE IN THE CITY OF DETROIT, WAYNE COUNTY, MI. AT 06:22 MICHCON PERSONNEL ARRIVED AND REPORTED A WALL DOWN INSIDE THE BUILDING WITH NO OUTSIDE STRUCTURE DAMAGE. MICHCON LOCATED A LEAK OVER A 4-INCH CAST IRON MAIN LOCATED ON DOWNING STREET APPROXIMATELY 67 FEET WEST OF BEATRICE. A CIRCUMFERENTIAL CRACK WAS FOUND IN THE 4-INCH CAST IRON MAIN. AT 11:30 MICHCON REPAIRED THE 4-INCH CAST IRON MAIN WITH A 4"X9" REPAIR CLAMP AND THE LEAK WAS STOPPED. THE DEPTH OF FROST WAS 18-INCHES WHICH CAUSED THE MAIN TO BREAK. THE DEPTH OF MAIN IS APPROXIMATELY 48-INCHES. THE INCIDENT WAS A RESULT OF LEAKING GAS MIGRATING FROM THE BROKEN MAIN, THROUGH THE FRONT YARD, AND INTO A STORAGE ROOM LOCATED IN THE CENTER OF THE BUILDING. SOURCE OF IGNITION UNKNOWN.
2025-03-31 10:13 | NO | NO | NO | 20110048 | 15217 | 2011-03-16 14:59 | ORIGINAL | 1088 | BALTIMORE GAS & ELECTRIC CO | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2011-02-16 11:04 |  |  | 2011 | 1203 PARK-RIDGE DR. | MOUNT AIRY |  | MD | 21771 | 39.366 | -77.1757 | [9 empty] | 2011-02-16 13:45 |  |  | NATURAL GAS |  | 440 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2011-02-16 11:04 |  |  |  | 2011-02-16 11:26 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1996 | [5 empty] | 6 | D2513 | PERFORMANCE PIPE A DIVISION OF CHEVERONE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 2.3 | 0.9 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 79583 | 103060.795417515274787 | 0 | 0 | NO OTHER COSTS. |  | 2872 | 2178.230905861456483126110124333925399645 |  | 0 | 82455 | 44699.6816485368752678028419182948490231 | 105239.0263233767312701261101243339253996 | 0 | 0 | 247 |  |  |  |  | 85 | 85 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | CALL TO DISPATCH OFFICE. |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 11058181 | UTILQUEST |  | CONTRACT LOCATOR | NO | YES | 9 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | BERNIE SMITH | SUPERVISOR GAS SERVICE | bernard.smith@bge.com | 4104707106 |  |  |  |  | WILLIAM BROWN | MGR-GAS SERVICE | 4104707105 | william.h.brown@bge.com | ON FEBRUARY 16, 2011 AT 11:04 AM ROSS CONTRACTING DAMAGED AN UNMARKED 6" PLASTIC GAS MAIN AT THE INTERSECTION OF PARK-RIDGE DR. & RIDGEVILLE BLVD. WITH AN EXCAVATOR WHILE DIGGING ON MISS UTILITY TICKET #11058181 TO INSTALL A WATER MAIN. BGE MAINTANCE & REPAIR CREW MEMBERS MADE REPAIRS TO THE 6" PLASTIC PIPE WITH 2- 6" COUPLINGS AND 2' OF PLASTIC PIPE. OTHER WORK ASSOCIATED WITH THE MAIN REPAIRS INCLUDED RELIGHTING 247 RESIDENTIAL HOMES. THIS WAS NECESSARY BECAUSE SUPPLY WAS CUT OFF IN ORDER TO MAKE TIMELY REPAIRS.
2025-03-31 10:13 | YES | NO | NO | 20110049 | 15218 | 2011-03-18 12:50 | ORIGINAL FINAL | 1088 | BALTIMORE GAS & ELECTRIC CO | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2011-02-18 23:52 |  |  | 2011 | 6345 LOUDON AV | ELKRIDGE | HOWARD COUNTY | MD | 21075-5636 | 39.197 | -76.7384 | [9 empty] | 2011-02-19 01:40 | 967945 |  | NATURAL GAS |  | 1.2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2011-02-19 00:18 |  |  |  | 2011-02-19 00:35 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1980 | [8 empty] | CAST/WROUGHT IRON | [10 empty] | OTHER | [8 empty] | ABOVE GROUND METER INSTALLATION WAS COMPROMISED DUE TO THE FIRE WHICH MELTED AND CAUSED THE RELEASE OF NATURAL GAS | CLASS 4 LOCATION | 0 | 0 | 100 | 129.5010183299389 | 5000 | 6475.050916496945 | 300000 | 388503.0549898167 | THE VALUE OF HOUSE AND ALL CONTENTS OF HOUSE ESTIMATED BY FD, PLUS 2 VEHICLES |  | 12 | 9.10124333925399644760213143872113676732 |  | 0 | 305112 | 163650.1401605451489309058614564831261101 | 395116.7081679828378964476021314387211368 | 0 | 0 | 1 |  |  |  |  | 92 | 92 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MICHAEL DENNIS BOWLING | GAS SERVICE SUPERVISOR | michael.bowling@bge.com | 410-470-7104 | 410-470-7103 |  |  |  | WILLIAM H. BROWN JR | MANAGER GAS SERVICE | 410-470-7105 | william.h.brown@bge.com | ACCORDING TO HOWARD COUNTY FIRE DEPARTMENT, THE POINT OF FIRE ORIGINATED NEAR THE FRONT DOOR OF 6345 LOUDON AV NEAR THE SERVICE ENTRANCE CABLE. THE HEAT AND/OR FIRE IMPINGED ON THE BODY OF THE REGULATOR CAUSING IT TO MELT ALLOWING GAS TO ESCAPE THAT CAUGHT FIRE. THE FIRE DEPARTMENT KEPT A SPRAY OF WATER TO KEEP THE FIRE UNDER CONTROL UNTIL WE OPERATED THE VALVE ON RISER TO EXTINGUISH THE FIRE. THE DAMAGE TO THE REGULATOR THAT ALLOWED GAS TO ESCAPE WAS SUBSEQUENT TO THE FIRE DAMAGE IT SUSTAINED.
2025-03-31 10:13 | NO | YES | NO | 20110050 | 15219 | 2011-03-18 18:31 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2011-02-22 12:01 |  |  | 2011 | 13 BAILEY ROAD | PARK FOREST | COOK | IL | 60466 | 41.4907 | -87.6709 | [9 empty] | 2011-02-22 15:30 | 968265 |  | NATURAL GAS |  | 23.96 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES |  | 2011-02-22 12:01 |  |  |  | 2011-02-22 12:11 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1969 | [5 empty] | 1.05 | API 5L | UNKNOWN | STEEL |  | OTHER | CBW | 0.113 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 2400 | 3108.0244399185336 | 2800 | 3626.0285132382892 | 303000 | 392388.085539714867 | PROPERTY DAMAGE AND CONTENTS OF STRUCTURE |  | 130 | 98.59680284191829484902309058614564831261 |  | 0 | 308330 | 165395.6273672100542348134991119005328597 | 399220.7352957136080948490230905861456483 | 0 | 0 | 2 |  |  |  |  | 24 | 24 | 28 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 460588 | JULIE INC. NOTE: THERE IS AN X IN FRONT OF THE TICKET NUMBER BUT THE DB WILL NOT ACCEPT LETTERS, ONLY NUMBERS. |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | lquezad@nicor.com | 630-388-2316 |  |  |  |  | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | 630-388-2316 | lquezad@nicor.com | THIRD PARTY EXCAVATOR WAS INSTALLING WATER MAIN. EXCAVATOR HIT A 3/4" STEEL SERVICE LINE CAUSING A RELEASE OF GAS NEAR THE FOUNDATION OF THE HOME. GAS MIGRATED INSIDE AND RESULTED IN AN EXPLOSION AND FIRE.
2025-03-31 10:13 | NO | YES | YES | 20110051 | 15254 | 2011-03-19 09:07 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-03-16 13:25 |  |  | 2011 | 82 UNIVERSITY PLACE | NEW YORK | NEW YORK | NY | 10003-4684 | 40.7335 | -73.9932 | [9 empty] | 2011-03-16 14:04 | 970255 |  | NATURAL GAS |  | 61.25 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | NO |  |  |  |  | NO | 0 | 2011-03-16 13:25 |  |  |  | 2011-03-16 13:33 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1980 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | SERVICE WAS MECHANICAL DISCONNECTED FROM THE MAIN AS PART OF A PLANNED RETIREMENT OF THE SERVICE. | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 225 | 291.377291242362525 | 0 | 0 |  |  | 100 | 75.84369449378330373001776198934280639432 |  | 0 | 325 | 190.839593138301082548845470692717584369 | 367.220985736145828730017761989342806394 | 0 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | FAILED TO FOLLOW PROCEDURE |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER--GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON WEDNESDAY MARCH 16, 2011 AT 13:25 THE NEW YORK CITY FIRE DEPARTMENT (FDNY) REPORTED AN OUTSIDE GAS ODOR TO THE GAS EMERGENCY RESPONSE CENTER (GERC). THE FDNY REPORTED THE FOLLOWING, ' CONTRACTOR WORKING ON GAS LINE HAS UNCAPPED GAS LINE IN STREET AND GETTING A GAS ODOR'. THE GERC DISPATCHED GAS DISTRIBUTION SERVICES (GDS) AND SUPERVISION. THE FDNY CALLED BACK AT 13:27 AND STATED 'THAT A CONTRACTOR HAD CUT THROUGH A GAS LINE IN THE STREET' AT THIS SAME LOCATION. A CODE MURRE (MULTIPLE RESOURCE RESPONSE EVENT) WAS INITIATED AND THE GERC DISPATCHED ADDITIONAL RESOURCES. GDS RESPONDED AND REPORTED THAT A HALLEN CONTRACTOR CREW WORKING FOR MANHATTAN GAS OPERATIONS WAS ON LOCATION TO CUT, CAP AND RETIRE A 2' LOW PRESSURE STEEL GAS SERVICE AND THAT THE LEAK REPORTED BY THE FDNY WAS FOUND SECURED UPON GDS" ARRIVAL. THE HALLEN MAINTENANCE MECHANIC REPORTED TO THE GDS SUPERVISOR THAT HIS PARTNER, A HALLEN LABORER WAS IN THE EXCAVATION INSTALLING A 2' SCREW CAP AT THE SERVICE'S MAIN CONNECTION AND HE BECAME UNCONSCIOUS. THE MAINTENANCE MECHANIC REMOVED THE LABORER FROM THE EXCAVATION AND CALLED 911. THE FDNY RESPONDED AND TRANSPORTED THE LABORER (CONSCIOUS WHEN FDNY ARRIVED) TO BELLEVUE HOSPITAL.A REVIEW OF THIS INCIDENT WAS COMPLETED AND WAS RULED PREVENTABLE. BASED ON THE INVESTIGATION THE FOLLOWING ACTIONS WERE TAKEN: APPROPRIATE ADMINISTRATIVE ACTIONS WERE ENFORCED AGAINST THE CONTRACTOR; DISCIPLINARY ACTIONS WERE IMPOSED AGAINST THE MECHANICS; FINDINGS WERE COMMUNICATED; AND CORRECTIVE ACTIONS WERE INSTITUTED. THE NYS PSC, US DOT AND NYC DEP WERE NOTIFIED. THIS IS AN UPGRADED LEVEL INCIDENT.
2025-03-31 10:13 | YES | NO | NO | 20110052 | 15221 | 2011-03-20 20:15 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2011-02-19 06:05 |  |  | 2011 | 8403 POTOMAC AVENUE | COLLEGE PARK | PRINCE GEORGE'S | MD | 20742 | 38.9918 | -76.9253 | [9 empty] | 2011-02-19 08:12 | 967955 |  | NATURAL GAS |  | 50 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2011-02-19 06:05 |  |  |  | 2011-02-19 06:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1998 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | OTHER | [8 empty] | DAMAGE TO AN OUTSIDE SERVICE RISER AS A RESULT OF A HOUSE FIRE. | CLASS 3 LOCATION | 0 | 0 | 100 | 129.5010183299389 | 10500 | 13597.6069246435845 | 500000 | 647505.0916496945 | DAMAGE ESTIMATE TO THE STRUCTURE AS A RESULT OF A HOUSE FIRE. |  | 250 | 189.609236234458259325044404973357015986 |  | 0 | 510850 | 274037.9454696073253438721136767317939609 | 661421.808828902481659325044404973357016 | 0 | 0 | 45 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MICHAEL UPSHAW | SUPERVISOR - DOT PIPELINE SAFETY COMPLIANCE | mupshaw@washgas.com | 703-750-4479 | 703-750-5591 |  |  |  | DAVID W. SPANGLER | MANAGER - DOT PIPELINE SAFETY COMPLIANCE | 703-750-4341 | dspangler@washgas.com | WASHIGNTON GAS RESPONDED TO A HOUSE FIRE AT 8403 POTOMAC AVENUE IN COLLEGE PARK, MD ON FEBRUARY 19, 2011. UPON ARRIVAL, WASHINGTON GAS CONFIRMED THERE WAS NO GAS AT 8403 BUT THE SERVICE TO 8401 HAD BEEN COMPROMISED BY THE HEAT OF THE FIRE AT 8403. A 360 DEGREE SUBSURFACE BAR HOLE SURVEY WAS CONDUCTED AROUND 8401. THE SERVICE TO 8401 WAS CAPPED OFF AT THE CURB. CONVERSTIONS WITH FIRE DEPARTMENT PERSONNEL INDICATED THAT THEY BELIEVED THE FIRE STARTED ON THE FRONT PORCH OF 8403 WHERE THERE WAS A CERAMIC FLOWER POT WITH SMOKING MATERIALS.
2025-03-31 10:13 | NO | YES | YES | 20110053 | 15222 | 2011-03-21 10:34 | ORIGINAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2011-02-21 16:35 |  |  | 2011 | WEAVER DAIRY RD NEAR MLK BLVD | CHAPEL HILL | ORANGE COUNTY | NC | 27514 | 35.9639 | -79.0491 | [9 empty] | 2011-02-21 17:42 | 968154 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2011-02-21 16:35 |  |  |  | 2011-02-21 16:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 60 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1982 | [5 empty] | 4 | API - 5L | UNKNOWN | STEEL |  | OTHER | ERW | 0.188 | [6 empty] | OTHER | [8 empty] | BLOWING AIR THROUGH ABANDONED PIPE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | CONTRACTOR EMPLOYEE PURGED RESIDUAL NATURAL GAS WITH FORCED AIR OUT OF PIPE THAT WAS BEING ABANDONED INTO AN EXCAVATION WHERE TWO CONTRACTOR EMPLOYEES WERE WRAPPING PIPE USING A TORCH. |  |  | YES |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | TUCKER BULLOCK | MANAGER - OPERATIONS | tbullock@scana.com | 919-598-7417 | 803-933-8273 |  |  |  | MILTON SCOTT SWINDLER | GENERAL MANAGER CONSTRUCTION AND MAINTENANCE | 704-810-3230 | sswindler@scana.com | CONTRACTOR EMPLOYEE PURGED RESIDUAL NATURAL GAS WITH FORCED AIR OUT OF PIPE THAT WAS BEING ABANDONED INTO AN EXCAVATION WHERE TWO CONTRACTOR EMPLOYEES WERE WRAPPING PIPE. THE NATURAL GAS/AIR MIXTURE WAS IGNITED BY OPEN FLAME ON A PROPANE TORCH THAT THE TWO CONTRACTOR EMPLOYEES WERE USING TO WRAP PIPE.
2025-03-31 10:13 | NO | YES | NO | 20110054 | 15223 | 2011-03-23 16:57 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2011-02-23 11:45 |  |  | 2011 | 22 FREEWAY @ BOLSA CHICA | GARDEN GROVE | ORANGE COUNTY | CA | 92844 | 33.7739 | -118.0391 | [9 empty] | 2011-02-23 13:55 | 968363 |  | NATURAL GAS |  | 11032 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-02-23 11:45 |  |  |  | 2011-02-23 12:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1959 | [5 empty] | 16 | GRADE B | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 28000 | 36260.285132382892 | 2000 | 2590.020366598778 | 0 | 0 |  |  | 66000 | 50056.8383658969804618117229129662522202 |  | 0 | 96000 | 62396.1375812583799822380106571936056838 | 88907.1438648786504618117229129662522202 | 0 | 0 | 0 |  |  |  |  | 175 | 175 | 188 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | YES | 3510041 | USA SOUTH |  | UTILITY OWNER | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | JEFF KOSKIE | PIPELINE SAFETY ADVISOR | wkoskie@semprautilities.com | 213 305-8660 | 213 244-8155 |  |  |  | JEFF KOSKIE | PIPELINE SAFETY ADVISOR | 213 305-8660 | wkoskie@semprautilities.com | ON MARCH 23, 2011, A 16 INCH STEEL NATURAL GAS SUPPLY LINE WAS DAMAGED BY MECHANIZED GRADING EQUIPMENT. AS A RESULT OF THIS DAMAGE, PORTIONS OF THE 22 FREEWAY WERE TEMPORARILY CLOSED. THE FACILITIES HAD BEEN PROPERLY LOCATED AND MARKED IN RESPONSE TO A USA REQUEST. UPON FURTHER INVESTIGATION, IT WAS LEARNED THAT EXCAVATOR DID NOT INDICATE TO SOCALGAS EMPLOYEE THAT ANY EXCAVATING WOULD BE TAKING PLACE OVER THE 16 INCH PIPELINE. AS A RESULT, NO STANDBY WAS TAKING PLACE AT TIME OF DAMAGE. PRESSURE WAS LOWERED IN SECTION OF DAMAGED PIPELINE. REPAIRS WERE COMPLETED WITH NO GAS IGNITION AND NO INJURIES. NO CUSTOMERS WERE OUT OF SERVICE. THIS INCIDENT BECAME REPORTABLE TO PHMSA WHEN ESTIMATES OF DAMAGE COST AND GAS LOST MET REPORTING CRITERIA. THIS INCIDENT WAS ALSO REPORTED TO THE CALIFORNIA PUBLIC UTILITIES COMMISSION.
2025-03-31 10:13 | NO | NO | NO | 20110055 | 15234 | 2011-03-28 13:34 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-03-09 14:33 |  |  | 2011 | 748 MANIDA STREET | NEW YORK | BRONX | NY | 10474-5808 | 40.8157 | -73.8884 | [9 empty] | 2011-03-09 18:27 | 969651 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 40 | 2011-03-09 14:33 |  |  |  | 2011-03-09 14:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | INSIDE-- BUIDING FIRE | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | BUILDING FIRE | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 700 | 906.5071283095723 | 0 | 0 |  |  | 0 | 0 |  | 0 | 700 | 375.4480651731159 | 906.5071283095723 | 0 | 0 | 3 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THIS WAS A FIRE-FIRST EVENT. GAS NOT INVOLVED PER FDNY FIRE MARSHAL'S INVESTIGATION. | [154 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ***THIS REPORT IS FOR RECORD PURPOSES ONLY. FINAL INVESTIGATION DETERMINED THIS DOES NOT MEET DOT REPORTING CRITERIA*** ON WEDNESDAY MARCH 9, 2011 AT 1433 HRS GAS EMERGENCY RESPONSE GROUP (ERG) VITALE REPORTED TO THE GAS EMERGENCY RESPONSE CENTER (GERC) A 3 ALARM FIRE AT #748 MANIDA ST. IN THE BRONX. GAS DISTRIBUTION SERVICES (GDS) AND SUPERVISION WERE DISPATCHED AND REPORTED THE NEW YORK CITY FIRE DEPARTMENT (FDNY) WAS ON LOCATION. GDS REPORTED SHUTTING THE CURB VALVE TO #754 MANIDA ST. AT 1522 HRS, BUT WERE UNABLE TO VERIFY SHUTDOWN. THE FIRE ORIGINATED IN #754 MANIDA ST., WHICH IS A 40 FAMILY APARTMENT HOUSE SUPPLIED BY A 3" LOW PRESSURE STEEL SERVICE. THE FIRE SPREAD TO BUILDINGS #750 AND #748 MANIDA ST., AND GDS WAS UNABLE TO LOCATE THE CURB VALVES FOR THESE BUILDINGS DUE TO FDNY ACTIVITY. GAS CONSTRUCTION-EMERGENCY RESPONSE FORCE (ERF) RESPONDED TO LOCATION AND ONCE FDNY GRANTED ACCESS TO THE AREA, ERF CUT AND CAPPED THE SERVICES TO #750 & #754 MANIDA ST. THE SERVICE SUPPLYING #748 MANIDA ST WAS TURNED OFF AT THE SERVICE VALVE BY GDS AND WAS VERIFIED HOLDING. AN INVESTIGATION INTO THE CAUSE OF THE FIRE, WHICH MEDIA ATTRIBUTED AS POSSIBLY GAS-RELATED, WAS CONDUCTED BY FDNY FIRE MARSHAL BILL LAW. THE FIRE WAS DETERMINED NOT TO BE GAS RELATED. CIG, PSC, DOT WERE NOTIFIED BASED UPON INITIAL MEDIA REPORTS. ****THIS REPORT IS FOR RECORD PURPOSES ONLY. OFFICIAL FDNY INVESTIGATION DETERMINED FIRE WAS NOT GAS RELATED****
2025-03-31 10:13 | YES | NO | NO | 20110056 | 15226 | 2011-03-28 16:22 | ORIGINAL FINAL | 1088 | BALTIMORE GAS & ELECTRIC CO | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2011-02-28 12:48 |  |  | 2011 | 10567 OLD-ELLICOTT CIR | ELLICOTT CITY | HOWARD COUNTY | MD | 21042-2277 | 39.2836 | -76.8782 | [9 empty] | 2011-02-28 15:35 | 968757 |  | NATURAL GAS |  | 1.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 7 | 2011-02-28 13:25 |  |  |  | 2011-02-28 14:06 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2010 | [8 empty] | CAST/WROUGHT IRON | [10 empty] | OTHER | [8 empty] | ABOVE GROUND METER INSTALLATION WAS COMPROMISED DUE TO THE FIRE WHICH MELTED AND CAUSED THE RELEASE OF NATURAL GAS | CLASS 4 LOCATION | 0 | 0 | 100 | 129.5010183299389 | 5000 | 6475.050916496945 | 1600000 | 2072016.2932790224 | THE VALUE OF THE THREE HOUSES, CONTENTS OF ALL THREE HOUSES, TWO VEHICLES. |  | 14 | 10.6181172291296625222024866785079928952 |  | 0 | 1605114 | 860912.2358220613306360568383658969804618 | 2078631.46333107841356252220248667850799 | 0 | 0 | 3 |  |  |  |  | 93 | 93 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MICHAEL DENNIS BOWLING | GAS SERVICE SUPERVISOR | michael.bowling@bge.com | 410-470-7104 | 410-470-7103 |  |  |  | WILLIAM H. BROWN JR | MANAGER GAS SERVICE | 410-470-7105 | william.h.brown@bge.com | ACCORDING TO HOWARD COUNTY FIRE DEPARTMENT, THE POINT OF FIRE ORIGINATED ON THE ENTRANCE LEVEL OF THE HOUSE IN THE BASEMENT. THE HEAT AND/OR FIRE IMPINGED ON THE BODY OF THE REGULATOR CAUSING IT TO MELT ALLOWING GAS TO ESCAPE THAT CAUGHT FIRE. THE FIRE DEPARTMENT KEPT A SPRAY OF WATER TO KEEP THE FIRE UNDER CONTROL UNTIL WE OPERATED THE MAINLINE VALVE TO EXTINGUISH THE FIRE. THE DAMAGE TO THE REGULATOR THAT ALLOWED GAS TO ESCAPE WAS SUBSEQUENT TO THE FIRE DAMAGE IT SUSTAINED.
2025-03-31 10:13 | NO | NO | NO | 20110057 | 15599 | 2011-03-29 13:48 | SUPPLEMENTAL FINAL | 4060 | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2011-02-27 15:20 |  |  | 2011 | 2820 EAST 90TH STREET | CLEVELAND | CUYAHOGA | OH | 44101-3304 | 41.4822 | -81.6261 | [9 empty] | 2011-02-27 19:46 | 968681 |  | NATURAL GAS |  | 902 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2011-02-27 15:30 |  |  |  | 2011-02-27 15:50 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 18 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1996 | [5 empty] | 2 | ASTMD2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | OTHER | [8 empty] | DRESSER 711 END CAP BLEW OFF | CLASS 3 LOCATION | 75000 | 97125.763747454175 | 1000 | 1295.010183299389 | 5000 | 6475.050916496945 | 0 | 0 |  |  | 4970 | 3769.431616341030195381882770870337477798 |  | 0 | 85970 | 46931.6496221507343001776198934280639432 | 108665.2564635915391953818827708703374778 | 1 | 1 | 0 |  |  |  |  | 81 | 81 | 95 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | AARON MCCOY | TECHNICAL SPECIALIST | aaron.m.mccoy@dom.com | 330-458-9186 | 330-478-3760 |  |  |  | AARON MCCOY | TECHNICAL SPECIALIST | 330-458-9186 | aaron.m.mccoy@dom.com | INITIAL NRC REPORT WAS FOR 2800 EAST 90TH STREET, CLEVELAND, OH. ACTUAL ADDRESS WAS 2820 EAST 90TH STREET, CLEVELAND, OH. ON FEBRUARY 26, 2011 DOMINION RECEIVED A CALL FOR BLOWING GAS AT 2800 EAST 90TH STREET, CLEVELAND, OH. UPON ARRIVAL PERSONNEL DISCOVERED THAT A THIRD PARTY PERFORMING DEMOLITION OF A STRUCTURE LOCATED AT 2820 EAST 90TH STREET, CLEVELAND, OH HAD CAUSED DAMAGE TO AN ABOVE-GROUND INDUSTRIAL SERVICE REGULATOR SET. DOMINION PERSONNEL EXCAVATED THE 2" IPS PLASTIC SERVICE, PERFORMED SQUEEZE-OFF AND INSTALLED A DRESSER 711 END CAP TO STOP THE FLOW OF GAS. AT APPROXIMATELY 3:30 P.M. ON FEBRUARY 27, 2011 DOMINION RECEIVED A CALL FROM THE CLEVELAND FIRE DEPARTMENT FOR BLOWING GAS AT 2800 EAST 90TH STREET, CLEVELAND, OH. UPON ARRIVAL DOMINION PERSONNEL DISCOVERED A STRUCTURE FIRE AT 2820 EAST 90TH STREET, CLEVELAND, OH BEING FUELED BY NATURAL GAS AT THE REPAIR SITE FROM THE PRIOR DAY. AT 5:51 P.M. DOMINION PERSONNEL SHUT A MAINLINE VALVE LOCATED AT THE INTERSECTION OF EAST 90TH AND HOLTON AVE TO STOP THE FLOW OF GAS. ON FEBRUARY 28, 2011 DOMINION ALONG WITH INVESTIGATORS FROM THE PUBLIC UTILITIES COMMISSION OF OHIO RETRIEVED A DRESSER 711 END CAP AND APPROXIMATELY 3 FEET OF THE 2" IPS SERVICE LINE FOR FURTHER INVESTIGATION. ON MARCH 18, 2011 FURTHER INVESTIGATION INDICATED THAT COMPONENTS OF THE DRESSER 711 END CAP TO BE IMPROPERLY ASSEMBLED, GRIP RINGS INSTALLED IN THE PIPE END IMPROPERLY AND THE INCORRECT GASKET INSTALLED IN THE END CAP SIDE OF THE COUPLING. DEO ENGAGED A THIRD PART TESTING AGENCY WHO CONDUCTED A TEST USING AN IMPROPERLY ASSEMBLED DRESSER 711 END CAP INSTALLED IN AN IDENTICAL MANNER AS THE END CAP WAS INSTALLED AT THE E. 90TH STREET INCIDENT LOCATION. THE IMPROPERLY ASSEMBLED DRESSER 711 END CAP HELD OPERATING PRESSURE FOR A DURATION OF 24 HOURS. THE TEST ENDED WITHOUT LEAK OR ANY FORM OF FAILURE; THE COUPLING DID NOT MOVE RELATIVE TO THE PIPE. THIS TEST CONCLUSIVELY DEMONSTRATED THAT THE DRESSER 711 END CAP REMAINED INTACT AND DID NOT FAIL UNDER OPERATING PRESSURE AND THEREFORE DEO CANNOT, WITH CERTAINTY, DEEM THE IMPROPERLY ASSEMBLED END CAP AS THE CAUSE OF THE INCIDENT. AS AN ADDITIONAL MATTER, THERE WAS A SEPARATE CRIMINAL INVESTIGATION OF THE PROPERTY OWNER ALREADY UNDERWAY AT THE TIME OF THE GAS RELATED INCIDENT. DOCUMENTS CRITICAL TO THIS ONGOING INVESTIGATION WERE DESTROYED IN THE FIRE. CURRENTLY, THE CLEVELAND POLICE DEPARTMENT IS INVESTIGATING THIS INCIDENT AS A POTENTIAL ARSON CASE. SUPPLEMENTAL REPORTS CAN BE FILED IF ANY NEW INFORMATION SURFACES AS A RESULT OF THE CLEVELAND PD'S INVESTIGATION.
2025-03-31 10:13 | NO | YES | NO | 20110058 | 15228 | 2011-04-01 16:45 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 200 CIVIC CENTER DR, P.O. BOX 117 | COLUMBUS | OH | 43215 | 2011-02-22 15:22 |  |  | 2011 | DETROIT RD. | AVON | LORAIN | OH | 44011 | 41.4301 | -82.0679 | [9 empty] | 2011-03-02 17:00 | 968994 |  | NATURAL GAS |  | 368.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-02-22 15:22 |  |  |  | 2011-02-22 15:50 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 90 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1966 | [5 empty] | 10 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 28100 | 36389.7861507128309 | 58816 | 76167.318940936863424 | 4000 | 5180.040733197556 | RAILWAY CLOSURE |  | 2010 | 1524.458259325044404973357015985790408526 |  | 0 | 92926 | 50173.4078485564067687317939609236234458 | 119261.6040841722947289733570159857904085 | 0 | 0 | 1 |  |  |  |  | 41 | 41 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [5 empty] | YES | [6 empty] | CONTRACTOR | DIRECTIONAL DRILLING | SEWER (SANITARY/STORM) | YES | 10410089800 | OHIO UTILITY PROTECTION SERVICE |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ROB R. SMITH | OPERATIONS COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB R. SMITH | OPERATIONS COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | COLUMBIA CREWS RESPONDED TO FIND A THIRD PARTY DIRECTIONAL BORE CONTRACTOR INSTALLING A 42" SANITARY SEWER HAD SPOTTED COLUMBIA'S 10" TREATED STEEL GAS MAIN LINE AT ONE LOCATION. THE THIRD PARTY EXCAVATOR ATTEMPTED TO DIRECTIONAL BORE PERPENDICULAR UNDER OUR 10" FACILITY AT A SEPARATE LOCATION AND FAILED TO EXPOSE OUR PROPERLY LOCATED FACILITY AT THE POINT IT WAS STRUCK. COLUMBIA CREWS SET A PERIMETER, MONITORED FOR GAS MIGRATION AND MAINTAINED PUBLIC SAFETY BY COORDINATING WITH THE LOCAL AUTHORITIES. COLUMBIA IMMEDIATELY BROUGHT IN A PIPELINE CONTRACTOR AND BYPASSED AROUND THE DAMAGED SECTION OF MAIN LINE AND MADE PERMANENT REPAIRS. COLUMBIA WORKED ON THE LEAK CONTINUOUS UNTIL PERMANENT REPAIRS WERE COMPLETED. THE TRIGGERING EVENT THAT MADE THIS DAMAGE REPORTABLE WAS THAT THE COSTS ASSOCIATED WITH THE DAMAGE EXCEEDED THE $50,000 DOLLAR REPORTING THRESHOLD.
2025-03-31 10:13 | NO | NO | NO | 20110059 | 15308 | 2011-04-08 12:33 | SUPPLEMENTAL FINAL | 13400 | NEW ULM PUBLIC UTILITIES COMMISSION | 310 FIRST NORTH STREET | NEW ULM | MN | 56073 | 2011-03-26 15:45 |  |  | 2011 | BROADWAY ST AND COTTONWOOD ST | NEW ULM | BROWN | MN | 56073 | 44.2901 | -94.4398 | [9 empty] | 2011-03-26 19:00 | 971248 |  | NATURAL GAS |  | 90 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2011-03-26 15:45 |  |  |  | 2011-03-26 15:53 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | UNDER THE RIVER | 96 |  | YES | [6 empty] | YES | UNCASED, BORED/DRILLED | COTTONWOOD RIVER | 18 |  | MUNICIPALLY OWNED |  | MAIN |  | 2010 | [5 empty] | 4 | ASTM D2513 | US POLY | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | LEAK |  |  | OTHER | ABRASION | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 35000 | 45325.356415478615 | 3500 | 4532.5356415478615 | 0 | 0 |  |  | 530 | 401.97158081705150976909413854351687389 |  | 0 | 39030 | 21021.4908314130263650088809946714031972 | 50259.8636378435280097690941385435168739 | 0 | 0 | 25 |  |  |  |  | 18 | 18 | 80 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | FLOODING CAUSED BY SNOWMELT AND HEAVY RAINS | [213 empty] | GARY PORTNER | GAS SUPERVISOR | gary.portner@ci.new-ulm.mn.us | 507-359-8298 | 507-354-7318 |  |  |  | GARY PORTNER | GAS SUPERVISOR | 507-359-8289 | gary.portner@ci.new-ulm.mn.us | ON 3-26-2011 AT 15:45 RICK KONOKOWITZ WAS DISPATCHED TO COTTONWOOD ST. BRIDGE FOR A GAS SMELL. HE ARRIVED AT 15:53 TO FIND WHAT APPEARED A GAS LEAKING FROM UNDER THE RIVER. HE SECURED THE AREA AND CALLED HIS SUPERVISOR AT 16:10. PAUL MACHO ARRIVED AT 16:20 AND AT 16:30 DISPATCHED NEW ULM FIRE DEPT TO HELP SECURE THE AREA. ADDITIONAL STAFF WAS CALLED IN TO ASSIST. AT 16:40 STAFF BEGAN TO SHUT DOWN CUSTOMERS AND THE SYSTEM. RICK AND THE FIRE DEPT. CONTINUED TO MONITOR THE AREA WITH CGI'S FOR MIGRATING GAS. AT 17:20, PAUL MACHO NOTIFED THE STATE DUTY OFFICER OF THE SITUATION, CASE#117947 WAS ASSIGNED. AT 17:40, TOOD STANSBURY FROM OPS CALLED. PAUL MACHO UPDATED TODD ABOUT THE SITUATION. ALL CUSTOMERS AND REGULATING STATION WERE OFF AT 17:45 GOPHER ONE CALL WAS NOTIFED FOR AN EMERGENCY LOCATE NEEDED TO EXPOSE THE MAIN ON BOTH SIDES OF THE COTTONWOOD RIVER TO SUPPLY TEMPORARY SERVICE TO THE 25 CUSTOMERS AFFECTED BY THE SHUT DOWN. THE FEDERAL DUTY OFFICER WAS NOTIFIED AT 19:00 AND CASE #971248 WAS ASSIGNED TO THIS INCIDENT.TEMPORARY GAS LINE, 1" PE, WAS USED TO REPLACE THE DAMAGED 4" MAIN. THE TEMPORARY GAS LINE WAS SUPPORTED BY THE BRIDGE AND SOME TREES. STAFF KEPT CUSTOMERS UPDATED ON THE PROGRESS OF THE RESTORATION. THE FIRE DEPT. WAS RELEASED AFTER THE TEMPORARY LINE WAS SECURED AT 20:35. TEMPORARY GAS SERVICE WAS RESTORED TO COTTONWOOD STREET SECTION AT 23:45. THE TEMPORARY GAS LINE WILL BE MONITORED DAILY UNTIL A NEW 4" GAS MAIN CAN BE INSTALLED AFTER FLOOD WATERS DROP. SUPPLEMENTAL REPORT COMPLETED 8/23/2011 TO ADD INFORMATION REGARDING PIPE THAT WAS DAMAGED, WATER DEPTH, AND CORRECT TYPOGRAPHICAL ERRORS.
2025-03-31 10:13 | NO | NO | NO | 20110060 | 15236 | 2011-04-11 12:36 | ORIGINAL | 13420 | NEW YORK STATE ELECTRIC & GAS CORP | 180 SOUTH CLINTON AVENUE | ROCHESTER | NY | 14607 | 2011-03-11 14:29 |  |  | 2011 | 31 MILFORD ST | BINGHAMTON | BROOME | NY | 13902 | 42.0986 | -75.9183 | [9 empty] | 2011-03-11 15:09 | 969844 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 6 | 2011-03-11 14:29 |  |  |  | 2011-03-11 14:29 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | OTHER | INTERNAL HOUSE PIPING | OTHER | CUSTOMER OWNED PIPING | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | DRIP LEG FOR APPLIANCE IN 3RD FLOOR APARTMENT FOUND DISCONNECTED". | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 2000 | 2590.020366598778 | 1000 | 1295.010183299389 | ADMINISTRATIVE REPORTING |  | 0 | 0 |  | 0 | 3000 | 1609.063136456211 | 3885.030549898167 | 0 | 0 | 3 |  |  |  |  | 0.4 | 0.4 | 0.43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | OTHER COMPRESSION TYPE FITTING | APPLIANCE DRIP LEG | OTHER | APPLIANCE DRIP LEG |  |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | DOMESTIC APPLIANCE DRIP LEG | [7 empty] | NO | [86 empty] | MICHAEL D. EASTMAN | VICE PRESIDENT OF GAS OPERATIONS | mdeastman@nyseg.com | 585-724-8253 |  |  |  |  | MICHAEL D. EASTMAN | VICE PRESIDENT OF GAS OPERATIONS | 585-724-8253 | mdeastman@nyseg.com | THE DRIP LEG FOR DOMESTIC APPLIANCE ON 3RD FLOOR NON-LIVING AREA WAS FOUND DISCONNECTED AND LYING ON THE FLOOR. WHILE THIS EXPLOSION WAS NOT A RESULT OF ANYTHING ON NYSEG'S SYSTEM, THIS REPORT IS BEING FILED AS INFORMATIONAL AND IN THE INTERESTS OF CAUTION.
2025-03-31 10:13 | NO | NO | NO | 20110062 | 15317 | 2011-04-19 18:32 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 400 EAGLE STATION LANE | CARSON CITY | NV | 897018401 | 2011-03-02 12:41 |  |  | 2011 | 10397 ROYAL CREST | TRUCKEE | NEVADA | CA | 96161-1187 | 39.3487 | -120.1077 | [9 empty] | 2011-03-23 15:45 | 970970 |  | NATURAL GAS |  | 158 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 10 | 2011-03-02 12:41 |  |  |  | 2011-03-02 13:25 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1996 | [5 empty] | 0.5 | ASTM D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.091 |  | 3408 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 900 | 1165.5091649694501 | 1800 | 2331.0183299389002 | 67929 | 87968.746741344195381 | 17972 | 23273.923014256619108 | CUSTOMER REIMBURSEMENT DURING EVACUATION. |  | 1275 | 967.007104795737122557726465364120781528 |  | 0 | 89876 | 48416.0725059960039707477797513321492007 | 115706.2043553049019115577264653641207815 | 0 | 0 | 6 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | NUT FOLLOWER |  | SERVICE OR MAIN TEE |  | CONTINENTAL |  | OTHER | MATERIALS JOINED: 1ST PLASTIC, 2ND PLASTIC | [22 empty] | YES | N/A | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | YES | 1996 | 90 | [84 empty] | MATTHEW HELMERS | SUPERVISOR ENGINEERING | matthew.helmers@swgas.com | 775-887-2871 | 775-884-3012 |  |  |  | BYRON ELKINS | DIRECTOR DISTRICT OPERERATIONS NORTHERN NEVADA | 775-887-2744 | byron.elkins@swgas.com | ON WEDNESDAY, MARCH 2, 2011, A HOMEOWNER IN TRUCKEE, CA CONTACTED SOUTHWEST GAS CORPORATION DUE TO NO PRESSURE AT HIS HEATER AND A NATURAL GAS ODOR OUTSIDE. SOUTHWEST GAS PERSONNEL RESPONDED TO THE SITE AND DISCOVERED 97% GAS OVER THE SERVICE LINE. THE SERVICE TECHNICIAN REQUESTED ASSISTANCE FROM THE CONSTRUCTION DEPARTMENT AND ASKED THAT THE FIRE DEPARTMENT BE NOTIFIED. TEN HOMES WERE INITIALLY EVACUATED WITH THE HELP OF THE FIRE DEPARTMENT. A LEAK WAS REPAIRED BY REPLACING THE SERVICE TAP TEE. THE PROBABLE CAUSE OF THE LEAK WAS A CONSTRUCTION DEFECT. THE RESIDENCES FOR SIX OF THE HOMES WERE ALLOWED TO RETURN TO THEIR RESIDENCES THAT EVENING ONCE THE HAZARD WAS ELIMINATED AND GAS READS AT THE BASE OF THE STRUCTURES WERE NON-HAZARDOUS. DUE TO RESIDUAL GAS READS AT THE FOUNDATION OF THE STRUCTURES OF THE REMAINING FOUR HOMES, THEIR EVACUATION LASTED FOR 12 DAYS UNTIL, MARCH 14, 2011. THE CUSTOMERS WERE ALLOWED TO RETURN TO THEIR RESIDENCES ONCE THE HAZARD WAS ELIMINATED AND GAS READS AT THE BASE OF THE STRUCTURES WERE NON-HAZARDOUS. AERATION OF RESIDUAL GAS AWAY FROM THE STRUCTURES CONTINUED UNTIL MARCH 25, 2011 WHEN GAS READS WERE ELIMINATED. ON THURSDAY, MARCH 21, 2011, SOUTHWEST GAS BECAME AWARE OF LOCAL MEDIA ATTENTION DUE TO THE EXTENDED EVACUATION AND NOTIFIED THE CALIFORNIA PUBLIC UTILITIES COMMISSION (CPUC) BASED ON THEIR REPORTING STANDARDS. ON MARCH 23, 2011, IT WAS DETERMINED BY SOUTHWEST GAS THAT THE EXTENDED AERATION AND CUSTOMER REIMBURSEMENT COSTS WOULD ACCUMULATE ABOVE THE $50,000 REPORTABLE THRESHOLD. THE INCIDENT WAS THEN REPORTED TO THE NATIONAL RESPONSE CENTER.
2025-03-31 10:13 | NO | NO | NO | 20110063 | 15240 | 2011-04-20 15:51 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-03-26 19:10 |  |  | 2011 | 306 E 116 ST | NEW YORK | NEW YORK | NY | 10029-1530 | 40.7965 | -73.9374 | [9 empty] | 2011-03-26 19:30 | 971247 |  | NATURAL GAS |  | 9.24 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2011-03-26 19:10 |  |  |  | 2011-03-26 19:10 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | METER-ALUMINUM | [9 empty] | OTHER | [8 empty] | METER MELTED DUE TO FIRE | CLASS 4 LOCATION | 0 | 0 | 50 | 64.75050916496945 | 200 | 259.0020366598778 | 0 | 0 |  |  | 100 | 75.84369449378330373001776198934280639432 |  | 0 | 350 | 204.248452608769507548845470692717584369 | 399.596240318630553730017761989342806394 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | FIRE AT RANGE DAMAGED METER RESULTING IN SECONDARY IGNITION PER FDNY INVESTIGATION. | [154 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER--GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON MARCH 26, 2011 THE GAS EMERGENCY RESPONSE CENTER RECEIVED A REPORT FROM THE FIRE DEPARTMENT OF NEW YORK (FDNY) OF A FIRE AT A STOVE AT 306 E 116 ST. GAS DISTRIBUTION SERVICES (GDS) CREW AND SUPERVISOR WERE DISPATCHED AND UPON ARRIVAL IT WAS FOUND THE FIRE IN APARTMENT (1A) HAD BEEN EXTINGUISHED AND THE APARTMENT SUSTAINED EXTENSIVE DAMAGE. THE GDS' CREWS INVESTIGATION FOUND THE FDNY HAD TURNED OFF THE GAS METER LOCATED IN THE APARTMENT WHICH WAS DAMAGED BY THE FIRE. THE FDNY REPORTED THE CAUSE OF THE FIRE WAS AN OVERLOADED ELECTRICAL JUNCTION BOX NEAR THE REFRIGERATOR. A GDS SUPERVISOR REPORTED THAT THERE WAS A 3" HOLE IN THE GAS METER AND SECONDARY IGNITION OCCURRED AS A RESULT OF THE ELECTRICAL FIRE DAMAGE TO THE GAS METER. THE METER WAS REMOVED AND THE METER BAR PLUGGED. THERE WERE NO INJURIES OR EVACUATIONS OF OTHER APARTMENTS AS A RESULT OF THIS FIRE. THE DOT AND PSC WERE NOTIFIED.
2025-03-31 10:13 | NO | NO | NO | 20110064 | 15241 | 2011-04-21 12:15 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2011-04-01 11:40 |  |  | 2011 | 9816 HOUSTON AVENUE | LAMONT | KERN | CA | 93241 | 35.2653 | -118.9085 | [9 empty] | 2011-04-01 13:45 | 971757 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 12 | 2011-04-01 11:40 |  |  |  | 2011-04-01 12:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | ILLEGALLY INSTALLED PIPING AND FITTIINGS | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | LEAK |  |  | OTHER | VARIOUS PIPING AND FITTINGS | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 1000 | 1295.010183299389 | 250 | 323.75254582484725 | 0 | 0 |  |  | 50 | 37.92184724689165186500888099467140319716 |  | 0 | 1300 | 705.522902475463878774422735346358792185 | 1656.684576371127901865008880994671403197 | 0 | 0 | 3 |  |  |  |  | 45 | 45 | 52 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | ILLEGAL INSTALLATION OF PIPING AND FITTINGS BY INDIVIDUAL(S) OTHER THAN OPERATOR | [154 empty] | W. JEFF KOSKIIE | PIPELINE SAFETY ADVISOR | wkoskie@semprautilities.com | 213 305-8660 | 213 244-8155 |  |  |  | W. JEFF KOSKIE | PIPELINE SAFETY ADVISOR | 213 305-8660 | wkoskie@semprautilities.com | ON APRIL 1, 2011, AT APPROXIMATELY 8:40 AM, AN FIRE OCCURRED AT THE ADDRESS OF 9816 HOUSTON AVENUE IN LAMONT, CA. THE FIRE DESTROYED THIS HOME AND DAMAGED ADJACENT HOME. NO INJURIES OCCURRED, AND REPAIRS WERE COMPLETED WITH SERVICE DISCONTINUED UNTIL PROPERTY REPAIRS ARE COMPLETED. INVESTIGATION DETERMINED THAT METER SET ASSEMBLY HAD BEEN MOVED BY INDIVIDUAL(S). THIS RELOCATION WAS ILLEGAL AND THE OPERATOR WAS NOT AWARE OF CONDITION UNTIL FIRE OCCURRED. PIPING AND FITTINGS INSTALLED BY OTHERS WERE LEAKING AND ULTIMATELY IGNITED. ALL ILLEGALLY INSTALLED PIPING AND FITTINGS HAVE BEEN REMOVED FROM THE SOUTHERN CALIFORNIA GAS PIPELINE SYSTEM.
2025-03-31 10:13 | NO | NO | NO | 20110065 | 15323 | 2011-04-22 08:20 | SUPPLEMENTAL FINAL | 31636 | NORTHERN STATES POWER CO OF MINNESOTA | 414 NICOLLET MALL | MINNEAPOLIS | MN | 55402 | 2011-03-24 10:36 |  |  | 2011 | UNIVERSITY AVE AND FRY | SAINT PAUL | RAMSEY | MN | 55104-3820 | 44.9558 | -93.1696 | [9 empty] | 2011-03-24 15:24 | 974055 |  | NATURAL GAS |  | 1681 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2011-03-24 10:36 |  |  |  | 2011-03-24 10:36 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1986 | [5 empty] | 12 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 7343 | 9509.259775967413427 | 0 | 0 | 0 |  | 13500 | 10238.8987566607460035523978685612788632 |  | 0 | 20843 | 13410.0310207174955600941385435168738899 | 19748.1585326281594305523978685612788632 | 51 | 0 | 709 |  |  |  |  | 60 | 60 | 66 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 8 | 0 | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | JOHN BROWERS | GAS ENGINEER | john.e.browers@xcelenergy.com | 651-229-5515 | 651-229-2376 |  |  |  | WILLIAM KAPHING | VP CONTROL CENTER | 651-229-2435 | william.l.kaphing@xcelenergy.com | PART A #16 - TOTAL NUMBER OF PEOPLE WAS NOT TRACKED SINCE SEVERAL COMMERCIAL OR PUBLIC BUILDINGS WERE EVACUATED. 12 BUILDINGS WERE EVACUATED. A 12 INCH END CAP BLEW OFF THE END OF A 60 PSIG STEEL GAS MAIN WHILE RESETTING THE SEALING ELEMENT DURING A STOPPLE PROCEDURE. A TEMPORARY COMPRESSION END CAP WAS INSTALLED ON THE END OF THE MAIN. AS THE TAPPER WORKED TO RESET THE STOPPER, GAS IMMEDIATELY BUILT UP ON THE TEMPORARY COMPRESSION CAP AND THE PRESSURE CAUSED THE CAP TO BLOW OFF THE MAIN. WHEN THE MAIN WAS BLOWING THE TAPPER MOMENTARILY WAS ABLE TO RE-STOP THE FLOW OF GAS BY RESETTING THE STOPPER BUT THEN THE SEALING ELEMENT ON THE STOPPER PARTIALLY ROLLED CAUSING A VOID OF APPROXIMATELY 12 SQUARE INCHES AROUND THE SEALING ELEMENT, ALLOWING GAS TO ESCAPE.
2025-03-31 10:13 | NO | YES | NO | 20110066 | 15243 | 2011-04-29 15:51 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 200 CIVIC CENTER DR, P.O. BOX 117 | COLUMBUS | OH | 43215 | 2011-04-01 08:30 |  |  | 2011 | FAWCETT ST & LAUREL LN | EAST LIVIERPOOL | COLUMBIANA | OH | 43920 | 40.3722 | -80.3442 | [9 empty] | 2011-04-01 10:26 | 971706 |  | NATURAL GAS |  | 0.34 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2011-04-01 08:30 |  |  |  | 2011-04-01 08:30 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | 8" BRANCH CONNECTION PARTIALLY TORN FROM 16" MAIN CAUSING 2"X 5" HOLE | CLASS 3 LOCATION | 0 | 0 | 75000 | 97125.763747454175 | 19286 | 24975.566395112016254 | 0 | 0 |  |  | 1894 | 1436.479573712255772646536412078152753108 |  | 0 | 96180 | 51899.536670006811559975133214920071048 | 123537.8097162784470266465364120781527531 | 1 | 0 | 10 |  |  |  |  | 0.5 | 0.5 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | OPERATOR EMPLOYEE WORKING NEARBY RESPONDED TO THE SITE-SEE NARRATIVE IN PART H |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ROB SMITH | OPERATIONS COMPLIANCE MANAGER | rrsmith@nisource.com | 6148182110 | 6148182151 |  |  |  | ROB SMITH | OPERATIONS COMPLIANCE MANAGER | 6148182110 | rrsmith@nisource.com | A COLUMBIA GAS EMPLOYEE WORKING IN THE AREA HEARD A CRASH AND THEN SMELLED NATURAL GAS. THE EMPLOYEE INVESTIGATED AND FOUND A REGULATOR STATION DAMAGED BY A GARBAGE TRUCK WHICH HAD LOST CONTROL STRIKING THE CONCRETE BLOCK BUILDING AND DAMAGING PIPELINE FACILITIES INSIDE. COLUMBIA CREWS AND CONTRACTORS SHUT DOWN THE REGULATOR STATION USING AN INLINE VALVE AND PIPELINE STOPPING EQUIPMENT. DAMAGE TO THE PIPELINE FACILITIES INSIDE THE BUILDING INCLUDED AN ABOVE GROUND 8" REGULATOR SETTING PIPE WHICH WAS STRUCK AND TORN FROM THE TOP OF A 16" LOW PRESSURE MAIN BELOW GROUND. THE COST TO REPLACE THE REGULATOR STATION PIPING AND BUILDING MET THE THRESHOLD FOR REPORTABILITY.
2025-03-31 10:13 | NO | YES | YES | 20110067 | 15486 | 2011-05-05 18:50 | SUPPLEMENTAL FINAL | 4060 | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2011-04-05 04:30 |  |  | 2011 | 885 HOMEWOOD DRIVE | PAINESVILLE | LAKE | OH | 44077-3719 | 41.7107 | -81.2337 | [9 empty] | 2011-04-05 09:45 | 972023 |  | NATURAL GAS |  |  |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2011-04-05 04:52 |  |  |  | 2011-04-05 05:39 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | FRACTURE AT 90 DEGREE ELBOW | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 5000 | 6475.050916496945 | 150000 | 194251.52749490835 | STRUCTURE AT 885 HOMEWOOD DRIVE |  | 0 | 0 |  | 0 | 155000 | 83134.928716904235 | 200726.578411405295 | 0 | 0 | 1 |  |  |  |  | 0.5 | 0.5 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 108703085 | OHIO UTILITY PROTECTION SERVICES |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | STEVEN W. BUCK | TECHNICAL CONSULTANT | steven.w.buck@dom.com | 330-401-8033 | 866-521-4877 |  |  |  | STEVEN W. BUCK | TECHNICAL CONSULTANT | 330-401-8033 | steven.w.buck@dom.com | AT APPROXIMATELY 4:30 A.M. ON APRIL 5, 2011, A SINGLE FAMILY STRUCTURE LOCATED AT 885 HOMEWOOD DRIVE, PAINESVILLE, OH WAS INVOLVED IN A FIRE/EXPLOSION. DOMINION RECEIVED NOTIFICATION FROM THE PAINESVILLE FIRE DEPARTMENT AT APPROXIMATELY 4:52 A.M. AND DISPATCHED CUSTOMER SERVICE PERSONNEL. FIRST REPONDERS ARRIVED AT THE SCENE AT 5:39 A.M. AND WERE UNABLE TO LOCATE THE CURB STOP VALVE. DISPATCH WAS NOTIFIED AND CONTACTED A CONSTRUCTION CREW WHICH ARRIVED AT 6:45 A.M. AND SHUT OFF THE GAS AT 7:00 A.M. FURTHER INVESTIGATION REVEALED THAT FARINACCI EXCAVATING INC., WORKING FOR H JACKS PLUMBING AND HEATING, A CONTRACTOR FOR THE HOMEOWNER, HAD CAUSED DAMAGE TO THE INTERIOR STEEL SERVICE LINE DURING CONSTRUCTION ACTIVITIES OUTSIDE THE STRUCTURE ON APRIL 1, 2011. H JACKS PLUMBING AND HEATING NOTIFIED THE ONE-CALL, THE MAIN LINE WAS LOCATED AND THE SERVICE WAS MARKED AS UNABLE TO BE TONED PRIOR TO STARTING EXCAVATION. SERVICE WAS EXPOSED DURING EXCAVATION , DAMAGE OCCURRRED DURING BACKFILLING ACTIVITIES.
2025-03-31 10:13 | NO | YES | YES | 20110068 | 15247 | 2011-05-06 15:23 | ORIGINAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2011-04-07 01:36 |  |  | 2011 | 1160 W. VIRGINIA AVE | DENVER | DENVER | CO | 80223-2076 | 39.7073 | -105.0007 | [9 empty] | 2011-04-07 10:05 | 972249 |  | NATURAL GAS |  | 25555 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 0 | 2011-04-07 08:38 |  |  |  | 2011-04-07 08:58 |  | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | CONCRETE PAD | 31 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1970 | [5 empty] | 0.5 | API 5L CLASS II | UNKNOWN | STEEL |  | OTHER | BUTT WELD | 0.109 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 500000 | 647505.0916496945 | 200 | 259.0020366598778 | 2000 | 2590.020366598778 | 0 | 0 |  |  | 120 | 91.01243339253996447602131438721136767318 |  | 0 | 502320 | 269441.3608722546237090586145648312611012 | 650445.1264863456957644760213143872113677 | 2 | 0 | 0 |  |  |  |  | 5 | 5 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | UNKNOWN/OTHER | NO |  |  |  | UNKNOWN/OTHER | NO | YES |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | ADRIENNE GRANDJEAN | SENIOR INVESTIGATOR | adrienne.grandjean@xcelenergy.com | 303-294-2815 | 303-294-2311 |  |  |  | JOHN KARTUS | MANAGER OF CLAIMS SERVICES - MANAGING INVESTIGATOR | 303-294-2665 | john.j.kartus@xcelenergy.com | THIRD PARTY EXCAVATION WAS BEING PERFORMED ON APRIL 2ND, APRIL 4TH, AND APRIL 5TH IN THE AREA OF THE GAS SERVICE DAMAGE AT 1172 W. VIRGINIA AVE. THE GAS SERVICE WAS PULLED CAUSING THE LINE TO SEPARATE FROM THE MECHANICAL COUPLING. THE EXPLOSION OCCURRED ON THE ADJACENT PROPERTY AT 1160 W. VIRGINIA AVE. THE STRUCTURE OF 1160 W. VIRGINIA AVE IS APPROXIMATELY 10 FEET EAST OF THE GAS SERVICE SERVING 1172 W. VIRGINIA AVE. THE FIRE DEPARTMENT'S ORIGINAL NOTIFICATION TO THE OPERATOR WAS THAT A STRUCTURE FIRE HAD OCCURRED AT 1160 W. VIRGINIA AVE WITH NO GAS INVOLVEMENT. THE OPERATOR PERFORMED A BAR HOLE LEAK SURVEY AND DETERMINED THAT THERE WAS GAS PRESENT UNDERGROUND, PROMPTING FURTHER INVESTIGATION AND ULTIMATELY LEADING TO THE DISCOVERY OF THE THIRD PARTY DAMAGE. AS CLARIFICATION FOR SECTION A13 OF THIS REPORT, THE SERVICES AT 1160 W. VIRGINIA AVE AND 1172 W. VIRGINIA AVE WERE PERMANENTLY CUT-OFF FROM THE MAIN AND WILL NOT BE REACTIVATED WITHOUT A NEW APPLICATION FOR SERVICE. AS CLARIFICATION FOR SECTION A17.B OF THIS REPORT, THE FIRST GAS RESPONDER ARRIVED AT 03:30 AM ON 4/7/11 BUT WAS TOLD THAT THE INCIDENT WAS NOT GAS RELATED. THE INVESTIGATION REVEALED THAT THE EXACT DATE AND TIME OF THE DAMAGE TO THE GAS SERVICE AT 1172 W. VIRGINIA AVE COULD NOT BE DETERMINED, BUT THE DAMAGE WAS RECENTLY CAUSED BY A THIRD PARTY.
2025-03-31 10:13 | NO | NO | NO | 20110070 | 15250 | 2011-05-13 14:05 | ORIGINAL FINAL | 2604 | COLUMBIA GAS OF VIRGINIA INC | 1809 COYOTE DRIVE | CHESTER | VA | 23836 | 2011-04-17 20:17 |  |  | 2011 | 14200 JOHN MARSHALL HIGHWAY | GAINESVILLE | PRINCE WILLIAM | VA | 20155 | 38.7992 | -77.6157 | [9 empty] | 2011-04-18 00:50 | 973247 |  | NATURAL GAS |  | 651.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-04-17 20:25 |  |  |  | 2011-04-17 21:03 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1967 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS | SEAMLESS | 0.125 | [6 empty] | OTHER | [8 empty] | PIPE CUT IN HALF WITH TRACK HOE | CLASS 2 LOCATION | 0 | 0 | 60219 | 77984.218228105906191 | 0 | 0 | 0 | 0 | NONE |  | 3564 | 2703.069271758436944937833037300177619893 |  | 0 | 63783 | 34799.2216737871219820408525754884547069 | 80687.2874998643431359378330373001776199 | 30 | 0 | 832 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 109701338 | MISS UTILITY |  | CONTRACT LOCATOR | YES | YES | 15 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | ANNETTE TUCKER | OPERATIONS | aedwards@nisource.com | 804-768-6473 | 804-768-5913 |  |  |  | TIMOTHY BEELER | OPERATIONS COMPLIANCE MANGER | 804-768-6404 | tbeele@nisource.com | ON SATURDAY 4-17-11 AT 20:25 COLUMBIA GAS OF VIRGINIA (CGV) RECEIVED A CALL FROM GENERAL EXCAVATING INC. (GEI) STATING THEY HAD DAMAGED A 4 INCH STEEL GAS MAIN AT 14200 JOHN MARSHALL HIGHWAY IN GAINESVILLE, VA. 20155 AT 20:17 HRS. CGV ARRIVED ON THE SCENE AT 21:03 HRS. TO FIND A 4 INCH STEEL MAIN SEVERED IN HALF BY A HITACHI 450 TRACK EXCAVATOR. GEI HAD BEEN EXCAVATING TO INSTALL A 23 INCH CONDUIT FOR A FUTURE WATERLINE. THE PRINCE WILLIAM COUNTY FIRE DEPARTMENT AND POLICE WERE ON THE SCENE. THE CRITICAL VALVE WAS TURNED OFF TO ISOLATE THE SECTION OF MAIN WHICH EFFECTED 862 CGV CUSTOMERS AT 22:38 HRS. GEI WAS EXCAVATING UNDER MISS UTILITY TICKET #A109701138. GEI HAD ALREADY SCHEDULED A ROAD CLOSURE WITH VDOT SO TRAFFIC FLOW WAS NOT INTERRUPTED. THE ROOT CAUSE INVESTIGATION INDICATED THAT CGV'S THIRD PARTY LOCATOR, UTILIQUEST FAILED TO MARK THE 4 INCH STEEL GAS MAIN AS INDICATED ON COMPANY FACILITY MAPS. CGV CREWS COMPLETED REPAIRS ON MONDAY 4-18-2011 AT 13:00 HRS. AND BEGAN THE PURGING PROCESS WITH CUSTOMER RELIGHTS TO FOLLOW.
2025-03-31 10:13 | NO | NO | NO | 20110071 | 15261 | 2011-05-17 09:20 | SUPPLEMENTAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDENCE BOULEVARD | VIRGINIA BEACH | VA | 23452 | 2011-04-18 10:00 |  |  | 2011 | 1441 OCEANA BLVD | VIRGINIA BEACH |  | VA | 23454 | 36.7941 | -75.9969 | [9 empty] | 2011-04-18 11:44 | 973285 |  | NATURAL GAS |  | 2909 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2011-04-18 10:14 |  |  |  | 2011-04-18 10:56 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1994 | [5 empty] | 4 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 6 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 24303 | 31472.632484725050867 | 0 | 0 | 12781 | 16551.525152749490809 | EXCAVATOR'S EQUIPMENT DAMAGE |  | 19827 | 15037.5293072824156305506216696269982238 |  | 0 | 56911 | 33800.7608107570269222095914742451154529 | 63061.6869447569573065506216696269982238 | 1 | 0 | 123 |  |  |  |  | 58 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EXCAVATION DAMAGE OCCURRED AT A TERMINAL LOCATION WITHIN THE GAS DISTRIBUTION SYSTEM THAT HAD NO TELEMETRY DOWNSTREAM OF THE DAMAGE. IT WAS ALSO A WARM DAY WITH NO GAS LOAD, SO THERE WAS AMPLE GAS PRESSURE IN THE MAIN. THEREFORE, THE DAMAGE WAS UNDETECTABLE BY GAS CONTROL. | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 109501824 | VIRGINIA UTILITY PROTECTION SERVICE (VUPS) |  | CONTRACT LOCATOR | YES | YES | 7 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | BILL ROBINSON | STAFF ENGINEER | brobinso@aglresources.com | 757-616-7530 | 757-616-7517 |  |  |  | ROBERT S. DUVALL | VICE PRESIDENT AND GENERAL MANAGER OF VA OPS | 757-616-7503 | rduvall@aglresources.com | TIDEWATER UTILITIES CONSTRUCTION, INC. WAS INSTALLING NEW WATER MAIN FOR THE CITY OF VIRGINIA BEACH AND HIT A 4 INCH PLASTIC NATURAL GAS MAIN ON OCEANA BOULEVARD IN VIRGINIA BEACH, VIRGINIA WITH MECHANIZED EQUIPMENT. THE RELEASED GAS WAS APPARENTLY IGNITED BY A NEARBY GASOLINE-FIRED SUMP-PUMP AND CAUSED A NATURAL GAS FIRE AT THE DAMAGE LOCATION. THE EXCAVATION DAMAGE OCCURRED IN THE ROAD MEDIAN AND WAS AWAY FROM ANY BUILDING STRUCTURES. THE FIRE DAMAGED SOME OF THE EXCAVATORS EQUIPMENT AND CAUSED A GAS OUTAGE DOWNSTREAM (THE SYSTEM WAS NOT BACK FED).
2025-03-31 10:13 | NO | YES | YES | 20110072 | 15253 | 2011-05-19 11:54 | ORIGINAL FINAL | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | P.O. BOX 430 | MEMPHIS | TN | 38101 | 2011-04-24 16:36 |  |  | 2011 | 1020 DAVID STREET | MEMPHIS | SHELBY | TN | 38114-3203 | 35.1073 | -89.9742 | [9 empty] | 2011-04-24 19:22 | 973896 |  | NATURAL GAS |  | 26.2 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 4 | 2011-04-24 17:35 |  |  |  | 2011-04-24 17:35 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1990 | [8 empty] | STEEL |  |  |  | 0.133 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 1 LOCATION | 0 | 0 | 934 | 1209.539511201629326 | 2155 | 2790.746945010183295 | 70000 | 90650.71283095723 | COST OF THE HOUSE, CONTENTS AND VEHICLE RESPONSIBLE FOR DAMAGED. |  | 4630 | 3511.563055062166962699822380106571936057 |  | 0 | 77719 | 42450.0066144418160175115452930728241563 | 98162.5623422312095836998223801065719361 | 0 | 0 | 1 |  |  |  |  | 49 | 50 | 100 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OUR MEDIUM PRESSURE SYSTEM HAS A PRESSURE RANGE OF 31-60 PSIG. THE LOW PRESSURE ALARM ON OUR SCADA SYSTEM IS SET TO ALARM AT 45 PSIG. ON THE DATE AND TIME OF THE DAMAGE TO THE SERVICE AT 1020 DAVID ST THE PRESSURE DROPPED FROM 50 PSIG TO 49 PSIG THEREFORE NOT ACTIVATING THE ALARM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | BINFORD HOLLAND | SAFETY TRAINING SPECIALIST | bholland@mlgw.org | 901-321-6956 | 901-320-1588 |  |  |  | BRENT E. HAYWOOD P.E. | MANAGER GAS ENGINEERING OPERATIONS | 901-320-1401 | bhaywood@mlgw.org | ON SUNDAY, APRIL 24, 2011 AT APPROXIMATELY 1636 THE MEMPHIS FIRE DEPARTMENT (MFD) REQUESTED OF MEMPHIS LIGHT GAS AND WATER DIVISION (MLGW) TO SEND A FIRST RESPONDER (GAS) TO A FIRE CALL AT 1020 DAVID STREET IN MEMPHIS, TENNESSEE AND COUNTY OF SHELBY. UPON ARRIVAL AT THE SCENE THE CUSTOMER SERVICE PERSON NOTIFIED DISPATCH TO SEND A GAS DISTRIBUTION CREW TO TERMINATE THE GAS SERVICE AT THE STREET BECAUSE THE FIRE WAS CONSUMING THE CAR AND HOUSE IN THE AREA WHERE THE GAS METER USED TO BE. AN SUV TYPE VEHICLE DRIVEN BY WILLIAM TERRANCE FREEMAN LEFT THE STREET, JUMPED THE CURB, RAN THROUGH A CHAIN LINK FENCE HITTING AND DESTROYING THE GAS METER WHILE ENTERING THE SOUTH WALL OF THE HOUSE. THIS VEHICLE WAS APPROXIMATELY EIGHT TO TEN FEET INSIDE THE HOUSE. THE LEAKING NATURAL GAS WAS IGNITED BY THE VEHICLE AND QUICKLY SPREAD TO THE HOUSE. MR. FREEMAN WAS BURNED AND WAS ABLE TO GET OUT THE VEHICLE BUT HAD TO GO INSIDE THE HOUSE TO EXIT AND ESCAPE THE FIRE. FIRE PREVENTED MR. FREEMAN FROM EXITING THE HOUSE THE SAME WAY HE ENTERED. THREE OTHER PEOPLE WERE IN THE BACK OF THE HOUSE WHEN THE VEHICLE CRASH OCCURRED, ALL ESCAPED WITH NO INJURIES. MFD KNOCKED THE FIRE DOWN WITHIN THE STRUCTURE AND MLGW PERSONNEL ELIMINATED THE BLOWING GAS BY TERMINATING GAS SERVICE TO THE HOUSE. MR. FREEMAN WAS TRANSPORTED TO THE MED WHERE HE WAS KEPT OVERNIGHT FOR TREATMENT TO BURNS HE RECEIVED IN THIS INCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20110152 | 30818 | 2011-05-24 15:39 | SUPPLEMENTAL FINAL | 15462 | PECO ENERGY CO | 2301 MARKET STREET, S9-1 | PHILADELPHIA | PA | 19103 | 2011-04-25 13:30 |  |  | 2011 | 1333 ELSON RD | BROOKHAVEN | DELAWARE | PA | 19015 | 39.8547 | -75.3919 | [9 empty] | 2011-04-25 17:23 | 973988 |  | NATURAL GAS |  | 0.01 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2011-04-25 13:30 |  |  |  | 2011-04-25 13:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1961 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.14 | [6 empty] | OTHER | [8 empty] | RELEASE DUE TO CUTTING SERVICE PIPE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  | YES |  |  |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | DAVID BONNER | PRINCIPAL ENGINEER | david.bonner@exeloncorp.com | 215-841-6476 |  |  |  |  | DAVID BONNER | PRINCIPAL ENGINEER | 215-841-6476 | david.bonner@exeloncorp.com | ON APRIL 25, 2011, A PECO GAS CONSTRUCTION AND MAINTENANCE CREW WAS REPAIRING A LEVEL ONE LEAK. WHILE CUTTING-OUT THE LEAKING PORTION OF A SERVICE PIPE WITH A BATTERY POWERED SAW, NATURAL GAS IGNITED. IMMEDIATELY, THE FIRE WAS EXTINGUISHED AND THE FLOW OF GAS WAS STOPPED. A CREW MEMBER RECEIVED MINOR BURNS TO HIS FACE. EMPLOYEE SHOULD HAVE VERIFIED THE SERVICE WAS PROPERLY PURGED OUT OF SERVICE PRIOR TO USING THE BATTERY POWERED SAW OR A MANUAL PIPE CUTTER COULD HAVE ALSO BEEN USED TO ELIMINATE THE SOURCE OF IGNITION.
2025-03-31 10:13 | NO | NO | NO | 20110161 | 15252 | 2011-05-31 16:06 | ORIGINAL | 32468 | CITY OF MAPLETON | 513 MAIN STREET | MAPLETON | IA | 51034 | 2011-04-09 19:20 |  |  | 2011 | 409 SO. 4TH WAS SITE OF BREAK | MAPLETON |  | IA | 51034 | 42.1613 | -95.7934 | [12 empty] | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | [6 empty] | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1994 | [5 empty] | 2 | POLYETHALENE | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | OTHER | [8 empty] | TORNADO UPROOTED LARGE TREE PULLING THE LINE UP AND IN HALF WITH THE ROOTS | CLASS 1 LOCATION | 0 | 0 | 200 | 259.0020366598778 | 0 | 0 | 0 | 0 |  |  | 200 | 151.687388987566607460035523978685612789 |  | 0 | 400 | 247.590591571917915097690941385435168739 | 410.689425647444407460035523978685612789 | 77 | 0 | 458 |  |  |  |  | 25 | 25 | 26 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [56 empty] | HIGH WINDS | [5 empty] | YES |  |  | YES | [215 empty] | KARLA UHL | CITY CLERK | maphall@longlines.com | 712-881-1351 | 712-881-2726 |  |  |  | MIKE HAHN | CITY SUPERINTENDENT | 712-881-1351 | maphall@longlines.com | APRIL 9, 2011, APPROXIMATELY 7:20 PM TORNADO STRUCK MAPLETON AFFECTING 60% OF COMMUNITY. LARGE TREE UPROOTED AND PULLED 2" POLYETHYLENE MAIN OUT OF THE GROUND SEVERING LINE. IT WAS UNCERTAIN OF THE DAMAGE TO THE REST OF THE SYSTEM SO THE TBS WAS SHUT DOWN, AFFECTING ALL 600 CUSTOMERS. ALL METERS WERE SHUT OFF BY NOON APRIL 10. AFTER REPAIRS SYSTEM REPRESSURIZED AT 3:00 PM TO VERIFY NO LEAKS. RELIGHTS BEGAN AT 4:09 PM AND FIRST PASS THROUGH TOWN COMPLETE BY 5:00 P.M. ON APRIL 11. FINAL CUSTOMER THAT COULD BE RELIT WAS AT 9:00 AM APRIL 13, 2011.
2025-03-31 10:13 | YES | NO | NO | 20110169 | 15256 | 2011-06-07 08:22 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2011-05-08 00:51 |  |  | 2011 | 3015 ELLICOTT ROAD | BELTSVILLE | PRINCE GEORGE'S | MD | 20904 | 39.0523 | -76.9449 | [9 empty] | 2011-05-08 02:49 | 975617 |  | NATURAL GAS |  | 17 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2011-05-08 00:51 |  |  |  | 2011-05-08 01:23 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | 1964 | [8 empty] | OTHER | CAST ALUMINUM | [9 empty] | OTHER | [8 empty] | DAMAGE TO AN INSIDE METER BUILD-UP DUE TO A HOUSE FIRE. | CLASS 3 LOCATION | 0 | 0 | 200 | 259.0020366598778 | 2200 | 2849.0224032586558 | 400000 | 518004.0733197556 | APPROXIMATE DAMAGE TO THE STRUCTURE AS A RESULT OF A HOUSE FIRE. |  | 80 | 60.67495559502664298401420959147424511545 |  | 0 | 402480 | 215885.1299229830370060390763765541740675 | 521172.7727152691602429840142095914742451 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MICHAEL UPSHAW | SUPERVISOR - DOT PIPELINE SAFETY COMPLIANCE | mupshaw@washgas.com | 703-750-4479 | 703-750-5591 |  |  |  | DAVID SPANGLER | MANAGER - DOT PIPELINE SAFETY COMPLIANCE | 703-750-4341 | dspangler@washgas.com | WASHINGTON GAS WAS NOTIFIED BY THE PRINCE GEORGE'S FIRE BOARD OF A HOUSE FIRE AT 3015 ELLICOTT ROAD IN BELTSVILLE, MD, ON SUNDAY, MAY 8, 2011 AT 00:51. WASHINGTON GAS PERSONNEL ARRIVED ON THE SITE AT 01:23. THE SERVICE LINE WAS TURNED OFF AT THE OUTSIDE CURB VALVE. A 360 DEGREE BAR AND TEST SURVEY WAS CONDUCTED AROUND THE STRUCTURE AND OVER THE SERVICE LINE AND MAIN. NO LEAK INDICATIONS WERE FOUND. AN ODORANT SAMPLE WAS TAKEN AND ODORANT LEVEL WAS FOUND TO BE ACCEPTABLE. THE SERVICE LINE WAS CAPPED OFF AT THE CURB VALVE. A PRESSURE TEST OF THE SERVICE LINE WAS CONDUCTED ON MAY 13, 2011 AND NO LEAK INDICATIONS WERE FOUND. DISCUSSIONS ON SITE WITH FIRE PERSONNEL THE DAY OF THE INCIDENT INDICATED THAT THE FIRE STARTED ON THE SECOND FLOOR AND THEN COLLAPSED INTO THE BASEMENT WHERE THE WASHINGTON GAS FACILITIES WERE. WASHINGTON GAS FACILITY INVOLVEMENT WAS SECONDARY.
2025-03-31 10:13 | NO | NO | NO | 20110173 | 15376 | 2011-06-09 11:45 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2011-05-10 14:39 |  |  | 2011 | 30TH AND STINSON | ST. ANTHONY |  | MN | 55418 | 45.0223 | -93.2269 | [9 empty] | 2011-05-10 18:06 | 975890 |  | NATURAL GAS |  | 6970.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 48 | 2011-05-10 14:39 |  |  |  | 2011-05-10 14:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 54 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1949 | [5 empty] | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 21881 | 28336.117820773930709 | 21878 | 28332.232790224032542 | 0 | 0 |  |  | 30949 | 23472.865008880994671403197158081705151 |  | 0 | 74708 | 45184.1056854644587417921847246891651865 | 80141.215619878957922403197158081705151 | 0 | 0 | 0 |  |  |  |  | 95 | 95 | 100 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE CHANGES WERE NOT SIGNIFICANT ENOUGH TO TRIGGER ALARMS. | [12 empty] | NO |  |  | YES | 2 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | AUGER | NATURAL GAS | YES | 111191312 | GOPHER STATE ONE CALL |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | dean.headlee@centerpointenergy.com | 612-321-5366 | 612-399-1422 |  |  |  | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 612-321-5366 | dean.headlee@centerpointenergy.com | A CENTERPOINT ENERGY CONTRACTOR WAS ATTEMPTING TO INSTALL ANODES ON A 1949, 12 INCH STEEL GAS MAIN IN A CLASS THREE NEIGHBORHOOD. THE CONTRACTOR DRILLED THROUGH THE TOP OF THE MAIN WITH AN EARTH AUGER LEAVING A HOLE ALMOST THREE INCHES IN DIAMETER. THIS LINE HAD BEEN ACCURATELY MARKED JUST SOUTH OF THE INTERSECTION OF 30TH ST NE AND STINSON BLVD NE AT THE SITE OF THE DAMAGE. THE LINE WAS ONE WAY FED AND WAS LEFT IN SERVICE UNTIL A BYPASS COULD BE CONSTRUCTED AND THE GAS FLOW STOPPED WITHOUT LOSING ANY CUSTOMERS. FINAL REPAIRS WERE MADE THE FOLLOWING AFTERNOON BY WELDING A PATCH OVER THE DAMAGE AND THEN SUBSEQUENTLY A FULL CIRCUMFERENCE COVER SLEEVE OVER THE ENTIRE AREA.
2025-03-31 10:13 | NO | NO | NO | 20110190 | 15265 | 2011-06-22 15:58 | ORIGINAL FINAL | 4350 | ELIZABETHTOWN GAS CO | 520 GREEN LANE | UNION | NJ | 07083 | 2011-05-31 10:24 |  |  | 2011 | WEST JERSEY ST. NEAR UNION ST. | ELIZABETH | UNION | NJ | 07203 | 40.6652 | -74.2174 | [9 empty] | 2011-05-31 16:10 | 977899 |  | NATURAL GAS |  | 1250 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 100 | 2011-05-31 10:24 |  |  |  | 2011-05-31 10:51 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1984 | [5 empty] | 6.625 | ASTM D2513 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 5100 | 6604.5519348268839 | 0 | 0 | 0 | 0 |  |  | 1093 | 828.97158081705150976909413854351687389 |  | 0 | 6193 | 3502.254578867210565008880994671403197158 | 7433.52351564393540976909413854351687389 | 0 | 0 | 0 |  |  |  |  | 20 | 20 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ELECTRIC | YES | 111172023 | NEW JERSEY ONE CALL |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | PHIL SALVATORE | COMPLIANCE ENGINEER | psalvato@aglresources.com | 908 662 8306 | 908 662 8304 |  |  |  | DONALD F. CARTER | VICE PRESIDENT AND GENERAL MANAGER | 908 771 8200 | dcarter@aglresources.com | A CONTRACTOR DAMAGED A 6 INCH PE MAIN ON WEST JERSEY STREET NEAR UNION ST. IN ELIZABETH, NJ. DAMAGE TO THE MAIN OCCURRED WHEN A 2 INCH SERVICE TEE WAS STRUCK, PULLING IT OFF THE MAIN. CONTRACT LOCATOR'S MARKS WERE 19 INCHES FROM THE MAIN. HOWEVER, THE EXCAVATOR WAS ABLE TO HAND DIG AND LOCATE THE MAIN AS REQUIRED. THE EXCAVATOR THEN PROCEEDED TO USE A BACKHOE TO EXCAVATE A TRENCH PARALLEL TO BUT NOT ADJACENT TO THE MAIN WITHOUT FURTHER EXPOSING THE GAS PIPE. THE ROOT CAUSE WAS THE EXCAVATOR'S FAILURE TO ADEQUATELY PROBE FOR THE MAIN AND APPURTENANCES AS HE PROGRESSED AWAY FROM THE ORIGINAL EXPOSED SECTION IN CLOSE PROXIMITY TO THE MAIN. NEW JERSEY CODE REQUIRES PROPER CARE AND ADEQUATE SUPERVISION BE USED TO AVOID DAMAGE TO THE UNDERGROUND FACILITY AFTER LOCATING THE FACILITY BY HAND (REF. N.J.A.C.14-2-3.3). THE CLOSE PROXIMITY AND STRUCTURAL INTEGRITY OF THE DAMAGED FACILITY SUGGESTS NO CLOSE SUPERVISION OF THE MECHANICAL EXCAVATION WAS BEING PRACTICED ALTHOUGH THE EXCAVATOR KNEW THE EXCAVATION WAS BEING PERFORMED WITHIN INCHES OF THE GAS MAIN AND ITS LIKELY APPURTENANCES. THE TEE WAS RIPPED COMPLETELY FROM THE MAIN, INDICATING CONSIDERABLE FORCE WAS APPLIED. THE NEARBY NJ TRANSIT & AMTRAK NE CORRIDOR TRACKS WERE SHUT DOWN FOR APPROXIMATELY 2 HOURS. WEST JERSEY STREET WAS CLOSED BETWEEN CHERRY STREET AND BROAD STREET AND THE KELLOGG BUILDING OF UNION COUNTY COLLEGE WAS EVACUATED (APPROX 100 PEOPLE). NO INJURIES AND NO PROPERTY DAMAGE OTHER THAN TO GAS LINE WERE REPORTED.
2025-03-31 10:13 | NO | NO | NO | 20110204 | 15266 | 2011-06-27 13:01 | ORIGINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2011-06-25 05:04 |  |  | 2011 | 11217 WILLAM PLAZA | OMAHA | DOUGLAS | NE | 68144 | 41.246 | -96.0143 | [9 empty] | 2011-06-25 09:30 | 980759 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2011-06-25 05:42 |  |  |  | 2011-06-25 06:08 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1981 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | LIGHTING STRIKE | CLASS 1 LOCATION | 50000 | 64750.50916496945 | 1000 | 1295.010183299389 | 60 | 77.70061099796334 | 1000 | 1295.010183299389 | THERE ARE NO ADDITIONAL COST. |  | 50 | 37.92184724689165186500888099467140319716 |  | 0 | 52110 | 27957.6888902554908487744227353463587922 | 67456.1519898130829918650088809946714032 | 0 | 0 | 1 |  |  |  |  | 9.4 | 10 | 10 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING | [5 empty] | NO | [218 empty] | MIKE PALMESANO | CLAIMS MANAGER | mike_palmesano@mudnebr.com | 402-504-7108 | 402-504-5108 |  |  |  | MIKE PLAMESANO | CLAIMS MANAGER | 402-504-7108 | mike_palmesano@mudnebr.com | LIGHTING STRUCK A HOME AT 11217 WILLIAM PLAZA IN OMAHA NEBRASKA ON 06/25/2011. THE LIGHTING STRIKE DAMAGED THE METER SET RELEASING GAS.
2025-03-31 10:13 | YES | NO | NO | 20110205 | 15267 | 2011-06-27 17:14 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2011-06-01 17:40 |  |  | 2011 | 320 N. 2ND ST. | ST. CHARLES | KANE | IL | 60174 | 41.9164 | -88.3168 | [9 empty] | 2011-06-01 20:25 | 978172 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2011-06-01 17:40 |  |  |  | 2011-06-01 18:24 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET | [10 empty] | OTHER | STEEL/ALUMINUM METER SET | [9 empty] | OTHER |  |  |  | MELTING OF FACILITIES - FIRE |  |  |  |  | METER SET COMPONENTS MELTED/DAMAGED DUE TO FIRE FIRST EVENT. | CLASS 3 LOCATION | 0 | 0 | 9100 | 11784.5926680244399 | 2700 | 3496.5274949083503 | 200000 | 259002.0366598778 | DAMAGE TO PORTION OF ROOF, ITEMS NEAR METER SET AND SOOTING OF BRICK WALL |  | 165 | 125.142095914742451154529307282415630551 |  | 0 | 211965 | 113715.6211993502372749555950266429840142 | 274408.2989187253326511545293072824156306 | 1 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | lquezad@nicor.com | 630-388-2316 |  |  |  |  | LETICIA QUEZADA | MANAGER REGULATORY COMPLIANCE | 630-388-2316 | lquezad@nicor.com | IGNITION OF UNKNOWN MATERIALS IN THE VICINITY OF THE METER SET WHICH CAUSED DAMAGE TO THE METER SET AND RESULTED IN A RELEASE OF NATURAL GAS. REGULATOR DELIVERY PRESSURE IS 1/4-PSIG. REGULATOR INLET PRESSURE IS 58-PSIG.
2025-03-31 10:13 | NO | NO | NO | 20110207 | 15382 | 2011-06-28 12:26 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-06-06 13:13 |  |  | 2011 | 533 EAST 11 STREET | NEW YORK | NEW YORK | NY | 10009-4653 | 40.728 | -73.9802 | [9 empty] | 2011-06-06 14:58 | 978815 |  | NATURAL GAS |  | 15 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 12 | 2011-06-06 13:13 |  |  |  | 2011-06-06 13:22 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1978 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | COPPER | [10 empty] | MECHANICAL PUNCTURE | [9 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 1180 | 1528.11201629327902 | 0 | 0 |  |  | 45 | 34.12966252220248667850799289520426287744 |  | 0 | 1225 | 664.470103062948025896980461811722912966 | 1562.241678815481506678507992895204262877 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  |  | YES | CONTRACTOR WORKING FOR ELECTRIC OPERATIONS INCORRECTLY IDENTIFIED 3" STEEL GAS SLEEVE (WITH GAS SERVICE INSIDE SLEEVE) FOR A 3" ELECTRIC CONDUIT SLEEVE | OTHER MAINTENANCE | NO | [50 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | *********************THIS IS NOT A DOT REPORTABLE INCIDENT----THIS REPORT IS FOR INFORMATION ONLY************************ A CON EDISON CONSTRUCTION INSPECTOR REPORTED A CONTRACTOR DAMAGED AT 533 E 11 ST., MANHATTAN, NEW YORK TO THE GAS EMERGENCY RESPONSE CENTER (GERC). A MULTIPLE RESOURCE RESPONSE EVENT (CODE MURRE) WAS INITIATED AND THE GERC DISPATCHED THE FIRE DEPARTMENT OF THE CITY OF NY (FDNY), GAS DISTRIBUTION SERVICES (GDS), CONSTRUCTION AND SUPERVISION. GDS RESPONDED AND AT 13:22 HRS. REPORTED RECEIVING A 4% GAS READING IN THE ATMOSPHERE OF THE BASEMENT. THE FDNY EVACUATED 12 RESIDENTS OF THIS 7 STORY BUILDING AT 13:25 HRS., GDS REPORTED THAT SICON ELECTRICAL CONTRACTORS WORKING FOR CON EDISON CONSTRUCTION MANAGEMENT CUT THROUGH A 3" STEEL PIPE 5 FEET FROM THE OUTSIDE FOUNDATION WALL, THE PIPE CONTAINED A 1 1/4" LOW PRESSURE COPPER GAS SERVICE. ADDITIONAL GDS MECHANICS RESPONDED TO LOCATION AND TOGETHER THEY WERE ABLE TO SECURE THE DAMAGED 1 1/4" COPPER SERVICE IN THE 3" SLEEVE AT 14:30 HRS. THE FDNY VENTED THE BASEMENT AND THE EVACUATION ENDED AT 14:42 HRS. A GDS MECHANIC WAS OFFERED OXYGEN BY THE FD AFTER SECURING THE LEAK, THE FDNY ADMINISTERED THE OXYGEN AND HE WAS LATER EVALUATED BY EMS ON SCENE AND RETURNED TO WORK AT 15:41 HRS. FDNY, NYC OEM, NYC DEP HAZMAT AND THE NEW YORK TIMES WERE ON LOCATION. THE NYS PSC, NYC DEP AND US DOT WERE ALL NOTIFIED. THIS WAS AN UPGRADED LEVEL INCIDENT. *********************THIS IS NOT A DOT REPORTABLE INCIDENT----THIS REPORT IS FOR INFORMATION ONLY************************
2025-03-31 10:13 | NO | NO | NO | 20110213 | 15380 | 2011-06-30 09:00 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-06-03 15:08 |  |  | 2011 | INTERSECTION 75 AVE AND MAIN STREET | NEW YORK | QUEENS | NY | 11367-2436 | 40.7239 | -73.82 | [9 empty] | 2011-06-03 21:25 | 978598 |  | NATURAL GAS |  | 65 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 20 | 2011-06-03 15:08 |  |  |  | 2011-06-03 15:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1993 | [5 empty] | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | ELECTRIC BURNOUT DAMAGED GAS MAIN | CLASS 4 LOCATION | 0 | 0 | 50000 | 64750.50916496945 | 11500 | 14892.6171079429735 | 0 | 0 |  |  | 202 | 153.204262877442273534635879218472468917 |  | 0 | 61702 | 33127.5172103185777202486678507992895204 | 79796.3305357898657735346358792184724689 | 2 | 0 | 1 |  |  |  |  | 49 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SYSTEM INVOLVEMENT RE:GAS CONTROL. NORMAL PRESSURES. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON FRIDAY JUNE 3, 2011 AT 1508 HRS THE GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A CALL FROM THE FIRE DEPARTMENT OF THE CITY OF NEW YORK (FDNY) REPORTING A GAS ODOR IN THE AREA OF 75 AVE. AND MAIN ST. THE CON EDISON ELECTRIC EMERGENCY CONTROL CENTER CALLED THE GERC AT 1512 HRS. REPORTING A MANHOLE FIRE AT THE SAME LOCATION WITH A GAS ODOR PRESENT. GAS DISTRIBUTION SERVICES (GDS), SUPERVISION AND CONSTRUCTION WERE DISPATCHED. GDS ARRIVED AT 1515 HRS. AND CONFIRMED THE ELECTRIC MANHOLE WAS ON FIRE ON THE NORTHEAST CORNER OF 75 AVE. AND MAIN ST. GDS DETECTED A STRONG GAS ODOR IN THE AREA, THE GERC & GAS CONTROL PROVIDED THE LOCATIONS OF FOUR MAIN VALVES (20150, 12277, 10099 AND 11947) NEEDED TO ISOLATE THE HIGH PRESSURE DISTRIBUTION SYSTEM IN THIS INTERSECTION. GDS LOCATED AND CLOSED THE FOUR MAIN VALVES TO ISOLATE THE AREA. THE FDNY EVACUATED AN UNKNOWN NUMBER OF PEOPLE FROM 12 BUILDINGS (7 COMMERCIAL AND 5 RESIDENTIAL) AS A PRECAUTION. GAS CONSTRUCTION EXCAVATED THREE FIRE BANKS NORTH, SOUTH AND EAST OF THE FIRE AND INSERTED STOPPERS IN THE 4" STEEL MAIN ON MAIN ST. AND IN THE 2" STEEL MAIN ON 75 AVE. AND VERIFIED SHUT-DOWN. THE FDNY EXTINGUISHED THE FIRE IN THE INTERSECTION AT 1829 HRS. THREE GAS SERVICES WERE INTERRUPTED; 73-27 MAIN ST., 75-03 MAIN ST. AND 75-09 MAIN ST. THE FDNY AND GDS RE-CHECKED ALL BUILDINGS THAT WERE EVACUATED, ALL WERE FOUND CLEAR AND THE EVACUATION ENDED AT 1945 HRS. THE FDNY, NYPD, OEM, DEP HAZMAT WERE ON LOCATION. GAS CONSTRUCTION REMAINED ON LOCATION TO MAKE REPAIRS AND (2) OF THE THREE GAS SERVICES WERE RESTORED THAT SAME EVENING AT 2230 HRS. THE 4" MAIN ON MAIN ST. WAS CUT AND CAPPED AND BETWEEN 73 AVE. AND 75 RD., AND THE 2" STEEL MAIN ON 75 AVE. WAS CUT AND CAPPED AT THE INTERSECTION AT MAIN ST. GAS CONSTRUCTION CREWS INSTALLED A NEW 4" HPPE MAIN ON MAIN ST FROM 73 AVE. TO 75 RD. GAS SERVICE WAS TIED ON MAIN ST. GOING NORTH/SOUTH, AND THE ABANDONED, DAMAGED SECTION EFFECTED BY THE BURNOUT WAS EXCAVATED AND THE CAUSE OF THE LEAK WAS CONFIRMED DUE TO A BURNOUT. TOTAL COST OF DAMAGE FROM THIS EVENT EXCEEDED $50,000. THE US DOT, NYS PSC AND NYC DEP WERE NOTIFIED. THIS WAS A SERIOUS LEVEL INCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20110214 | 15295 | 2011-06-30 09:18 | SUPPLEMENTAL FINAL | 32513 | AMEREN ILLINOIS COMPANY | 300 LIBERTY | PEORIA | IL | 61602 | 2011-06-01 15:29 |  |  | 2011 | 610 CRUGER ROAD | EUREKA | WOODFORD | IL | 61530 | 40.7194 | -89.3295 | [9 empty] | 2011-06-01 17:22 | 978158 |  | NATURAL GAS |  | 8 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2011-06-01 15:29 |  |  |  | 2011-06-01 15:47 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2002 | [5 empty] | 1 | ASTM D2513 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | OTHER | [8 empty] | CONTRACTOR CUT SERVICE | CLASS 3 LOCATION | 0 | 0 | 525 | 679.880346232179225 | 1225 | 1586.387474541751525 | 0 | 0 |  |  | 54 | 40.95559502664298401420959147424511545293 |  | 0 | 1804 | 976.50648620099578907637655417406749556 | 2307.223415800573734014209591474245115453 | 1 | 0 | 0 |  |  |  |  | 30 | 30 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | OCCUPANT | BACKHOE/TRACKHOE | WATER | YES | 1401009 | JULIE |  | CONTRACT LOCATOR | YES | YES | 4 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JEROME THEMIG | MANAGER GAS COMPLIANCE | jthemig@ameren.com | 217-625-6804 | 217-625-8031 |  |  |  | JEROME THEMIG | MANAGER GAS COMPLIANCE | 217-625-6804 | jthemig@ameren.com | A MAINTENANCE WORKER WAS EXCAVATING WITH A MINI-TRACKHOE WHEN A 1" PE SERVICE LINE WAS DAMAGED. THE MAINTENANCE WORKER ATTEMPTED TO BEND OVER THE SERVICE AND INSTALL HOSE CLAMPS TO CONTROL THE RELEASE OF GAS. THE MAINTENANCE WORKER INTRODUCED A SOURCE OF IGNITION WHEN A BATTERY OPERATED DRILL WAS USED TO TIGHTEN THE HOSE CLAMPS. THE RELEASE OF GAS IGNITED RESULTING IN SECOND DEGREE BURNS TO THE ARM OF THE MAINTENANCE WORKER NECESSITATING ONE NIGHT OF INPATIENT HOSPITALIZATION. THE 1" PE SERVICE WAS PROPERLY LOCATED AND MARKED. SUPPLEMENTAL REPORT CREATED TO CORRECT LOCATE TICKET NUMBER.
2025-03-31 10:13 | YES | NO | NO | 20110215 | 15286 | 2011-06-30 11:58 | SUPPLEMENTAL FINAL | 1088 | BALTIMORE GAS & ELECTRIC CO | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2011-06-02 02:05 |  |  | 2011 | 5809 KEY AVENUE | BALTIMORE |  | MD | 21215-4009 | 39.3589 | -76.6793 | [9 empty] | 2011-06-02 04:45 | 978297 |  | NATURAL GAS |  | 3.4 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 1 | 2011-06-02 02:05 |  |  |  | 2011-06-02 02:29 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | OTHER | NATURAL GAS DISTIBUTION, INVESTOR OWNED | INSIDE METER/REGULATOR SET |  | 1951 | [8 empty] | OTHER | MALLEABLE IRON /METER SWIVEL | [9 empty] | OTHER | [8 empty] | CAUSE UNKNOWN AT THIS TIME | CLASS 4 LOCATION | 155000 | 200726.578411405295 | 100 | 129.5010183299389 | 10000 | 12950.10183299389 | 0 | 0 |  |  | 116 | 87.97868561278863232682060390763765541741 |  | 0 | 165216 | 88633.4933781422175987566607460035523979 | 213894.1599483419125323268206039076376554 | 0 | 0 | 1 |  |  |  |  | 0.31 | 0.31 | 0.36 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | BERNARD F SMITH | SUPERVISOR GAS SERVICE | bernard.smith@bge.com | 410-470-7106 | 410-470-7103 |  |  |  | WILLIAM H BROWN | MANAGER GAS SERVICE | 410-470-7105 | william.h.brown@bge.com | BALTIMORE CITY FIRE DEPARTMENT CALLED FOR ASSISTANCE AT THE ADDRESS OF 5809 KEY AVENUE AT 2:05 AM FOR A REPORTED EXPLOSION. THE OPERATORS FIRST RESPONDER ARRIVED AT 2:29 AM AND AFTER THE INITIAL INVESTIGATION OF THIS INCIDENT AT 4:30 AM, IT WAS DETERMINED THAT THIS INCIDENT MET THE CRITERIA OF A D.O.T. REPORTABLE INCIDENT AND D.O.T. WAS NOTIFIED AT 4:45 AM. THE GAS WAS TURNED OFF AT 7:33 AM. ONE PERSON SUSTAINED INJURIES REQUIRING HOSPITALIZATION. OPERATOR'S SERVICE FACILITIES WAS TESTED AND HELD PRESSURE TEST THAT WAS WITNESSED BY THE MARYLAND PUBLIC SERVICE COMMISSION. DAMAGE TO COMPANY'S PIPING AS A RESULT OF UNKNOWN CAUSE SUBSEQUENT BUILDING EXPLOSION. FOLLOWING INVESTIGATION SELECTIVE INSIDE OPERATOR'S PIPING WAS ABLE TO BE RECOVERED AND UPON EXAMINATION BY THE MARYLAND PUBLIC SERVICE COMMISSION WAS FREE OF DEFECTS.
2025-03-31 10:13 | NO | YES | YES | 20110222 | 15272 | 2011-07-01 15:08 | ORIGINAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2011-06-21 12:44 |  |  | 2011 | 11818 CROSSROADS PLACE | CONCORD | CABARRUS | NC | 28025 | 35.2655 | -80.5992 | [9 empty] | 2011-06-22 12:38 | 980407 |  | NATURAL GAS |  | 35.8 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 12 | 2011-06-21 12:44 |  |  |  | 2011-06-21 12:56 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 18 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2000 | [5 empty] | 0.075 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.095 |  | 2406 | OTHER | [8 empty] | PIPE WAS HEATED WITH HAND HELD TORCH AND MELTED PLASTIC PIPE. | CLASS 3 LOCATION | 0 | 0 | 37 | 47.915376782077393 | 1876 | 2429.439103869653764 | 0 | 0 |  |  | 163 | 123.625222024866785079928952042628774423 |  | 0 | 2076 | 1140.406495063902850804618117229129662522 | 2600.979702676597942079928952042628774423 | 0 | 0 | 8 |  |  |  |  | 60 | 60 | 66 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | GAS FACILITIES WERE NOT PROPERLY PROTECTED WHILE THE CABLE UTILITY REPAIRED THEIR FACILITIES. GAS PIPE WAS MELTED DURING A CABLE REPAIR OPERATION RESULTING IN GAS LEAK AND IGNITION (FIRE). | [154 empty] | M.D. HARRIS | MANAGER - OPERATIONS | mdharris@scana.com | 8286703559 | 7048103177 |  |  |  | MILTON SCOTT SWINDLER | GENERAL MANAGER - CONTSTRUCTION- MAINTENANCE | 7048103230 | sswindler@scana.com | CITY OF CONCORD (NC) DAMAGED ELECTRICAL AND CABLE TV LINES WHILE EXCAVATING TO REPAIR A SEWER LINE AT 11818 CROSSROADS PLACE CONCORD, NC. AFTER THE ELECTRIC COMPANY REPAIRED THEIR LINES, THE CABLE TV COMPANY WAS IN THE PROCESS OF INSTALLING A HEAT SHRINK SLEEVE OVER A CABLE REPAIR WHEN THE TORCH THE CABLE TV EMPLOYEE WAS USING MELTED A HOLE IN THE GAS LINE, IGNITED THE ESCAPING GAS, AND INJURED THE CABLE TV EMPLOYEE. THE 3/4" PLASTIC GAS SERVICE WAS APPROXIMATELY 1-1/2" TO 2" AWAY FROM THE CABLE TV LINE AND NO PRECAUSTIONS WERE TAKEN TO PROTECT THE GAS SERVICE LINE DURING THE REPAIR OPERATION. THE CABLE TV EMPLOYEE WAS TAKEN TO A HOSPITAL FOR MEDICAL TREATMENT FOR BURNS.
2025-03-31 10:13 | NO | YES | NO | 20110224 | 15537 | 2011-07-03 20:22 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2011-06-04 21:00 |  |  | 2011 | 3605 E MARGINAL WAY S | SEATTLE | KING | WA | 98134 | 47.5727 | -122.3398 | [9 empty] | 2011-06-06 17:12 | 978852 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-06-06 16:15 |  |  |  | 2011-06-06 16:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 40 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1960 | [5 empty] | 16 | API 5L X-42 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | OTHER | [8 empty] | NO RELEASE OF GAS | CLASS 4 LOCATION | 0 | 0 | 44601 | 57758.749185336048789 | 23503 | 30436.624338085539667 | 35029 | 45362.911710794297281 | ADDITIONAL OPERATOR LABOR, MATERIAL AND RENTED EQUIPMENT |  | 0 | 0 |  | 0 | 103133 | 55315.836150712803021 | 133558.285234215885737 | 0 | 0 | 0 |  |  |  |  | 143 | 143 | 150 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT IS A RESULT OF A THIRD-PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | POLE | YES | 11106851 | UTILITIES UNDERGROUND LOCATION CENTER |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | ANTOINETTE IMAD | CONSULTING ENGINEER | antoinette.imad@pse.com | 425 456 2970 | 425 462 3770 |  |  |  | CHERYL MCGRATH | MANAGER | 4254623207 | cheryl.mcgrath@pse.com | SEE ATTACHED
2025-03-31 10:13 | NO | YES | NO | 20110229 | 15782 | 2011-07-07 12:57 | SUPPLEMENTAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2011-06-08 10:45 |  |  | 2011 | 1411 GRANITE AVE. | BILLINGS | YELLOWSTONE | MT | 59101 | 45.8012 | -108.5514 | [9 empty] | 2011-06-08 12:30 | 979029 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2011-06-08 11:00 |  |  |  | 2011-06-08 11:15 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1956 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | TOTAL BREAK OF STEEL LINE | [5 empty] | CLASS 3 LOCATION | 1500000 | 1942515.2749490835 | 2500 | 3237.5254582484725 | 5000 | 6475.050916496945 | 10000 | 12950.10183299389 | 5 CUSTOMERS HAD SERVICE LINES RETIRED. |  | 0 | 0 |  | 0 | 1517500 | 813917.7698574333975 | 1965177.9531568228075 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | VERY HIGH RAINFALL TOTALS CREATED MOVEMENT/SETTLING IN ROCKY UNSTABLE GROUND ALONG RIMS AREA IN BILLINGS | NO | [218 empty] | DARYL ANDERSON | DIRECTOR OF DISTRIBUTION ENGINEERING | daryl.anderson@mdu.com | 701-222-7994 | 701-222-7853 |  |  |  | DARYL ANDERSON | DIRECTOR OF DISTRIBUTION ENGINEERING | 701-222-7994 | daryl.anderson@mdu.com | HIGH RAINFALL TOTALS ARE BELIEVED TO HAVE LED TO UNSTABLE GROUND SHIFTING/MOVEMENT IN THE POOR ROCKY SOIL CONDITIONS ALONG THE RIMS AREA IN BILLINGS. THE STEEL SERVICE LINE FAILED IN SERVICE RESULTING IN A MAJOR LEAK IN THE LINE. HIGH PRESSURES GENERATED FROM THE MOVEMENT OF THE ROCKS AND SOIL IN THE GROUND BROKE THE SERVICE LINE AT A FIELD BEND LOCATED CLOSE TO THE HOUSE. ANALYSIS OF THE SERVICE LINE ITSELF SHOWS A LARGE SUDDEN CATASHROPHIC BREAK IN THE LINE.
2025-03-31 10:13 | NO | YES | YES | 20110232 | 15276 | 2011-07-07 15:19 | ORIGINAL FINAL | 13360 | ENTERGY NEW ORLEANS, INC | 3700 TULANE AVENUE L-TUL-111 | NEW ORLEANS | LA | 70119 | 2011-06-01 08:33 |  |  | 2011 | 2121-23 BIENVILLE ST. | NEW ORLEANS | ORLEANS PARISH | LA | 70112 | 29.9634 | -90.0804 | [9 empty] | 2011-07-01 16:30 | 978151 |  | NATURAL GAS |  | 7.4 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 1 | 2011-06-01 08:33 |  |  |  | 2011-06-01 08:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | CONRTACTOR CUT RISER WITH POWER SAW. | CLASS 2 LOCATION | 0 | 0 | 100 | 129.5010183299389 | 250 | 323.75254582484725 | 0 | 0 |  |  | 40 | 30.33747779751332149200710479573712255773 |  | 0 | 390 | 215.787975748192053019538188277087033748 | 483.591041952299471492007104795737122558 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | THE CONTRACTOR CUT THROUGH THE 1 1/2 GAS RISER WITH AN ELECTRIC SAWS-ALL. AFTER THE PIPE WAS CUT, THE SAW IGNITED THE BLOWING GAS UNDER THE HOUSE. | [47 empty] | ROBERT A. BORNE | COMPLIANCE SUPERVISOR | rborne@entergy.com | 225.354.3289 | 225.354.3061 |  |  |  | DONALD W. VINCI | V.P. GAS DISTRIBUTION BUSINESS | 504.593.3434 | dvinci@entergy.com | ENTERGY EMPLOYEE, EVERETT JOHNSON, RESPONDED TO A FIRE CALL BY THE NEW ORLEANS FIRE DEPARTMENT (NOFD). AFTER ARRIVING ON LOCATION, EMPLOYEE CONFIRMED WITH THE FIRE CHIEF ON SITE, LARRY WHITE, THAT GAS WAS INVOLVED AND THAT THERE WERE THREE INJURIES. ONE CONTRACTOR, MIGUEL MEJIA, WHO RECEIVED 2ND DEGREE BURNS TO HIS HANDS, ARMS AND FACE, AND TWO FIREMEN, PETER EVERRETT AND NEAL DUGAS, WHO BOTH RECEIVED 1ST DEGREE BURNS TO THE FACIAL AREA. EMPLOYEE NOTIFIED HIS SUPERVISOR, DAVID HOFFMAN, WHO RESPONDED TO THE LOCATION WITH SUPERVISOR LOUIS LAFOURCADE. AFTER CONDUCTING INITIAL INVESTIGATION, SUPERVISORS DETERMINED THAT THE CONTRACTOR WAS CUTTING ALL PIPING FROM UNDER THE HOUSE TO PREPARE IT FOR RAISING. THE CONTRACTOR CUT THROUGH THE LIVE 1 1/2 UP (UTILIZATION PRESSURE OR 7"WATER COLUMN) GAS RISER ON THE 2123 SIDE OF THE DOUBLE UNIT WITH AN ELECTRIC SAWS-ALL. AFTER THE PIPE WAS CUT, THE SAWS-ALL IGNITED THE BLOWING GAS UNDER THE HOUSE. AT THIS TIME, THE FIRE DEPT. WAS NOTIFIED OF THE FIRE. THE FIREMEN WERE INJURED AFTER THE GAS FIRE WAS OUT HOWEVER IT REIGNITED TWICE BY THE BURNING WOOD IN THE HOUSE, FLASHING THE TWO FIREMEN BEFORE THEY COULD DRIVE A WOODEN PLUG INTO THE OPEN GAS RISER. GAS MAINTENANCE CREWS WERE NOTIFIED TO CUT SERVICE OFF IN THE SIDEWALK AREA.
2025-03-31 10:13 | NO | NO | NO | 20110233 | 15484 | 2011-07-07 16:04 | SUPPLEMENTAL FINAL | 13783 | NORTHERN STATES POWER CO OF WISCONSIN | 1414 WEST HAMILTON AVE., STE. 3 | EAU CLAIRE | WI | 54702 | 2011-07-01 20:52 |  |  | 2011 | 3311 CITY HEIGHTS RD | ASHLAND | ASHLAND | WI | 54806 | 46.5692 | -90.9178 | [9 empty] | 2011-07-02 09:30 | 981518 |  | NATURAL GAS |  | 8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 8 | 2011-07-01 21:16 |  |  |  | 2011-07-01 21:37 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUM / METER AND REGUALTOR | [9 empty] | OTHER | [8 empty] | LIGHTNING STRIKE DIRECTLY TO GAS METER. | CLASS 3 LOCATION | 50000 | 64750.50916496945 | 1200 | 1554.0122199592668 | 1200 | 1554.0122199592668 | 0 | 0 |  |  | 37 | 28.0621669626998223801065719360568383659 |  | 0 | 52437 | 28130.9285975263303452930728241563055062 | 67886.5957718506834223801065719360568384 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | YES |  |  |  | YES | SEVERE THUNDERSTORM | [213 empty] | RANDY RISEN | PIPELINE COMPLIANCE AND STANDARDS CONSULTANT | randy.s.risen@xcelenergy.com | 715-737-1595 | 715-7372611 |  |  |  | BRIAN AMUNDSON | DIRECTOR AREA ENGINEERING AND CONTROL CENTER | 715-737-4645 | brian.d.amundson@xcelenergy.com | DURING A SERVER THUNDERSTORM, LIGHTNING HIT THE RESIDENTIAL GAS METER AT 3311 CITY HEIGHTS RD IN ASHLAND WI. THE GAS METER WAS BLOWN OFF THE METER SET PIPING AND IGNITED THE BLOWING GAS. AS A RESULT OF THE BURNING GAS THE HOME SUSTAINED DAMAGES IN EXCESS OF $50,000. THE FIRE DEPARTMENT, UPON ARRIVAL EXTINGUISHED THE FIRE AND BENT OVER THE RISER PIPING TO ELIMINATE THE BLOWING GAS. ONCE THE NORTHERN STATES POWER COMPANY ON CALL EMERGENCY RESPONDER ARRIVED THE SERVICE WAS DUG AT THE BASE OF THE RISER AND CUT AND CAPPED. A NEW SERVICE AND METER SET WILL BE INSTALLED ONCE THE HOME IS REPAIRED. IT WAS NOT CLEAR UNTIL 8:00 AM THE NEXT MORNING THAT LIGHTNING HIT THE METER SET DIRECTLY CAUSING THE SUBSEQUENT FIRE AND DAMAGE.
2025-03-31 10:13 | YES | NO | NO | 20110235 | 15278 | 2011-07-08 16:02 | ORIGINAL FINAL | 2764 | COOKEVILLE GAS DEPT, CITY OF | 16 N OAK AVENUE | COOKEVILLE | TN | 38501 | 2011-07-04 19:34 |  |  | 2011 | 841 WILLOW VALLEY CT | COOKEVILLE | PUTNAM | TN | 38501 | 36.1451 | -85.5254 | [12 empty] | NATURAL GAS |  | 0.56 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2011-07-04 20:03 |  |  |  | 2011-07-04 20:10 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | RUBBER DIAPHRAGM IN A REGULATOR | [9 empty] | OTHER | [8 empty] | FIRE LOCATED IN A TRASH CONTAINER BESIDE GAS METER/REGULATOR CAUGHT FIRE, THE FIRE THEN CAUSED THE DIAPHRAM TO RUPTURE ALLOWING THE GAS TO ESCAPE TO THE ATMOSPHERE | CLASS 3 LOCATION | 0 | 0 | 100 | 129.5010183299389 | 50 | 64.75050916496945 | 75000 | 97125.763747454175 | ETIMATED COST OF STRUCTURE PER COOKEVILLE FIRE DEPT |  | 5 | 3.79218472468916518650088809946714031972 |  | 0 | 75155 | 40310.5395611232898128774422735346358792 | 97323.8074596737725151865008880994671403 | 0 | 0 | 3 |  |  |  |  | 15 | 15 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | JEFF MILLS | ADMINISTRATIVE AND COMPLIANCE SUPERINTENDENT | jmills@cookeville-tn.org | 9315204427 | 9313728735 |  |  |  | JEFF MILLS | ADMINISTRATIVE AND COMPLIANCE SUPERINTENDENT | 9315204427 | jmills@cookeville-tn.org | OUR LOCAL FIRE DEPT WAS DISPATCHED 7/4/11 TO A FIRE OUTSIDE A RESIDENCE IN A GARBAGE CAN. UPON ARRIVAL THE FIRE DEPT DETERMINED THAT THE FIRE HAD CAUSED THE DIAPHRAGM IN THE GAS REGULATOR (WHICH WAS ADJACENT TO THE GARBAGE) TO RUPTURE AND RELEASE GAS TO THE ATMOSPHERE OUTSIDE. THE SHUT OFF TO THE METER SET WAS IMMEDIATELY SHUT OFF BY FIRE DEPT PERSONNEL AND REMAINING FIRE WAS EXTINQUISHED WITH WATER.OUR PERSONNEL RECEIVED THE NOTIFICATION OF THE SITUATION FROM THE FIRE DEPT AND RESPONDED TO THE SCENE AND MADE OUR INVESTIGATION.
2025-03-31 10:13 | NO | YES | YES | 20110240 | 15442 | 2011-07-12 17:01 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202-1408 | 2011-06-13 11:24 |  |  | 2011 | 2220 LAKE AVE | PUEBLO | PUEBLO | CO | 81004-3819 | 38.2293 | -104.6252 | [9 empty] | 2011-06-13 13:14 | 979532 |  | NATURAL GAS |  | 4.77 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 1 | 2011-06-13 11:24 |  |  |  | 2011-06-13 11:33 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 20 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1955 | [5 empty] | 1 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.133 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 3.3 | 1 |  | CLASS 3 LOCATION | 0 | 0 | 500 | 647.5050916496945 | 3137 | 4062.446945010183293 | 402091 | 520711.939613034622399 | ESTIMATED PUBLIC / PRIVATE PROPERTY DAMAGE THAT OPERATOR IS NOT RESPONSIBLE FOR. |  | 17 | 12.89342806394316163410301953818827708703 |  | 0 | 405745 | 217625.9165852122200297833037300177619893 | 525434.7850777584433536341030195381882771 | 1 | 0 | 0 |  |  |  |  | 11 | 11 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 114600936 | UNCC |  | CONTRACT LOCATOR | YES | YES | 72 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | BILL YENKO | GAS SYSTEMS ENGINEERING MANAGER |  | 303-571-3946 |  |  |  |  | JOHN KARTUS | CLAIMS SERVICES MANAGER AND MANAGING INVESTIGATOR | 303-294-2665 | john.j.kartus@xcelenergy.com | BRIEF DESCRIPTION OF INCIDENT: DAMAGE RESULTED WHEN THIRD PARTY CONTRACTOR SNAGGED GAS SERVICE WITH TRACKHOE WHILE EXCAVATING TRENCH FOR INSTALLATION OF SANITARY SEWER. GAS SERVICE WAS ACCURATELY LOCATED AND MARKED. FOLLOW UP EXCAVATION REVEALED THAT A TRACKHOE PULLED THE SERVICE PIPE WHICH RESULTED IN A CIRCUMFERENTIAL RUPTURE WHERE THE SERVICE PIPE THREADS CONNECTED TO THE BURIED ELBOW NEAR THE BASE OF THE SERVICE RISER. EXISTING SERVICE WAS TERMINATED AT GAS MAIN TAP AND RETIRED; THEREFORE, PART A 13B PIPELINE/FACILITY WAS NOT RESTARTED. NOTE: PART A LINE 16 THE INJURED PARTY WAS EVACUATED FROM THE BUILDING POST INCIDENT. NOTE: PART G3, LINE 13.A WILL NOT ACCEPT THE CORRECT DURATION OF INTERRUPTION WHICH IS 3 OR MORE DAYS (72 HOURS OR MORE).
2025-03-31 10:13 | NO | YES | YES | 20110260 | 15392 | 2011-07-28 10:56 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 800 LASALLE AVENUE, P.O. BOX 59038 | MINNEAPOLIS | MN | 55406 | 2011-06-10 15:45 |  |  | 2011 | RIVERSIDE AND FRANKLIN AVE | MINNEAPOLIS | HENNEPIN | MN | 55406 | 44.9628 | -93.2298 | [9 empty] | 2011-06-10 17:54 | 979316 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | YES | 0 | 2011-06-10 15:45 |  |  |  | 2011-06-10 17:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 60 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1962 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | ABANDONED SECTION OF PIPE CONTAINED GAS. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 2240 | 2900.82281059063136 | 0 | 0 | NONE |  | 0 | 0 |  | 0 | 2240 | 1201.43380855397088 | 2900.82281059063136 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SECTION OF MAIN WAS BEING ABANDONED AND WOULD NOT HAVE BEEN ON SCADA WHEN THE INCIDENT OCCURRED. | [12 empty] | YES | 2 | 0 | YES | 5 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | ABANDONED SECTION OF MAIN WAS NOT EVACUATED OF GAS. |  |  | YES |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | STEVE OLINGER | OPERATIONAL SPECIALIST I | steve.olinger@centerpointenergy.com | 612.321.5453 |  |  |  |  | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 612.321.5366 | dean.headlee@centerpointenergy.com | THE CONTRACTOR, MICHELS PIPELINE, PURGED A 16" GAS MAIN THAT WAS BEING ABANDONED. THERE WERE TWO OPEN ENDS OF AN 8" MAIN THAT TEED OFF THE 16". THE STUB ATTACHED TO THE 16" MAIN WAS SEALED WITH FOAM AND COVERED WITH ELECTRICAL TAPE. A WELDER FROM MICHELS WAS IN THE PROCESS OF WELDING AN END CAP ON THE OTHER END OF THE 8" MAIN. AFTER MAKING HIS INITIAL TACK, THE END OF THE PIPE THAT WAS TAPED AND SEALED WITH FOAM COMBUSTED OUTWARD BLOWING THE FOAM OUT AND BURNING THE MICHELS WELDER.
2025-03-31 10:13 | YES | NO | NO | 20110263 | 15289 | 2011-08-02 13:16 | ORIGINAL | 17360 | RICHMOND, CITY OF | 730 EAST BROAD STREET | RICHMOND | VA | 23219 | 2011-07-17 04:50 |  |  | 2011 | 1413 BOWEN STREET | RICHMOND |  | VA | 23219 | 37.3006 | -77.2618 | [9 empty] | 2011-07-17 06:40 | 982932 |  | NATURAL GAS |  | 6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-07-17 04:50 |  |  |  | 2011-07-17 05:11 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 20 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 2004 | [5 empty] | 1 | D2513 | YELLOWSTRIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  |  | 3408 | RUPTURE | [6 empty] | 1 | 1 |  | CLASS 3 LOCATION | 0 | 0 | 126 | 163.171283095723014 | 600 | 777.0061099796334 | 0 | 0 |  |  | 29 | 21.99467140319715808170515097690941385435 |  | 0 | 755 | 409.739637814587786689165186500888099467 | 962.172064478553572081705150976909413854 | 0 | 0 | 1 |  |  |  |  | 22 | 22 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CARL V. JAMES | OPERATIONS MANAGER - GAS MAINTENANCE | carl.james@richmondgov.com | 804/646-8341 | 804/646-8399 |  |  |  | CARL V. JAMES | OPERATIONS MANAGER - GAS MAINTENANCE | 804/646-8341 | carl.james@richmondgov.com | THIS IS A FOLLOW-UP TO THE TELEPHONE CALL PLACED ON 7/7/11. INCIDENT REPORT #982932, WHICH OCCURRED AT 1413 BOWEN STREET, RICHMOND, VA. THE INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER AT 06:40 ON SUNDAY, 7/7/11. A FIRE, UNRELATED TO NATURAL GAS, WAS THE PRIMARY CAUSE OF THE INCIDENT. THE TOTAL DAMAGE IS ESTIMATED TO BE MORE THAN $50,000. THE ORIGIN OF THE FIRE HAS NOT BEEN DETERMINED, BUT THE FIRE DEPT. HAS RULED THAT WAS NOT THE INITIATING CAUSE OF THE EVENT. THE CITY OF RICHMOND PERFORMED A SERIES OF TESTS WHICH INCLUDED A LEAK SURVEY OF THE OUTER PERIMETER OF THE BUILDING, BAR HOLE TEST, AND A PRESSURE TEST OF THE GAS SERVICE. DURING THE FIRE, THE RISER, REGULATOR, AND METER WERE DESTROYED, WHICH CAUSED A LEAK ON THE RISER THAT SHOWED UP DURING THE PRESSURE TEST OF THE SERVICE. A TEST OF THE RISER DETERMINED THAT THE FAILURE WAS DUE TO THE HEAT FROM THE FIRE. ALSO, THE CITY OF RICHMOND, DEPARTMENT OF PUBLIC UTILITIES, HAD AN ODOROMETER TEST PERFORMED BY THE SUPERVISOR OF PRESSURE CONTROL AND FOUND THE ODORANT TO BE IN THE ACCEPTABLE RANGE.
2025-03-31 10:13 | NO | NO | NO | 20110269 | 15290 | 2011-08-04 14:34 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2011-07-05 14:24 |  |  | 2011 | 3600 SHAWNEE TRAIL | LAKE WORTH | TARRANT | TX | 76135 | 32.8077 | -97.4425 | [9 empty] | 2011-07-05 16:10 | 981757 |  | NATURAL GAS |  | 98 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2011-07-05 14:24 |  |  |  | 2011-07-05 15:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | EXC. REMOVED PAVEMENT PRIOR TO MIXING | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1984 | [5 empty] | 6 | 11.5 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 1105 |  |  | 2406 | RUPTURE |  |  |  |  | LONGITUDINAL |  | 24 | 5 |  | CLASS 3 LOCATION | 0 | 0 | 18140 | 23491.48472505091646 | 0 | 0 | 0 | 0 |  |  | 750 | 568.827708703374777975133214920071047957 |  | 0 | 18890 | 10255.6673660525286116163410301953818828 | 24060.312433754291237975133214920071048 | 0 | 0 | 6 |  |  |  |  | 29 | 29 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER'S ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT CAUSE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | UNKNOWN/OTHER | MILLING EQUIPMENT | MILLING | NO |  |  |  | UNKNOWN/OTHER | YES | YES | 6 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JEFF JORDAN | OPERATIONS SUPERVISOR | jeffrey.jordan@atmosenergy.com | 817-215-4326 | 817-215-4734 |  |  |  | ANDREW MARSHALL | COMPLIANCE MANAGER | 214-206-2703 | andrew.marshall@atmosenergy.com | EXCAVATOR WAS MIXING QUICKLIME INTO STREET AND STRUCK A 6" MAIN, IGNITING THE GAS AND BURNING UP THE EXCAVATOR'S MIXER. DAMAGE TO MIXER ESTIMATED AT $100,000. EXCAVATOR DID NOT CALL FOR LOCATES, WAS WORKING ON LOCATES MARKED FOR ANOTHER EXCAVATOR.
2025-03-31 10:13 | NO | YES | NO | 20110271 | 15559 | 2011-08-05 08:50 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2011-07-06 13:44 |  |  | 2011 | 135 CRAWFORD STREET | OXFORD | OAKLAND | MI | 48371 | 42.8203 | -83.2616 | [9 empty] | 2011-07-06 16:48 | 981870 |  | NATURAL GAS |  | 40.67 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 24 | 2011-07-06 13:44 |  |  |  | 2011-07-06 14:09 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 8 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1976 | [5 empty] | 1.125 | ASTM D 2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3407 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 4375 | 5665.669551934826875 | 0 | 0 | 100000 | 129501.0183299389 | NOT PAID BY OPERATOR: ESTIMATED COST OF DAMAGE TO THE THIRD PARTY'S EQUIPMENT |  | 374 | 283.655417406749555950266429840142095915 |  | 0 | 104749 | 56244.3861577669532382326820603907637655 | 135450.3432992804764309502664298401420959 | 0 | 0 | 24 |  |  |  |  | 41.7 | 41.7 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | 911 OPERATOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY THIRD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | MILLING EQUIPMENT | MILLING | YES | 11671065 |  |  | CONTRACT LOCATOR | YES | YES | 1 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | SITE GRADING AFTER 1976 INSTALL DAMAGED DURING PAVEMENT REMOVAL | [169 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 | 517-788-1369 |  |  |  | TRACY A. GOBLE | REGULATORY COMPLIANCE MANAGER | 517-768-3187 | tracy.goble@cmsenergy.com | CONTRACTOR ASI PAVING WHILE MILLING A PARKING LOT CUT THROUGH A 1-1/8" PLASTIC MEDIUM PRESSURE GAS SERVICE TO 135 CRAWFORD CAUSING A FIRE AND IGNITING CONTRACTOR'S EQUIPMENT. THE APARTMENT COMPLEX WAS EVACUATED. THERE WERE NO INJURIES. OXFORD FIRE DEPARTMENT RESPONDED TO EXTINGUISH THE FIRE AND PUT IT OUT AT 14:41. GAS FLOW WAS SQUEEZED OFF AT 15:30. ONCE THE DAMAGED EQUIPMENT WAS REMOVED, THE DAMAGED SERVICE WAS REPAIRED AND THE GAS WAS BACK ON AT 00:30. ASI PAVING HAD REQUESTED STAKING, WHICH WAS THEN ACCURATELY PROVIDED. HOWEVER, THE 1-1/8" PLASTIC THAT WAS DAMAGED WAS ONLY 2 INCHES BELOW THE BOTTOM OF THE 6-INCH THICK PAVEMENT BEING REMOVED. THIS MINIMAL DEPTH DID NOT ALLOW ASI TO HAND EXPOSE THE SERVICE TO DETERMINE DEPTH PRIOR TO REMOVING PAVEMENT (THE DAMAGE OCCURRED DURING THE PAVEMENT REMOVAL OPERATION). IT IS SURMISED THAT THE 1-1/8" PLASTIC SERVICE WAS BURIED AT PROPER DEPTH WHEN INSTALLED IN 1976, BUT SUBSEQUENT PARKING AREA GRADING SINCE THE INSTALLATION LIKELY CAUSED THE SERVICE TO BE AT A SHALLOW DEPTH.
2025-03-31 10:13 | NO | NO | NO | 20110278 | 15298 | 2011-08-09 15:16 | ORIGINAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202-1408 | 2011-07-12 08:40 |  |  | 2011 | 800 BLOCK OF S. GARRISON ST | LAKEWOOD | JEFFERSON | CO | 80226 | 39.7 | -105.103 | [9 empty] | 2011-07-12 12:46 | 982461 |  | NATURAL GAS |  | 348.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 8 | 2011-07-12 08:40 |  |  |  | 2011-07-12 08:51 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1963 | [5 empty] | 20 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 5 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 61000 | 78995.621181262729 | 28000 | 36260.285132382892 | 0 | 0 |  |  | 2000 | 1516.873889875666074600355239786856127886 |  | 0 | 91000 | 49138.7368729492981509769094138543516874 | 116772.7802035212870746003552397868561279 | 0 | 0 | 0 |  |  |  |  | 130 | 130 | 150 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE AND NOTIFICATION FROM EMERGENCY RESPONDERS IMMEDIATELY AFTER EVENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 119300224 | UNCC |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | BOB MACIAS | MANAGER GAS EMERGENCY REPAIR | robert.macias@xcelenergy.com | 3035713922 |  |  |  |  | JOHN KARTUS | CLAIMS SERVICES MANAGER | 3032942665 | john.j.kartus@xcelenergy.com | A CONTRACTOR DROPPED A 1 INCH BY 4 FOOT BY 10 FOOT STEEL STREET PLATE ON AN EXPOSED 20'' IP GAS MAIN. THE STEEL PLATE PUNCTURED THE GAS MAIN AND REMAINED LODGED IN THE PIPELINE UNTIL IT WAS TAKEN OUT OF SERVICE.
2025-03-31 10:13 | NO | YES | NO | 20110280 | 15299 | 2011-08-10 10:58 | ORIGINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2011-07-11 15:54 |  |  | 2011 | STRINGTOWN ROAD BETWEEN GATEWAY CENTER DRIVE & I-270 | CLARKSBURG | MONTGOMERY | MD | 20871 | 39.2552 | -77.275 | [9 empty] | 2011-07-11 21:11 | 982398 |  | NATURAL GAS |  | 11339 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-07-11 15:54 |  |  |  | 2011-07-11 16:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 240 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 2002 | [5 empty] | 8 | API5L | UNKNOWN | STEEL |  | SEAMLESS | SEAMLESS | 0.322 | [6 empty] | MECHANICAL PUNCTURE | 2 | 6 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 64000 | 82880.651731160896 | 23500 | 30432.7393075356415 | 0 | 0 |  |  | 53220 | 40364.0142095914742451154529307282415631 |  | 0 | 140720 | 84270.0845231936615674955595026642984014 | 153677.4052482880117451154529307282415631 | 9 | 0 | 1 |  |  |  |  | 215 | 215 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATION DAMAGE | [12 empty] | NO |  |  | YES | 2 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | NATURAL GAS | YES | 11334752 | MISS UTILITY OF MARYLAND |  | CONTRACT LOCATOR | YES | YES |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | T. MICHAEL UPSHAW | SUPERVISOR - DOT PIPELINE SAFETY COMPLIANCE | mupshaw@washgas.com | 703-750-4479 | 703-750-5591 |  |  |  | DAVID W. SPANGLER | MANAGER - DOT PIPELINE SAFETY COMPLIANCE | 703-750-4341 | dspangler@washgas.com | ON MONDAY, JULY 11, 2011, A WASHINGTON GAS CONTRACTOR, UTILITY LINE SERVICES, INC. (ULS), DAMAGED AN EIGHT-INCH, WRAPPED-STEEL, HIGH-PRESSURE MAIN LOCATED ON STRINGTOWN ROAD BETWEEN GATEWAY CENTER DRIVE AND I-270 IN CLARKSBURG, MARYLAND. ULS HAD SEVERAL LOCATE TICKETS FOR THE AREA. THESE TICKET NUMBERS WERE 11334752, 11348536, AND 11353091. ULS HAD BEEN WORKING IN THE AREA FOR SEVERAL MONTHS RELOCATING A SECTION OF MAIN AND WERE EXCAVATING TO ABANDON A PORTION OF MAIN WHEN THE DAMAGE OCCURRED. ULS HAD THE LINES IN QUESTION EXPOSED VIA VACUUM EXCAVATION ON JUNE 23, 2011, AND LATER BACKFILLED THE EXCAVATION. THE DEPTH OF THE DAMAGED LINE WAS 20 FEET. DURING THE PROCESS OF INSTALLING A SLIDE RAIL SHORING SYSTEM ON JULY 11, 2011, ULS WAS USING A TRACKHOE TO DRIVE DOWN A CORNER POST FOR THIS SHORING SYSTEM WHEN THE DAMAGE OCCURRED. I-270 AND STRINGTOWN ROAD WERE CLOSED FOR APPROXIMATELY 6 HOURS AS A RESULT OF THIS DAMAGE. AS OF THE TIME OF THIS REPORT, ULS IS STILL WORKING TO ABANDON THE SECTION OF MAIN. ONCE THIS SECTION HAS BEEN ABANDONED AND GAS IS RESTORED, A SUPPLEMENTAL REPORT WILL BE FILED.
2025-03-31 10:13 | NO | NO | NO | 20110281 | 15301 | 2011-08-11 09:46 | ORIGINAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2011-07-15 11:38 |  |  | 2011 | 7200 DUPONT AVE NORTH | BROOKLYN CENTER | HENNEPIN | MN | 55430 | 45.0844 | -93.2956 | [9 empty] | 2011-07-15 13:00 | 982785 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2011-07-15 11:39 |  |  |  | 2011-07-15 11:51 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1965 | [8 empty] | COPPER | [10 empty] | LEAK |  |  | OTHER | LIGHTNING STRIKE | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 50 | 64.75050916496945 | 825 | 1068.383401221995925 | 0 | 0 |  |  | 0 | 0 |  | 0 | 875 | 469.310081466394875 | 1133.133910386965375 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DUE TO LIGHTNING STRIKE | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [218 empty] | CHRISTE SINGLETON | OPERATIONS SPECIALIST I | christe.singleton@centerpointenergy.com | 612.321.5203 |  |  |  |  | DEAN HEADLEE | MANAGER PIPELINE SAFETY AND COMPLIANCE | 612.321.5366 | dean.headlee@centerpointenergy.com | HOUSE WAS DAMAGED WHEN LIGHTNING STRIKE TRAVELLED FROM A TREE TO THE RISER.
2025-03-31 10:13 | NO | NO | NO | 20110282 | 15302 | 2011-08-11 | ORIGINAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2011-07-15 10:06 |  |  | 2011 | 4110 78 COURT NO | BROOKLYN PARK | HENNEPIN | MN | 55443-3431 | 45.0974 | -93.3341 | [9 empty] | 2011-07-15 11:56 | 982777 |  | NATURAL GAS |  | 4.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 7 | 2011-07-15 10:06 |  |  |  | 2011-07-15 10:50 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1978 | [8 empty] | COPPER | [10 empty] | LEAK |  |  | OTHER | LIGHTNING STRIKE | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 50 | 64.75050916496945 | 800 | 1036.0081466395112 | 0 | 0 |  |  | 21 | 15.92717584369449378330373001776198934281 |  | 0 | 871 | 470.634792155784354085257548845470692718 | 1116.685831648175143783303730017761989343 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NATURAL FORCES FROM LIGHTNING STRIKE | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [218 empty] | CHRISTE SINGLETON | OPERATIONS SPECIALIST I | christe.singleton@centerpointenergy.com | 612.321.5203 |  |  |  |  | DEAN HEADLEE | MANAGER PIPELINE SAFETY AND COMPLIANCE | 612.321.5366 | dean.headlee@centerpointenergy.com | HOUSE AT 4110 78 CT NORTH, BROOKLYN PARK, MINNESOTA WAS STRUCK BY LIGHTNING AND SUBSEQUENT HOUSE FIRE DAMAGED THE GAS METER AND RISER RESULTING IN RELEASE OF GAS.
2025-03-31 10:13 | NO | YES | YES | 20110285 | 16001 | 2011-08-11 12:41 | SUPPLEMENTAL | 18799 | SUPERIOR UTILITIES, CITY OF | 135 W 4TH STREET - PO BOX 160 | SUPERIOR | NE | 68978 | 2011-07-19 12:24 |  |  | 2011 | 320 E 2ND | SUPERIOR | NUCKOLLS | NE | 68978 | 40.0178 | -98.0684 | [9 empty] | 2011-07-19 16:30 | 98390 |  | NATURAL GAS |  | 1024 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES |  |  |  |  | NO | 12 | 2011-07-19 12:24 |  |  |  | 2011-07-19 12:24 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 37 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  |  |  | 0.25 | [6 empty] | OTHER | [8 empty] | FAILURE OF LINE STOPPER. | CLASS 2 LOCATION | 150 | 194.25152749490835 | 45008 | 58285.818329938900112 | 1174 | 1520.341955193482686 | 0 | 0 |  |  | 913 | 692.45293072824156305506216696269982238 |  | 0 | 47245 | 25490.9305820940210854209591474245115453 | 60692.8647433555327110550621669626998224 | 0 | 0 | 0 |  |  |  |  | 1.17 | 1.17 | 1.44 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 5 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | INFLATABLE LINE STOPPER | [71 empty] | LARRY SIBERT | GAS DEPARTMENT FOREMAN | larrysibert@yahoo.com | 402-879-4750 | 402-879-4752 |  |  |  | LARRY SIBERT | GAS DEPARTMENT FOREMAN | 402-879-4750 | larrysibert@yahoo.com | THIS IS A CONDENSED SUMMARY OF THE EVENTS. THIS NARRATIVE WILL TRUNCATE DUE TO SPACE CONSIDERATIONS. FOR THE FULL REPORT, SEE THE COMPLETE ATTACHMENT SUBMITTED ORIGINALLY. ON JULY 11, 2011 OPERATIONS WERE BEGAN TO ABANDON A SEGMENT OF 6' PIPING, OPERATING AT 18 OUNCES OF PRESSURE, FROM WITHIN THE SYSTEM. AN INFLATABLE BAG WAS INSERTED INTO THE 6' MAIN AND INFLATED TO STOP GAS FLOW TO DOWNSTREAM PIPING. THE DOWNSTREAM PIPING WAS PURGED OF GAS AND GAS FLOW WAS CONFIRMED STOPPED AT 10:25 AM. A SEGMENT OF PIPING WAS REMOVED DOWNSTREAM OF THE STOP POINT AND PREPARATION BEGAN TO SEAL THE END OF PIPE. AT APPROXIMATELY 12:20 PM. THERE WAS A FAILURE OF THE INFLATABLE LINE STOPPER, A RELEASE OF NATURAL GAS AND INSTANTANEOUS IGNITION OF THAT NATURAL GAS. UPON IGNITION, THE GAS DEPARTMENT EMPLOYEE SAFELY EXITED THE EXCAVATION AS A SECOND EMPLOYEE ATTEMPTED TO EXTINGUISH THE FIRE. EMERGENCY OPERATIONS BEGAN AND GAS FLOW WAS STOPPED AND 6' PIPING SEALED BY 3:00 PM. THIS RELEASE OF NATURAL GAS AND SUBSEQUENT FIRE DAMAGED EXCAVATOR EQUIPMENT AND LOCAL UTILITY FACILITIES IN THE AREA. THIS FIRE NECESSITATED THE SHUTDOWN OF PART OF THE ELECTRICAL POWER SYSTEM.
2025-03-31 10:13 | NO | YES | YES | 20110287 | 15306 | 2011-08-11 17:14 | ORIGINAL FINAL | 20211 | ATMOS ENERGY CORPORATION - KY/MID-STATES (MID-STATES) | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2011-05-20 08:30 |  |  | 2011 | ALGONQUIN ST AND IRQUOIS ST | MORRISTOWN | HAMBLEN | TN | 37814 | 36.1234 | -83.1679 | [9 empty] | 2011-05-20 10:30 | 976868 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2011-05-20 08:36 |  |  |  | 2011-05-20 08:48 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 4 |  | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | PRIVATELY OWNED |  | MAIN | [7 empty] | 2 | PE 2406 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 500 | 647.5050916496945 | 0 | 0 | 0 | 0 | 0 |  | 50 | 37.92184724689165186500888099467140319716 |  | 0 | 550 | 303.257118361411128774422735346358792185 | 685.426938896586151865008880994671403197 | 0 | 0 | 0 |  |  |  |  | 25 | 25 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | CITY STREET | [12 empty] | MUNICIPALITY | UNKNOWN/OTHER | ROAD WORK | NO |  |  |  | DATA NOT COLLECTED | NO | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JACK SANDERS | MGR. COMPLIANCE | jack.sanders@atmosenergy.com | 615 771-8387 |  |  |  |  | JACK SANDERS | MGR. COMPLIANCE | 615 771-8387 | jack.sanders@atmosenergy.com | MUNICIPALITY CUTTING ROAD WITH CONCRETE SAW DAMAGED 2 INCH PE GAS LINE.
2025-03-31 10:13 | NO | NO | NO | 20110307 | 15310 | 2011-08-24 14:56 | ORIGINAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2011-07-31 08:14 |  |  | 2011 | 44534 VIRGO ROAD | GARRISON | CROW WING | MN | 56450 | 46.1929 | -93.7613 | [9 empty] | 2011-07-31 10:14 | 984423 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2011-07-31 08:20 |  |  |  | 2011-07-31 09:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1995 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 2025-05-08 |  |  | 418 | OTHER | [8 empty] | THE RISER WAS BURNING; THE PLASTIC ON THE ANODELSS RISER MELTED DUE TO THE HOUSE FIRE. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 320 | 414.40325865580448 | 0 | 0 |  |  | 0 | 0 |  | 0 | 320 | 171.63340122199584 | 414.40325865580448 | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO ACTIVE GAS SERVICE TO THE HOME. THE GAS METER HAD BEEN REMOVED AND THE RISER LOCKED. THE ASSISTANT FIRE CHIEF STATED THAT THERE WAS A REPORT OF A MINOR NATIVE AMERICAN RUNNING FROM THE SCENE BETWEEN 6:00 AM AND 6:30 AM. ADDITIONALLY, OUR FIRE INVESTIGATOR WAS REQUESTED TO LEAVE THE SCENE OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | CHRISTE SINGLETON | OPERATIONS SPECIALIST I | christe.singleton@centerpointenergy.com | 612.321.5203 | 612.321.5279 |  |  |  | DEAN HEADLEE | MANAGER PIPELINE SAFETY AND COMPLIANCE | 612.321.5366 | dean.headlee@centerpointenergy.com | WE WERE REQUESTED TO RESPOND TO A FULLY ENGULFED HOUSE FIRE BY MILLE LACS COUNTY. FOUND RISER ON FIRE BECAUSE THE PLASTIC ON THE ANODELESS RISER MELTED DUE TO THE HOUSE FIRE. GAS SERVICE TO THE ADDRESS HAD BEEN SHUT OFF AT THE CUSTOMER'S REQUEST ON MARCH 17, 2004. CENTERPOINT ENERGERY REMOVED THE METER DUE TO INACTIVITY AND THE HOUSE BEING BOARDED UP ON OCTOBER 13, 2005.
2025-03-31 10:13 | NO | YES | NO | 20110318 | 15311 | 2011-08-30 16:03 | ORIGINAL FINAL | 11032 | LACLEDE GAS CO | 720 OLIVE STREET | ST. LOUIS | MO | 63101 | 2011-08-01 16:50 |  |  | 2011 | BIG TIMBER LANE AT MILL SPRING COURT | CHESTERFIELD | ST. LOUIS | MO | 63017 | 38.6363 | -90.5305 | [9 empty] | 2011-08-02 12:20 | 984661 |  | NATURAL GAS |  | 87 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-08-01 16:50 |  |  |  | 2011-08-01 17:36 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 37 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1978 | [5 empty] | 4 | ASTM D2513 | PLEXO (PHILLIPS RESIN TR 418) | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | MECHANICAL PUNCTURE | 4.5 | 1.8 | [7 empty] | CLASS 3 LOCATION | 2400 | 3108.0244399185336 | 137258 | 177750.507739307535362 | 2000 | 2590.020366598778 | 0 | 0 |  |  | 568 | 430.79218472468916518650088809946714032 |  | 0 | 142226 | 76377.3965875998502088774422735346358792 | 183879.3447305495361271865008880994671403 | 0 | 0 | 259 |  |  |  |  | 17.5 | 18 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM PRESSURE WAS WITHIN NORMAL OPERATING RANGE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | ESCAPING WATER AT HIGH PRESSURE FROM NEARBY WATER MAIN BREAK SCOURED A HOLE IN THE PLASTIC GAS MAIN. | [154 empty] | MARK D. LAUBER | SUPERINTENDENT MAINTENANCE ENGINEERING | mlauber@lacledegas.com | 314-658-5413 | 314-535-5075 |  |  |  | CRAIG R. HOEFERLIN | ASSISTANT VP ENGINEERING AND FIELD SERVICES | 314-658-5410 | choeferlin@lacledegas.com | WATER ESCAPING AT HIGH PRESSURE THROUGH A HOLE IN A 6" DIAMETER WATER MAIN SCOURED A LARGE OVAL SHAPED HOLE IN A 4" PLASTIC GAS MAIN. ACCORDING TO INFORMATION OBTAINED FROM THE WATER COMPANY WATER SYSTEM PRESSURE WAS BETWEEN 160 AND 170 PSI AT THAT LOCATION AT THE TIME. THE TWO MAINS CROSS EACH OTHER AT THIS INTERSECTION.
2025-03-31 10:13 | NO | YES | YES | 20110320 | 15312 | 2011-08-31 16:47 | ORIGINAL FINAL | 12778 | MORGANFIELD GAS SYSTEM, CITY OF | 526 N COURT ST526 N COURT ST | MORGANFIELD | KY | 42437 | 2011-08-16 11:05 |  |  | 2011 | 231 MULBERRY ST | UNIONTOWN | UNION | KY | 42461 | 37.7726 | -87.9343 | [9 empty] | 2011-08-16 12:00 | 986132 |  | NATURAL GAS |  | 3.85 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2011-08-16 11:14 |  |  |  | 2011-08-16 11:14 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | 1984 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | GAS RISER HIT BY A BUSHHOG | CLASS 4 LOCATION | 0 | 0 | 200 | 259.0020366598778 | 0 | 0 | 0 | 0 |  |  | 47 | 35.64653641207815275310834813499111900533 |  | 0 | 247 | 140.246008978667471047957371225577264654 | 294.648573071955952753108348134991119005 | 0 | 0 | 0 |  |  |  |  | 42 | 42 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LES PIPER | ASSIST SUPERINTENDANT | lpiper8215@yahoo.com | (270)389-2186 | (270)389-2187 |  |  |  | LES PIPER | ASSIST SUPERINTENDANT | (272)389-2186 | lpiper8215@yahoo.com | ON 8/16/11 THE GAS DEPARTMENT GOT A CALL AT 11:09 THAT A GAS LINE HAD HIT BY TRACTOR&BUSHOG AT 231 MULBERRY ST UNIONTOWN .AT 11:15 THE MORGANFIELD GAS DEPARTMENT ARRIVED ON SCENE .ONCE ON SCENE WE GOT THE GAS LEAK STOPPED AT 11:19 .AFTER INVESTIGATING THE SCENE WE FOUND OUT THAT A TRAILOR AND BEEN MOVED LEAVING THE GAS METER &RISER ON THE LOT ,THE GRASS GROWED UP AROUND IT THE LAND OWNER WAS MOWING AND FORGOT IT WAS THERE AND HIT WHILE MOWING CAUSING IT TO IGNITE BURNING TRACTOR AND HIMSELF WERE HE STAYED THE NIGHT IN THE HOSPITAL AND RELEASED THE NEXT DAY .THE LINE WAS TERMINATED AT THE MAIN THAT AFTERNOON
2025-03-31 10:13 | NO | NO | NO | 20110326 | 15313 | 2011-09-07 16:29 | ORIGINAL | 2812 | CORPUS CHRISTI, CITY OF - GAS DIV | 4225 SOUTH PORT AVENUE | CORPUS CHRISTI | TX | 78415 | 2011-08-05 09:00 |  |  | 2011 | 900 BLK LIPAN | CORPUS CHRISTI | NUECES | TX | 78401 | 27.7953 | -97.3997 | [9 empty] | 2011-08-05 12:00 | 985039 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-08-05 09:00 |  |  |  | 2011-08-05 09:10 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 27 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 3 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 373 | 483.038798370672097 | 200 | 259.0020366598778 | 0 | 0 |  |  | 50 | 37.92184724689165186500888099467140319716 |  | 0 | 623 | 342.410988015178929774422735346358792185 | 779.962682277441548865008880994671403197 | 0 | 0 | 0 |  |  |  |  | 10 | 10 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | NO |  |  |  | UTILITY OWNER | UNKNOWN/OTHER |  |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JESSE CANTU | PETROLEUM SUPERINTENDENT | jessecantu@cctexas.com | (361)885-6941 | (361)853-3200 |  |  |  | DEBORAH A. MARROQUIN | DIRECTOR OF GAS SERVICES | (361)885-6924 | debbiem@cctexas.com | THE EXCAVATOR WAS IN THE PROCESS OF INSTALLING STORM DRAIN PIPES IN THE ROADWAY ALONG LIPAN STREET WHEN A 3" STUB OUT WAS STRUCK RESULTING IN A GAS RELEASE. THE WORK WAS BEING CONDUCTED TO RECONSTRUCT THE INFRASTRUCTURE THAT WAS DAMAGED AS A RESULT OF A WATER LEAK. THE LEAK WAS STOPPED AT 10:20AM AND PERMANENT REPAIRS WERE THEN COMPLETED ON AUGUST 5, 2011. THE EXCAVATOR DID NOT PRODUCE A VALID LINE LOCATE TICKET REQUEST FOR THE EXCAVATION THAT TOOK PLACE FOR THE INSTALLATION OF THE STORM DRAIN.
2025-03-31 10:13 | NO | YES | NO | 20110327 | 15314 | 2011-09-07 16:38 | ORIGINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2011-08-10 11:10 |  |  | 2011 | WOODLAKE RD | ALBANY | ALBANY | NY | 12203 | 42.6792 | -73.8465 | [9 empty] | 2011-08-11 12:35 | 985628 |  | NATURAL GAS |  | 7495 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 20 | [6 empty] | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1967 | [5 empty] | 12 | API 5L GRADE B | UNKNOWN | STEEL |  | OTHER | ERW | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 7 | 6.3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 33000 | 42735.336048879837 | 7000 | 9065.071283095723 | 12000 | 15540.122199592668 | 2A. THIRD PARTY CONTRACTOR PERFORMED ALL EXCAVATING AND RESTORATION. |  | 36000 | 27303.730017761989342806394316163410302 |  | 0 | 88000 | 53147.976544045016717584369449378330373 | 94644.259549330217342806394316163410302 | 0 | 0 | 0 |  |  |  |  | 220 | 220 | 225 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CLEARLY CAUSED BY 3RD PARTY EXCAVATION. CONTROL ROOM OPERATORS NOT INVOLVED WITH DIG SAFE MARKOUTS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET |  |  | YES | YES | [8 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 808115004600 | YES, DIG SAFELY NEW YORK. |  | CONTRACT LOCATOR | NO | YES | 118 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | DEBORAH DEBERGALIS | MANAGER UPSTATE DISPATCH AND SCHEDULING | deborah.debergalis@us.ngrid.com | 315-460-2615 |  |  |  |  | DEBORAH DEBERGALIS | MANAGER UPSTATE DISPATCH AND SCHEDULING | 315-460-2615 | deborah.debergalis@us.ngrid.com | THIRD PARTY CONTRACTOR WAS EXCAVATING SEWER TO MAKE REPAIRS CAUSED BY PREVIOUS EXCAVATING DAMAGE CAUSED BY SAME CONTRACTOR. CONTRACTOR CALLED DIG SAFE REQUESTING MARK-OUT FOR PIPELINE FACILITIES IN AREA. DIG SAFE ISSUED TICKET, NATIONAL GRID RECEIVED TICKET, NATIONAL GRID LOCATORS WERE IN THE PROCESS OF LOCATING FACILITIES, BUT HAD NOT YET COMPLETED MARK-OUTS. CONTRACTOR COMMENCED EXCAVATION ACTIVITIES 24 HOURS IN ADVANCE OF FIRST ALLOWABLE EXCAVATION DATE. CONTRACTOR SUBSEQUENTLY WAS ISSUED A CITATION BY NEW YORK STATE PUBLIC SERVICE COMMISSION RELATED TO INSUFFICIENT NOTIFICATION. EXCAVATOR PUNCTURED 12 INCH STEEL PIPELINE OPERATING AT 220 PSIG. APPROXIMATELY 20 RESIDENTS WERE EVACUATED BY FIRE OFFICIALS. NATIONAL GRID PERSONNEL CONTROLLED THE ESCAPING GAS BY CLOSING ISOLATING VALVES ON EITHER SIDE OF DAMAGED SECTION. NO CUSTOMER INTERRUPTIONS RESULTED, ALTHOUGH DAMAGED SECTION OF PIPELINE WAS REMOVED FROM SERVICE. ESCAPING GAS DID NOT IGNITE OR EXPLODE. THERE WERE NO INJURIES REQUIRING HOSPITALIZATION. ESCAPING GAS WAS CONTROLLED WITHIN 1 HOUR OF NOTIFICATION.
2025-03-31 10:13 | NO | NO | NO | 20110338 | 15316 | 2011-09-12 18:02 | ORIGINAL | 2812 | CORPUS CHRISTI, CITY OF - GAS DIV | 4225 SOUTH PORT AVENUE | CORPUS CHRISTI | TX | 78415 | 2011-08-11 17:34 |  |  | 2011 | 5821 SARATOGA | CORPUS CHRISTI | NUECES | TX | 78414 | 27.6827 | -97.3795 | [12 empty] | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-08-11 17:34 |  |  |  | 2011-08-11 18:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 2 | ASTM 2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 500 | 647.5050916496945 | 200 | 259.0020366598778 | 0 | 0 |  |  | 50 | 37.92184724689165186500888099467140319716 |  | 0 | 750 | 410.527994125158528774422735346358792185 | 944.428975556463951865008880994671403197 | 0 | 0 | 0 |  |  |  |  | 10 | 10 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | TRENCHER | TELECOMMUNICATIONS | YES | 112206582 | TESS |  | UTILITY OWNER | YES |  |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | JESSE M. CANTU JR | PETROLEUM SUPERINTENDENT | jessecantu@cctexas.com | (361)885-6941 | (361)853-3200 |  |  |  | DEBORAH A. MARROQUIN | DIRECTOR OF GAS SERVICES | (361)885-6924 | debbiem@cctexas.com | THE LINE LOCATOR MARKED AND FLAGGED THE 2" MAIN BUT FAILED TO LOCATE A 2" SERVICE LINE RESULTING IN THE EXCAVATOR STRIKING THE SERVICE LINE. THE SERVICE LINE WAS IN ACTIVE AT THE TIME OF THE INCIDENT. PERMANENT REPAIRS WERE MADE BY REPLACING THE DAMAGED SECTION.
2025-03-31 10:13 | NO | YES | YES | 20110348 | 30722 | 2011-09-16 17:03 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2011-08-18 15:10 |  |  | 2011 | 8163 DORSETT STREET APT. 5A | DOUGLASVILLE | DOUGLAS | GA | 30134 | 33.7557 | -84.7295 | [9 empty] | 2011-08-18 17:25 | 986433 |  | NATURAL GAS |  | 80 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 50 | 2011-08-18 15:12 |  |  |  | 2011-08-18 15:37 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1987 | [5 empty] | 1.25 | ASTM D2513 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | LEAK |  |  | OTHER | CRACKED CAP ON SERVICE TEE | [5 empty] | CLASS 3 LOCATION | 350000 | 453253.56415478615 | 3000 | 3885.030549898167 | 7074 | 9160.902036659877786 | 0 | 0 |  |  | 400 | 303.374777975133214920071047957371225577 |  | 0 | 360474 | 193407.9060303942475681953818827708703375 | 466602.8715193193280009200710479573712256 | 0 | 0 | 5 |  |  |  |  | 58 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | [197 empty] | THREADED CONNECTION FAILURE | [12 empty] | OTHER | CRACKED CAP ON PLASTIC SERVICE TEE | [69 empty] | RALPH T. MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R. LONN | DIRECTOR - COMPLIANCE AND PRM | (404) 584-3552 | rlonn@southernco.com | A 1-1/4 INCH CAP ON A PLEXCO PE SERVICE TEE CRACKED CAUSING NATURAL GAS TO LEAK AND MIGRATE TO THE BUILDING WALL OF AN APARTMENT BUILDING. THE CAP WAS APPROXIMATELY 10 FEET OFF THE BUILDING WALL. AT SOME POINT AFTER THE INSTALLATION, THE PROPERTY OWNER HAD CONCRETE PATIOS POURED ADJACENT TO THE BUILDING AND OVER THE SERVICE TEES. THE PROPERTY OWNER ALSO HAD VINYL SIDING INSTALLED TO THE EXTERIOR OF THE TOWNHOMES. THE SIDING COVERED THE GAP BETWEEN THE CONCRETE PATIOS AND THE BUILDING'S FOUNDATION SLAB WHICH PREVENTED MIGRATING GAS FROM VENTING TO THE ATMOSPHERE. THE ESCAPING GAS MIGRATED INTO THE TOWNHOUSE AND IGNITED WHEN THE MAINTENANCE MAN ADJUSTED THE THERMOSTAT WHEN RESPONDING TO A REPORT OF AN ODOR OF NATURAL GAS IN THE STRUCTURE. THE MAINTENANCE MAN WAS INJURED REQUIRING HOSPITALIZATION AS PART OF THE INCIDENT. THE PIPELINE SEGMENT SUPPLYING GAS TO THE APARTMENT BUILDING WAS SHUT DOWN AS A RESULT OF THE INCIDENT WHERE PIPING WITHIN THE APARTMENT COMPLEX HAS SINCE BEEN REPLACED WITH NEW POLYETHYLENE (PE) PLASTIC ON 9/10/2012.
2025-03-31 10:13 | NO | NO | NO | 20110357 | 15570 | 2011-09-22 11:06 | SUPPLEMENTAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2011-05-16 12:35 |  |  | 2011 | 4TH ST. AND 3RD AVE. | ODESSA | LINCOLN | WA | 99159 | 47.3326 | -118.6851 | [9 empty] | 2011-08-25 16:50 | 987277 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-05-16 12:38 |  |  |  | 2011-05-16 14:10 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1979 | [5 empty] | 0.5 | ASTM D 2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 7 |  |  | 2406 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 65332 | 84605.605295315682148 | 11168 | 14462.673727087576352 | 2500 | 3237.5254582484725 | 0 | 0 |  |  | 0 | 0 |  | 0 | 79000 | 42371.995926680223 | 102305.804480651731 | 0 | 0 | 1 |  |  |  |  | 35 | 35 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [28 empty] | YES |  | YES | [9 empty] | YES |  |  |  | OTHER | CRACK IN 1970'S VINTAGE ALDYL A PIPE | NO | [86 empty] | WILLIAM D. BAKER | GAS TRAINING AND CODES COORDINATOR | william.baker@avistacorp.com | 509-495-4894 | 509-495-8810 |  |  |  | JODY MOREHOUSE | MANAGER OF GAS COMPLIANCE | 509-495-2760 | jody.morehouse@avistacorp.com | THIS WAS REPORTED WHEN THE ACCUMULATED PROPERTY RESTORATION COSTS AND COMBINED REPAIR COSTS EXCEEDED $50,000. RESTORATION OF PROPERTY DAMAGE WAS DUE TO MIGRATION OF GAS TO SEVERAL PROPERTY OWNERS WHICH RESULTED IN YARD AND TREE DAMAGE OVER TIME. TO CLOSE OUT THIS REPORT IT IS BEING SUBMITTED AS A SUPPLEMENTAL/FINAL. THERE IS NO NEW INFORMATION FOR THIS REPORT. 12/27/12
2025-03-31 10:13 | NO | YES | NO | 20110364 | 15576 | 2011-09-26 18:09 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD. NE, STE. 20 | ALBUQUERQUE | NM | 87109 | 2011-08-31 15:42 |  |  | 2011 | CHURCH ST. & W. BROADWAY AVE. | BLOOMFIELD | SAN JUAN | NM | 87413 | 36.7112 | -107.9925 | [9 empty] | 2011-08-31 16:42 | 988033 |  | NATURAL GAS |  | 691 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1200 | 2011-08-31 15:42 |  |  |  | 2011-08-31 15:43 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 98 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1966 | [5 empty] | 4 | API 5L B | UNKNOWN | STEEL |  |  |  | 0.141 | [6 empty] | MECHANICAL PUNCTURE | 5 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 8350 | 10813.33503054989815 | 15890 | 20577.71181262729121 | 145000 | 187776.476578411405 | A TRACKHOE WAS BURNED IN ADDITION TO TELEPHONE AND TELEVISION CABLE FACILITIES. |  | 3695 | 2802.42451154529307282415630550621669627 |  | 0 | 172935 | 93365.0218208390001464298401420959147425 | 221969.9479331338874328241563055062166963 | 1 | 0 | 0 |  |  |  |  | 57 | 57 | 57 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | YES | [7 empty] | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 2011360494 | NEW MEXICO ONE-CALL |  | UTILITY OWNER | YES | YES | 376 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | GARY G. ROYBAL | MANAGER | gary.roybal@nmgco.com | 505-697-3636 | 505-697-4481 |  |  |  | ED KACER | SR. DIRECTOR ENGINEERING AND OPERATIONS SUPPORT | 505-697-3303 | ed.kacer@nmgco.com | LARGE CONSTRUCTION CONTRACTOR WORKING ON SANITARY AND STORM SEWER PROJECT WAS EXCAVATING WITH A TRACKHOE NEAR THE COMPANY'S PIPELINE. THE COMPANY LOCATED AND MARKED THE LOCATION OF ITS PIPELINE PRIOR TO EXCAVATION. THE CONTRACTOR DID NOT EXPOSE THE PIPELINE AS REQUIRED BY STATE LAW. THE CONTRACTOR WAS EXCAVATING CLOSE TO THE PIPELINE AND HIT AND PUNCTURED THE PIPELINE. ESCAPING GAS IGNITED WHICH BURNED THE TRACKHOE AND SEVERAL PIECES OF SMALL EQUIPMENT AROUND THE EXCAVATION AREA. THERE WERE NO INJURIES OR DEATHS. ONLY 1 CUSTOMER'S (GOVERNMENT BUILDING) SERVICE WAS INTERRUPTED DUE TO THE INCIDENT. THE CUSTOMER'S GAS USE WAS FOR A WATER HEATER. THE PIPELINE WAS PINCHED UPSTREAM OF THE CUSTOMER'S SERVICE LINE CAUSING THE INTERRUPTION. THE CUSTOMER'S SERVICE WAS RESTORED ON SEPTEMBER 16, 2011.
2025-03-31 10:13 | NO | YES | NO | 20110367 | 15324 | 2011-09-28 15:02 | ORIGINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2011-08-29 06:45 |  |  | 2011 | 1518 LINCOLN AVENUE | POMPTON LAKES | PASSAIC COUNTY | NJ | 07442 | 40.9845 | -74.2834 | [9 empty] | 2011-08-29 10:00 | 987580 |  | NATURAL GAS |  | 114.42 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2011-08-29 07:00 |  |  |  | 2011-08-29 07:06 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1964 | [5 empty] | 0.75 | ASTM A53 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  |  |  |  | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PSE&G WAS PRESENTLY ONSITE FOR MAJOR FLOODING DUE TO HURRICANE IRENE. |  | 76582 | 58082.6181172291296625222024866785079929 |  | 0 | 76582 | 53729.8223801065719360568383658969804618 | 58082.6181172291296625222024866785079929 | 0 | 0 | 450 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | MEDIA, INCIDENT OCCURED IN A INACCESSABLE AREA OF HURRICANE IRENE'S FLOOD ZONE. |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | FOUNDATION COLLAPSE DUE TO HEAVY FLOODING. | YES | YES | [217 empty] | CHRIS LAROSSA | PRICIPAL - REGULATORY | christopher.larossa@pseg.com | 973-896-7617 |  |  |  |  | JORGE CARDENAS |  | 973-430-5100 | No Email Address | AT APPROXIMATELY 7 AM, AUGUST 29, 2011 PUBLIC SERVICE ELECTRIC AND GAS (PSE&G) LEARNED ABOUT A GAS EXPLOSION AT 1518 LINCOLN AVENUE, POMPTON LAKES, NEW JERSEY THROUGH LOCAL MEDIA OUTLETS. THE INCIDENT OCCURRED IN AN AREA THAT WAS IMPACTED BY HISTORIC FLOODING DUE TO RAINFALL FROM HURRICANE IRENE. THE AREA WAS INACCESSIABLE TO BOTH EMERGENCY RESPONDERS AND PSE&G CREWS AT THE TIME OF THE INCIDENT. AN INVESTGATION THAT TOOK PLACE AFTER FLOOD WATER RECEDED FOUND THAT THE FOUNDATION OF THE HOME AT 1518 LINCOLN AVENUE COLLAPED DUE TO STRESS FROM SURROUNDING FLOOD WATERS. AS A RESULT OF THE FOUNDATION COLLAPSE THE HOMES 3/4 - INCH STEEL GAS SERVICE RUPTURED JUST INSIDE THE FOUNDATION WALL.
2025-03-31 10:13 | NO | YES | YES | 20110368 | 15325 | 2011-09-30 14:59 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-09-27 11:00 |  |  | 2011 | INTERSECTION OF PELL PL AND BEECHMONT PL | NEW ROCHELLE | WESTCHESTER | NY | 10804-4512 | 40.9274 | -73.7795 | [9 empty] | 2011-09-28 08:30 | 991036 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | NO |  |  |  |  | NO | 0 | 2011-09-27 11:00 |  |  |  | 2011-09-27 11:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2011 | [5 empty] | 3 | UNKNOWN | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | UNKNOWN | OTHER | [8 empty] | NO RELEASE OF NATURAL GAS. MAIN WAS SHUTDOWN EARLIER IN THE DAY AS PART OF A PLANNED MAIN INSERTION. | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NA |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | WHILE ATTEMPTING TO INSERT A 4" CAST IRON MAIN WITH 3" POLYETHELENE PIPE, THE INSERTION PROCESS STOPPED DUE TO A SUSPECTED BLOCKAGE IN THE 4" CAST IRON. THE CONTRACTOR EMPLOYEE ENTERE THE EXCAVATION AT THE POINT OF INSERTION AND WHILE INVESTIGATING THE POINT OF INSERTION, THE POLYETHELENE PIPE SHIFTED AND STRUCK THE CONTRACTOR CAUSING AN INJURY. | [47 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON SEPTEMBER 27, 2011 AT 1100 HRS, PETMAR CONSTRUCTION LABORER, JESUS BECERRA AGE 49, INJURED HIS CHIN WHILE ASSIGNED TO A GAS MAIN INSERTION. WHILE PERSONNEL ON LOCATION WERE ATTEMPTING TO INSERT 3" LOW PRESSURE POLYETHELENE (LPPE) PIPING IN A 4" LOW PRESSURE CAST IRON SLEEVE, THE 3" LPPE BECAME STUCK. MR. BECERRA ENTERED THE EXCAVATION AND THE 3" LPPE WHICH WAS PARTIALLY INSERTED, MOVED AND STRUCK MR. BECERRA KNOCKING HIM BACKWARDS. THE NEW ROCHELLE FIRE DEPARTMENT WAS NOTIFIED AND RESPONDED. THE CONTRACTOR EMPLOYEE WAS TRANSPORTED TO SOUND SHORE HOSPITAL VIA EMS. MR. BUCERRA WAS ADMITTED TO THE HOSPITAL FOR OBSERVATION OVERNIGHT AND WAS RELEASED FROM SOUND SHORE HOSPITAL THE NEXT DAY, SEPTEMBER 28, 2011 AT 1640 HRS. THE NYS PUBLIC SERVICE COMMISION AND THE US DEPT. OF TRANSPORTATION, VIA THE NATIONAL RESPONSE CENTER, WERE NOTIFIED. THIS WAS A SERIOUS LEVEL INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20110369 | 15584 | 2011-09-30 19:00 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2011-08-31 12:00 |  |  | 2011 | 20299 NORTHWEST SQUARE | CUPERTINO | SANTA CLARA | CA | 95014 | 37.337 | -122.0289 | [9 empty] | 2011-08-31 16:06 | 988036 |  | NATURAL GAS |  | 120 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 5 | 2011-08-31 12:34 |  |  |  | 2011-08-31 12:34 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1973 | [5 empty] | 2 | ASTM D2513 | DU PONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.27 |  | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 600000 | 777006.1099796334 | 2000 | 2590.020366598778 | 5000 | 6475.050916496945 | 0 | 0 |  |  | 5000 | 3792.184724689165186500888099467140319716 |  | 0 | 612000 | 329075.1008381776218774422735346358792185 | 789863.3659874182881865008880994671403197 | 0 | 0 | 7 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | EMPLOYEE SAW SMOKE AND INVESTIGATED |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [10 empty] | SERVICE OR MAIN TEE |  | DUPONT |  | OTHER | MATERIALS JOINED: 1ST PLASTIC, 2ND PLASTIC | [15 empty] | YES | [9 empty] | YES |  |  |  | OTHER | SLOW CRACK GROWTH DRIVEN BY SYSTEM PRESSURE | NO | [86 empty] | CHERYL DIZON | GAS COMPLIANCE ENGINEER | c1dz@pge.com | 9249744378 |  |  |  |  | LAURENCE DENISTON | ACTING MANAGER REGULATORY COMPLIANCE | 9259744313 | lcd1@pge.com | ON AUGUST 31, 2011, AT 1228 HOURS, PG&E WAS NOTIFIED BY THE LOCAL FIRE DEPARTMENT OF A FIRE AT 20299 NORTHWEST SQUARE IN CUPERTINO. AROUND THIS SAME TIME, A PG&E GAS SERVICE REPRESENTATIVE (GSR) OBSERVED SMOKE WHILE DRIVING NEARBY AND WENT TO THE SCENE. THE GSR OBSERVED A HOUSE STRUCTURE ON FIRE AS WELL AS FLAMES IN THE LANDSCAPE AREA IN FRONT OF THE HOUSE. THE HOMEOWNER INDICATED SHE NOTICED THE SMELL OF GAS AT APPROXIMATELY 0800 HOURS THAT MORNING BUT DID NOT THINK MUCH ABOUT IT AND LEFT HER RESIDENCE AT APPROXIMATELY 1130 HOURS. THE HOMEOWNER DID NOT NOTIFY PG&E OF THE OBSERVED SMELL OF GAS. A GAS CONSTRUCTION CREW ARRIVED AT APPROXIMATELY 1251 HOURS, AND THE FLOW OF GAS WAS STOPPED BY EXCAVATING AND SQUEEZING THE PLASTIC MAIN AT THREE LOCATIONS. GAS SERVICE WAS INTERRUPTED TO SEVEN CUSTOMERS. SERVICE TO ONE AFFECTED RESIDENCE WAS RESTORED WHEN STRUCTURE REPAIRS WERE COMPLETED. SERVICE TO THE REMAINING SIX CUSTOMERS WERE RESTORED BY 1400 HOURS ON SEPTEMBER 1, 2011. EXCAVATION OF THE PLASTIC GAS DISTRIBUTION MAIN REVEALED A CRACK IN A 2-INCH ALDYL A PLASTIC TEE, WHICH WAS THE SOURCE OF THE GAS LEAK. THE TEE FAILED AS A RESULT OF STRESS RISERS FORMED IN THE TEE MATERIAL FROM THE STEPWISE INCREASE IN WALL THICKNESS WHERE THE COUPLING AND SERVICE PIPE FIRST BOND. THE FRACTURE PROPOGATED BY SLOW CRACK GROWTH DRIVEN BY THE SYSTEM PRESSURE. GAS FROM THE LEAKING TEE MIGRATED UNDERGROUND TO THE GARAGE OF THE RESIDENCE AND CAUGHT FIRE FROM THE PILOT LIGHT OF THE FURNACE IN THE GARAGE. PG&E CONDUCTED LEAK SURVEYS AT THE 422 TOWNHOUSE COMPLEX WHERE 20299 NORTHWEST SQUARE IS LOCATED IN APRIL AND MAY OF 2011. A REVIEW OF THE LEAK SURVEY RECORDS DID NOT REVEAL ANY ISSUES AT THIS RESIDENCE, ALTHOUGH THERE WERE LEAKS DETECTED IN OTHER AREAS OF THE COMPLEX. LEAK SURVEYS WERE CONDUCTED FOLLOWING THE INCIDENT, AND SIX LEAKS WERE IDENTIFIED AND REPAIRED THROUGHOUT THE COMPLEX. THERE WERE NO INJURIES OR FATALITIES. HOWEVER, DAMAGE TO THE HOUSE STRUCTURE EXCEEDS $50,000, MAKING THIS INCIDENT REPORTABLE. IN ADDITION, MAJOR BAY AREA TV MEDIA WAS ON THE SCENE.
2025-03-31 10:13 | NO | NO | NO | 20110370 | 15982 | 2011-10-04 12:17 | SUPPLEMENTAL FINAL | 11713 | KEYSPAN ENERGY DELIVERY - LONG ISLAND | 175 E. OLD COUNTRY ROAD | HICKSVILLE | NY | 11801 | 2011-09-06 01:44 |  |  | 2011 | 150 LINCOLN STREET | ELMONT | NASSAU | NY | 11003 | 40.7035 | -73.7008 | [9 empty] | 2011-09-06 10:59 | 988544 |  | NATURAL GAS |  | 50 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 15 | 2011-09-06 01:45 |  |  |  | 2011-09-06 01:58 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | NO INDICATION OF NATIONALGRID FACILITIES INVOLVED | UNKNOWN | [8 empty] | OTHER | NO INDICATION OF NATIONALGRID FACILITIES | [9 empty] | OTHER | [8 empty] | NO INDICATION OF NATIONALGRID FACILITIES INVOLVED IN THE INCIDENT | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 5000 | 6475.050916496945 | 4000 | 5180.040733197556 | MISCELLANEOUS COSTS FOR TESTING, REPORTING, ETC. |  | 250 | 189.609236234458259325044404973357015986 |  | 0 | 9250 | 5002.589054128846143872113676731793960924 | 11844.700885928959259325044404973357016 | 0 | 0 | 3 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS LOCALIZED TO A SINGLE RESIDENCE AND NOT A SYSTEM ISSUE. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | THE METER HEADER FROM THE HOUSE WAS TAKEN INTO CUSTODY BY THE NASSAU COUNTY FIRE MARSHALL. IT IS STILL IN THEIR POSSESSION. THE SERVICE TO HOUSE 150 LINCOLN STREET WAS RETIRED. NO NOTIFICATION OR REQUEST FOR INFORMATION HAS BEEN RECEIVED FROM THE NASSAU COUNTY FIRE MARSHALL. | [47 empty] | KIM GEHM | MANAGER LONG ISLAND GAS DISPATCH AND SCHEDULE | kim.gehm@nationalgrid.com | 516-545-2524 | 516-545-4193 |  |  |  | KIM GEHM | MANAGER LONG ISLAND GAS DISPATCH AND SCHEDULE | 516-545-2524 | kim.gehm@nationalgrid.com | AT 0144, NATIONAL GRID RESPONDED TO A REPORTED DISTURBANCE AT 150 LINCOLN STREET, ELMONT. UPON ARRIVAL AT 0158, THE CMS RESPONDER FOUND THAT THERE WAS EXTENSIVE DAMAGE TO 150 LINCOLN STREET AND THE TWO HOMES ON EACH SIDE OF THAT LOCATION. NATIONAL GRID CONDUCTED A LEAK SURVEY OF THE AREA AND A CHECK OF THE SERVICE HISTORY FOR THE RESIDENCE AND FOUND NOTHING THAT WOULD HAVE CONTRIBUTED TO THE INCIDENT. THE METER HEADER FROM THE HOUSE WAS TAKEN INTO CUSTODY BY THE NASSAU COUNTY FIRE MARSHALL. THE METER HEADER WAS NEVER RETURNED. THE SERVICE TO HOUSE 150 LINCOLN STREET WAS RETIRED. NO NOTIFICATION OR REQUEST FOR INFORMATION HAS BEEN RECEIVED FROM THE NASSAU COUNTY FIRE MARSHALL. NO CLAIMS HAVE BEEN RECEIVED. OUR FILE IN THIS MATTER HAS BEEN CLOSED.
2025-03-31 10:13 | NO | YES | YES | 20110371 | 15332 | 2011-10-06 12:13 | SUPPLEMENTAL FINAL | 19520 | TOMBALL GAS DEPT, CITY OF | 501 JAMES ST | TOMBALL | TX | 77375 | 2011-09-17 02:45 |  |  | 2011 | 28100 SH 249 | TOMBALL | HARRIS | TX | 77375 | 30.0818 | -95.6305 | [12 empty] | NATURAL GAS |  |  |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2011-09-17 02:51 |  |  |  | 2011-09-17 03:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | 2008 | [8 empty] | OTHER | 1 INCH RISER | [9 empty] | OTHER | [8 empty] | THE VEHICLE BROKE THE VALVE OFF OF THE RISER | CLASS 3 LOCATION | 5000 | 6475.050916496945 | 600 | 777.0061099796334 | 200 | 259.0020366598778 | 1000 | 1295.010183299389 | STOP SIGN BULLARDS |  | 50 | 37.92184724689165186500888099467140319716 |  | 0 | 6850 | 3682.289704919454228774422735346358792185 | 8843.991093682736851865008880994671403197 | 1 | 0 | 0 |  |  |  |  | 28 | 28 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | TOBY WEDGMAN | NATURAL GAS FOREMAN | twedgman@ci.tomball.tx.us | 281-290-1432 | 281-351-4735 |  |  |  | TOBY WEDGMAN | NATURAL GAS FOREMAN | 281-290-1432 | No Email Address | UNIT #2 WAS TRAVELING SOUTH BOUND IN THE #3 LANE (INSIDE LANE). UNIT #1 WAS TRAVELING SOUTH BOUND IN THE #1 LANE (OUTSIDE), ACCELERATED AND CHANGED LANES INTO THE #2 LANE ( CENTER LANE) AND TRAVEVELLED INTO THE #3 LANE, STRICKING UNIT #2. UNIT 1 THEN LOSING CONTROL AND CROSSED BACK OVER THE SOUTH BOUND LANES AND STRUCK UNIT #3, WHICH WAS STOPPED AT THE STOP SIGN AT HIRSCHFEILD AND SH 249. BOTH UNITS THEN CAUGHT FIRE DUE TO A NATURAL GAS METER THAT WAS DAMAGED . THE DRIVER OF UNIT #3 WAS KILLED
2025-03-31 10:13 | NO | NO | NO | 20110372 | 15330 | 2011-10-07 16:24 | ORIGINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2011-09-08 12:45 |  |  | 2011 | LOCK #9 / ROUTE 5S AREA | ROTTERDAM JUNCTION | SCHENECTADY | NY | 12150 | 42.877 | -74.0433 | [9 empty] | 2011-09-09 19:25 | 989070 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 423 | 2011-09-08 12:45 |  |  |  | 2011-09-08 12:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | YES | YES | UNCASED | [9 empty] | PRIVATELY OWNED |  | MAIN |  | 1997 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | OTHER | [8 empty] | TBD IN SUPPLEMENTAL REPORT. | CLASS 2 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TBD |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 5 | 1 | 417 |  |  |  |  | 10 | 99 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FLOOD TOOK OUT BRIDGE AND PIPE ON THE BRIDGE. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  | YES | [216 empty] | DEBORAH DEBERGALIS | MANAGER UPSTATE DISPATCH AND SCHEDULING | deborah.debergalis@us.ngrid.com | 315-460-2615 | 315-460-2762 |  |  |  | DEBORAH DEBERGALIS | MANAGER UPSTATE DISPATCH AND SCHEDULING | 315-460-2615 | deborah.debergalis@us.ngrid.com
2025-03-31 10:13 | NO | NO | NO | 20110373 | 15333 | 2011-10-18 15:13 | ORIGINAL FINAL | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2011-09-25 23:50 |  |  | 2011 | 1467 TERRACE STREET | MUSKEGON | MUSKEGON | MI | 49442-5015 | 43.2259 | -86.238 | [9 empty] | 2011-09-26 01:43 | 990777 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2011-09-25 23:50 |  |  |  | 2011-09-26 00:03 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1994 | [8 empty] | OTHER | ALUMINUM METER CASE | [9 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 52000 | 67340.529531568228 | 103 | 133.386048879837067 | 1665 | 2156.191955193482685 | 500 | 647.5050916496945 | SERVICE LINE CUT OFF AT MAIN; SERVICE, SERVICE RISER & METER ASSEMBLY ABANDONED |  | 1 | 0.7584369449378330373001776198934280639432 |  | 0 | 54269 | 29107.5810283142603685754884547069271758 | 70278.3710642361800850373001776198934281 | 0 | 0 | 1 |  |  |  |  | 49 | 49 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JOHN F KENYON | CODES FIELD CONSULTANT | kenyonj@dteenergy.com | 616.632.2744 | 616.632.2687 |  |  |  | JOHN D LUEDERS | CODES AND STANDARDS SUPERVISOR | 616.632.2646 | luedersj@dteenergy.com | ON SUNDAY SEPTEMBER 25, 2011 AT APPROXIMATELY 11:40 PM A VEHICLE BACKING INTO A DRIVEWAY RAN OFF THE PAVEMENT AND STRUCK THE OUTSIDE METER ASEMBLY AT 1467 TERRACE STREET. AT 11:50 PM MICHCON RECEIVED A REPORT OF A STRUCTURE FIRE AT 1457 TERRACE; THE CORRECT ADDRESS WAS DETERMINED TO BE 1467 TERRACE. THE LOCAL FIRE DEPARTMENT REQUESTED THE GAS TO BE SHUT OFF TO ENABLE FIREFIGHTING OPERATIONS. GAS SERVICE WAS TERMINATED AT APPROXIMATELY 1:54 AM ON SEPTEMBER 26, 2011 BY A MICHCON CREW EXCAVATING THE 5/8-INCH OD HIGH DENSITY POLYETHYLENE PLASTIC SERVICE LINE NEAR THE MAIN TAP, PINCHING THE PLASTIC TUBING, AND CUTTING AND CAPPING THE SERVICE LINE. THE METER ASSEMBLY WAS DESTROYED IN THE FIRE AND WAS NOT RECOVERED. SUBSEQUENT INVESTIGATION REVEALED THAT THE CAUSE OF THE STRUCTURE FIRE WAS LIKELY THE IMPACT OF THE VEHICLE ON THE OUTSIDE METER ASSEMBLY, APPARENTLY BREAKING THE METER AND OTHER COMPONENTS, AND CAUSING A GAS LEAK. NATURAL GAS LEAKING FROM THE METER ASSEMBLY WAS IGNITED BY AN UNKNOWN SOURCE AND WAS FOUND BURNING AT THE SOUTH WALL OF THE HOUSE. THE OCCUPANTS OF THE HOUSE ESCAPED WITHOUT INJURY. THE TWO-STORY HOME AT 1467 TERRACE STREET SUSTAINED MAJOR FIRE DAMAGE TO THE STRUCTURE AND CONTENTS.
2025-03-31 10:13 | NO | YES | YES | 20110375 | 15588 | 2011-10-25 13:51 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2011-09-26 06:16 |  |  | 2011 | 12312 5TH AVE NE | SEATTLE | KING | WA | 98125 | 47.7183 | -122.3227 | [9 empty] | 2011-09-26 09:51 | 990833 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | YES | [7 empty] | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE | [7 empty] | 0.75 | UNKNOWN |  | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | LEAK |  |  | OTHER | [6 empty] | CLASS 3 LOCATION | 400000 | 518004.0733197556 | 1000 | 1295.010183299389 | 100000 | 129501.0183299389 | 10000 | 12950.10183299389 | INVESTIGATION AND CLAIMS HANDLING |  | 500 | 379.218472468916518650088809946714031972 |  | 0 | 511500 | 274427.8868658950332877442273534635879218 | 662129.422138456695518650088809946714032 | 0 | 0 | 3 |  |  |  |  | 42 | 42 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 9 | 0 | YES | 12 | 0 | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | ANTOINETTE IMAD | CONSULTING ENGINEER | antoinette.imad@pse.com | 425 456 2970 | 425 462 3770 |  |  |  | CHERYL A. MCGRATH | MANAGER COMPLIANCE AND REGULATORY AUDITS - GAS | 425-462-3207 | cheryl.mcgrath@pse.com | THIS INCIDENT IS THE RESULT OF AN ELECTRICAL ARCING PROCESS INITIATED BY ELECTRICITY FROM A DOWNED POWER LINE.A REPORT ISSUED ON DECEMBER 26, 2012 BY THE WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION, PREPARED AFTER ITS INVESTIGATION, HAS A NARRATIVE DESCRIPTION OF THIS INCIDENT. THIS REPORT IS AVAILABLE AT HTTP://WWW.UTC.WA.GOV/DOCS/PAGES/RECORDSCENTER.ASPX UNDER DOCKET PG-111723.
2025-03-31 10:13 | NO | NO | NO | 20110376 | 15336 | 2011-10-26 16:28 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2011-10-05 05:27 |  |  | 2011 | 12611 LACEY BLVD | HANFORD | KINGS | CA | 93230 | 36.328 | -119.684 | [9 empty] | 2011-10-05 11:20 | 991690 |  | NATURAL GAS |  | 39 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2011-10-05 05:27 |  |  |  | 2011-10-05 05:38 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1966 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | ELECTRICAL ARCING FROM ELECTRIC EQUIPMENT PUT HOLE IN GAS SERVICE 1.5" X .75" | CLASS 3 LOCATION | 75000 | 97125.763747454175 | 1500 | 1942.5152749490835 | 200 | 259.0020366598778 | 0 | 0 |  |  | 250 | 189.609236234458259325044404973357015986 |  | 0 | 76950 | 41313.7805001573410438721136767317939609 | 99516.890295297594559325044404973357016 | 0 | 0 | 1 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | W. JEFF KOSKIE | PIPELINE SAFETY ADVISOR | wkoskie@semprautilities.com | 213-305-8660 | 213-244-8155 |  |  |  | W. JEFF KOSKIE | PIPELINE SAFETY ADVISOR | 213-305-8660 | wkoskie@semprautilities.com | APPARENT ELECTRIC TRANSFORMER FAILURE SENT ELECTRICITY DOWN ONTO CUSTOMER HOUSELINE. ELECTRICITY ARCED FROM HOUSELINE ONTO GAS SERVICE, BURNING HOLE AND ALLOWING DISTRICT PRESSURE TO ENTER HOUSELINE WHICH CAUSED A FIRE/EXPLOSION IN AN ADJACENT BUILDING.. LEAK REPAIRED, FACILITY TEMPORARLIY ABANDONED PENDING REBUILDING OF STRUCTURE. NO INJURIES.
2025-03-31 10:13 | NO | YES | YES | 20110377 | 15540 | 2011-11-03 23:01 | SUPPLEMENTAL FINAL | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2011-10-04 13:00 |  |  | 2011 | 456 MORAN | GROSSE POINTE FARMS | WAYNE | MI | 48236 | 42.4079 | -82.9124 | [9 empty] | 2011-10-04 15:08 | 991604 |  | NATURAL GAS |  |  |  | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-10-04 13:00 |  |  |  | 2011-10-04 13:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1928 | [5 empty] | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | RUPTURE |  |  |  |  | OTHER | 2 HOLES IN BOTTOM OF CAST IRON MAIN APPROXIMATELY THE SIZE OF A SOFTBALL. |  |  |  | CLASS 3 LOCATION | 0 | 0 | 7500 | 9712.5763747454175 | 0 | 0 | 0 | 0 |  |  | 200 | 151.687388987566607460035523978685612789 |  | 0 | 7700 | 4162.977556948698015097690941385435168739 | 9864.263763732984107460035523978685612789 | 0 | 0 | 0 |  |  |  |  | 5 | 5 | 5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | OTHER | GRAPHITIC LOCALIZED CORROSION | [5 empty] | YES | GRAPHITIZATION |  |  |  | YES |  |  | YES | NO |  | NO | NO | [8 empty] | NO | NONE | [21 empty] | 2011-01-18 | NO | [227 empty] | ROBERT FRECKELTON | MANAGER - CODES AND STANDARDS | freckeltonr@dteenergy.com | 313-389-7755 | 313-389-7757 |  |  |  | ROBERT FRECKELTON | MANAGER - CODES AND STANDARDS | 313-389-7755 | freckeltonr@dteenergy.com | ON OCTOBER 4, 2011, A GAS LEAK REPAIR ORDER FOR THE ADDRESS OF 456 MORAN IN GROSSE POINTE FARMS, WAYNE COUNTY, MI WAS ASSIGNED TO A TWO PERSON CREW. THE CREW CONSISTED OF A DISTRIBUTION GENERAL FITTER AND A SERVICE TECHNICIAN. THE CREW EXCAVATED AND EXPOSED A 6-INCH CAST IRON DISTRIBUTION MAIN OPERATING AT 5 PSIG. THE DISTRIBUTION GENERAL FITTER, WHILE WEARING A SUPPLIED AIR-RESPIRATOR, PREPARED THE CAST IRON MAIN FOR INSTALLATION OF A 6-INCH BY 9-INCHES IN LENGTH PIPE REPAIR CLAMP. THE DISTRIBUTION GENERAL FITTER INSTALLED THE CLAMP AND TIGHTENED THE BOLTS TO STOP THE LEAK. THE DISTRIBUTION GENERAL FITTER REMOVED THE SUPPLIED AIR-RESPIRATOR FOR UNKNOWN REASONS. THEREAFTER, HE PROCEEDED TO FINISH TIGHTENING THE BOLTS AND SOAP CHECK THE PIPE TO VERIFY THAT THE LEAK WAS STOPPED. AT THAT TIME, THE SERVICE TECHNICIAN LEFT THE TOP OF THE EXCAVATION AND WENT TO THE TRUCK TO RETRIEVE COATING FOR THE REPAIR CLAMP WHEN HE HEARD THE SOUND OF GAS BLOWING FROM THE EXCAVATION. THE SERVICE TECHNICIAN IMMEDIATELY RETURNED TO THE EXCAVATION AND FOUND THE DISTRIBUTION GENERAL FITTER KNEELING FACE DOWN OVER THE GAS MAIN AND UNRESPONSIVE TO VERBAL COMMANDS. THE SERVICE TECHNICIAN ATTEMPTED TO RETRIEVE THE DISTRIBUTION GENERAL FITTER FROM THE EXCAVATION BUT WAS UNABLE TO DO SO AND CALLED 911. GROSSE POINTE FARMS POLICE AND EMS PERSONNEL RESPONDED TO THE SCENE AND PULLED THE DISTRIBUTION GENERAL FITTER FROM THE EXCAVATION; HE WAS TRANSFERRED TO ST. JOHN'S HOSPITAL IN DETROIT, MI WHERE HE WAS PRONOUNCED DEAD. A SECOND REPAIR CREW WAS CALLED IN TO REPAIR THE GAS MAIN FOLLOWING THE INCIDENT AND INSTALLED A 6-INCH BY 12-INCHES IN LENGTH REPAIR CLAMP ADJACENT TO THE FIRST REPAIR CLAMP; HOWEVER THE CLAMP FURTHER CRUSHED THE CORRODED/WEAKENED PIPE. BOTH REPAIR CLAMPS WERE REMOVED AND A 6-INCH BY 30-INCHES IN LENGTH REPAIR CLAMP WAS INSTALLED TO REPAIR THE LEAK. ON NOVEMBER 1, 2011, THE PIPE WAS REMOVED AND RECOVERED FOR EXAMINATION AND A METALLURGICAL ANALYSIS BY A THIRD PARTY LABORATORY. THE ANALYSIS CONCLUDED THAT LOCALIZED GRAPHITIC CORROSION WEAKENED THE FRACTURED PIECES OF PIPE THAT WERE CRUSHED WHEN TIGHTENING THE REPAIR CLAMPS.
2025-03-31 10:13 | NO | YES | NO | 20110378 | 15341 | 2011-11-04 09:55 | ORIGINAL | 1640 | BOSTON GAS CO | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2010-01-15 09:06 |  |  | 2010 | 47 CHESTNUT STREET | WALTHAM | MIDDLESEX | MA | 02451 | 42.3688 | -71.2392 | [9 empty] | 2010-01-15 14:00 | 928688 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 20 | 2010-01-15 09:06 |  |  |  | 2010-01-15 09:06 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2002 | [8 empty] | STEEL | [10 empty] | LEAK |  |  | OTHER | [6 empty] | CLASS 3 LOCATION | 500000 | 660554.747558695 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 500000 | 273581.965510077 | 660554.747558695 | 0 | 0 | 4 |  |  |  |  | 0.33 | 0.5 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | METER TECHNICIAN WAS IN PROCESS OF PERFORMING METER CHANGE WHEN FLASH FIRE OCCUR | [12 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | METER TECHNICIAN WAS IN PROCESS OF PERFOMING METER CHANGE WHEN FLASH FIRE OCCURRED |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | CHRISTOPHER S ARONSON | SENIOR COUNSEL | christopher.aronson@us.ngrid.com | 7819071854 | 7819075701 |  |  |  | CHRISTOPHER ARONSON | SENIOR COUNSEL | 7819071854 | christopher.aronson@us.ngrid.com
2025-03-31 10:13 | NO | YES | YES | 20110379 | 15342 | 2011-11-04 10:03 | ORIGINAL FINAL | 1640 | BOSTON GAS CO | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2010-01-25 18:06 |  |  | 2010 | 22 MANNING STREET | READING | MIDDLESEX | MA | 01867 | 42.5268 | -71.094 | [9 empty] | 2010-01-25 21:00 | 929643 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 3 | 2010-01-25 18:06 |  |  |  | 2010-01-25 18:37 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1930 | [5 empty] | 6 | UNKNOWN |  | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 250000 | 330277.3737793475 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 250000 | 136790.9827550385 | 330277.3737793475 | 0 | 0 | 4 |  |  |  |  | 1.8 | 1.8 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOT APPLICABLE SINCE THIS WAS LEAK CAUSED BY CRACK ON SINGLE MAIN | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | NO | [218 empty] | CHRISTOPHER S ARONSON | SENIOR COUNSEL | christopher.aronson@us.ngrid.com | 7819071854 | 7819075701 |  |  |  | CHRISTOPHER S ARONSON | SENIOR COUNSEL | 7819071854 | christopher.aronson@us.ngrid.com
2025-03-31 10:13 | NO | YES | NO | 20110381 | 15349 | 2011-11-16 14:37 | ORIGINAL FINAL | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ONE ENERGY PLAZA | DETROIT | MI | 48226 | 2011-10-17 10:15 |  |  | 2011 | COLLINDALE DISTRICT REGULATING STATION | GRAND RAPIDS | KENT | MI | 49504 | 42.963 | -85.7349 | [9 empty] | 2011-10-17 20:13 | 992840 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-10-17 10:15 |  |  |  | 2011-10-17 10:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 84 |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1971 | [8 empty] | OTHER | STEEL,COPPER,PLASTIC SERVICES AND MAINS | [9 empty] | OTHER | [8 empty] | NO RELEASE - THIS INCIDENT RESULTED FROM THE ACCIDENTAL INTRODUCTION OF A AIR/GAS MIXTURE INTO A DISTRIBUTION SYSTEM, RESULTING IN SERVICE OUTAGES. THERE WAS NO RELEASE. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 664451 | 860470.811303462320439 | 1356 | 1756.033808553971484 | CUSTOMER APPLIANCE REPAIRS PERFORMED BY DEALERS OTHER THAN MICHCON. |  | 0 | 0 |  | 0 | 665807 | 357108.499898166825759 | 862226.845112016291923 | 70 | 0 | 1300 |  |  |  |  | 10 | 10 | 10 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | WRITTEN PROCEDURE DID NOT RECOGNIZE AN AIR/GAS MIXTURE WAS IN THE PIPELINE BEING DEPRESSURIZED. AIR/GAS MIXTURE WAS INTRODUCED INTO DISTRIBUTION SYSTEM, CAUSING OUTAGES. | YES |  |  |  |  | COMMISSIONING | NO | [50 empty] | JOHN F KENYON | REGIONAL CODES CONSULTANT | kenyonj@dteenergy.com | 616.632.2744 | 616.632.2687 |  |  |  | JOHN D LUEDERS PE | SUPERVISING ENGINEER | 616.632.2646 | luedersj@dteenergy.com | ON OCTOBER 17, 2011, BEGINNING AT APPROXIMATELY 8:45 AM, MICHCON TECHNICIANS EXECUTED A PRESSURE REDUCTION PROCEDURE TO FACILITATE THE CONNECTION OF A NEWLY-CONSTRUCTED REGULATING STATION AT COLLINDALE AVENUE ALONG MICHCON'S 22-INCH SOUTH GRAND RAPIDS 238 PSIG PIPELINE. THE PURPOSE OF THE PROCEDURE WAS TO DISPOSE OF A BUILD-UP OF NATURAL GAS (DETERMINED LATER TO HAVE ACTUALLY BEEN A MIXTURE OR AIR AND GAS) IN THE 22-INCH PIPELINE BY TRANSFERRING IT AT 10 PSIG INTO MICHCON'S GRAND RAPIDS/WALKER DISTRIBUTION SYSTEM RATHER THAN RELEASING IT TO THE ATMOSPHERE AND FLARING (BURNING) THE GAS. THE PROCEDURE WAS EXECUTED PRECISELY AS WRITTEN AND APPROVED BY MICHCON ENGINEERING. AT APPROXIMATELY 10:15 AM, WHILE THE PRESSURE REDUCTION PROCEDURE WAS STILL IN PROGRESS, MICHCON BEGAN TO RECEIVE "NO-GAS" REPORTS FROM CUSTOMERS SERVED BY THE SURROUNDING 10 PSIG DISTRIBUTION SYSTEM. AT APPROXIMATELY 11:00 AM, MICHCON PERSONNEL REALIZED THERE HAD BEEN AN AIR AND GAS MIXTURE IN THE 22-INCH PIPELINE, RATHER THAN GAS. PRESSURE REDUCTION OPERATIONS WERE HALTED IMMEDIATELY. MICHCON ENGINEERING AND OPERATIONS PERSONNEL IMMEDIATELY CONVENED TO DETERMINE THE EXTENT OF THE AFFECTED AREA AND THE SOURCE OF THE AIR/GAS MIXTURE. MICHCON DETERMINED THAT APPROXIMATELY 5500 CUSTOMERS OVER AN AREA OF ABOUT 10 SQUARE MILES COULD ULTIMATELY BE AFFECTED. HOWEVER, BETWEEN THE INITIAL OUTAGE REPORTS AT 10:15 AM AND THE EARLY AFTERNOON OF OCTOBER 17, THERE WERE ONLY ABOUT 100 "NO-GAS" REPORTS. THIS NUMBER GREW TO APPROXIMATELY 350 OUTAGE REPORTS BY 8 PM AS CUSTOMERS RETURNED HOME AT THE END OF THE DAY. AT 8 PM MICHCON MANAGEMENT DECLARED THIS A "SIGNIFICANT EVENT" AND A TELEPHONIC REPORT WAS MADE TO THE NATIONAL RESPONSE CENTER. CREWS WERE MOBILIZED FROM MICHCON REGIONS ACROSS THE STATE OF MICHIGAN TO MAKE A DOOR-TO-DOOR INVESTIGATION OF EVERY CUSTOMER PREMISES IN THE AFFECTED AREA TO ENSURE THAT GAS SERVICE WAS BEING RESTORED AND THAT ALL APPLIANCES WERE OPERATING PROPERLY. MICHCON ENGINEERS DEVELOPED A PLAN TO SYSTEMATICALLY PURGE THE AIR/GAS MIXTURE FROM THE 10 PSIG DISTRIBUTION SYSTEM, AND INDIVIDUAL SERVICE LINES WERE PURGED OF THE AIR/GAS MIXTURE WHEREVER IT WAS FOUND. BY FRIDAY, OCTOBER 21, 2011, EVERY CUSTOMER HAD EITHER BEEN CONTACTED OR THEIR PREMISES WERE ENTERED WITH THE ASSISTANCE OF LAW ENFORCEMENT AND LOCKSMITHS TO CONFIRM THAT GAS SERVICE HAD BEEN RESTORED. THERE WERE NO FIRES, EXPLOSIONS, OR INJURIES REPORTED AS A RESULT OF THIS EVENT. MICHCON HAS DETERMINED THE FORMATION OF THE AIR/GAS MIXTURE INSIDE THE 2.5-MILE SECTION OF THE 22-INCH 238 PSIG PIPELINE BEGAN ALMOST IMMEDIATELY AFTER THE SEGMENT WAS TAKEN OUT OF SERVICE DURING AUGUST 2011. THE 22-INCH PIPELINE HAD BEEN SHUT IN BETWEEN MICHCON'S SOUTH GRAND RAPIDS GATE STATION TO THE WEST AND THE NEW COLLINDALE REGULATING STATION ON THE EAST END OF THE 22-INCH PIPELINE SEGMENT. THE 2.5-MILE SECTION OF PIPELINE HAD BEEN EVACUATED AND PURGED OF GAS, THEN CAPPED OFF AT THE COLLINDALE REGULATING STATION SITE WHILE CONSTRUCTION OF THE STATION WAS COMPLETED. A 22-INCH BLOCK VALVE AT THE SOUTH GRAND RAPIDS GATE STATION THAT WAS USED TO ISOLATE THE WEST END OF THE 2.5-MILE SECTION OF 22-INCH PIPELINE ALLOWED GAS TO SLOWLY BLEED PAST THE VALVE SEAT, MIXING WITH THE AIR LEFT IN THE PURGED SECTION OF 22-INCH PIPELINE DURING THE PERIOD BETWEEN AUGUST AND OCTOBER 2011. THE MICHCON ENGINEER WHO DEVELOPED THE WRITTEN PROCEDURE FOR OCTOBER 17 RECOGNIZED THAT THE GAS BLEEDING THROUGH THE 22-INCH BLOCK VALVE WAS CREATING A PRESSURE BUILD-UP, BUT FAILED TO RECOGNIZE THIS WOULD CREATE AN AIR/GAS MIXTURE THAT WOULD BE UNFIT FOR DISTRIBUTION TO CUSTOMERS. MICHCON HAS DETERMINED APPROXIMATELY 136,000 CUBIC FEET OF AN AIR/GAS MIXTURE HAD ACCUMULATED IN THE 2.5-MILE SECTION OF 22-INCH PIPELINE. A SIGNIFICANT PORTION OF THIS MIXTURE WAS INTRODUCED INTO THE SURROUNDING 10 PSIG DISTRIBUTION SYSTEM DURING THE PROCEDURE EXECUTED ON OCTOBER 17, 2011, RESULTING IN THE CUSTOMER OUTAGES.
2025-03-31 10:13 | NO | YES | YES | 20110382 | 15865 | 2011-11-18 16:50 | SUPPLEMENTAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2011-09-13 12:25 |  |  | 2011 | 1988 SE LUND AVE | PORT ORCHARD | KITSAP | WA | 98366-5525 | 47.519 | -122.6256 | [9 empty] | 2011-09-13 13:51 | 989522 |  | NATURAL GAS |  | 49.2 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 1 | 2011-09-13 12:29 |  |  |  | 2011-09-13 12:40 |  | NO | PRIVATE PROPERTY | TRANSITION AREA | OTHER | BROKE FITTING BELOW METER STOP |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1987 | [8 empty] | STEEL |  | OTHER | COLD ROLLED | 0.113 | [6 empty] | OTHER | [8 empty] | VEHICLE HIT METER AT SUBSTANTIAL SPEED, SEVERING METER FROM RISER JUST BELOW METER STOP | CLASS 4 LOCATION | 57370 | 74294.73421588594693 | 387 | 501.168940936863543 | 955 | 1236.734725050916495 | 145 | 187.776476578411405 | SALES TAX |  | 344 | 260.902309058614564831261101243339253996 |  | 0 | 59201 | 31809.5595853244568949680284191829484902 | 76481.316667510752937831261101243339254 | 0 | 0 | 1 |  |  |  |  | 59 | 59 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | PATTI CHARTREY | PIPELINE SAFETY SPECIALIST | patti.chartrey@cngc.com | 206 225 8510 | 360 377 2091 |  |  |  | TINA BEACH | MGR STANDARDS AND COMPLIANCE | 206 445 4121 | tina.beach@cngc.com | ON 9/13/2011 AT 12:29 911 KITSAP COUNTY NOTIFIED CASCADE NATURAL GAS CORP. (CNGC) OF A CAR CRASH INTO A HOME CAUSING A STRUCTURE FIRE. THE VEHICLE SEVERED THE GAS RISER AT THE THREADS BELOW THE METER STOP WHICH CAUSED THE GAS TO BLOW WIDE OPEN AT 59 PSIG ON THE UNDERSIDE OF THE VEHICLE TRIGGERING IGNITION OF THE GAS AND BURNING THE VEHICLE AND HOME. NO ONE WAS IN THE HOME AND BYSTANDERS EXTRACTED THE DRIVER FROM THE VEHICLE AND HE WAS TRANSPORTED TO HARRISON GENERAL HOSPITAL WITH NON LIFE THREATENING INJURIES. AT 13:40 THE FLOW OF GAS WAS STOPPED.
2025-03-31 10:13 | NO | NO | NO | 20110384 | 15352 | 2011-11-21 16:52 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-10-29 17:45 |  |  | 2011 | 189 CLEVELAND DRIVE | CROTON | WESTCHESTER | NY | 10520-2422 | 41.2115 | -73.8757 | [9 empty] | 2011-10-29 17:54 | 993959 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-10-29 17:45 |  |  |  | 2011-10-29 18:07 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 29 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1959 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | ORIGINALLY REPORTED AS ELECTRIC BURNED THROUGH GAS MAIN. | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 200 | 259.0020366598778 | 0 | 0 |  |  | 0 | 0 |  | 0 | 200 | 107.2708757637474 | 259.0020366598778 | 0 | 0 | 0 |  |  |  |  | 59 | 60 | 90 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | ORIGINAL REPORT INDICATED OVERHEAD ELECTRIC WIRES FELL AND IGNITED THE GAS MAIN. THE INVESTIGATION REVEALED NO GAS LEAK, NO GAS IGNITION. | [47 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER--GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | **THIS REPORT IS FOR RECORD PURPOSE ONLY. NO GAS IGNITION*** ON SATURDAY OCTOBER 29, 2011 THE CROTON FIRE DEPARTMENT REPORTED DOWNED ELECTRIC WIRES TO THE GERC, THE GERC NOTIFIED THE BRONX/WESTCHESTER ELECTRIC CONTROL CENTER. AT 17:45 THE CALL CENTER REPORTED A STRONG OUTDOOR GAS ODOR WITH DOWNED ELECTRIC WIRES REPORTED FROM THE PUBLIC TO THE GERC. THE CALL CENTER'S REPORT INDICATED THE CFD AND CPD WERE ON LOCATION; THE REMARKS ON THE TICKET STATED THAT THE CUSTOMER REPORTED THAT THE POWER LINE IGNITED HIS GAS LINE. A CODE MURRE WAS INITIATED AND THE GERC DISPATCHED A GDS PLANNER AND CREW. GDS RESPONDED, INVESTIGATED AND REPORTED THAT THERE WERE NO NATURAL GAS READINGS, NO GAS ODORS AND NO GAS IGNITION. THE DOWNED WIRES WERE SMOKING IN THE STREET AND ELECTRIC OPERATIONS-OVERHEAD WAS ON LOCATION. THERE WERE NO REPORTED INJURIES, NO MEDIA ATTENTION; THIS WAS AN UPGRADED LEVEL INCIDENT. NOTE: THIS REPORT DOES NOT MEET THE REPORTING CRITERIA FOR GAS IGNITION. THE INVESTIGATION THE INITIAL REPORT WAS INCORRECT; NO GAS IGNITION. AS SUCH THIS REPORT IS FOR RECORD PURPOSES ONLY.
2025-03-31 10:13 | NO | NO | NO | 20110385 | 15374 | 2011-11-23 17:50 | SUPPLEMENTAL FINAL | 2812 | CORPUS CHRISTI, CITY OF - GAS DIV | 4225 SOUTH PORT AVENUE | CORPUS CHRISTI | TX | 78415 | 2011-10-25 06:15 |  |  | 2011 | 5129 KOSTORYZ | CORPU CHRISTI | NUECES | TX | 78415 | 27.7276 | -97.4137 | [9 empty] | 2011-10-25 08:10 | 993494 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 10 | 2011-10-25 07:00 |  |  |  | 2011-10-25 07:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 2958 | 3830.640122199592662 | 400 | 518.0040733197556 | 0 | 0 |  |  | 100 | 75.84369449378330373001776198934280639432 |  | 0 | 3458 | 1871.237861977404103548845470692717584369 | 4424.487890013131565730017761989342806394 | 0 | 0 | 0 |  |  |  |  | 14 | 14 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1960 | NO | YES | YES |  |  | 2011 |  |  |  |  | NO | COAL TAR | [21 empty] | 2010-12-21 | NO | [227 empty] | JESSE M. CANTU JR. | PETROLEUM SUPERINTENDENT | jessecantu@cctexas.com | (361)885-6941 | (361)853-3200 |  |  |  | DEBORAH A. MARROQUIN | DIRECTOR OF GAS SERVICES | (361)885-6924 | debbiem@cctexas.com | THE GAS DISPATCH OFFICE WAS NOTIFIED OF A POSSIBLE GAS LEAK AT 6:15AM AND DISPATCHES LEAK CREW. THE 2" STEEL MAIN WAS ISOLATED AT 10:58AM USING STOPPLE EQUIPMENT. THE MAIN WAS EXPOSED AND A PIN HOLE CAUSED BY CORROSION WAS DISCOVERED. A 24 FOOT SEGMENT OF MAIN WAS ABANDONED.
2025-03-31 10:13 | NO | YES | NO | 20110387 | 15356 | 2011-11-29 12:38 | ORIGINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2011-10-31 13:30 |  |  | 2011 | 10 MANOR AVENUE | MILLERSVILLE | LANCASTER COUNTY | PA | 17551-1123 | 40.0084 | -76.3583 | [9 empty] | 2011-10-31 14:52 | 994104 |  | NATURAL GAS |  | 729 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | YES |  | 2011-10-31 13:30 |  |  |  | 2011-10-31 13:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1998 | [5 empty] | 8.625 | PE 2306 | UPONOOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2306 | MECHANICAL PUNCTURE | 2.5 | 7.7 | [7 empty] | CLASS 3 LOCATION | 425000 | 550379.327902240325 | 18000 | 23310.183299389002 | 12500 | 16187.6272912423625 | 0 | 0 |  |  | 6180 | 4687.140319715808170515097690941385435169 |  | 0 | 461680 | 248645.298770407172416518650088809946714 | 594564.2788125874976705150976909413854352 | 2 | 0 | 7 |  |  |  |  | 42 | 42 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS THE RESULT OF A DAMAGED GAS LINE AND WAS NOT RELATED TO THE CONTROLLER OR CONTROL ROOM. | [12 empty] | YES | 4 | 0 | YES | 3 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 20112851016 | PA ONE CALL |  | UTILITY OWNER | YES | YES | 13 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ERIC S. SWARTLEY | MANAGER COMPLIANCE AND DAMAGE PREVENTION | eswartley@ugi.com | 610-796-3513 | 610-796-3402 |  |  |  | ROBERT F. BEARD | PRESIDENT AND CEO | 610-796-3434 | rbeard@ugi.com | ON OCTOBER 31ST AN EXPLOSION OCCURRED AT 10 MANOR AVENUE IN MILLERSVILLE, PA. DESTROYING THE BUILDING. THERE WERE NO INJURIES OR FATALITIES. THE SOURCE OF THE NATURAL GAS INVOLVED IN THE EXPLOSION WAS FROM AN 8" PE GAS MAIN THAT WAS DAMAGED BY A HORIZONTAL DIRECTIONAL DRILLING (HDD) UNIT INSTALLING CONDUIT FOR FIBER OPTIC CABLE. ALTHOUGH THERE WAS CLEAR EVIDENCE OF THE PE GAS MAIN WITHIN THE CONSTRUCTION PATH, AS IT WAS IDENTIFIED WITH YELLOW PAINT ON THE PAVEMENT PRIOR TO THE INCIDENT, THE THIRD PARTY HDD CONTRACTOR FAILED TO VERIFY THE PRECISE LOCATION OF THE GAS MAIN BEFORE THE DAMAGE OCCURRED. A (16)- AN AREA WAS EVACUATED (2) BLOCKS EAST AND WEST OF THE INCIDENT SITE AND (1) BLOCK TO THE SOUTH. AN EXACT NUMBER WAS NOT AVAILABLE. A- (4, 17 A & B). THE INPUTTING OF ACCURATE TIMES WAS DISCUSSED WITH THE PHMSA INFORMATION RESOURCES MANAGER PRIOR TO SUBMITTING. 4- THE TIME OF THE EXPLOSION WAS 13:30 17 A- THE TIME THE OPERATOR BECAME AWARE OF THE EXPLOSION WAS 13:30. 17B- OPERATOR ARRIVED ON SITE AT 12:24, BASED ON OUR RESPONSE TO A CALL FROM LOCAL EMA AT 11:57 OF A POSSIBLE LINE STRIKE AND LEAKING GAS . IF IT IS DETERMINED FIELDS REQUIRE CHANGING THIS CAN BE ACCOMPLISHED IN A SUPPLEMENTAL FILING.
2025-03-31 10:13 | NO | NO | NO | 20110388 | 15428 | 2011-11-29 16:54 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2011-11-01 01:23 |  |  | 2011 | SAINT ROSE PARKWAY AND EASTERN AVENUE | HENDERSON | CLARK | NV | 89052 | 36.0071 | -115.1139 | [9 empty] | 2011-11-09 08:19 | 995019 |  | NATURAL GAS |  | 646 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-11-01 01:54 |  |  |  | 2011-11-01 01:54 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 96 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1995 | [5 empty] | 6.625 | ASTM D2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.602 |  | 3408 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 855 | 1107.233706720977595 | 71620 | 92748.62932790224018 | 0 | 0 |  |  | 2396 | 1817.214920071047957371225577264653641208 |  | 0 | 74871 | 40553.3138002698468458703374777975133215 | 95673.0779546942657323712255772646536412 | 52 | 0 | 2265 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 336024 | USA NORTH |  | CONTRACT LOCATOR | YES | YES | 16 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | KELLY EVERSON | ADMINISTRATOR OF COMPLIANCE | kelly.everson@swgas.com | (702) 365-2324 | (702) 221-4116 |  |  |  | PHIL ANDREW | DIRECTOR OF GAS OPERATIONS | (702) 365-2207 | phil.andrew@swgas.com | AN OPERATOR WORKING FOR C.G. AND B. ENTERPRISES STRUCK AND DAMAGED A SIX-INCH PE MAIN WITH A TRACKHOE WHILE EXCAVATING TO INSTALL A WATER LINE IN THE INTERSECTION OF SAINT ROSE PARKWAY AND EASTERN AVENUE IN HENDERSON. LINE LOCATION MARKS WERE PROVIDED FOR THIS SECTION OF MAIN, HOWEVER, THE MARKS WERE NOT WITHIN TWENTY-FOUR INCHES OF THE FACILITY. NO DEATH OR INJURY RESULTED FROM THE INCIDENT AND SERVICE TO 2317 ACTIVE CUSTOMERS WAS RESTORED AFTER THE MAIN WAS REPAIRED. THE INCIDENT WAS TELEPHONICALLY REPORTED TO THE NATIONAL RESPONSE CENTER WHEN THE ESTIMATED INCIDENT COST TO SOUTHWEST GAS WAS DETERMINED TO EXCEED 50,000 DOLLARS. SUPPLEMENTAL: FOLLOWING THE REPORT SUBMITTED ON NOVEMBER 29, 2011, ADDITIONAL DETAILS WERE DISCOVERED. AFTER THE EXCAVATOR FAILED TO MANUALLY DETERMINE THE LOCATION OF THE DISTRIBUTION MAIN WITHIN THE AREA MARKED BY SOUTHWEST GAS, THE EXCAVATOR DID NOT CONTACT THE ONE-CALL CENTER OR SOUTHWEST GAS TO REQUEST ADDITIONAL LOCATION INFORMATION AS REQUIRED. INSTEAD, THE EXCAVATOR BEGAN POWERED EXCAVATION OPERATIONS AND DAMAGED THE DISTRIBUTION MAIN. SUPPLEMENTAL: FOLLOWING THE REPORT SUBMITTED ON DECEMBER 9, 2011, ADDITIONAL DETAILS WERE DISCOVERED. THE EXCAVATOR WAS NOT REQUIRED BY STATE LAW TO REQUEST ADDITIONAL LOCATION INFORMAION. ACCORDINGLY, THE PREDOMINANT CAUSE WAS INCORRECT FACILITY RECORDS/MAPS.
2025-03-31 10:13 | YES | NO | NO | 20110389 | 15449 | 2011-12-02 15:57 | SUPPLEMENTAL FINAL | 13840 | NORTHWEST NATURAL GAS CO | 250 SW TAYLOR ST | PORTLAND | OR | 97204 | 2011-11-06 11:39 |  |  | 2011 | 763 SE HIGH STREET | HILLSBORO | WASHINGTON | OR | 97123 | 45.5129 | -122.977 | [9 empty] | 2011-11-06 13:45 | 994739 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 5 | 2011-11-06 11:39 |  |  |  | 2011-11-06 12:08 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | CAST ALUMINUM | [9 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 80000 | 103600.81466395112 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 80000 | 42908.35030549896 | 103600.81466395112 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A RESIDENTIAL HOUSE FIRE WITH CAUSE OF FIRE UNKNOWN. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | DAKOTA DUNCAN | COMPLIANCE SPECIALIST | dakota.duncan@nwnatural.com | 503-226-4211 | 503-273-4822 |  |  |  | KERRY SHAMPINE | CODE COMPLIANCE MANAGER | 503-226-4211 | kerry.shampine@nwnatural.com | AT APPROXIMATELY 11:39AM ON NOVEMBER 6, 2011 NW NATURAL WAS NOTIFIED OF A HOUSE FIRE AT 763 SE HIGH ST. IN HILLSBORO, OREGON. NWN FIRST RESPONDER ARRIVED ON SITE AT ABOUT 12:08PM TO FIND THE FIRE DEPARTMENT ON SITE AND WORKING ON CONTAINMENT. FIVE PEOPLE HAD SELF-EVACUATED DUE TO THE FIRE. ACCESS TO METER AND REGULATOR, WHICH WERE IN THE GARAGE, WAS DENIED UNTIL FIRE DEPARTMENT EXTINGUISHED FLAMES AND HOTSPOTS. UPON ACCESS TO METER AND REGULATOR, NW NATURAL'S FIRST RESPONDER FOUND A GAS LEAK AT THE RISER VALVE CORE BECAUSE PACKING GREASE BURNED OUT AT CORE FROM TEMPERATURES GENERATED BY THE FIRE. THE GAS WAS CONTROLLED AND REPAIRS WERE COMPLETED BY APPROXIMATELY 3:51PM. NW NATURAL DOES NOT HAVE A REASON TO BELIEVE THAT NATURAL GAS WAS INVOLVED IN THE CAUSE OF THE FIRE, HOWEVER, THE FIRE DEPARTMENT'S FINAL REPORT LISTS THE CAUSE OF FIRE AS UNDETERMINED.
2025-03-31 10:13 | NO | YES | NO | 20110390 | 15359 | 2011-12-05 14:04 | ORIGINAL FINAL | 1088 | BALTIMORE GAS & ELECTRIC CO | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2011-11-07 10:27 |  |  | 2011 | 1230 E FORT AV | BALTIMORE |  | MD | 21230-5105 | 39.2702 | -76.5968 | [9 empty] | 2011-11-07 11:33 | 994789 |  | NATURAL GAS |  | 512 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 10 | 2011-11-07 10:27 |  |  |  | 2011-11-07 10:31 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1900 | [5 empty] | 12 | N/A | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | OTHER | [8 empty] | 12" CAST IRON MAIN WAS DAMAGED BY A CATERPILLAR EXCAVATOR | CLASS 3 LOCATION | 0 | 0 | 15000 | 19425.152749490835 | 5000 | 6475.050916496945 | 400000 | 518004.0733197556 | TIME AND MATERIAL FOR RESTORING DISTRIBUTION SYSTEM BACK TO OPERATING CONDITIONS |  | 3062 | 2322.333925399644760213143872113676731794 |  | 0 | 423062 | 227417.1339528926305861456483126110124334 | 546226.6109111430247602131438721136767318 | 7 | 0 | 813 |  |  |  |  | 0.3 | 0.3 | 0.36 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE REASON WAS BGE HAD A 3 MINUTE RESPONSE TIME TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 11563755 | MISS UTILITY |  | CONTRACT LOCATOR | NO | YES | 60 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | MICHAEL DENNIS BOWLING | GAS SERVICE SUPERVISOR | michael.bowling@bge.com | 410-470-7104 | 410-470-7103 |  |  |  | WILLIAM H. BROWN JR | MANAGER GAS SERVICE | 410-470-7105 | william.h.brown@bge.com | CONTRACTOR PERFORMING WORK IN THE ROADWAY OF THE 1200 BLOCK OF E FORT AVE IN BALTIMORE CITY CAUSED DAMAGE TO OUR 12" CAST-IRON LOW PRESSURE NATURAL GAS DISTRIBUTION MAIN. DAMAGE TO THIS MAIN CAUSED A LOW PRESSURE CONDITION IMPACTING APPROXIMATELY 820 CUSTOMERS AND REQUIRING CREWS TO OPERATE VALVES ON A DISTRICT REGULATOR STATION TO SHUT DOWN THE 12" LP MAIN AND CONNECTED LP NATURAL GAS DISTRIBUTION SYSTEM.
2025-03-31 10:13 | NO | NO | NO | 20110392 | 15361 | 2011-12-06 12:33 | ORIGINAL FINAL | 630 | ARKANSAS WESTERN GAS CO | 655 MILSAP RD. | FAYETTEVILLE | AR | 72703 | 2011-11-16 23:15 |  |  | 2011 | 1623 S. 48TH ST. | SPRINGDALE | WASHINGTON | AR | 72762 | 36.1718 | -94.1835 | [9 empty] | 2011-11-17 09:01 | 995783 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-11-17 09:01 |  |  |  | 2011-11-17 09:01 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | BROKE THREADS OFF BELOW STOP AT SERVICE RISER. | CLASS 3 LOCATION | 15622 | 20230.649083503054958 | 1290 | 1670.56313645621181 | 535 | 692.830448065173115 | 0 | 0 | NO OTHER COST ASSOCIATED WITH THIS INCIDENT. |  | 71 | 53.84902309058614564831261101243339253996 |  | 0 | 17518 | 9407.588346362404971859680284191829484902 | 22647.8916911150260286483126110124333925 | 2 | 0 | 0 |  |  |  |  | 35 | 35 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JIM MEEKS | ANALYST | jim.meeks@sourcegas.com | 479-575-1508 | 479-575-1438 |  |  |  | JIM MEEKS | ANALYST | 479-575-1508 | jim.meeks@sourcegas.com | VEHICLE EXITED ROADWAY BREAKING OFF SERVICE RISER BELOW STOP.
2025-03-31 10:13 | NO | YES | YES | 20110393 | 15604 | 2011-12-06 15:22 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2011-11-08 16:20 |  |  | 2011 | 312 WOODROW AVE. | NEW ALBANY | FLOYD | IN | 41750 | 38.2978 | -85.7951 | [9 empty] | 2011-11-08 17:25 | 994958 |  | NATURAL GAS |  | 63 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 5 | 6 | YES |  |  |  |  | YES | 10 | 2011-11-08 16:26 |  |  |  | 2011-11-08 16:37 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 28 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1946 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 0.8 | 0.8 | [7 empty] | CLASS 3 LOCATION | 80000 | 103600.81466395112 | 0 | 0 | 8500 | 11007.5865580448065 | 0 | 0 |  |  | 404 | 306.408525754884547069271758436944937833 |  | 0 | 88904 | 47750.8083513907289404973357015985790409 | 114914.8097477508110470692717584369449378 | 0 | 0 | 8 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 8 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | NATURAL GAS | YES | 1110310276 | INDIANA811 |  | CONTRACT LOCATOR | NO |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | MONTRE MCMANIGELL | QUALITY ASSURANCE SPECIALIST | mmcmanigell@vectren.com | 812-306-8504 |  |  |  |  | JAMES FRANCIS | DIRECTOR OF ENGINEERING ASSET MANAGEMENT | 812-491-4369 | jmfrancis@vectren.com | WHILE PERFORMING A HORIZONTAL DIRECTION DRILLING OPERATION FOR REPLACEMENT OF AGED GAS FACILITIES, MILLER PIPELINE, (CONTRACTOR FOR VECTEN), STRUCK AN UNMARKED 4" STEEL MAIN STUB. OTHER EXISTING GAS FACILITIES IN THE AREA WERE CORRECTLY MARKED. CONTRACTOR INSTALLING FACILITIES FOR VECTREN WAS RESPONSIBLE FOR MARKING EXISTING VECTREN NATURAL GAS FACILITIES AT THE JOB SITE. GAS LEAKING FROM THIS DAMAGE APPEARS TO HAVE MIGRATED INTO THE STRUCTURE AT 312 WOODROW AVE. IN NEW ALBANY, IN RESULTING IN IGNITION AND EXPLOSION. FIVE (5) PERSONS IN THE STRUCTURE, (GENERAL PUBLIC), AND ONE (1) CONTACT EMPLOYEE WORKING FOR VECTREN SUSTAINED INJURIES THAT REQUIRED HOSPITILIZATION. 2/14/13 SUPPLEMENTAL REPORT FILED TO ADDRESS REGULATORY CONCERNS ASSOCIATED WITH: PART D (2D.) "UNKOWN AT THIS TIME" WAS ELIMINATED PART H - CLARIFYING INFORMATION INSERTED IN NARRATIVE ASSOCIATED WITH CONTRACTOR RESPONSIBILITY FOR LOCATING.
2025-03-31 10:13 | NO | YES | NO | 20110394 | 15363 | 2011-12-07 12:26 | ORIGINAL FINAL | 14210 | OKLAHOMA NATURAL GAS CO | 401 N. HARVEY | OKLAHOMA CITY | OK | 73102 | 2011-11-09 13:00 |  |  | 2011 | 522 NO. WEWOKA | WETUMKA | HUGHES | OK | 74883 | 35.2426 | -96.2455 | [9 empty] | 2011-11-11 17:50 | 995284 |  | NATURAL GAS |  | 15 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-11-09 13:00 |  |  |  | 2011-11-09 13:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 28 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1986 | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 100 | 129.5010183299389 | 16274 | 21074.995723014256586 | 38500 | 49857.8920570264765 | REMOVAL OF WATER FROM SEVERAL LINES IN THE LOW PRESSURE SYSTEM. |  | 54874 | 41618.4689165186500888099467140319715808 |  | 0 | 109748 | 67931.4306095871183653534635879218472469 | 112680.8577148893220748099467140319715808 | 0 | 0 | 41 |  |  |  |  | 28 | 28 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | WATER | YES | 11110909260531 | OKIE ONE CALL |  | CONTRACT LOCATOR | YES | YES | 51 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | NICK NORMAN | ENGINEER III | nick.norman@oneok.com | 918-831-8303 | 918-831-8208 |  |  |  | BRYAN BREWSTER | DIRECTOR - DIVISIONS OPERATIONS | 405-551-6653 | bbrewster@ong.com | THE CITY OF WETUMKA WAS EXCAVATING FOR REPAIR OF AN 8" WATER LINE LEAK. THE CITY WORK WAS PERFORMED UNDER A VALID LOCATE REQUEST ISSUED FROM THE ONE CALL SYSTEM. AT 13:00 HOURS ON 11-9-2011 THE CITY NOTIFIED ONG THAT A GAS LINE HAD BEEN DAMAGED AND GAS WAS VENTING. AN ONG CREW ARRIVED AT 13:40 HOURS AND HAD THE GAS TURNED OFF AT 14:24 HOURS. SYSTEM WAS A ONE WAY FEED. PORTIONS OF THE SYSTEM DOWNSTREAM OF THE DAMAGE FILLED WITH WATER FROM THE LEAKING WATER LINE, CAUSING AN EXTENDED TIME TO RETURN THE LINE TO SERVICE (SEE COSTS IN PART D, 2, 2.D). DOWNSTREAM LINES WERE EXCAVATED AND CLEARED OF WATER BY 17:00 HOURS ON 11-11-2011 WITH SERVICE TO ALL CUSTOMERS RESTORED.
2025-03-31 10:13 | NO | YES | YES | 20110395 | 15381 | 2011-12-09 08:43 | SUPPLEMENTAL FINAL | 31470 | VECTREN ENERGY DELIVERY OF OHIO | 1300 EXPERIMENT FARM ROAD | TROY | OH | 45373-9409 | 2011-11-12 13:55 |  |  | 2011 | 367/369 WAYNE DRIVE | FAIRBORN | GREENE | OH | 45324-5414 | 39.7565 | -84.1815 | [9 empty] | 2011-11-12 15:30 | 995328 |  | NATURAL GAS |  | 8 |  | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 0 | 0 | 0 | 1 | 5 | 6 | YES |  |  |  |  | YES | 12 | 2011-11-12 14:06 |  |  |  | 2011-11-12 14:12 |  | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | BASEMENT | 54 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1.66 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.14 | [6 empty] | OTHER | [8 empty] | SEE PART H NARRATIVE | CLASS 3 LOCATION | 246000 | 318572.505091649694 | 750 | 971.25763747454175 | 3362 | 4353.824236252545818 | 0 | 0 |  |  | 30 | 22.75310834813499111900532859680284191829 |  | 0 | 250142 | 134169.7143524831741212646536412078152753 | 323920.3400737249165591190053285968028419 | 0 | 0 | 6 |  |  |  |  | 0.31 | 0.31 | 0.97 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | UNKNOWN/OTHER | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | NO |  |  |  | UNKNOWN/OTHER | NO |  |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | JOHN A. SPINKS | MANAGER QUALITY ASSURANCE | jaspinks@vectren.com | 937-440-1844 | 937-440-1818 |  |  |  | JAMES M. FRANCIS | DIRECTOR ENGINEERING AND ASSET MANAGEMENT | 812-491-4369 | jmfrancis@vectren.com | ON SATURDAY, NOVEMBER 11, 2011, AT 2:06 PM, VECTREN ENERGY DELIVERY OF OHIO WAS NOTIFIED BY THE CITY OF FAIRBORN FIRE DEPARTMENT OF A HOUSE EXPLOSION AT 367/369 WAYNE DRIVE IN FAIRBORN. VECTREN PERSONNEL WERE DISPATCHED TO THE SCENE AND SUBSEQUENTLY CLOSED THE VALVE TO THE SERVICE LINE PROVIDING NATURAL GAS TO THE STRUCTURE. AN INITIAL REPORT FROM THE FAIRBORN FIRE DEPARTMENT INDICATED THE STRUCTURE INVOLVED IN THE INCIDENT WAS 'TOTALLY DESTROYED AND REDUCED TO A FLAMING PILE OF RUBBLE'. IT FURTHER DESCRIBED THE DAMAGE TO ADJACENT STRUCTURES INCLUDING BLOWN OUT WINDOWS, A COLLAPSED EXTERIOR WALL AND SMALL AMOUNTS OF FIRE TO THE ROOF LINES. THE INITIAL REPORT ALSO COMMENTED THAT ALTHOUGH THE CAUSE REMAINS UNDER INVESTIGATION, THE PRELIMINARY THOUGHT IS THAT 'EXCAVATION WORK AROUND A NATURAL GAS LINE CAUSED THE LINE TO FRACTURE ON THE INSIDE OF THE BASEMENT WALL'' 'ALLOWING THE FREE FLOW OF GAS TO FILL THE INTERIOR OF THE STRUCTURE AND A UNDETERMINED IGNITION SOURCE SPARKED THE EXPLOSION.' VECTREN IS CONTINUING ITS OWN INDEPENDENT INVESTIGATION INTO THE ORIGIN OF THIS INCIDENT. SUPPLEMENTAL REPORT NARRATIVE, JANUARY 10, 2012: THE NATURAL GAS SERVICE LINE FOR THE DUPLEX AT 367-369 WAYNE DRIVE RAN UNDERGROUND FROM THE CURB BOX THROUGH THE CONCRETE BASEMENT WALL INTO THE BASEMENT OF 367 WAYNE DRIVE. AFTER GOING STRAIGHT THROUGH THE BASEMENT WALL, THE NATURAL GAS SERVICE LINE THEN WENT TO THE LEFT AT A TEE CONNECTION TO THE METER FOR 367 WAYNE DRIVE AND THEN TO THE RIGHT AT AN NINETY DEGREE ELBOW THROUGH THE BLOCK WALL, DIVIDING THE BASEMENTS, TO THE METER FOR 369 WAYNE DRIVE. VECTREN GENERALLY CONCLUDES THAT THE BACKHOE OPERATOR, DIGGING A TRENCH OUTSIDE THE BASEMENT FOUNDATION BETWEEN THE SIDEWALK AND THE DUPLEX, DAMAGED THE NATURAL GAS SERVICE LINE. THIS DAMAGE CAUSED THE NATURAL GAS SERVICE LINE TO BEND AND PULL AND TO PLACE A LARGE AMOUNT OF TENSION ON THE GAS SERVICE LINE AND THE THREADS THAT SCREWED INTO THE NINETY DEGREE ELBOW INSIDE THE BASEMENT OF 367 WAYNE DRIVE. THIS LARGE AMOUNT OF TENSION CAUSED THE THREADS OF THE GAS SERVICE LINE, WHICH WERE SCREWED INTO THE NINETY DEGREE ELBOW, TO FRACTURE AT THIS THREAD JOINT RELEASING NATURAL GAS INTO THE BASEMENT OF 367 WAYNE DRIVE. THE NATURAL GAS EXPLODED FROM AN UNDETERMINED IGNITION SOURCE ONCE THE NATURAL GAS AND AIR MIXTURE HAD REACHED A POINT BETWEEN THE LOWER EXPLOSIVE LIMIT AND THE UPPER EXPLOSIVE LIMIT. THE FORCE OF THE EXPLOSION DID NOT CAUSE THE FRACTURE TO THIS THREAD JOINT. VECTREN'S INVESTIGATION ALSO DETERMINED THAT THE PROPER AMOUNT OF MERCAPTAN OR ODORANT WAS IN THE NATURAL GAS AT THE TIME AND THAT THERE WERE NO OTHER NATURAL GAS LEAKS. THE SERVICE LINE WAS IN GOOD CONDITION AND LEAK TIGHT. VECTREN'S INVESTIGATION ALSO DETERMINED THAT THERE WERE NO REQUESTS TO LOCATE THE NATURAL GAS SERVICE LINE BEFORE THESE UNFORTUNATE EVENTS AND THAT THERE WAS NO REQUEST TO TURN OFF THE NATURAL GAS. ALTHOUGH VECTREN DOES NOT RELY ON THE INITIAL REPORT OF THE FAIRBORN FIRE DEPARTMENT OR THE INCIDENT REPORT AND SUPPLEMENTAL REPORT OF THE STATE FIRE MARSHAL, VECTREN'S CONCLUSIONS ARE CONSISTENT WITH THE FACTS CONTAINED IN THESE REPORTS.
2025-03-31 10:13 | NO | NO | NO | 20110396 | 15453 | 2011-12-09 15:50 | SUPPLEMENTAL FINAL | 18308 | NV ENERGY | PO BOX 10100 | RENO WASHOE | NV | 89520 | 2011-09-16 12:15 |  |  | 2011 | 330 MONUMENTAL CIRCLE | SPARKS | WASHOE | NV | 89436-8938 | 39.6427 | -119.7305 | [9 empty] | 2011-11-17 15:47 | 995857 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-09-16 12:15 |  |  |  | 2011-09-16 12:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | SERVICE TEE | 1996 | [8 empty] | OTHER | POLYACETAL | [9 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 61138 | 79174.332586558044682 | 0 | 0 |  |  | 0 | 0 |  | 0 | 61138 | 32791.634012219942706 | 79174.332586558044682 | 0 | 0 | 0 |  |  |  |  | 86 | 86 | 90 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA SYSTEM ONLY USED FOR SYSTEM PRESSURE MONITORING. THIS GAS LEAK DID NOT IMPACT SYSTEM PRESSURES. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | CONSTRUCTION | NO | [50 empty] | JAY WIGGINS | SUPERVISOR GAS COMPLIANCE OPERATIONS | jwiggins@nvenergy.com | 775-834-7850 | 775-834-1225 |  |  |  | JOHN OWENS | DIRECTOR GAS BUSINESS | 775-834-5644 | jowens@nvenergy.com | DURING A SCHEDULED LEAK SURVEY CONDUCTED ON SEPTEMBER 16, 2011, A LEAK WAS DISCOVERED BY NV ENERGY PERSONNEL. THE AREA WAS MADE SAFE AND REPAIRS WERE MADE. INVESTIGATION DETERMINED THAT THE LEAK WAS CAUSED BY A CRACKED SERVICE TEE CAP. SUBSEQUENT AERATION ACTIVITIES WERE PERFORMED TO REMOVE THE NATURAL GAS FROM THE SOIL. THE AERATION COSTS ASSOCIATED WITH THIS LEAK EXCEEDED THE INCIDENT REPORTING THRESHOLD OF $50,000 ON NOVEMBER 17, 2011. THE MANUFACTURER INSTALLATION PROCEDURES FOR THE CRACKED SERVICE TEE CAP STATE THAT THESE TYPES OF CAPS ARE DESIGNED TO BE HAND TIGHTENED ONLY. THE CRACKED CAP FROM THIS FAILURE HAS WRENCH MARKS. BASED ON THIS EVIDENCE, WE CONCLUDE THAT THE CAP FAILURE WAS MOST LIKELY CAUSED BY OVER TIGHTENING OF THE CAP.
2025-03-31 10:13 | NO | YES | YES | 20110397 | 16023 | 2011-12-12 16:41 | SUPPLEMENTAL FINAL | 15329 | PEOPLES GAS LIGHT & COKE CO | 130 E RANDOLPH STREET | CHICAGO | IL | 60601 | 2011-11-13 06:39 |  |  | 2011 | 6652 S. KEATING | CHICAGO | COOK | IL | 60629-5634 | 41.7714 | -87.7412 | [9 empty] | 2011-11-13 07:45 | 995364 |  | NATURAL GAS |  | 38.97 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | YES | 9 | 2011-11-13 06:39 |  |  |  | 2011-11-13 07:05 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2007 | [5 empty] | 0.625 | ASTM D 2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 6.94 |  |  | 2406 | MECHANICAL PUNCTURE | 3 | 0.6 | [7 empty] | CLASS 4 LOCATION | 518349 | 671267.233503054988761 | 8500 | 11007.5865580448065 | 5000 | 6475.050916496945 | 5825606 | 7544219.093890020354734 | BODILY INJURY CLAIMS |  | 300 | 227.531083481349911190053285968028419183 |  | 0 | 6357755 | 3410059.30696678589010764653641207815275 | 8233196.49595109844490619005328596802842 | 0 | 0 | 73 |  |  |  |  | 22 | 22 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | POWER RODDING TOOL APPARENTLY PIERCED OR PERHAPS SEVERED THE NATURAL GAS SERVICE LINE. | [154 empty] | HARSH MEHTA | ENGINEER | hbmehta@peoplesgasdelivery.com | 312-240-3999 |  |  |  |  | THOMAS J. WEBB | COMPLIANCE MANAGER | 312-240-4650 | tjwebb@peoplesgasdelivery.com | DESCRIPTION OF INCIDENT WE ARE TOLD THAT ON NOVEMBER 12, 2011 AND AGAIN ON NOVEMBER 13, 2011, THE MALE OWNER/OCCUPANT OF A SINGLE-FAMILY HOME AT 6652 S. KEATING, CHICAGO, IL ("PREMISES") WAS USING A POWER RODDING TOOL IN THE CLAY SEWER LATERAL TO THE PREMISES. THERE WAS A 5/8 INCH POLYETHYLENE NATURAL GAS SERVICE LINE TO THE PREMISES EQUIPPED WITH AN EXCESS FLOW VALVE. THE NATURAL GAS SERVICE LINE BREACHED A PORTION OF THE CLAY SEWER LATERAL IN WHICH THE POWER RODDING TOOL WAS BEING USED. AT SOME POINT, THE POWER RODDING TOOL APPARENTLY PIERCED OR PERHAPS SEVERED THE NATURAL GAS SERVICE LINE. AN EXPLOSION AND FIRE OCCURRED AT THE PREMISES ON NOVEMBER 13, 2011 THAT DESTROYED THE PREMISES ("INCIDENT") AND DAMAGED THE SINGLE-FAMILY HOMES AT 6650 S. KEATING, 6658 S. KEATING AND 6646 S. KEATING. 3/13/2012 UPDATE: THE INVESTIGATION OF THE INCIDENT AT 6652 S. KEATING ON NOVEMBER 13, 2011 IS NOT COMPLETE. AS A NEXT STEP IN THE INVESTIGATION, THE EXCESS FLOW VALVES FROM 6652 S. KEATING AND 6650 S. KEATING ARE SCHEDULED TO BE X-RAYED ON MARCH 15, 2012. THERE IS NO FURTHER UPDATE AT THIS TIME. 6/7/2012 UPDATE: THE INVESTIGATION OF THE INCIDENT AT 6652 S. KEATING ON NOVEMBER 13, 2011 IS NOT COMPLETE. THE EXCESS FLOW VALVES WERE X-RAYED AS PLANNED. THERE IS NO FURTHER UPDATE AT THIS TIME. 9/4/2012 UPDATE: ON 7/24/2012, THE EXCESS FLOW VALVE THAT WAS ON THE NATURAL GAS SERVICE LINE TO 6652 S. KEATING ON THE DATE OF THE INCIDENT WAS TESTED AND FOUND TO WORK PROPERLY. THE INVESTIGATION OF THIS INCIDENT IS NOT COMPLETE. CONSIDERATION IS BEING GIVEN TO FURTHER INSPECTION AND TESTING OF COMPANY OWNED FACILITIES. NO FURTHER UPDATE AT THIS TIME. 6/12/2013 UPDATE: NO NEW INFORMATION IS AVAILABLE AT THIS TIME. 9/25/2013 UPDATE: NO NEW INFORMATION IS AVAILABLE AT THIS TIME. 12/17/2013 UPDATE: NO NEW INFORMATION IS AVAILABLE AT THIS TIME. 3/5/2014 UPDATE: NO NEW INFORMATION IS AVAILABLE AT THIS TIME. 6/4/2014 UPDATE: NO NEW INFORMATION IS AVAILABLE AT THIS TIME. 9/24/2014 UPDATE: NO NEW INFORMATION IS AVAILABLE AT THIS TIME. 12/31/2014 UPDATE: THIS INCIDENT HAS BEEN CLOSED.
2025-03-31 10:13 | YES | NO | NO | 20110401 | 15373 | 2011-12-30 11:47 | ORIGINAL FINAL | 20110 | DUKE ENERGY KENTUCKY | 139 EAST FOURTH STREET PO BOX 960 - ROOM 460-ANNEX | CINCINNATI | OH | 45202 | 2011-12-03 02:11 |  |  | 2011 | 104 MADISON | BUTLER | PENDLETON | KY | 41006 | 38.7871 | -84.3705 | [9 empty] | 2011-12-03 06:59 | 997072 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2011-12-03 02:11 |  |  |  | 2011-12-03 03:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | CUSTOMER HOUSE PIPING | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | FIRE CAUSED A LEAK IN THE HOUSE PIPING | CLASS 4 LOCATION | 50000 | 64750.50916496945 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 50000 | 26817.71894093685 | 64750.50916496945 | 0 | 0 | 1 |  |  |  |  | 1 | 1 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS HOUSE LINE PRESSURE. UNDER 1 POUND. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | RANDALL L. SUTTLES | SPECIALIST COMPLIANCE AND THIRD PARTY CLAIMS | randall.suttles@duke-energy.com | 513-312-8550 | 859-815-6427 |  |  |  | RANDALL L. SUTTLES |  | 513-312-8550 | No Email Address | RESIDENTIAL HOUSE FIRE. WE WERE NOTIFIED AT 2:11 AM OF A HOUSE FIRE. DUKE ARRIVED AROUND 3 AM AND FOUND THE GAS OFF BY THE FIRE DEPARTMENT. THEY DID NOT TELL US THAT GAS MAY HAVE FED THE FIRE UNTIL AROUND 6 AM. THAT IS WHEN WE NOTIFIED THE DOT. THE FIRE DEPARTMENT SAID THAT GAS DID NOT START THE FIRE.
2025-03-31 10:13 | NO | YES | NO | 20120001 | 30428 | 2012-01-05 16:16 | SUPPLEMENTAL FINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 820 WEST BROADWAY, PO BOX 32030 | LOUISVILLE | KY | 40202 | 2011-12-06 07:03 |  |  | 2011 | 5206 RIVER TRAIL PLACE | LOUSIVILLE | JEFFERSON | KY | 40299 | 38.1054 | -85.6629 | [9 empty] | 2011-12-06 09:46 | 997289 |  | NATURAL GAS |  | 26 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 10 | 2011-12-06 07:03 |  |  |  | 2011-12-06 07:03 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2001 | [5 empty] | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | OTHER | [8 empty] | THE NATURAL GAS MAIN HAD AN OVAL HOLE IN IT ON THE SIDE OF THE NATURAL GAS MAIN FACING THE HOLE AND CRACK FOUND IN THE [ADJACENT] WATER SERVICE. THE HOLE IN THE NATURAL GAS MAIN WAS APPROXIMATELY ONE HALF INCH. | CLASS 3 LOCATION | 520000 | 673405.29531568228 | 23166 | 30000.205906313645574 | 2784 | 3605.308350305498976 | 0 | 0 |  |  | 122 | 92.52930728241563055062166962699822380107 |  | 0 | 546072 | 292908.2681427324491642095914742451154529 | 707103.3388795838401805506216696269982238 | 0 | 0 | 3 |  |  |  |  | 59 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT INVESTIGATION DID NOT INDICATE ANY CONTRIBUTING FACTORS THAT COULD BE RELATED TO THE CONTROL ROOM OR THE CONTROLLER. | [12 empty] | YES | 3 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | EXAMINATION OF THE PE NATURAL GAS MAIN FOUND THAT, THE AREA CLOSEST TO THE LOUISVILLE WATER COMPANY'S LEAKING SERVICE HAD SUSTAINED SEVERE EXTERIOR ABRASIONS. THIS INVESTIGATION HAS CONCLUDED THAT THE ABRASIVE AND SANDBLASTING POWER OF THE LEAKING WATER SERVICE LINE COMBINED WITH THE GRAVEL, SAND, AND BRICK FOUND IN THE UTILITY TRENCH ERODED THE EXTERIOR WALL OF THE PE NATURAL GAS MAIN CAUSING THE HOLE IN THE GAS MAIN. | [154 empty] | JIM DIMAS | SENIOR CORPORATE ATTONEY | jim.dimas@lge-ku.com | 502-627-3712 | 502.627-3367 |  |  |  | JIM DIMAS | SENIOR CORPORATE ATTORNEY | 502-627-3712 | jim.dimas@lge-ku.com | PREVIOUSLY SUBMITTED WITH ORIGINAL REPORT.
2025-03-31 10:13 | NO | YES | NO | 20120002 | 15462 | 2012-01-09 17:47 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2011-12-08 15:18 |  |  | 2011 | 3045 KENTUCKY COURT, APT. #9 | EAST POINT | FULTON | GA | 30344 | 33.6736 | -84.4608 | [9 empty] | 2011-12-08 17:00 | 997595 |  | NATURAL GAS |  | 25.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 18 | 2011-12-08 15:22 |  |  |  | 2011-12-08 15:51 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2005 | [8 empty] | OTHER | SERVICE VALVE | [9 empty] | OTHER | [8 empty] | 3RD PARTY OPERATION OF SERVICE VALVE / OPEN FUEL LINE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 3300 | 4273.5336048879837 | 1200000 | 1554012.2199592668 | PER DEMAND |  | 130 | 98.59680284191829484902309058614564831261 |  | 0 | 1203430 | 645486.4318478615429348134991119005328597 | 1558384.35036699670199484902309058614565 | 0 | 0 | 8 |  |  |  |  | 0.25 | 0.25 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | INCORRECT OPERATION | INCORRECT VALVE POSITION | [222 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | NO | [50 empty] | RALPH T. MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@aglresources.com | 404-584-3733 | 404-584-4807 |  |  |  | RICHARD LONN | DIRECTOR REGULATORY COMPLIANCE | 404-584-3552 | rlonn@aglresources.com | AS PART OF A MASTER METER CONVERSION IN YEAR 2005, AGLC INSTALLED MULTI-METER HEADERS ON THE OUTSIDE BUILDING WALLS AT AN APARTMENT COMPLEX. AGLC PERFORMED ITS WORK WITHOUT INCIDENT AND CONNECTED ITS EQUIPMENT TO THE CUSTOMERS' FUEL LINES. THE OWNER OF THE APARTMENT COMPLEX RETAINED A THIRD PARTY PLUMBER TO INSTALL THE NOW JURISDICTIONAL FUEL LINES TO THE INDIVIDUAL APARTMENTS AND COMPLETE THE DISCONNECTION FROM THE MASTER METER SYSTEM. IN GENERAL, THE THIRD PARTY APPEARS TO HAVE COMPLETED THE CONNECTIONS TO THE INDIVIDUAL APARTMENTS, BUT THE MASTER METER FUEL LINE TO THE PARTICULAR BUILDING IN QUESTION WAS DISCONNECTED BUT NOT CAPPED AS APPROPRIATE. ON THE DAY OF THE INCIDENT A THIRD PARTY INDIVIDUAL WITH THE APARTMENT COMPLEX SOMEHOW OPERATED THE CUSTOMER VALVE ON THE FUEL LINE, AND NATURAL GAS WAS EMITTED INTO THE CRAWL SPACE OF THE APARTMENT BUILDING THROUGH THE UNCAPPED LINE, WHERE THE ESCAPING GAS IGNITED.
2025-03-31 10:13 | NO | NO | NO | 20120005 | 15388 | 2012-01-19 16:23 | ORIGINAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY SUITE 100 | CANONSBURG | PA | 15317 | 2011-12-19 15:25 |  |  | 2011 | 280 OLD HICKORY RIDGE ROAD | WASHINGTON | WASHINGTON | PA | 15301 | 40.0007 | -80.2564 | [9 empty] | 2011-12-19 17:27 | 998515 |  | NATURAL GAS |  | 288 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2011-12-19 15:25 |  |  |  | 2011-12-19 16:10 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1978 | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | UNKNOWN |  | 11.5 |  |  |  | OTHER | [8 empty] | TRACKHOE CUT THE 2 INCH PLASTIC MAIN LINE IN HALF. | CLASS 1 LOCATION | 86000 | 111370.875763747454 | 80 | 103.60081466395112 | 4522 | 5856.036048879837058 | 0 | 0 |  |  | 1516 | 1149.790408525754884547069271758436944938 |  | 0 | 92118 | 49658.402875561142178440497335701598579 | 118480.3030358169970625470692717584369449 | 0 | 0 | 28 |  |  |  |  | 38 | 38 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | NO |  |  |  | DATA NOT COLLECTED | NO | YES | 7 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | RICK W BURKE | OPERATIONS COMPLIANCE MANAGER | rburke@nisource.com | 724-416-6332 | 724-416-6381 |  |  |  | DAN COTE | GENERAL MANAGER OPERATIONS EAST | 724-416-6334 | dcote@nisource.com | ON DECEMBER 19, 2011 AT 15:25, AN EMPLOYEE FOR MILLLINGTON EXCAVATING WAS DIGGING A TRENCH TO INSTALL A WATER LINE AT 280 OLD HICKORY RIDGE ROAD IN WASHINGTON, PENNSYLVANA. HE STRUCK A TWO INCH MEDIUM PRESSURE PLASTIC NATURAL GAS MAIN LINE, NATURAL GAS IGINITED AND THE TRACKHOE BEING USED FOR TRENCHING CAUGHT WAS DESTROYED. MILLINGTON EXCAVATING FAILED TO NOTIFY THE PENNSYVANIA ONE CALL SYSTEM ITS INTENTION TO EXCAVATE AND CONSEQUENTLY OUR FACILITIES WERE NOT LOCATED. THERE WERE NO INJURIES OR FATALITIES.
2025-03-31 10:13 | YES | NO | NO | 20120006 | 15389 | 2012-01-24 06:23 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-01-11 13:58 |  |  | 2012 | 17 HERITAGE DRIVE | MOUNT PLEASANT | WESTCHESTER | NY | 10570-1414 | 41.1392 | -73.765 | [9 empty] | 2012-01-11 15:38 | 100015 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-01-11 14:00 |  |  |  | 2012-01-11 14:06 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1979 | [8 empty] | OTHER | ALUMINUM METER | [9 empty] | OTHER | [8 empty] | RESIDENTIAL METER MELTED DUE TO BUILDING FIRE | CLASS 4 LOCATION | 0 | 0 | 100 | 127.17 | 350 | 445.095 | 0 | 0 |  |  | 10 | 9.02748414376321353065539112050739957717 |  | 0 | 460 | 245.36595137420718816067653276955602537 | 581.292484143763213530655391120507399577 | 0 | 0 | 1 |  |  |  |  | 60 | 60 | 90 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-579-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-579-2350 | dadariov@coned.com | ******MPFD FINAL DETERMINATION POST-NOTIFICATION IS NATURAL GAS WAS NOT INVOLVED. REPORT FOR RECORD PURPOSES ONLY******* ON WEDNESDAY, JANUARY 11, 2012 @ 13:58 HRS, WESTCHESTER ELECTRIC OPERATIONS EMERGENCY RESPONSE GROUP (ERG) FEENEY REPORTED A HOUSE FIRE AT 17 HERITAGE DRIVE, MT. PLEASANT, N.Y. WITH POSSIBLE NATURAL GAS IGNITION TO THE GAS EMERGENCY RESPONSE CENTER (GERC). A CODE MURRE (MULTIPLE RESOURCE RESPONSE EVENT) WAS INITIATED AND THE GAS OPERATIONS ERG, GAS DISTRIBUTION SERVICES (GDS), GAS CONSTRUCTION AND SUPERVISION RESPONDED. UPON ARRIVAL, THE ONE FAMILY HOME AT THIS LOCATION WAS FOUND ENGULFED IN FIRE AND THERE WAS NATURAL GAS FED FIRE AT THE OUTSIDE GAS METER SET. THE MT. PLEASANT FIRE DEPARTMENT (MPFD) WAS ABLE TO EXTINGUISH THE FIRE AT THE GAS METER, AND TURNED OFF THE OUTSIDE SERVICE VALVE UNDER GDS' DIRECTION. THE CURB VALVE WAS LOCATED AND TURNED OFF, AND GAS CONSTRUCTION CUT AND CAPPED THE SERVICE DUE TO THE EXTENSIVE STRUCTURAL DAMAGE CAUSED BY THE FIRE. DUE TO THE GAS IGNITION AND DAMAGE GREATER THAN $50,000.00, THE U.S. DOT WAS NOTIFIED OF THE CONDITIONS FOUND. UPON COMPLETION OF THEIR INVESTIGATION, MPFD CHIEF MALONE LATER REPORTED THAT THE FIRE WAS NOT CAUSED BY NATURAL GAS, AND THAT THE GAS FED FIRE WAS A RESULT OF THE STRUCTURAL FIRE (SECONDARY IGNITION). THERE ARE NO REPORTED INJURIES. THE NYS PSC AND US DOT WERE NOTIFIED. THIS WAS AN UPGRADED LEVEL INCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20120008 | 16083 | 2012-01-27 09:40 | SUPPLEMENTAL FINAL | 30892 | HERITAGE PROPANE | 10519 SPRING HILL DRIVE | SPRING HILL | FL | 34608 | 2011-12-19 14:30 |  |  | 2011 | 4690 KEYSVILLE ROAD | SPRING HILL | HERNANDO | FL | 34608 | 28.4945 | -82.5551 | [9 empty] | 2011-12-19 16:30 | 998506 |  | PROPANE GAS |  | 18 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2011-12-19 14:30 |  |  |  | 2011-12-19 15:00 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | OTHER | PROPANE DISTRIBUTION, PRIVATELY OWNED | OTHER | VAPORIZER/REGULATOR STATION | 2004 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | OTHER | [8 empty] | UNINTENTIONAL RELEASE FROM UNCAPPED LINE | CLASS 3 LOCATION | 0 | 0 | 18000 | 23310.183299389002 | 5350 | 6928.30448065173115 | 0 | 0 |  |  | 1000 | 758.436944937833037300177619893428063943 |  | 0 | 24350 | 13225.4733244583615254884547069271758437 | 30996.9247249785661873001776198934280639 | 0 | 0 | 434 |  |  |  |  | 10 | 10 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | INCORRECT OPERATION | INCORRECT VALVE POSITION | [222 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  | ROUTINE MAINTENANCE | NO | [50 empty] | MIKE MCLEAN | AMERIGAS OPS MANAGER | mike.mclean@amerigas.com | 904-716-3006 |  |  |  |  | MIKE MCLEAN | AMERIGAS OPS MANAGER | 904-716-3006 | mike.mclean@amerigas.com | 5/20/2015 SUPPLEMENTAL REPORT ENTERED BY PHMSA PER THE OPERATOR'S HARD COPY MARK UP SINCE THE OPID IS NOW INACTIVE IN OUR SYSTEM: EMPLOYEE WAS DOING MAINTENANCE WORK AT THE REGULATOR STATION AND FAILED TO LOCK OUT TWO VAPORIZERS THAT HAD OPEN PILOT FLAME. THE EMPLOYEE ACCIDENTALLY OPENED A VALVE THAT CAUSED A RELEASE OF GAS WHICH WAS THEN IGNITED BY THE VAPORIZERS CAUSING A FLASH FIRE INJURING THE EMPLOYEE. 1/27/2012 COMMENTS: OR EMPLOYEE WAS WORKING AT THE GAS FACILITY, PROPANE GAS VAPOR WAS UNINTENTIONALLY RELEASED FROM THE SYSTEM WHICH RESULTED IN A FIRE. THE EMPLOYEE RECEIVED BURNS AS A RESULT OF THE INCIDENT. THE EMPLOYEE CALL "911" FOR HELP AND OUR LOCAL OFFICE. THE SPRING HILL FIRE DEPARTMENT AS WELL AS PERSONNEL FROM OUR LOCAL OFFICE RESPONDED AND THE FIRE WAS EXTINGUISHED IN APPROXIMATELY 30 MINUTES. THIS WAS ACCOMPLISHED BY CLOSING THE MAIN VALVES IN THE SYSTEM AND THEN ALLOWING THE PROPANE GAS FIRE TO BURN ITSELF OUT. THE EMPLOYEE WAS TRANSPORTED TO THE HOSPITAL FOR TREATMENT.
2025-03-31 10:13 | NO | YES | YES | 20120009 | 15394 | 2012-01-30 16:13 | ORIGINAL FINAL | 4499 | ENTEX, A NORAM ENERGY COMPANY (FORM. DIV OF ARKLA | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2011-12-31 09:31 |  |  | 2011 | 17107 SUNSHINE BAY DR. | HOUSTON | HARRIS | TX | 77060 | 29.9487 | -95.3897 | [9 empty] | 2011-12-31 17:02 | 999374 |  | NATURAL GAS |  | 15 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 4 | 4 | YES |  |  |  |  | YES | 4 | 2011-12-31 10:17 |  |  |  | 2011-12-31 10:17 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1978 | [5 empty] | 1.25 | ALDYL "A" | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.166 |  | 2306 | RUPTURE |  |  |  |  | LONGITUDINAL |  | 1.5 | 0.5 |  | CLASS 3 LOCATION | 150000 | 194251.52749490835 | 0 | 0 | 8132 | 10531.022810590631348 | 0 | 0 |  |  | 100 | 75.84369449378330373001776198934280639432 |  | 0 | 158232 | 84884.9504892686045415488454706927175844 | 204858.3939999927646517300177619893428064 | 0 | 0 | 1 |  |  |  |  | 43 | 43 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF SYSTEM | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [8 empty] | YES |  |  |  | POOR CONSTRUCTION/INSTALLATION PROCEDURES |  |  | NO | [86 empty] | LESLIE J. DAVENPORT | ADVANCED OPERATIONS COORDINATOR | leslie.davenport@centerpointenergy.com | 713-967-8025 | 713-923-9794 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steve.yarbrough@centerpointenergy.com | GAS ESCAPED FROM MAIN AND COMMUNICATED THROUGH SANITARY SEWER INTO STRUCTURE RESULTING IN FIRE/EXPLOSION BY UNKNOWN IGNITION SOURCE.
2025-03-31 10:13 | NO | NO | NO | 20120010 | 15410 | 2012-01-31 10:48 | SUPPLEMENTAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2012-01-04 15:41 |  |  | 2012 | 2164 AVENUE B | SCHENECTADY | SCHENECTADY | NY | 12308 | 42.8303 | -73.9166 | [9 empty] | 2012-01-04 17:43 | 999596 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 6 | 2012-01-04 15:41 |  |  |  | 2012-01-04 15:45 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 2010 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 1.125 |  | 3408 | MECHANICAL PUNCTURE | [9 empty] | CLASS 4 LOCATION | 0 | 0 | 6000 | 7630.2 | 7500 | 9537.75 | 0 | 0 | ESTIMATED COST OF PUBLIC AND NON OPERATOR PRIVATE PROPERTY DAMAGE UNKNOWN. |  | 0 | 0 |  | 0 | 13500 | 7110.45 | 17167.95 | 0 | 0 | 4 |  |  |  |  | 32 | 32 | 32 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | SCHENECTADY FD 911 |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSED BY THIRD PARTY CONTRACTOR | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | UNINTENDED DAMAGE - MANUALLY (BY HUMAN) DRIVEN (BY HAMMER) 1/2" TO 5/8" COPPER ELECTRIC GROUND ROD INTO SIDE OF 1" PLASTIC GAS SERVICE FROM INSIDE HOUSE THROUGH A HORIZONTALLY DRILLED HOLE THROUGH THE BASEMENT WALL. SERVICE PERMANENTLY RETIRED ON 1/4/12. | [47 empty] | BRIAN J. DOWNING | LEAD SUPERVISOR UPSTATE DISPATCH AND SCHEDULING | brian.downing@us.ngrid.com | 315-460-2035 | 315-460-2762 |  |  |  | DEBORAH DEBERGALIS | MANAGER UPSTATE DISPATCH AND SCHEDULING | 315-460-2615 | deborah.debergalis@us.ngrid.com | UNINTENDED DAMAGE - MANUALLY (BY HUMAN) DRIVEN (BY HAMMER) 1/2" TO 5/8" COPPER ELECTRIC GROUND ROD INTO SIDE OF 1" PLASTIC GAS SERVICE FROM INSIDE HOUSE THROUGH A HORIZONTALLY DRILLED HOLE THROUGH THE BASEMENT WALL. SERVICE PERMANENTLY RETIRED ON 1/4/12.
2025-03-31 10:13 | NO | YES | YES | 20120011 | 15401 | 2012-02-03 15:36 | SUPPLEMENTAL | 18532 | TEXAS GAS SERVICE COMPANY | 1301 S MOPAC EXPY, SUITE 400 | AUSTIN | TX | 78746-6918 | 2012-01-09 08:43 |  |  | 2012 | 1712 AND 1710 PAYNE AVENUE | AUSTIN | TRAVIS | TX | 78757 | 30.3375 | -97.7336 | [9 empty] | 2012-01-09 10:20 | 999918 |  | NATURAL GAS |  |  |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 5 | 2012-01-09 08:43 |  |  |  | 2012-01-09 08:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 38 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1950 | [5 empty] | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | OTHER | [8 empty] | CIRCUMFERENTIAL; APPROXIMATE BREAK SIZE IS 2MM AT WIDEST OPENING AND APPROXIMATELY 10 INCHES CIRCUMFERENTIALLY. | CLASS 3 LOCATION | 500000 | 635850 | 32000 | 40694.4 | 3000 | 3815.1 | 0 | 0 | UNKNOWN AT THIS TIME. |  | 800 | 722.198731501057082452431289640591966173 |  | 0 | 535800 | 282452.5761099365750528541226215644820296 | 681081.6987315010570824524312896405919662 | 0 | 0 | 73 |  |  |  |  | 48 | 48 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | LIKELY CONTRIBUTING CAUSE OF THE BREAK IN THE MAIN ON 1-9-12 WAS SHIFTING SOIL DUE TO SEVERE DROUGHT CONDITIONS FOLLOWED BY RAINFALL. | YES |  |  |  | YES | DROUGHT AND RAINFALL | [213 empty] | MARK MONTGOMERY | DIRECTOR OF ENGINEERING AND COMPLIANCE | mbmontgomery@txgas.com | (512) 370-8348 | (512) 370-8254 |  |  |  | PAUL WILSON | REGIONAL VICE PRESIDENT | (512) 465-1149 | jpwilson@txgas.com | THE INCIDENTS AT 1710 AND 1712 PAYNE AVENUE, JANUARY 9, 2012, WERE CAUSED BY THE IGNITION OF NATURAL GAS THAT ESCAPED FROM A BREAK IN A 4 INCH CAST IRON GAS MAIN RUNNING PARALLEL TO PAYNE AVENUE AND THROUGH THE FRONT YARDS OF 1710 AND 1712. THIS BREAK IN THE MAIN OCCURRED SOMETIME SHORTLY BEFORE THE INCIDENT(S). THE EXACT PATH OF GAS MIGRATION HAS NOT BEEN DETERMINED. THE SOURCE OF THE IGNITION IS UNKNOWN.
2025-03-31 10:13 | NO | YES | YES | 20120012 | 15511 | 2012-02-06 11:09 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 1102 E 1ST STREET | PAPILLION | NE | 68046-7641 | 2012-01-08 09:03 |  |  | 2012 | 104 WOOTEN | SUBLETTE | HASKELL | KS | 67877 | 37.4817 | -100.8424 | [9 empty] | 2012-01-08 10:35 | 999858 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 4 | 4 | YES |  |  |  |  | YES | 15 | 2012-01-08 09:03 |  |  |  | 2012-01-08 09:11 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 28 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1964 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | MECHANICAL PUNCTURE | 1 | 3 | [7 empty] | CLASS 3 LOCATION | 125000 | 158962.5 | 10000 | 12717 | 20000 | 25434 | 25000 | 31792.5 | REPLACED LINE IN ALLEY |  | 2500 | 2256.871035940803382663847780126849894292 |  | 0 | 182500 | 96893.7378435517970401691331923890063425 | 231162.8710359408033826638477801268498943 | 30 | 0 | 220 |  |  |  |  | 9 | 9 | 9.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2011-11-11 | NO | [12 empty] | NO | YES | OTHER | [12 empty] | UNKNOWN/OTHER | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | JERRY WATKINS | SENIOR MANAGER OF TECHNICAL SERVICES | jerry.watkins@blackhillscorp.com | 316-941-1642 | 402-829-2790 |  |  |  | VANCE CROCKER | GENERAL MANAGER KANSAS GAS | 785-832-3950 | vance.crocker@blackhillscorp.com | ON SUNDAY, JANUARY 8, 2012, AT APPROXIMATELY 9:00 AM THERE WAS A HOUSE EXPLOSION AND SUBSEQUENT FIRE LOCATED AT 104 WOOTEN STREET IN SUBLETTE, KS. TWO LOCAL COMPANY EMPLOYEES HEARD THE EXPLOSION FROM THEIR HOMES AND REPORTED TO THE SITE IMMEDIATELY. UPON ARRIVAL, BHE EMPLOYEES REQUESTED THE ASSISTANCE FROM LOCAL EMERGENCY MANAGEMENT PERSONNEL TO TREAT INJURIES AND ASSIST WITH EVACUATING THE SURROUNDING AREA. SEVEN PEOPLE WERE HOME AT THE TIME OF THE EXPLOSION AND FOUR WERE TAKEN TO THE HOSPITAL. BAR-HOLE TESTING WAS COMPLETED IN THE ALLEY ADJACENT TO THE INCIDENT SITE AND NATURAL GAS WAS DETECTED. BHE PERSONNEL TOOK PRECAUTIONARY MEASURES AND SHUT OFF THE EAST SIDE OF TOWN IN ORDER TO ISOLATE THE SECTION OF LINE. SERVICE WAS SHUT OFF TO APPROXIMATELY 250 CUSTOMERS. BHE PERSONNEL CONTINUED TO TEST FOR GAS READINGS IN THE ALLEY WHILE OTHER WORK WAS BEING PERFORMED. BHE PERSONNEL RESTORED GAS TO THE EASTERN PART OF THE SYSTEM AND BEGAN THE RE-LIGHTING PROCESS THAT EVENING. BHE PERSONNEL EXPOSED THE 2' COATED STEEL MAIN AT EACH END OF THE ALLEY AND CAPPED IT OFF. A PRESSURE TEST WAS THEN CONDUCTED ON THE MAIN AT UTILIZATION PRESSURE (9 PSI) AND THE LINE WOULD NOT PRESSURE UP. EXCAVATIONS BEGAN IN THE ALLEY NEAR THE SERVICE LINE AND TAP TO THE INCIDENT SITE AND THEN CONTINUED EAST ALONG THE MAIN. THE 2' MAIN WAS UNCOVERED AND DAMAGE WAS FOUND ON THE LINE APPROXIMATELY 15' FROM THE AFOREMENTIONED TAP. IT APPEARS THAT THE LINE HAD BEEN PREVIOUSLY DAMAGED BY A BACKHOE BUCKET. DAMAGE TO THE STEEL LINE WAS SEEN UNDER AND ALONG THE SIDES OF THE STEEL PIPE AND WHAT APPEARED TO BE A STRESS CRACK WAS NOTED ACROSS THE ENTIRE BOTTOM CIRCUMFERENCE OF THE PIPE. UPON FURTHER EXCAVATION WE DISCOVERED A SANITARY SEWER LATERAL CROSSING OUR LINE DIRECTLY UNDER THE DAMAGED AREA. THE DAMAGED SECTION OF PIPE WAS SECURED AND THEN REMOVED FROM THE SITE. THERE WERE NO SIGNS OF RECENT EXCAVATION IN THE AREA.
2025-03-31 10:13 | NO | NO | NO | 20120014 | 15471 | 2012-02-11 12:51 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-01-21 15:54 |  |  | 2012 | INTRERSECTION W 175 ST & ST. NICHOLAS AVE. | NEW YORK | NEW YORK | NY | 10033-8022 | 40.8456 | -73.9361 | [9 empty] | 2012-01-21 17:18 | 1000935 |  | NATURAL GAS |  | 271.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-01-21 15:54 |  |  |  | 2012-01-21 16:04 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 54 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | ELECTRIC BURN OUT CAUSED DAMAGE AND GAS LEAK TO MAIN | CLASS 4 LOCATION | 0 | 0 | 1000 | 1271.7 | 1000 | 1271.7 | 5000 | 6358.5 | 0 |  | 818 | 738.448202959830866807610993657505285412 |  | 0 | 7818 | 4370.007822410147991543340380549682875264 | 9640.348202959830866807610993657505285412 | 0 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER--GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | THE MANHATTAN REGIONAL ELECTRIC CONTROL CENTER REPORTED A MANHOLE FIRE TO THE GAS EMERGENCY RESPONSE CENTER (GERC). GAS DISTRIBUTION SERVICES (GDS) RESPONDED AND CONFIRMED A FIRE IN MANHOLE (MH) 44060 WHICH WAS BEING FED BY NATURAL GAS. A CODE MURRE (MULTIPLE RESOURCE RESPONSE EVENT)WAS INITIATED AND THE GERC DISPATCHED ADDITIONAL GDS AND CONSTRUCTION CREWS AND SUPERVISION. ELECTRIC OPERATIONS CREWS WERE IN THE PROCESS OF MITIGATING A SMOKING MANHOLE WITH A BURNOUT WHEN THE FIRE ERUPTED. A 6" LOW PRESSURE POLYETHELENE GAS MAIN WAS OFFSET AROUND THE ELECTRIC MANHOLE WHICH WAS ON FIRE. GAS MAIN VALVE 4570, TO THE EAST AT AUDUBON AVE, WAS IDENTIFIED IN CASE NEEDED FOR MAIN SHUT DOWN, AND THREE FIRE BANKS WERE EXCAVATED TO THE NORTH, SOUTH, AND EAST OF MH 44060. STOPPERS WERE INSTALLED IN THE MAIN AT ALL THREE LOCATIONS AND THE FIRE WAS EXTINGUISHED AT 22:59 HOURS. THERE WERE NO REPORTED OUTAGES, NO INJURIES AND THERE WAS NO MEDIA ATTENTION. THIS WAS A SERIOUS LEVEL INCIDENT AND THE US DOT, NYS PSC AND NYC DEP WERE NOTIFIED.
2025-03-31 10:13 | NO | YES | YES | 20120015 | 15408 | 2012-02-15 07:16 | ORIGINAL | 14330 | ORANGE & ROCKLAND UTILITY INC | ONE BLUE HILL PLAZA | PEARL RIVER | NY | 10965 | 2012-01-16 12:13 |  |  | 2012 | 52 ZARRIELLO LANE | WEST HAVERSTRAW |  | NY | 10993 | 41.2053 | -73.9809 | [9 empty] | 2012-01-16 16:20 | 1000507 |  | NATURAL GAS |  | 96 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 1 | 0 | 0 | 2 | YES |  |  |  |  | YES |  | 2012-01-16 12:13 |  |  |  | 2012-01-16 12:23 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1991 | [5 empty] | 2 | ASTM D2513, HDPE | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 1.2 | 1.2 | [7 empty] | CLASS 3 LOCATION | 1000000 | 1271700 | 10000 | 12717 | 350000 | 445095 | 22000 | 27977.4 | MUTUAL AID |  | 576 | 519.983086680761099365750528541226215645 |  | 0 | 1382576 | 728380.4147991543340380549682875264270613 | 1758009.38308668076109936575052854122622 | 0 | 0 | 94 |  |  |  |  | 60 | 60 | 80 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | NO |  |  |  | UTILITY OWNER | NO | YES | 7 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | DANIEL POLIN | SECTION MANAGER | polind@oru.com | [5 empty] | DANIEL POLIN | SECTION MANAGER | 845 577 3011 | No Email Address | A VERIZON SUBCONTRACTOR, FGC COMMUNICATION SERVICES (FGC), INSTALLING FIOS CABLE USED A PNEUMATIC TRENCHLESS TOOL, KNOWN AS A "BULLET" TO CROSS ZARRIELLO LANE IN WEST HAVERSTRAW, NEW YORK. THE "BULLET" PUNCTURED A 1991 VINTAGE TWO INCH PLASTIC GAS MAIN OPERATING AT 60 PSI. APPROXIMATELY 45 MINUTES AFTER RECEIVING NOTIFICATION OF THE INCIDENT, 52 ZARRIELLO LANE EXPLODED. THERE WERE NO FATALITIES AND THE RESIDENTS WERE NOT HOME AT THE TIME OF THE INCIDENT. TWO LOCAL VOLUNTEER FIRE FIGHTERS WERE INJURED AS WERE TWO ORU GAS SERVICE TECHNICIANS. A TOTAL OF 94 GAS SERVICES WERE INTERRUPTED. THE MAJORITY OF THE SERVICES WERE RESTORED BY MIDNIGHT ON MONDAY, JANUARY 16, 2012. ALL SERVICES WERE RESTORED BY MID DAY ON THURSDAY, JANUARY 19, 2012. ELECTRIC SERVICE WAS INTERRUPTED TO 4,688 CUSTOMERS AFTER THE EXPLOSION TO MITIGATE ADDITIONAL IGNITION SOURCES. ONCE THE SITE WAS SECURE, SWITCHING TO RESTORE SERVICE COMMENCED WITH THE MAJORITY OF CUSTOMERS RETURNED TO SERVICE WITHIN TWO HOURS. ALL CUSTOMERS WERE RESTORED BY MIDNIGHT WITH THE EXCEPTION OF 3 DAMAGED UNITS AT THE IMPACT ZONE.
2025-03-31 10:13 | NO | NO | NO | 20120016 | 15425 | 2012-02-20 13:41 | SUPPLEMENTAL FINAL | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | ONE ENERGY PLAZA | DETROIT | MI | 48226-1221 | 2012-01-22 15:12 |  |  | 2012 | 15098 LAHSER ROAD | DETROIT | WAYNE | MI | 48223-1948 | 42.3989 | -83.2564 | [9 empty] | 2012-01-22 16:40 | 1000980 |  |  |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 8 | 2012-01-22 15:12 |  |  |  | 2012-01-22 15:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1998 | [8 empty] | STEEL |  |  |  | 0.133 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 51969 | 66088.9773 | 1549 | 1969.8633 | 1204 | 1531.1268 | 0 | 0 |  |  | 5 | 4.51374207188160676532769556025369978858 |  | 0 | 54727 | 28826.2528756871035940803382663847780127 | 69594.4811420718816067653276955602536998 | 0 | 0 | 1 |  |  |  |  | 2 | 2 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JOHN D LUEDERS | SUPERVISOR CODES AND STANDARDS | luedersj@dteenergy.com | 6166322646 | 6166322687 |  |  |  | ROBERT H FRECKELTON | MANAGER CODES AND STANDARDS | 3133897755 | freckeltonr@dteenergy.com | A STRUCTURE FIRE AT 15098 LAHSER WAS REPORTED TO MICHCON BY THE DETROIT FIRE DEPT. A MICHCON EMERGENCY RESPONSE TECHNICIAN FOUND A PRIVATE VEHICLE LODGED IN THE SOUTH WALL OF THE SINGLE-FAMILY RESIDENCE APPROX 40 FEET FROM THE ROADWAY. WITNESSES REPORTED THE VEHICLE TRAVELLING NORTH AT 60-80 MPH MOMENTS BEFORE IMPACT AND, HAVING DISREGARDED A TRAFFIC SIGNAL APPROX ONE-HALF BLOCK TO THE SOUTH, JUMPED THE CURB AND LEFT THE ROADWAY PRIOR TO STRIKING THE LAHSER RESIDENCE, BREACHING THE OUTSIDE WALL, AND COMING TO REST INSIDE A BEDROOM. FIRE IGNITED BY AN UNKNOWN SOURCE ENGULFED THE RESIDENCE AND THE VEHICLE. EIGHT PERSONS IN THE RESIDENCE SELF-EVACUATED WITHOUT INJURY. WITNESSES WERE UNABLE TO EXTRICATE THE VEHICLE DRIVER, WHO DIED AT THE SCENE FROM ACCIDENTAL INJURIES, FROM THE FIRE, OR A COMBINATION OF THESE. A PASSENGER IN THE VEHICLE WAS TAKEN TO A LOCAL HOSPITAL AND UNDERWENT SURGERY FOR INJURIES. A THIRD OCCUPANT OF THE VEHICLE REPORTEDLY FLED THE SCENE ON FOOT. ALCOHOL WAS SUSPECTED AS PLAYING A ROLE IN THE CRASH. BOTH THE VEHICLE AND THE RESIDENCE WERE TOTAL LOSSES. THE VEHICLE HAD STRUCK THE MICHCON GAS SERVICE RISER AND METER ASSEMBLY MOUNTED ON THE OUTSIDE OF THE SOUTH WALL OF THE RESIDENCE. THE STEEL PIPE CONNECTIONS AT THE SERVICE REGULATOR INLET AS WELL AS THE INLET OF THE UNION CONNECTION TO THE CUSTOMER'S FUEL PIPING WERE CRACKED AND COMPLETELY SEPARATED FROM THE SERVICE RISER AND THE FUEL CONNECTION, RESPECTIVELY. THE SERVICE REGULATOR AND METER ASSEMBLY WERE CATAPULTED INTO THE ADJACENT VACANT YARD, AND NATURAL GAS LEAKING FROM THE BREACHED SERVICE RISER IGNITED AND APPEARS TO HAVE CONTRIBUTED TO THE FIRE. RESCUERS HAD PULLED THE CRASHED VEHICLE FROM THE SIDE OF THE RESIDENCE IN AN ATTEMPT TO REACH THE DECEASED DRIVER; THE MOVEMENT OF THE VEHICLE AWAY FROM THE BUILDING CAUGHT THE REMAINDER OF THE LEAKING PLASTIC SERVICE RISER AND BENT IT AT 90 DEGREES AWAY FROM THE BUILDING, CRIMPING AND PARTIALLY CLOSING OFF THE PLASTIC TUBING AND LIMITING THE ESCAPING GAS. MICHCON PERSONNEL ARRIVING TO THE SCENE TEMPORARILY CAPPED THE DAMAGED SERVICE RISER AT THE BUILDING WALL TO ELIMINATE THE LEAK, THEN CUT OFF AND PERMANENTLY ABANDONED THE REMAINDER OF THE SERVICE LINE AT THE MAIN LATER THAT SAME EVENING. THE SERVICE LINE WILL NOT BE RETURNED TO OPERATION. NO SIGN OF A PRE-EXISTING GAS LEAK WAS FOUND AT THIS RESIDENCE, AT EITHER OF THE TWO ON EITHER SIDE, OR AT ANY OF THE THREE IMMEDIATELY ACROSS THE STREET.
2025-03-31 10:13 | NO | NO | NO | 20120017 | 15494 | 2012-02-24 16:54 | SUPPLEMENTAL | 31159 | KANSAS GAS SERVICE | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2012-01-31 11:15 |  |  | 2012 | 3820 FT. RILEY BLVD. | MANHATTAN | RILEY | KS | 66503 | 39.1594 | -96.6294 | [9 empty] | 2012-02-02 16:40 | 1002015 |  | NATURAL GAS |  | 4504 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-01-31 11:24 |  |  |  | 2012-01-31 11:35 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 16 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1957 | [5 empty] | 8.625 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE |  | 8 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 4868 | 6190.6356 | 1232 | 1566.7344 | 0 | 0 |  |  | 22900 | 20672.9386892177589852008456659619450317 |  | 0 | 29000 | 22336.5486469344608879492600422832980973 | 28430.3086892177589852008456659619450317 | 0 | 0 | 4 |  |  |  |  | 150 | 150 | 170 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, BECAUSE THE CONTROL ROOM RESPONDED APPROPRIATELY AND NOTIFICATION OF THE OPERATOR OF THE HIT LINE HAD ALREADY OCCURED. THE CONTRACTOR THAT DAMAGED PIPING NOTIFIED THE OPERATOR. CONTROL ROOM ALSO NOTICED THE PRESSURE DROP AND IMMEDIATELY NOTIFIED THE EFFECTED OPERATING AREA. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  |  |  | YES | [9 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | YES | 12031039 | ONLY ONE, ONE CALL SYSTEM |  | CONTRACT LOCATOR | YES | YES | 4 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | BRUCE D. KUBIE | MANAGER STANDARDS | bkubie@kgas.com | 785 431-4250 | 785 431-4224 |  |  |  | ROB GREEN | DIRECTOR GAS ENGINEERING | 785-431-4241 | rgreen@kgas.com | A CONTRACTOR PERFORMING ROAD GRADING BEGAN EARTH MOVING ACTIVITIES ON THE NORTH SIDE OF K-18. THE OPERATORS PIPELINE HAD BEEN LOCATED. THE GRADER (EARTH MOVER) CAUGHT HOLD OF AN 8" BARE STEEL MAIN THAT WAS 16" DEEP AND PULLED A 40' SECTION OF COUPLED MAIN OUT OF THE GROUND. NO FIRE OR EXPLOSIONS OCCURRED WITH THE RESULTANT RELEASE OF GAS. THE OPERATOR RESPONDED SHORTLY AFTER THE CONTRACTOR NOTIFIED THEM. THE OPERATOR'S GAS CONTROL FACILITY ALSO NOTICED THE DROP IN PRESSURE, DUE TO ALARM NOTIFICATION FROM THE SCADA SYSTEM, AND IMMEDIATELY NOTIFIED THE OPERATING AREA EFFECTED BY THE RELEASE. REPAIRS WERE MADE TO RECONNECT THE LINE AND THE FOUR CUSTOMERS THAT LOST SERVICE HAD SERVICE RESTORED IN FOUR HOURS. UPON DISCOVERY (TWO DAYS LATER) THAT THE GAS LOSS HAD EXCEEDED THE 3000 MCF THRESHOLD; THE TELEPHONIC NOTICE WAS MADE TO THE NRC. THE INITIAL GAS LOST WAS ESTIMATED AT 2000 MCF. THE ACTUAL GAS LOSS WHEN CALCULATED TOOK INTO CONSIDERATION THAT THE GAS LOSS WAS FED FROM EACH END OF THE PIPE SECTION THAT WAS PULLED APART MORE THAN DOUBLING THE AMOUNT OF GAS THAT WAS RELEASED.
2025-03-31 10:13 | NO | YES | YES | 20120018 | 15767 | 2012-02-29 15:06 | SUPPLEMENTAL FINAL | 31159 | KANSAS GAS SERVICE | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2012-01-30 11:35 |  |  | 2012 | 1905 SW NAVAJO | TOPEKA | SHAWNEE | KS | 66604 | 39.0333 | -95.7538 | [9 empty] | 2012-01-30 13:33 | 1001701 |  | NATURAL GAS |  | 54 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2012-01-30 11:37 |  |  |  | 2012-01-30 11:37 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 14 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1969 | [5 empty] | 1 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE |  | 1 | [7 empty] | CLASS 3 LOCATION | 350000 | 445095 | 720 | 915.624 | 42350 | 53856.495 | 0 | 0 |  |  | 309 | 278.949260042283298097251585623678646934 |  | 0 | 393379 | 207288.0133974630021141649048625792811839 | 500146.0682600422832980972515856236786469 | 0 | 0 | 77 |  |  |  |  | 45 | 45 | 58 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | TRENCHER | IRRIGATION | YES | 12006700 | ONLY ONE, ONE CALL SYSTEM |  | CONTRACT LOCATOR | YES | YES | 12 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | BRUCE D. KUBIE | MANAGER QA AND TRAINING | bkubie@kgas.com | 785 431-4250 | 785 431-4224 |  |  |  | TONY CELLITTI | MANAGER ENGINEERING | 913 599-8981 | tcellitti@kgas.com | ON THE MORNING OF JANUARY 30, 2012, GLEN NIEHUES, WITH N-LINE LAWN SERVICE, WAS TRENCHING NEAR A NATURAL GAS DISTRIBUTION MAIN EASEMENT WITH A VERMEER VIBRATORY PLOW AT 1912 SW ARROWHEAD RD. DURING HIS TRENCHING OPERATIONS, MR. NIEHUES HIT THE JUNCTURE WHERE THE NATURAL GAS SERVICE LINE CONNECTED TO THE MAIN, SEPARATING THE TWO LINES AND CAUSING NATURAL GAS TO DISCHARGE FROM KANSAS GAS SERVICE'S MAIN AT A PRESSURE OF APPROXIMATELY 45 PSI. MR. NIECHUES WAS EXCAVATING UNDER AN EXPIRED LOCATE TICKET AT THE TIME OF THE INCIDENT. DESPITE THE EXISTENCE OF PREVIOUS LOCATE MARKINGS AND THE EXCAVATOR HAVING POT-HOLED THE SERVICE LINE, THE SERVICE LINE WAS HIT BY MR. NIEHUES. SOMETIME AFTER THE SERVICE LINE WAS HIT, MR. NIEHUES CONTACTED KANSAS GAS SERVICE AND REPORTED THE INCIDENT AT 10:37 A.M. KANSAS GAS SERVICE'S FIRST RESPONDER ARRIVED ON THE SCENE AT APPROXIMATELY 11:05 A.M. AND SUMMONED A WORK CREW. AS THE WORK CREW BEGAN MAKING AN ASSESSMENT OF THE SCENE, THE HOUSE AT 1905 SW NAVAJO LANE, LOCATED ON THE OPPOSITE SIDE OF THE GAS DISTRIBUTION MAIN EASEMENT, CAUGHT FIRE AND EXPLODED. THE HOUSE AT 1905 SW NAVAJO LANE WAS OCCUPIED BY LUCINDA TOLLIVER. MS. TOLLIVER WAS SPOTTED AND RESCUED FROM THE HOUSE BY A KANSAS GAS SERVICE EMPLOYEE. SHE WAS HOSPITALIZED AND LATER DIED. 12/3/13 - NO ADDED INFORMATION - CHANGED STATUS FROM ORIGINAL TO FINAL. BDK
2025-03-31 10:13 | NO | YES | NO | 20120019 | 15415 | 2012-03-08 10:53 | ORIGINAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2012-02-10 05:00 |  |  | 2012 | 2825 1ST AVE. | SPEARFISH | LAWRENCE | SD | 57783 | 44.4804 | -103.8123 | [9 empty] | 2012-02-10 09:41 | 1002638 |  | NATURAL GAS |  | 120 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 5 | 2012-02-10 05:00 |  |  |  | 2012-02-10 05:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2004 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | METER/REGULATOR SET CRUSHED AND PULLED OFF RISER BY LOGGING TRAILER. | CLASS 3 LOCATION | 100000 | 127170 | 2500 | 3179.25 | 5500 | 6994.35 | 0 | 0 |  |  | 650 | 586.786469344608879492600422832980972516 |  | 0 | 108650 | 57426.411839323467230443974630021141649 | 137930.3864693446088794926004228329809725 | 0 | 0 | 0 |  |  |  |  | 35 | 35 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | RICKY SCHATZ | STAFF ENGINEER | ricky.schatz@mdu.com | 701-222-7768 | 701-222-7853 |  |  |  | RICKY SCHATZ | STAFF ENGINEER | 701-222-7768 | ricky.schatz@mdu.com | A LOGGING TRUCK WAS TRAVELING WEST ALONG I-90 THRU SPEARFISH. THE TRAILER DE-COUPLED FOM THE TRUCK, CAREENED DOWN THE OFF-RAMP, DOWN THE DITCH, THRU THE FENCE, AND CRASHED INTO THE WAL-MART BUILDING AND THE METER/REGULATOR SET. THE SUBSEQUENT CRASHED BROKE THE METER/REGULATOR SET OFF THE RISER AND PULLED ON DOWNSTREAM PIPING MOVING AND DAMAGING ROOFTOP HVAC UNITS.
2025-03-31 10:13 | NO | YES | NO | 20120020 | 15533 | 2012-03-09 11:00 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2012-02-11 10:22 |  |  | 2012 | 3056 LANFRANCO | LOS ANGELES | LOS ANGELES | CA | 90063 | 34.0338 | -118.2032 | [9 empty] | 2012-02-11 14:00 | 100275 |  | NATURAL GAS |  | 19 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 6 | 2012-02-11 10:22 |  |  |  | 2012-02-11 10:34 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1979 | [5 empty] | 1 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | [9 empty] | CLASS 3 LOCATION | 0 | 0 | 1000 | 1271.7 | 300 | 381.51 | 150000 | 190755 | FIRE DAMAGE. AMOUNT OF OPERATOR CONTRIBUTION UNDETERMINED AT THIS TIME. |  | 115 | 103.816067653276955602536997885835095137 |  | 0 | 151415 | 79785.7459408033826638477801268498942918 | 192512.0260676532769556025369978858350951 | 0 | 0 | 2 |  |  |  |  | 18 | 18 | 20 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | PLUMBER SNAKING A SEWER LATERAL | [154 empty] | W. JEFF KOSKIE | PIPELINE SAFETY ADVISOR | wkoskie@semprautilities.com | 213 305-8660 | 213 244-8155 |  |  |  | W. JEFF KOSKIE | PIPELINE SAFETY ADVISOR | 213 305-8660 | wkoskie@semprautilities.com | PLUMBER STRUCK 1" PE SERVICE WHILE USING SNAKE TO CLEAR SEWER LINE BLOCKAGE. ESCAPING GAS IGNITED, DAMAGING HOME. NO INJURIES. ONE CUSTOMER RESTORED, SECOND WILL BE OUT OF SERVICE UNTIL FIRE DAMAGE TO HOUSE IS REPAIRED. INVESTIGATION DETERMINED GAS SERVICE WAS INSTALLED AT THIS LOCATION USING TRENCHLESS BORING CONSTRUCTION TECHNIQUES IN 1979. BORE WENT THROUGH NON-METALLIC SEWER LATERAL PLUMBER DID NOT FOLLOW SOCALGAS RECOMMENDATION/REQUEST TO CONTACT THE UTILITY PRIOR TO CLEARING BLOCKAGES IN AN EXTERIOR SEWER LINE.
2025-03-31 10:13 | NO | YES | NO | 20120022 | 15419 | 2012-03-12 13:21 | ORIGINAL | 1088 | BALTIMORE GAS & ELECTRIC CO | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2012-02-13 23:21 |  |  | 2012 | 314 MILLINGTON AV | BALTIMORE |  | MD | 21223 | 39.2818 | -76.6575 | [9 empty] | 2012-02-14 04:23 | 100291 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-02-13 23:51 |  |  |  | 2012-02-13 23:51 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 38 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1909 | [5 empty] | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | OTHER | [8 empty] | MAIN DAMAGED BY BALTIMORE CITY WATER DEPARTMENT DURING WATER MAIN REPAIR. LARGE PIECE OF ASPHALT FELL ON GAS MAIN AND BROKE MAIN ALLOWING WATER TO ENTER INTO THE DISTRIBUTION SYSTEM. | CLASS 2 LOCATION | 175000 | 222547.5 | 150000 | 190755 | 612226 | 778567.8042 | 25000 | 31792.5 | ESTIMATED COST THROUGH 3/6/2012. |  | 0 | 0 |  | 0 | 962226 | 506804.4342 | 1223662.8042 | 0 | 45 | 1000 |  |  |  |  | 0.28 | 0.28 | 0.36 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | BALTIMORE DEPT OF PUBLIC WORKS |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | WATER | YES | 12067226 | MISS UTILITY |  | CONTRACT LOCATOR | YES | YES | 58 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | MICHAEL GROSSCUP | SPECIAL FIELD OPERATIONS SUPERVISOR | michael.a.grosscup@bge.com | 443-250-8167 | 410-740-7103 |  |  |  | WILLIAM BROWN | MANGER GAS SERVICE | 410-470-7105 | william.h.brown@bge.com | BALTIMORE CITY DEPT OF PUBLIC WORKS DAMAGED A BGE 4 INCH CAST IRON LOW PREASURE MAIN ON 2/13/2012 AT 23:21. WHEN A PIECE OF ASPHALT FELL INTO THE OPEN TRENCH WHILE EXCAVATION TO REPAIR A BROKEN WATER MAIN. BGE'S FIRST RESPONDER ARRIVED ON SITE AT MILLINGTON AND SLOTHFIELD AVENUES, AND FOUND A LARGE WATER LEAK FROM AN APPARENT BROKEN WATER MAIN. THE FIRST RESPONDER CANVASSED THE AREA AND FOUND WATER HAD ENTERED INTO THE CUSTOMER'S FUEL LINES AT 2301 AND 2701 WILKENS AV. WATER FROM THE CITIES WATER MAIN HAD ENTERED INTO BGE'S DISTRIBUTION SYSTEM THROUGH THE DAMAGED 4" GAS MAIN.THE WATER PRESSURIZED AND FILLED A POTION OF THE GAS DISTRIBUTION SYSTEM CAUSING AN OUTAGE THAT AFFECTED APPROXIMATELY 1045 OF BGE'S CUSTOMERS. REPAIRS WERE MADE TO THE DISTRIBUTION SYSTEM AND APPROXIMITY 12,000 GALLONS OF WATER WERE REMOVED FROM THE GAS MAINS. 500 GAS SERVICES WERE CLEARED OF WATER, AND 450 GAS METERS WERE REPLACED. SERVICE WAS RESTORED TO CUSTOMERS METERS BY 19:00 ON SUNDAY 02/19/2012.
2025-03-31 10:13 | NO | NO | NO | 20120024 | 15959 | 2012-03-13 16:47 | SUPPLEMENTAL FINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2012-03-09 06:00 |  |  | 2012 | 4213 S 37TH STREET | OMAHA | DOUGLAS | NE | 68107 | 41.2181 | -95.9684 | [9 empty] | 2012-03-09 10:25 | 1005224 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2012-03-09 06:00 |  |  |  | 2012-03-09 06:09 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | INSIDE METER/REGULATOR SET |  | 1954 | [8 empty] | STEEL |  |  |  | 0.145 | [6 empty] | LEAK |  |  | OTHER | UNKNOWN AT THIS TIME | [5 empty] | CLASS 1 LOCATION | 50000 | 63585 | 2000 | 2543.4 | 0 | 0 | 0 | 0 |  |  | 1000 | 902.748414376321353065539112050739957717 |  | 0 | 53000 | 28223.495137420718816067653276955602537 | 67031.1484143763213530655391120507399577 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 0.25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CONATINED TO THE SINGLE RESIDENCE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | OTHER | MUD HAS CONCLUDED THAT THAT THE SOURCE OF THE GAS LEAK WAS THE INLET SWIVEL WHERE THE GAS SERVICE LINE CONNECTS TO THE GAS METER. MUD BELIEVES THAT THE INLET SWIVEL WAS INTENTIONALLY LOOSENED BY SOME PERSON OR PERSONS. THIS CONCLUSION IS BASED UPON THE PHYSICAL CONDITION OF THE GAS METER, THE PHYSICAL CONDITION OF THE GAS PIPING, THE DESCRIPTIONS OF THE FIRE EXPLOSION FROM WITNESSES AND MUD EMPLOYEE'S EXPERIENCE AND KNOWLEDGE OF GAS AND GAS DISTRIBUTION SYSTEMS. | [155 empty] | MICHAEL CONRAD | CLAIMS ADJUSTER | mike_conrad@mudnebr.com | 402-504-7165 | 402-504-5165 |  |  |  | MICHAEL CONRAD | CLAIMS ADJUSTER | 402-504-7165 | mike_conrad@mudnebr.com | AT APPROXIMATELY 0600HRS THE METROPOLITAN UTITLITES DISTRICT WAS NOTIFIED BY THE OMAHA FIRE DEPT. OF A WORKING FIRE AT 4213 S 13TH ST.. DISTRICT PERSONNEL ARRIVED AND ASSISTED THE OFD IN SHUTTING OFF THE GAS TO THIS RESIDENCE. IT WAS THEN DETERMINED THAT IT APPEARD THAT THERE WAS A POTENTIAL OF A NATURAL GAS EXPLOSION/IGNITION THAT CONTRIBUTED TO THIS INCIDENT/LOSS. THE EXACT CAUSE OF THE IGNITION SOURCE OR THE AREA WHERE GAS MAY HAVE BEEN RELEASED HAS NOT BEEN DETERMINED AS OF YET. ON 3/14/12 THERE WILL BE A COMBINED INVESTIGATION WITH SEVERAL PARTIES OF INTEREST TO TRY AND LOCATE THE ORIGIN OF THE LEAK AND OR THE CAUSE OF THE LOSS. 10/11/12- OUR INVESTIGATION REVEALED THAT THE COCK VALVE ON THE INSIDE OF THE DWELLING HAD A LEAK IN THE PACKING AND THE GAS ESCAPED THE COCK VALVE AND MIGRATED TOWARDS THE FURNACE AREA OF THE DWELLING. DUE TO THE HOUSE BEING VACANT AND VENELATION WAS MINIMAL THERE ENDED UP BEING A BUILD UP IN THE FURNACE AREA AND WHEN THE FURNACE CYCLED IT IGNITED THE GAS AND THE RESULT OF THIS IGNITION WAS THE LOSS OF THIS DWELLING. THE GAS SERVICE TO THE DWELLING WAS ABANDONED AT THE MAIN ON THE DAY OF THE LOSS AND THE DWELLING SINCE HAS BEEN TORN DOWN DUE TO THE LOSS. 10/22/12- THE INVESTIGATION REVEALED THAT ON THE UPSTREAM SIDE OF THE INSIDE METER, THE OPERATOR OWNED COCK VALVE LEAKED IN THE PACKING AND RELEASED NATURAL GAS INTO THE ATMOSPHERE. THE NATURAL GAS THAT WAS RELEASED, WHICH WAS THE FUEL SOURCE,IGNITED WHEN THE FURNACE CYCLED AND THE RESULT WAS THE LOSS THAT WAS BEEN REPORTED. OUR INVESTIGATION IS CLOSED IN REGARD TO THIS MATTER AND THIS ENTRY SHALL SERVE AS OUR FINAL ENTRY IN REGARD TO THIS MATTER. 11/10/14- MUD HAS CONTINUED ITS INVESTIGATION INTO THE CAUSE OF THE EXPLOSION AND FIRE AND, AS A RESULT, NOW DRAWS A DIFFERENT CONCLUSION THAN PREVIOUSLY ENTERED ON THIS REPORT. AS A RESULT OF THIS CONTINUED INVESTIGATION, MUD BELIEVES THAT THE PRIMARY GAS SOURCE THAT CAUSED THE EXPLOSION AND SUBSEQUENT FIRE WAS THE INLET SWIVEL AND NOT THE GAS COCK VALVE. THIS CONCLUSION IS BASED UPON THE CONDITION OF THE METER, THE DESCRIPTIONS OF THE FIRE WHEN THE FIRE DEPARTMENT AND MUD PERSONAL ARRIVED ON SCENE AND MUD EMPLOYEE'S EXPERIENCE AND KNOWLEDGE OF GAS AND GAS DISTRIBUTION SYSTEMS. MUD BELIEVES THAT THE ONLY WAY THE INLET SWIVEL COULD HAVE HAVE BEEN THE CAUSE OF THE LEAK WAS FOR THE INLET SWIVEL TO HAVE BEEN INTENTIONALLY LOOSENED FROM THE GAS METER. MUD BELIEVES THAT THE GAS COCK VALVE MOST LIKELY BECAME LOOSENED AS A RESULT OF THE EXTREME HEAT FROM THE INITIAL EXPLOSION AND RESULTING FIRE BUT THAT THE GAS COCK VALVE DID NOT CAUSE THE EXPLOSION AND SUBSEQUENT FIRE. MUD'S INVESTIGATION IS NOW CLOSED WITH RESPECT TO THIS MATTER AND IS THE SUBJECT OF ONGOING LITIGATION BETWEEN THE HOMEOWNER'S INSURANCE PROVIDER AND MUD.
2025-03-31 10:13 | NO | YES | YES | 20120025 | 15917 | 2012-03-16 13:59 | SUPPLEMENTAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY | 1301 S MOPAC EXPY, SUITE 400 | AUSTIN | TX | 78746-6918 | 2012-02-17 19:30 |  |  | 2012 | 2807 WONG PL | EL PASO | EL PASO | TX | 79936 | 31.7808 | -106.3139 | [9 empty] | 2012-02-18 00:30 | 100333 |  | NATURAL GAS |  | 4.8 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2012-02-17 19:30 |  |  |  | 2012-02-17 22:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1985 | [5 empty] | 0.5 | ASTMD2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 3000 | 3815.1 | 0 | 0 | 21500 | 27341.55 | MEDICAL |  | 20 | 18.05496828752642706131078224101479915433 |  | 0 | 24520 | 12920.8519027484143763213530655391120507 | 31174.7049682875264270613107822410147992 | 0 | 0 | 2 |  |  |  |  | 35 | 35 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | PE CAP ON SERVICE TAP CRACKED |  |  |  |  | YES | [9 empty] | YES |  |  |  | OTHER | PE CAP CRACKED | NO | [86 empty] | MARK MONTGOMERY P.E. | DIRECTOR OF ENGINEERING AND COMPLIANCE | mbmontgomery@txgas.com | (512) 370-8348 | (512) 370-8254 |  |  |  | MARK MONTGOMERY P.E. | DIRECTOR OF ENGINEERING AND COMPLIANCE | (512) 370-8348 | mbmontgomery@txgas.com | ON FRIDAY FEBRUARY 17, 2012 AT 19:30, A TEXAS GAS SERVICE EMPLOYEE RECEIVED A FLASH FIRE BURN WHILE EXCAVATING A LEAK. THIS LEAK WAS THE RESULT OF A CRACKED CAP ON A POLYETHYLENE SERVICE TEE AT 2807 WONG PLACE IN EL PASO, TX. WHILE EXCAVATING, THE PORTABLE LIGHTS USED TO ILLUMINATE THE EXCAVATION AREA FELL OVER, A BULB BROKE AND IGNITED RESIDUAL GAS. THE EMPLOYEE WAS TRANSPORTED TO THE MEDICAL FACILITY AND HOSPITALIZED.
2025-03-31 10:13 | NO | YES | YES | 20120028 | 15430 | 2012-04-05 09:53 | ORIGINAL FINAL | 11336 | LEBANON GAS DEPT, CITY OF | 215 MADDOX SIMPSON PARKWAY | LEBANON | TN | 37090 | 2012-02-28 13:25 |  |  | 2012 | 1213 LEEVILLE PIKE | LEBANON | WILSON | TN | 37087 | 36.1972 | -86.3198 | [9 empty] | 2012-02-28 14:30 | 1004254 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 5 | 2012-02-28 13:25 |  |  |  | 2012-02-28 13:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 2005 | [5 empty] | 1.25 | UNKNOWN | POLYPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | OTHER | [8 empty] | TRENCHER CUT | CLASS 1 LOCATION | 10000 | 12717 | 250 | 317.925 | 750 | 953.775 | 0 | 0 |  |  | 1 | 0.9027484143763213530655391120507399577167 |  | 0 | 11001 | 5794.535095137420718816067653276955602537 | 13989.60274841437632135306553911205074 | 1 | 0 | 0 |  |  |  |  | 42 | 42 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | CITY STREET | [12 empty] | MUNICIPALITY | TRENCHER | ELECTRIC | NO |  |  |  | UTILITY OWNER | NO |  |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JERRY SNODGRASS | MANAGER | jerry.snodgrass@lebanontn.org | 615-443-2835 | 615-443-2807 |  |  |  | JERRY SNODGRASS | MANAGER | 615-443-2835 | jerry.snodgrass@lebanontn.org | SCHOOL MAINTENANCE WORKERS CALLED IN WRONG LOCATION OF DIG SITE, TRENCHED THROUGH 1.25 SERVICE LINE THAT WAS NOT MARKED. WORKER RECIEVED MINOR BURNS TO FACE AND RIGHT ARM. WALK BEHIND TRENCHER WAS TOTAL LOSS.
2025-03-31 10:13 | NO | YES | YES | 20120029 | 15685 | 2012-04-06 17:01 | SUPPLEMENTAL FINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2012-04-05 13:35 |  |  | 2012 | N SKYLINE DR. & BRITTNAY CIRCLE | OMAHA | DOUGLAS | NE | 68022 | 41.2716 | -96.2439 | [9 empty] | 2012-04-05 16:48 | 1007915 |  | NATURAL GAS |  | 150 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO |  |  |  |  | NO | 8 | 2012-04-05 13:35 |  |  |  | 2012-04-05 13:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | COMPLETION PLUG BLEW OUT OF STOPPLE/CONTROL FITTING | CLASS 1 LOCATION | 0 | 0 | 2500 | 3179.25 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 2500 | 1316.75 | 3179.25 | 0 | 0 | 8 |  |  |  |  | 60 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, IT WAS DETERMINED THAT THE CONTROL ROOM WAS NOT INVOLVED IN THIS INCIDENT. | [12 empty] | YES | 6 | 0 | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [8 empty] | YES | [74 empty] | MICHAEL CONRAD | CLAIMS ADJUSTER | mike_conrad@mudnebr.com | 402-504-7165 | 402-504-5165 |  |  |  | MICHAEL CONRAD | CLAIMS ADJUSTER | 402-504-7165 | mike_conrad@mudnebraska.com | ON 4/5/12 AT 1335 HRS AT N SKYLINE DR & BRITTNAY CIR IN DOUGLAS COUNTY NEBRASKA THE METROPOLITAN UTILITIES DISTRICT HAD EMPLOYEES INSTALLING STOPPLE/CONTROL FITTINGS ON A NEWLY AQUIRED 4" STEEL GAS MAIN WHEN THE COMPLETION PLUG BLEW OUT OF THE STOPPLE/CONTROL FITTING AND CAUSED STEEL SHRAPNEL TO BE EMBEDDED IN THE FACES OF THREE EMPLOYEES. TWO OF THE EMPLOYEES WERE TREATED AT THE SCENE AND RELEASED, THE THIRD EMPLOYEE WAS TRANSPORTED BY EMS TO THE CREIGHTON MEDICAL CENTER IN OMAHA NEBRASKA WHERE HE WAS KEPT OVER NIGHT FOR OBSERVATION. THE EMPLOYEE WHO WAS HOSPITALIZED WAS RELEASED ON 4/6/12 BY CREIGHTON MEDICAL CENTER. 6/17/13- WE ARE UNABLE TO SAY WITH CERTANTY TO WHAT REALLY HAPPENED ON 4/5/12. THE FITTING AND COMPLETION PLUG ARE BOTH RELATIVELY UNDAMGED AND STILL FIT TOGETHER WITH EASE. THE EMPLOYEES INVOLVED BELIEVE THAT THE TAP AND STOP WERE MADE PROPERLY, A POSSIBLE THEORY IS THE PLUG WAS SLIGHTLY ENGAGED INTO THE FITTING AT THE TIME THE SLIDE VALVE WAS REMOVED, THE OPERATING OF THE SLIDE VALVE WAS ENOUGH TO JAR THE COMPLETION PLUG LOOSE. ALL OF THE TEST RESULTS FAILED TO INDICATE WHAT MAY HAVE OR ACTUALLY HAPPENED. THE METROPLITAN UTILITES DISTRICT HAS COMPLETED ALL INVESTIGATIONS IN REGARD TO THIS INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20120031 | 15435 | 2012-04-20 14:10 | ORIGINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-03-23 03:08 |  |  | 2012 | 529 W 217 STREET | NEW YORK | NEW YORK | NY | 10034-1302 | 40.8714 | -73.9165 | [9 empty] | 2012-03-23 04:46 | 1006642 |  | NATURAL GAS |  | 2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2012-03-23 03:08 |  |  |  | 2012-03-23 03:34 |  | NO | PUBLIC PROPERTY | UNDERGROUND | OTHER | GAS FED FIRE REPORTED @ ELECTRIC MANHOLE | 33 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1983 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | POSSIBLE 1.25" LPPE SERVICE DAMAGED DUE TO ELECTRIC BURNOUT CAUSING GAS IGNITION IN ELECTRIC MANHOLE---INVESTIGATION ONGOING | CLASS 4 LOCATION | 75000 | 95377.5 | 100 | 127.17 | 575 | 731.2275 | 0 | 0 |  |  | 10 | 9.02748414376321353065539112050739957717 |  | 0 | 75685 | 39866.3734513742071881606765327695560254 | 96244.9249841437632135306553911205073996 | 0 | 0 | 3 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-579-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-579-2350 | dadariov@coned.com | ON FRIDAY MARCH 23, 2012 AT 03:03 THE FIRE DEPARTMENT OF NEW YORK CITY (FDNY) REPORTED A TWO ALARM FIRE AT 529 WEST 217 STREET TO THE GAS EMERGENCY RESPONSE CENTER (GERC). THE GERC NOTIFIED SUPERVISION AND DISPATCHED GAS DISTRIBUTION SERVICES (GDS). WHILE GDS WAS ENROUTE THE FDNY CALLED BACK AT 03:15 AND STATED THAT THE FIRE WAS GAS FED. A CODE MURRE WAS INITIATED AND THE GERC DISPATCHED A CONSTRUCTION CREW. AT 03:19 THE FDNY CALLED THE GERC AGAIN AND REPORTED A SUBSURFACE STRUCTURE FIRE AT THE SAME LOCATION. ELECTRIC OPERATIONS WAS ASSIGNED AND UPON ARRIVAL GDS REPORTED THAT THERE WAS A HEAVY SMOKE CONDITION AT ELECTRIC SERVICE BOX 24282 IN FRONT OF 527 WEST 217 STREET BUT NO FIRE. GDS CLOSED TWO LOW PRESSURE CURB VALVES SUPPLYING # 529 AND #531 W. 217 ST. AT 04:30 CHANNEL 11 NEWS REPORTED THE FIRE MAY BE GAS RELATED AND/OR A COMBINED GAS AND ELECTRIC EVENT. AT 05:39 THE FDNY EVACUATED 3 OCCUPANTS FROM APARTMENT D-29 AT 520 W 217 ST. DUE TO 164 PPM CO READINGS IN THE ATMOSPHERE OF THE APARTMENT 28-D DUE TO 450 TO 700 PPM CO IN BASEMENT DIRECTLY BELOW THE APARTMENT AND VENTED THE BUILDING. THE FDNY FIRE MARSHAL RESPONDED AND THE INVESTIGATION IS ONGOING. THE US DOT, NYS PSC AND NYC DEP WERE NOTIFIED. THIS WAS A SERIOUS LEVEL INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20120032 | 15436 | 2012-04-20 14:33 | ORIGINAL | 1088 | BALTIMORE GAS & ELECTRIC CO | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2012-03-28 16:30 |  |  | 2012 | 8821 HOWARD-FOREST LA | BALTIMORE | BALTIMORE COUNTY | MD | 21208 | 39.3917 | -76.7384 | [9 empty] | 2012-03-28 18:56 | 1007150 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 15 | 2012-03-28 18:08 |  |  |  | 2012-03-28 18:08 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1997 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 3408 | MECHANICAL PUNCTURE | [9 empty] | CLASS 4 LOCATION | 40000 | 50868 | 300 | 381.51 | 5000 | 6358.5 | 0 | 0 | UNDETERMIND COST OF THE LANDSCAPERS FORD 4 DOOR STAKE BODY STYLE TRUCK. |  | 15 | 13.54122621564482029598308668076109936575 |  | 0 | 45315 | 23872.0364270613107822410147991543340381 | 57621.5512262156448202959830866807610994 | 0 | 0 | 1 |  |  |  |  | 93 | 99 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MICHAEL J SIMMONS | GAS SERVICE SUPERVISOR | michael.j.simmons@constellation.com | 410-470-7095 | 410-470-7099 |  |  |  | WILLIAM H. BROWN | MANAGER | 410-470-7106 | william.h.brwon@bge.com | ON 3/28/12 AT APPROXIMATELY 16:30 A LANDSCAPING TRUCK LOST CONTROL OF THEIR VEHICLE AND STRUCK THE FRONT OF A RESIDENTIAL HOUSE. THE TRUCK WAS A F450/F550 STAKE BODY STYLE TRUCK AND IT WAS LOADED FULL OF DIRT AND MULCH. THE TRUCK WAS HEADING SOUTH DOWN OLD PLANTATION WAY AND TRIED TO TURN LEFT ONTO HOWARD-FOREST LA. THE TRUCK LOST CONTROL IN THE TURN AND STRUCK THE FRONT OF 8821 HOWARD-FOREST LA. THE HOUSE SITS ABOUT 25FT OFF THE ROAD. ONCE THE TRUCK STRUCK THE HOUSE AT THE SAME TIME IT ALSO STRUCK THE GAS AND ELECTRIC METER INSTALLATIONS THAT WERE LOCATED OUTSIDE ON THE FRONT OF THE HOUSE. THE OUTSIDE 3/4 HP STEEL RISER WAS DAMAGED AND THEN IGNITED CAUSING THE GAS FED FIRE. THE GAS SERVICE WAS DUG UP IN THE FRONT YARD AND PINCHED OFF BY GAS SERVICE/M&R AT 18:21. ONCE THE FIRE DEPT MADE THE AREA SAFE THE GAS EQUIPMENT WAS REMOVED AND THE SERVICE CUT AND CAPPED IN THE FRONT YARD. DRIVING DOWN OLD PLANTATION WAY THE ROAD HAS A SLIGHT INCLINE HEADING TOWARDS HOWARD-FOREST LA. WEATHER CONDITIONS, THERE WAS A PASSING SHOWER AT THE TIME OF THE INCIDENT AND THE ROADWAYS WERE WET.
2025-03-31 10:13 | NO | YES | NO | 20120033 | 15493 | 2012-04-27 15:56 | SUPPLEMENTAL FINAL | 4060 | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2012-03-29 12:27 |  |  | 2012 | 2111 ACACIA PARK DR | LYNDHURST | CUYAHOGA | OH | 44124 | 41.5029 | -81.4817 | [9 empty] | 2012-03-29 14:18 | 1007229 |  | NATURAL GAS |  | 606 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 190 | 2012-03-29 12:37 |  |  |  | 2012-03-29 12:54 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 31 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1971 | [5 empty] | 3 | UNKNOWN | UNKNOWN | OTHER | FIBERGLASS | [9 empty] | MECHANICAL PUNCTURE | 8 | 2 | [7 empty] | CLASS 3 LOCATION | 3500000 | 4450950 | 29466 | 37471.9122 | 5000 | 6358.5 | 0 | 0 |  |  | 2500 | 2256.871035940803382663847780126849894292 |  | 0 | 3536966 | 1863690.98004355179704016913319238900634 | 4497037.28323594080338266384778012684989 | 1 | 0 | 0 |  |  |  |  | 45 | 45 | 56 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | AUGER | BUILDING CONSTRUCTION | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 1722 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | AARON MCCOY | TECHNICAL SPECIALIST | aaron.m.mccoy@dom.com | 330.458.9186 | 330.478.3760 |  |  |  | AARON MCCOY | TECHNICAL SPECIALIST | 330.458.9186 | aaron.m.mccoy@dom.com | AT APPROXIMATELY 12:27 P.M. ON MARCH 29, 2012, AN APARTMENT COMPLEX LOCATED AT 2111 ACACIA PARK DRIVE, LYNDHURST, OHIO WAS INVOLVED IN A FIRE. DOMINION RECEIVED NOTIFICATION FROM THE LYNDHURST FIRE DEPARTMENT AT APPROXIMATELY 12:37 P.M. AND DISPATCHED CUSTOMER SERVICE PERSONNEL. FIRST RESPONDERS ARRIVED AT THE SCENE AT 12:54 P.M. A CONSTRUCTION CREW DISPATCHED TO THE SCENE LOCATED THE BURRIED GATE VALVE, UNDER 18 INCHES OF SOIL, AND SHUT IT OFF AT 3:15 P.M. INVESTIGATION REVEALED THAT HIGGINS CONSTRUCTION WAS EXCAVATING TO ADD SUPPORTS FOR THE BALCONIES AT THE APARTMENT COMPLEX. HIGGINS CONSTRUCTION CAUSED THE DAMAGE WHEN THEIR AUGER PUNCTURED A 45 PSIG, 3 INCH FIBERGLASS SERVICE LINE. NO NOTIFICATION WAS MADE TO OUPS PRIOR TO THIS EXCAVATION ACTIVITY.
2025-03-31 10:13 | NO | YES | YES | 20120038 | 15446 | 2012-05-08 17:16 | ORIGINAL FINAL | 603 | RELIANT ENERGY ARKLA, DIV OF RELIANT ENERGY RESOURC | 10825 E GEDDES AVE SUITE 410 | CENTENNIAL | CO | 80112 | 2012-04-09 14:32 |  |  | 2012 | 4501 E MAIN | WEATHERFORD | CUSTER | OK | 73096 | 35.5351 | -98.6801 | [9 empty] | 2012-04-09 19:05 | 1008198 |  | NATURAL GAS |  | 157 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2012-04-09 14:32 |  |  |  | 2012-04-09 14:43 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 40 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1979 | [5 empty] | 2 | ASTM D2513 | NIPAK | PLASTIC | NIPAK ASTM D2513 |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 46254 | 58821.2118 | 5541 | 7046.4897 | 3051 | 3879.9567 | 0 | 0 | COST ABOVE REFLECT TOTAL COST WITH EXCEPTION OF GAS LOST |  | 746 | 673.450317124735729386892177589852008457 |  | 0 | 55592 | 29510.3691725158562367864693446088794926 | 70421.1085171247357293868921775898520085 | 54 | 0 | 3 |  |  |  |  | 42 | 42 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO | NO | NO | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 4 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | UTILITY | TRENCHER | TELECOMMUNICATIONS | YES | 12040408130198 |  |  | UTILITY OWNER | YES | YES | 20 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | GERAL KOLB | DISTRICT OPERATIONS MANAGER | gerald.kolb@centerpointenergy.com | 580-250-5490 | 580-250-5415 |  |  |  | KEITH A. KITTINGER | REGIONAL OPERATIONS DIRECTOR | 501-377-4669 | keith.kittinger@centerpointenergy.com | MAIN HAD BEEN LOCATED BY COMPANY EMPLOYEE. EMPLOYEE STATED THAT TONE FROM LOCATOR WAS GOOD FOR THE ENTIRE LOCATE. (MAIN HAD BEEN REPLACED WITH 2" PLASTIC IN MARCH OF 1979). THIRD PARTY INSTALLING FIBER OPTIC CABLE CUT 2" PLASTIC MAIN. IT WAS DETERMINED TO HAVE BEEN LOCATED INACCURATELY DUE TO AN INCORRECT MANUAL MAP POSTING OF THE 2" PLASTIC OFFSET ON A PAPER MAP (HAS SINCE BEEN CONVERTED TO AN ELECTRONIC MAP). BELL HOLES WERE DUG TO INSTALL A BYPASS AROUND THE DAMAGE. EMPLOYEES INSTALLED TAPS ON EITHER SIDE OF THE DAMAGE. AS EMPLOYEE BEGAN TO TAP OUT THE TAPPING TEE IN THE NORTH BELL HOLE, NATURAL GAS IGNITED AT APPROXIMATELY 17:15 HOURS ON APRIL 9, 2012. THE ACTUAL SOURCE OF IGNITION IS UNDETERMINED. THE BURNING NATURAL GAS IGNITED THE THIRD PARTIES TRENCHER AND SCORCHED A PIECE OF EQUIPMENT LOCATED AT THE FARM IMPLEMENT DEALERSHIP. EMT RESPONDED AND TRANSPORTED ONE (1) COMPANY EMPLOYEE TO HOSPITAL FOR BURN TREATMENT. THE REMAINING EMPLOYEES WERE NOT INJURED AND PLUGGED OFF THE 3" STEEL NATURAL GAS LINE AT APPROXIMATELY 18:55 HOURS. ALL FOUR (4) EMPLOYEES WERE DRUG AND ALCOHOL TESTED THE SAME EVENING (1 EMPLOYEE AT 22:00 HOURS AND 3 EMPLOYEES AT 23:30 HOURS). ALL EMPLOYEES RECEIVED NEGATIVE TEST RESULTS. THE FOLLOWING DAY THE LINE WAS REPAIRED AND ALL AFFECTED CUSTOMER WERE RESTORED.
2025-03-31 10:13 | NO | YES | NO | 20120039 | 15549 | 2012-05-09 11:27 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2012-04-08 03:20 |  |  | 2012 | 974 SOUTH J STREET | OAKDALE | STANISLAUS | CA | 95361 | 37.7646 | -120.8382 | [9 empty] | 2012-04-08 05:50 | 1008076 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2012-04-08 04:00 |  |  |  | 2012-04-08 04:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND |  |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL | METER SET | [9 empty] | OTHER |  |  | OTHER | VEHICLE HIT METER SET | OTHER | VEHICLE HIT METER SET |  |  | VEHICLE HIT METER SET | CLASS 3 LOCATION | 100000 | 127170 | 2000 | 2543.4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 102000 | 53723.4 | 129713.4 | 0 | 0 | 3 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA ON THIS PART OF THE SYSTEM | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LAURENCE DENISTON | SR. PROGRAM MANAGER | lcd1@pge.com | 925 974 4313 |  |  |  |  | BILL GIBSON | DIRECTOR REGULATORY COMPLIANCE AND SUPPORT | 925 974 4210 | wlg3@pge.com | AT APPROXIMATELY 0320 HOURS, A THIRD-PARTY LOST CONTROL OF THEIR VEHICLE, DROVE THROUGH TWO FENCES AND STRUCK A RESIDENTIAL METER SET. THE CAR, GARAGE AND A PORTION OF THE HOUSE CAUGHT FIRE AFTER THE VEHICLE IMPACT. THE METER SET WAS LOCATED AT THE SIDE OF THE GARAGE AND PROTECTED BY FENCING AND THE GARAGE WALL FROM LOW VELOCITY IMPACTS. THE FIRE DEPARTMENT WAS ON SITE WHEN PG&E'S CREW ARRIVED ON SCENE. PG&E CREWS WERE ON SITE AT 0430 HOURS AND THE FLOW OF GAS WAS STOPPED AT 0517 HOURS BY SQUEEZING OFF THE SERVICE LINE IN THE FRONT YARD OF THE HOUSE. THREE CUSTOMERS LOST SERVICE AS A RESULT OF THIS INCIDENT. THERE WERE NO FATALITIES OR INJURIES. DAMAGES EXCEED $50,000. THIS BECAME A CPUC AND DOT REPORTABLE INCIDENT WHEN IT WAS DETERMINED THAT DAMAGES WOULD EXCEED $50,000.
2025-03-31 10:13 | NO | NO | NO | 20120040 | 15451 | 2012-05-18 18:19 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2012-04-17 11:20 |  |  | 2012 | BLACK MOUNTAIN RD. & DENISE DR. | HILLSBOROUGH | SAN MATEO | CA | 94010 | 37.5454 | -122.3657 | [9 empty] | 2012-04-20 18:25 | 1009267 |  | NATURAL GAS |  | 872 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-04-17 11:20 |  |  |  | 2012-04-17 11:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2011 | [5 empty] | 2 | API 5L | UNKNOWN | STEEL |  |  |  | 0.154 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 51000 | 64856.7 | 0 | 0 | 0 | 0 |  |  | 2600 | 2347.145877378435517970401691331923890063 |  | 0 | 53600 | 29032.9473572938689217758985200845665962 | 67203.8458773784355179704016913319238901 | 0 | 0 | 0 |  |  |  |  | 285 | 285 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS CAUSED BY A POOR WELD. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | MATERIAL FAILURE OF PIPE OR WELD | BUTT WELD | [146 empty] | BUTT WELD |  |  | OTHER | TIE-IN WELD | [26 empty] | YES |  | YES | [7 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | YES | 2011 | 700 | [84 empty] | LAURENCE DENISTON | SR. PROGRAM MANAGER | lcd1@pge.com | 9259744313 |  |  |  |  | BILL GIBSON | DIRECTOR REGULATORY COMPLIANCE AND SUPPORT | 9259744210 | wlg3@pge.com | ON APRIL 17, 2012 A GAS LEAK WAS FOUND DURING ROUTINE LEAK SURVEY ON A 2-INCH DISTRIBUTION FEEDER MAIN (DFDS3639) TAPPED DIRECTLY OFF OF TRANSMISSION LINE 132 AT MP 32.32. UPON EXCAVATION, THREE 2-INCH GIRTH WELDS WERE FOUND LEAKING. ON APRIL 19, 2012 TL-132 WAS DEPRESSURIZED FROM MP 31.93 TO MP 36.99 TO MAKE WELD REPAIRS ON THE 2-INCH PIPE. THE REPAIRS WERE COMPLETED ON APRIL 19, 2012 AT 2030 HOURS AND LINE 132 WAS REPRESSURIZED. AT 1330 HOURS ON APRIL 20, 2012, THE COST OF REPAIRS WAS ESTIMATED TO EXCEED $50,000 MAKING THIS A REPORTABLE INCIDENT. THERE WAS NO IGNITION, INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. NO CUSTOMERS LOST SERVICE. THE CAUSE OF THIS INCIDENT IS FAULTY WELDS.
2025-03-31 10:13 | NO | YES | NO | 20120042 | 15535 | 2012-05-31 13:59 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2012-04-28 20:35 |  |  | 2012 | 14802 NE 61ST WAY | REDMOND |  | WA | 98052 | 47.6622 | -122.1431 | [9 empty] | 2012-05-03 11:50 | 1010466 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | [7 empty] | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET | [10 empty] | STEEL | [10 empty] | OTHER | [8 empty] | BREAK AT THE METER DUE TO A CAR HIT | CLASS 4 LOCATION | 150000 | 190755 | 3500 | 4450.95 | 1800 | 2289.06 | 0 | 0 |  |  | 50 | 45.13742071881606765327695560253699788584 |  | 0 | 155350 | 81838.2647568710359408033826638477801268 | 197540.1474207188160676532769556025369979 | 0 | 0 | 1 |  |  |  |  | 0.22 | 0.22 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ANTOINETTE IMAD | CONSULTING ENGINEER | antoinette.imad@pse.com | 425 456 2970 | 425 462 3770 |  |  |  | CHERYL MCGRATH | MGR COMPLIANCE AND REG AUDITS - GAS | 425 462 3207 | cheryl.mcgrath@pse.com | A CAR HIT THE GAS METER AT THE RESIDENCE AND IGNITED THE GAS.
2025-03-31 10:13 | YES | NO | NO | 20120043 | 15457 | 2012-06-02 17:00 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2012-05-04 17:39 |  |  | 2012 | 1323 GIRARD ST., NW | WASHINGTON |  | DC | 20010 | 38.926 | -77.0306 | [9 empty] | 2012-05-04 19:16 | 1010596 |  | NATURAL GAS |  | 12 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 0 | 1 | NO |  |  |  |  | NO | 0 | 2012-05-04 17:39 |  |  |  | 2012-05-04 17:58 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1978 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | DAMAGE TO AN OUTSIDE SERVICE RISER AS A RESULT OF AN ADJACENT BUILDING COLLAPSING DURING A HOUSE FIRE. | CLASS 3 LOCATION | 0 | 0 | 1100 | 1398.87 | 4000 | 5086.8 | 350000 | 445095 | DAMAGE ESTIMATE TO THE STRUCTURES AS A RESULT OF A HOUSE FIRE. |  | 30 | 27.0824524312896405919661733615221987315 |  | 0 | 355130 | 187056.2228541226215644820295983086680761 | 451607.7524524312896405919661733615221987 | 0 | 0 | 1 |  |  |  |  | 20 | 20 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | T. MICHAEL UPSHAW | SUPERVISOR - DOT PIPELINE SAFETY COMPLIANCE | mupshaw@washgas.com | (703) 750-4479 | (703) 750-4347 |  |  |  | DAVID W. SPANGLER | MANAGER - DOT PIPELINE SAFETY COMPLIANCE | (703) 750-4341 | dspangler@washgas.com | WASHIGNTON GAS RESPONDED TO A HOUSE FIRE AT 1327 GIRARD STREET, NW, WASHINGTON, DC ON MAY 4, 2012. UPON ARRIVAL, WASHINGTON GAS FOUND THAT THE STRUCTURE AT 1327 GIRARD STREET, NW, HAD COLLAPSED ONTO A METER RACK AT 1323 GIRARD STREET, NW DAMAGING THE METER RACK. A 360-DEGREE, SUB-SURFACE, BAR-HOLE SURVEY WAS CONDUCTED AROUND THE STRUCTURE AT 1323 GIRARD STREET, NW. THE SERVICE TO 1327 GIRARD STREET, NW WAS CAPPED-OFF AT THE CURB. AN ODORANT READING WAS TAKEN AND FOUND TO BE ACCEPTABLE. CONVERSATIONS WITH FIRE DEPARTMENT PERSONNEL INDICATED THAT THE RELEASE OF GAS WAS SECONDARY AS A RESULT OF THE BUILDING COLLAPSE.
2025-03-31 10:13 | NO | NO | NO | 20120044 | 15565 | 2012-06-04 14:50 | SUPPLEMENTAL FINAL | 8160 | INTERMOUNTAIN GAS CO | 555 SOUTH COLE ROAD | BOISE | ID | 83709 | 2012-05-31 02:15 |  |  | 2012 | AMERICAN FALLS GATE STATION | AMERICAN FALLS | POWER | ID | 83211 | 42.7324 | -112.8791 | [9 empty] | 2012-05-31 07:27 | 1013154 | [5 empty] | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-05-31 03:45 |  |  |  | 2012-05-31 03:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION | [10 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | NO RELEASE. WILLIAMS NORTHWEST PIPELINE INADVERTANTLY SHUT IN THE TOWN OF AMERICAN FALLS AT THE CUSTODY TRANSFER POINT BETWEEN THEIR SYSTEM AND OURS WHILE PREPARING FOR MAINTENANCE ACTIVITIES ON THEIR SYSTEM. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 20000 | 25434 | 0 | 0 |  |  | 0 | 0 |  | 0 | 20000 | 10534 | 25434 | 30 | 0 | 1265 |  |  |  |  | 0 | 150 | 150 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | INCORRECT OPERATION | INCORRECT VALVE POSITION | [222 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  |  | YES | WILLIAMS NORTHWEST PIPELINE CLOSED THEIR VALVE, AFFECTING OUR DISTRIBUTION SYSTEM. | ROUTINE MAINTENANCE | NO | [50 empty] | HART GILCHRIST | MANAGER OPERATIONS SERVICES | hart.gilchrist@intgas.com | 208-377-6086 | 208-377-6097 |  |  |  | HART GILCHRIST | MANAGER OPERATIONS SERVICES | 208-377-6086 | hart.gilchrist@intgas.com | WILLIAMS NORTHWEST PIPELINE INADVERTANTLY SHUT IN THE TOWN OF AMERICAN FALLS AT THE CUSTODY TRANSFER POINT BETWEEN THEIR SYSTEM AND OURS WHILE PREPARING FOR MAINTENANCE ACTIVITIES ON THEIR SYSTEM.
2025-03-31 10:13 | NO | YES | YES | 20120045 | 15461 | 2012-06-13 11:26 | ORIGINAL FINAL | 4350 | ELIZABETHTOWN GAS CO | 520 GREEN LANE | UNION | NJ | 07083 | 2012-05-15 08:24 |  |  | 2012 | UNION COUNTY PARKWAY | UNION | UNION | NJ | 07083 | 40.6917 | -74.2486 | [9 empty] | 2012-05-15 11:50 | 1011565 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2012-05-15 08:24 |  |  |  | 2012-05-15 08:42 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 42 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1972 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | TAP HOLE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 313 | 398.0421 | 0 | 0 |  |  | 0 | 0 |  | 0 | 313 | 164.8571 | 398.0421 | 0 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 0.25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | USE OF IMPROPER TOOL DURING LIVE GAS OPERATION. |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | PHILIP SALVATORE | COMPLIANCE ENGINEER | psalvato@aglresources.ccom | 908 662 8306 | 908 351 5127 |  |  |  | RICHARD LONN | DIRECTOR OF COMPLIANCE | 405 584 3552 | rlonn@aglresources.com | OPERATOR'S MAIN AND SERVICE INSTALLATION CONTRACTOR WAS WORKING ON DEAD ENDED 4" LOW PRESSURE (LP) STEEL MAIN. A CONTRACTOR CREW MEMBER REMOVED A DRIP SADDLE TO ACCESS THE TAP HOLE IN ORDER TO INCREASE THE TAP SIZE. THIS WOULD ALLOW THE CREW TO STOP THE FLOW OF GAS AND TO CONNECT A NEWLY INSTALLED EXTENSION TO THE MAIN. AFTER REMOVING THE SADDLE, THE CREWMEMBER ATTEMPTED TO ENLARGE THE HOLE USING A DRILL. AN IGNITION AND FLASH OCCURRED. IT WAS IMMEDIATELY EXTINGUISHED AND THE TAP HOLE RE-SEALED TO STOP THE FLOW. TWO CONTRACTOR WORKERS WERE INJURED IN THE FLASH. ONE WAS HELD AT THE HOSPITAL FOR FOUR DAYS FOR TREATMENT AND OBSERVATION.
2025-03-31 10:13 | NO | YES | YES | 20120046 | 15590 | 2012-06-15 13:56 | SUPPLEMENTAL | 13302 | NATIONAL GAS & OIL CORP | 1500 GRANVILLE ROAD | NEWARK | OH | 43055 | 2012-05-13 23:53 |  |  | 2012 | 36 S. UTAH AVENUE | NEWARK | LICKING | OH | 43055 | 40.1149 | -82.4371 | [9 empty] | 2012-05-14 04:15 | 1011391 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 3 | 2012-05-14 01:34 |  |  |  | 2012-05-14 02:05 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1962 | [5 empty] | 2.375 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK | [9 empty] | CLASS 3 LOCATION | 130000 | 165321 | 2500 | 3179.25 | 9300 | 11826.81 | 7500 | 9537.75 | ESTIMATED COSTS - STURCTURE, BELONGINGS, VEHICLE AND EMERGENCY RESPONSE |  | 100 | 90.27484143763213530655391120507399577167 |  | 0 | 149400 | 78719.8195137420718816067653276955602537 | 189955.0848414376321353065539112050739958 | 0 | 0 | 8 |  |  |  |  | 42 | 42 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | NO | NONE | [21 empty] | 2011-07-29 | NO | [227 empty] | SEAMUS MULLIGAN | ENGINEERING MANAGER | smulligan@theenergycoop.com | 740 403-8932 | 740 348-1131 |  |  |  | SEAMUS MULLIGAN | ENGINEERING MANAGER | 740 403-8932 | smulligan@theenergycoop.com | NOTE, THIS REPORT IS THE SAME AS THE 6/15/2012 REPORT. WE ARE RESUBMITTING TO CLOSE AND FINALIZE THE REPORT AN EXPLOSION AND SUBSEQUENT FIRE OCCURRED ON MAY 13TH 2012 AT 23:53 AT 36 S. UTAH STREET, NEWARK OHIO, 43055. MICHAEL CLARK OF THE RESIDENCE HAD JUST ENTERED HIS GARAGE AT THE TIME OF THE EXPLOSION. THE SOURCE OF IGNITION HAS NOT BEEN DETERMINED, HOWEVER IT HAS BEEN SPECULATED THAT HE WAS ENTERING THE GARAGE TO SMOKE A CIGARETTE. TWO OTHER RESIDENTS WERE HOME AT THE TIME OF THE EXPLOSION AND FIRE, DAKNEEKA PALMER, THE FIANCE OF MICHAEL CLARK, AND THEIR 9-MONTH-OLD DAUGHTER, LEGACEE. BOTH ESCAPED THE HOUSE UNHARMED. THE ENERGY COOP WAS CONTACTED BY THE LICKING COUNTY 911 DISPATCHER AT 01:34 (5/14/12 - 1 HOUR 41 MINUTES AFTER THE EXPLOSION) TO RESPOND TO THE SITE TO ENSURE GAS WAS OFF TO THE STRUCTURE. TWO ENERGY COOP EMPLOYEES WERE DISPATCHES, A LEAKAGE INSPECTOR MICHAEL CARR AND A SERVICE TECH TOM COOPER. TOM ARRIVED 02:05 AND MIKE ARRIVED AT 02:20. THEY VERIFIED GAS WAS OFF AND BEGAN A LEAKAGE INVESTIGATION. AT 3:05, A LEAK WAS FOUND UNDER THE 20' WIDE APPROACH APRON OF THE DRIVEWAY AT 36 S. UTAH. THE LEAKAGE EXTENTS WERE IDENTIFIED AND THE DECISION TO SHUT THE MAIN DOWN ALONG WITH 8 CUSTOMERS WAS MADE. THE VALVE TO SHUT THE LINE DOWN WAS TURNED AT 05:26 HOURS. THE 2" MAIN LINE SERVICING THE AREA WAS EXCAVATED AND CUT ON THE NORTH END AND SOUTH END OUTSIDE OF THE LEAKAGE AREA. APPROXIMATELY 250' OF 2" PLASTIC MAIN LINE WAS INSTALLED ON THE OPPOSITE SIDE OF UTAH AVENUE. THE NEW LINE WAS TIE BACK INTO THE EXISTING LINE IN A MANNER THAT ISOLATED THE GAS MAIN IN THE LEAKAGE AREA. THE OLD LINE WAS CAPPED TO PRESERVE THE LINE FOR FURTHER TESTING. GAS SERVICE WAS REESTABLISHED TO THE NEIGHBORHOOD. ODORANT READINGS WERE TAKEN AND FOUND TO BE WELL WITHIN REQUIRED LIMITS. THE REMAINDER OF THE NEIGHBORHOOD WAS SURVEYED FOR LEAKAGE TO ENSURE THE AREA WAS SAFE AS IT RELATED TO GAS SERVICE. AT 09:00 ON MAY 16TH , 2012 WE RETURNED TO THE SITE TO PERFORM AN INVESTIGATION. WE PRESSURE TESTED THE ISOLATED MAIN LINE AT NORMAL OPERATING PRESSURE (43#) TO TEST FOR LEAKAGE. WE FOUND LEAKAGE ON THE ISOLATED 191' OF 2" BARE STEEL. WE ISOLATED APPROXIMATELY 90' NORTH OF THE 36 S. UTAH DRIVEWAY AND PRESSURE TESTED IT. WE FOUND NO LEAKAGE. WE TESTED THE SOUTHERN SECTION (APPROXIMATELY 100') AND FOUND LEAKAGE. WE EXCAVATED TO EXPOSE THE MAIN LINE JUST SOUTH OF THE DRIVEWAY TO 36 S. UTAH AND CUT THE MAIN TO ISOLATE APROXIMATELY 45' THAT WAS UNDER THE DRIVE WAY. WE PRESSURE TESTED THE 65'SECTION SOUTH OF THE DRIVEWAY AND FOUND NO LEAKAGE. WE PRESSURE TESTED THE SERVICE LINE ON THE SOUTH SIDE OF THE STRUCTURE AND FOUND NO LEAKAGE. THIS ISOLATED THE LEAKAGE TO THE 45' SECTION LOCATED UNDER THE DRIVEWAY. WE CUT THE CONCRETE AND PUT PRESSURE ON THE PIPING AND DETERMINED THERE WERE 2 LEAKAGE AREAS APPROXIMATELY 12' APPART UNDER THE EXISTING 20' CONCRETE DRIVEWAY.
2025-03-31 10:13 | NO | NO | NO | 20120047 | 15475 | 2012-06-19 17:02 | SUPPLEMENTAL FINAL | 3200 | DEKALB - CHEROKEE COUNTIES GAS DISTRICT | 1405 GAULT AVENUE S/ P.O. BOX 376 | FORT PAYNE | AL | 35967 | 2012-06-10 03:00 |  |  | 2012 | INTERSECTIION OF HWY 68 &HWY 168 | KILPATRICK | DEKALB | AL | 35962 | 34.2686 | -86.0751 | [9 empty] | 2012-06-10 08:24 | 1014138 |  | NATURAL GAS |  | 66 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-06-10 03:31 |  |  |  | 2012-06-10 03:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1961 | [8 empty] | STEEL |  | OTHER | SEAMED | 0.13 | [6 empty] | OTHER | [8 empty] | WHEN FACILITY WAS STRUCK BY VEHICLE, THE THREADS ON REGULATOR PIPING BROKE. | CLASS 2 LOCATION | 1950 | 2479.815 | 853 | 1084.7601 | 1913 | 2432.7621 | 14000 | 17803.8 | THE CAR THAT HIT THE REGULATOR STATION. |  | 786 | 709.560253699788583509513742071881606765 |  | 0 | 19502 | 10514.1019780126849894291754756871035941 | 24510.6974536997885835095137420718816068 | 3 | 0 | 18 |  |  |  |  | 230 | 230 | 250 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY OUTSIDE FORCE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | W. KEITH DAVIS | GENERAL MANAGER | kdavis@dcgas.org | 256-845-3731 | 256-845-6252 |  |  |  | W. KEITH DAVIS | GENERAL MANAGER | 256-845-3731 | kdavis@dcgas.org | DURING A HEAVY RAIN EVENT. A CAR LOST CONTROL AND RAN THROUGH INTERSECTION AND PROTECTIVE BARRIERS STRIKING THE REGULATING STATION.
2025-03-31 10:13 | NO | NO | NO | 20120050 | 15585 | 2012-07-06 19:28 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2012-06-06 09:00 |  |  | 2012 | 1446 HECKMAN WAY | SAN JOSE | SANTA CLARA | CA | 95129 | 37.2969 | -122.0052 | [9 empty] | 2012-06-06 | 1013754 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2012-06-06 09:10 |  |  |  | 2012-06-06 09:45 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE | [7 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER |  |  |  | WATER ENTERED GAS LINE |  |  |  |  | A DOWNED 12KV POWER LINE CAUSED A SURGE TO A GROUNDED WATER LINE CREATING A HOLE IN THE COPPER WATER SERVICE LINE. THE COPPER WATER SERVICE LINE WAS TOUCHING THE STEEL GAS LINE AND THE ELECTRIC FAULT CURRENT ALSO CREATED A HOLE IN THE GAS LINE WHICH ALLOWED AN ENTRY POINT FOR THE WATER INTO THE GAS SYSTEM. | CLASS 3 LOCATION | 0 | 0 | 10000 | 12717 | 10000 | 12717 | 0 | 0 |  |  | 1000 | 902.748414376321353065539112050739957717 |  | 0 | 21000 | 11369.095137420718816067653276955602537 | 26336.7484143763213530655391120507399577 | 67 | 0 | 67 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA ON THIS PART OF THE SYSTEM | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | CHERYL DIZON | GAS COMPLIANCE ENGINEER | c1dz@pge.com | 925-974-4378 | 925-974-4232 |  |  |  | LAURENCE DENISTON | ACTING MANAGER REGULATORY COMPLIANCE | 925-974-4313 | lcd1@pge.com | AT APPROXIMATELY 0900 HOURS AT 1446 HECKMAN WAY IN SAN JOSE, WATER ENTERED A 3/4-INCH STEEL GAS DISTRIBUTION SERVICE LINE, CAUSING GAS SERVICE INTERRUPTION TO 67CUSTOMERS. THE NIGHT PRIOR TO THIS INCIDENT, A TREE BRANCH FELL ON A 12KV PRIMARY ELECTRICAL LINE CAUSING THE LINE TO SAG AND CONTACT THE 120V SECONDARY LINE CREATING A SURGE ON THE SECONDARY LINE. THE SURGE WENT TO GROUND THROUGH THE WATER LINE CREATING A HOLE IN THE 1-INCH COPPER POTABLE WATER LINE AND CAUSED A HIGH PRESSURE WATER STREAM. THE ELECTIC FAULT CURRENT ALSO DAMAGED THE STEEL GAS DISTRIBUTION SERVICE LINE NEARBY, RESULTING IN A RELEASE OF GAS AND ALLOWING AN ENTRY POINT FOR WATER INTO THE GAS SYSTEM. GSRS WERE ON SCENE AT 0945 HRS AND SHUT OFF GAS SERVICES AT THE RISER VALVES TO AFFECTED CUSTOMERS. PG&E CREWS WERE ON SCENE AT 1200 HOURS AND STOPPED THE FLOW OF GAS AT 1230 HOURS. AT 1255 HOURS AN EMERGENCY OPERATIONS CENTER WAS OPENED TO HELP IDENTIFY THE SCOPE OF THE INCIDENT, COORDINATE THE SHUT-IN AND RESTORE GAS SERVICE TO THE AFFECTED CUSTOMERS ALONG WITH OTHER COORDINATION ACTIVITIES. ALL 67 CUSTOMERS WERE READY TO HAVE GAS SERVICE RESTORED ON JUNE 7, 2012 AT 0900 HOURS. FOUR CAN'T GET IN (CGI) NOTICES WERE LEFT AT THE RESIDENT'S HOME AND THE REMAINING CUSTOMERS HAD GAS SERVICE RESTORED ON JUNE 7, 2012 AT 2030 HOURS. THE FOUR CGIS WERE RESTORED WHEN THE RESIDENTS CALLED FOR SERVICE RESTORATION. THERE WERE NO INJURIES OR FATALITIES AND NO IGNITION. DAMAGES TO COMPANY PROPERTY ARE LESS THAN $50,000. THE EVENT WAS REPORTED TO THE DOT AND CPUC BECAUSE OF THE SIGNIFICANCE OF THE EVENT.
2025-03-31 10:13 | YES | NO | NO | 20120051 | 15574 | 2012-07-09 20:17 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2012-06-09 21:00 |  |  | 2012 | 217 MASSOLO COURT | SALINAS | MONTEREY | CA | 93907 | 36.6842 | -121.6618 | [9 empty] | 2012-06-09 00:15 | 1014089 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2012-06-09 21:05 |  |  |  | 2012-06-09 21:44 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1990 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  |  | 2408 | LEAK |  |  | OTHER | METER MELTED FROM HOUSE FIRE | [5 empty] | CLASS 3 LOCATION | 150000 | 190755 | 2000 | 2543.4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 152000 | 80058.4 | 193298.4 | 0 | 0 | 1 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA ON THIS PART OF THE SYSTEM | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CHERYL DIZON | GAS COMPLIANCE ENGINEER | c1dz@pge.com | 925-974-4378 | 925-974-4232 |  |  |  | BILL GIBSON | DIRECTOR REGULATORY COMPLIANCE AND SUPPORT | 925-974-4210 | wlg3@pge.com | AT APPROXIMATELY 2105 HOURS, A RELEASE OF NATURAL GAS WAS REPORTED TO PG&E BY THE SALINAS FIRE DEPARTMEN DUE TO A HOUSE FIRE AT 217 MASSOLO COURT IN SALINAS. AT 2144 HOURS, A PG&E GAS SERVICE REPRESENTATIVE WAS ONSITE AND REPORTED THAT THE THE FIRE DEPARTMENT ATTEMPTED TO SHUT OFF THE FLOW OF GAS AT THE SERVICE VALVE, BUT THE METER WAS MELTED AND GAS WAS ESCAPING AT THE VALVE. PG&E FIELD CREWS SHUT OFF THE FLOW OF GAS BY SQUEEZING THE LINE AT THE BRANCH LOCATION AT 2359 HOURS. A SPECIAL LEAK SURVEY WAS PERFORMED FOLLOWING THE INCIDENT AND NO LEAKS WERE DETECTED. THERE WERE NO INJURIES, NO FATALITIES AND NO MAJOR MEDIA ON SCENE. FIRE AND POLICE WERE PRESENT, AND ONE CUSTOMER REMAINS OUT OF SERVICE UNTIL REPAIRS TO THE HOME ARE COMPLETE. REPORTED TO CPUC AND DOT BECAUSE ESTIMATED COST OF DAMAGES IS ABOVE $50,000 AND THE CAUSE IS UNKNOWN. THE SALINAS FIRE DEPARTMENT REPORT STATES THAT THE CAUSE OF THE FIRE IS UNDETERMINED AFTER INVESTIGATION.
2025-03-31 10:13 | YES | NO | NO | 20120052 | 15575 | 2012-07-11 19:26 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2012-06-11 23:55 |  |  | 2012 | 2351 PALAMINO ROAD | LIVERMORE | ALAMEDA | CA | 94551 | 37.7222 | -121.7451 | [9 empty] | 2012-06-11 02:00 | 1014275 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2012-06-11 23:55 |  |  |  | 2012-06-12 00:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | CAUSE OF HOUSE FIRE UNKNOWN | CLASS 3 LOCATION | 300000 | 381510 | 2000 | 2543.4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 302000 | 159063.4 | 384053.4 | 0 | 0 | 2 |  |  |  |  | 52 | 52 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA ON THIS PART OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CHERYL DIZON | GAS COMPLIANCE ENGINEER | c1dz@pge.com | 925-974-4378 | 925-974-4232 |  |  |  | BILL GIBSON | DIRECTOR REGULATORY COMPLIANCE AND SUPPORT | 925-974-4210 | wlg3@pge.com | ON 6/11/12 AT APPROXIMATELY 2355 HOURS, LIVERMORE FIRE DEPARTMENT REPORTED A GAS LEAK DUE TO A HOUSE FIRE AT 2351 PALAMINO RD, LIVERMORE IN ALAMEDA COUNTY. THE FIRE CONSUMED THE HOME AND THE METER SET WAS MELTED, CAUSING A RELEASE OF GAS TO THE ATMOSPHERE AT THE RISER. PG&E GSR WAS ONSITE AS 2430 HOURS AND FIELD CREWS STOPPED THE FLOW OF GAS ON 06/12/12 AT 0305 HOURS BY DIGGING AND SQUEEZING THE PIPE. AT 043 HOURS ON 06/12/12, THE GSR REPORTED THAT THE FIRE TOUCHED THE SIDE OF THE NEIGHBOR'S HOME AT 2355 PALAMINO RD AND GAS SERVICE WAS SHUT OFF AT THE SERVICE VALVE FOR THE SECOND RESIDENCE. A SPECIAL LEAK SURVEY WAS PERFORMED AFTER THE INCIDENT AND NO LEAKS WERE DETECTED. FIRE, POLICE AND KTVU WERE ON SCENE. THE LIVERMORE FIRE DEPARTMENT STATES THAT NEIGHBORS REPORTED THE FIRE ORIGINATED IN THE GARAGE; HOWEVER, THE CAUSE OF THE FIRE IS UNDETERMINED AFTER THEIR INVESTIGATION. ONE PERSON WAS INJURED AND SENT TO THE HOSPITAL, BUT DID NOT STAY OVERNIGHT. ADDITIONALLY, THERE WERE NO FATALITIES. THE ESTIMATED COST OF DAMAGES IS ABOVE $50,000 DEEMING THIS INCIDENT REPORTABLE TO DOT AND CPUC.
2025-03-31 10:13 | NO | YES | YES | 20120053 | 15497 | 2012-07-12 19:33 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2012-06-12 15:51 |  |  | 2012 | 2811 SAN BRUNO AVENUE | SAN FRANCISCO | SAN FRANCISCO | CA | 94134 | 37.7262 | -122.403 | [9 empty] | 2012-06-12 18:30 | 1014387 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | YES | 20 | 2012-06-12 15:51 |  |  |  | 2012-06-12 16:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2012 | [5 empty] | 1 | UNKNOWN | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | OTHER | [8 empty] | A 3RD PARTY CONTRACTOR WAS NOT PROTECTING THE PLASTIC GAS LINE WHEN SWEATING A COPPER WATER LINE AND MELTED THE PLASTIC PIPE CAUSING A RELEASE OF GAS AND EXPLOSION. | CLASS 3 LOCATION | 1000000 | 1271700 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 1000000 | 526700 | 1271700 | 5 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA ON THIS PART OF THE SYSTEM | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | A THIRD PARTY CONTRACTOR WAS SWEATING A COPPER WATER SERVICE LINE WITHOUT SHIELDING PG&E'S 1-INCH PLASTIC GAS SERVICE LINE WHEN AN EXPLOSION OCCURED. IT APPEARS THAT THE SWEATING TORCH MELTED THE GAS LINE, RELEASING GAS WHICH RESULTED IN AN EXPLOSION AND FIRE. | [154 empty] | CHERYL DIZON | GAS COMPLIANCE ENGINEER | c1dz@pge.com | 925-974-4378 | 925-974-4232 |  |  |  | BILL GIBSON | DIRECTOR REGULATORY COMPLIANCE AND SUPPORT | 925-974-4210 | wlg3@pge.com | AT APPROXIMATELY 1551 HOURS, THE SAN FRANCISCO FIRE DEPARTMENT NOTIFIED PG&E OF A GAS RELEASE DUE TO AN EXPLOSION AND FIRE AT 2811 SAN BRUNO AVE IN SAN FRANCISCO. THE PROPERTY IS AN UNOCCUPIED BUILDING UNDERGOING CONSTRUCTION AND APPEARS TO BE A MULTI-FAMILY RESIDENTIAL STRUCTURE. A THIRD PARTY CONTRACTOR DUG A BELL HOLE CLOSE TO THE FACE OF THE INCIDENT BUILDING TO EXPOSE THE WATER AND GAS LINES. THE CONTRACTOR WAS SWEATING A COPPER WATER SERVICE LINE WITHOUT SHIELDING PG&E'S 1-INCH PLASTIC GAS SERVICE LINE WHEN AN EXPLOSION OCCURRED. IT APPEARS THAT THE SWEATING TORCH MELTED THE GAS LINE, RELEASING GAS WHICH RESULTED IN THE EXPLOSION AND FIRE. THE CONTRACTOR DID NOT HOLD A VALID USA TICKET. TRAFFIC WAS REROUTED AND THE AREA WAS BLOCKED OFF. APPROXIMATELY 20 PEOPLE IN THE NEIGHBORING DENTAL OFFICE WERE EVACUATED. PG&E GSR WAS ONSITE AT 1615 HOURS AND FIELD CREWS STOPPED THE FLOW OF GAS TO THE INCIDENT BUILDING AT 1750 HOURS BY DIGGING AND SQUEEZING THE SERVICE LINE AT THE DISTRIBUTION MAIN. NO FATALITIES; FIVE TOTAL CUSTOMERS WERE OUT OF SERVICE; ONE OF THE THREE CONTRACTORS PRESENT WAS INJURED AND TAKEN TO THE HOSPITAL AND DAMAGES ARE ESTIMATED ABOVE $50,000 DEEMING THIS INCIDENT REPORTABLE TO DOT & CPUC. MAJOR TV MEDIA CHANNELS 2, 4, 5 & 7 WERE PRESENT. A LEAK SURVEY OF SERVICES ON BOTH SIDES OF THE 2800 BLOCK OF SAN BRUNO AVE WAS PERFORMED THE SAME NIGHT AS THE INCIDENT AND NO LEAKS WERE DETECTED. ONE CUSTOMER WAS RELIT BY 2100 HOURS ON 6/12/12 AND THE OTHER FOUR SERVICES WILL BE RELIT ONCE THE APPROPRIATE REPAIRS ARE COMPLETE AND AFTER THE CUSTOMERS REQUEST NEW SERVICE.
2025-03-31 10:13 | NO | NO | NO | 20120054 | 15479 | 2012-07-13 14:09 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2012-06-15 10:20 |  |  | 2012 | 1120 RHODE ISLAND AVE, NW | WASHINGTON |  | DC | 20005-4415 | 38.91 | -77.0279 | [9 empty] | 2012-06-15 11:31 | 101463 |  | NATURAL GAS |  | 2.89 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-06-15 10:20 |  |  |  | 2012-06-15 10:29 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 32 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1959 | [5 empty] | 1.5 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | OPERATOR'S CONTRACTOR DAMAGED SERVICE LINE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 8000 | 10173.6 | 0 | 0 |  |  | 8 | 7.22198731501057082452431289640591966173 |  | 0 | 8008 | 4220.280761099365750528541226215644820296 | 10180.8219873150105708245243128964059197 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 4 | 0 | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | PAUL MOSES | SUPERVISOR - DOT PIPELINE SAFETY | gmoses@washgas.com | 703-750-4496 |  |  |  |  | DAVID SPANGLER | MANAGER-DOT PIPELINE SAFETY | 703-750-4341 | dspangler@washgas.com | ON FRIDAY, JUNE 15, 2012 A WASHINGTON GAS CONTRACTOR, D.A. FOSTER, DAMAGED A 1 1/2 INCH WRAPPED STEEL LOW PRESSURE SERVICE LINE LOCATED AT 1120 RHODE ISLAND AVE, NW, DC. AT 10:20 AM WASHINGTON GAS WAS NOTIFIED BY THE DC FIRE DEPARTMENT OF A DAMAGED SERVICE LINE THAT HAD IGNITED. A WASHINGTON GAS CREW ARRIVED ON SITE AT 10:29 AM AND MADE THE AREA SAFE. THE GAS WAS OFF AT THE DAMAGED SERVICE LINE BY 10:48 AM. THE WASHINGTON GAS CREW REMOVED THE SERVICE TEE FROM THE MAIN AND SEALED THE MAIN WITH A STEEL PLUG. CREW CHECKED STRUCTURES ON EACH SIDE OF AFFECTED ADDRESS FOR EVIDENCE OF GAS MIGRATION. THE WASHINGTON GAS CREW ALSO PERFORMED BAR HOLE TESTING OVER THE GAS MAIN AND CHECKED ALL MANHOLES IN AREA FOR EVIDENCE OF MIGRATION. NONE WAS FOUND. SERVICE REPLACEMENT WAS COMPLETED ON JUNE 28, 2012. AS A RESULT OF THE INVESTIGATION, THE CAUSE OF THE INCIDENT HAS BEEN DETERMINED TO BE THE FAILURE OF THE CREW PERFORMING THE WORK TO FOLLOW WASHINGTON GAS PROCEDURE BY USING A POTENTIAL SPARK PRODUCING MECHANIZED TOOL TO CUT A LIVE GAS SERVICE.
2025-03-31 10:13 | NO | YES | NO | 20120055 | 15625 | 2012-07-17 12:25 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2012-07-13 10:31 |  |  | 2012 | 3286 S. STATE ROAD 43 | CHALMERS | WHITE | IN | 47929 | 40.7016 | -86.8714 | [12 empty] | NATURAL GAS |  | 2275 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-07-13 11:03 |  |  |  | 2012-07-13 11:14 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1963 | [5 empty] | 6 | API5LX42 | UNKNOWN | STEEL |  | OTHER | LONG SEAM WELD | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 4 | 1 | [7 empty] | CLASS 1 LOCATION | 500 | 635.85 | 10000 | 12717 | 76000 | 96649.2 | 1000 | 1271.7 | ROAD CLOSURE COSTS ARE SHOWN ABOVE. CSX DID NOT PROVIDE ANY COST DATA. |  | 8700 | 7853.911205073995771670190274841437632135 |  | 0 | 96200 | 53351.5776955602536997885835095137420719 | 119127.6612050739957716701902748414376321 | 0 | 0 | 0 |  |  |  |  | 275 | 275 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS DAMAGE DUE TO EXCAVATION. THE INCIDENT WAS CALLED IN IMMEDIATELY. THERE WERE NO ALARMS RECORDED DUE TO THIS INCIDENT. THE PRESSURE DROP WAS SEEN IN SCADA, BUT DID NOT PRODUCE AN ALARM, AND THEREFORE NO ADDITIONAL SCADA INVESTIGATION WAS COMPLETED. THE GAS LEAK WAS NOT SIGNIFICANT ENOUGH ON THE SYSTEM INVOLVED TO CREATE A LOW PRESSURE ALARM. THE DATA IN SCADA WAS REVIEWED TO DETERMINE ALL CONTROL ROOM PRODEDURES WERE FOLLOWED. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 1207131478 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | LUKE E. SELKING | MANAGER PIPELINE SAFETY AND COMPLIANCE | leselking@nisource.com | 260-439-1290 | 260-422-9151 |  |  |  | LUKE E. SELKING | MANAGER PIPELINE SAFETY AND COMPLIANCE | 260-439-1290 | leselking@nisource.com | CONTRACTOR WAS DOING BRIDGE CONSTRUCTION WORK ON SR 43 APPROXIMATELY 2.25 MILES NORTH OF CHALMERS, INDIANA AT BIG CREEK. THE EXCAVATOR OPERATOR WAS ATTEMPTING TO MOVE A WOODEN PLATFORM IN THE BOTTOM OF A CREEK BED WHEN THE BUCKET SLIPPED PUNCTURING THE GAS PIPELINE. THE PIPELINE PUNCTURE CAUSED GAS TO BLOW OVER THE RAILROAD TRACKS APPROXIMATELY 50 EAST OF THE PIPELINE, RUNNING PARALLEL TO SR 43. THE TRAIN AND AUTOMOBILE TRAFFIC WAS HALTED UNTIL THE GAS LEAK WAS STOPPED. THERE WAS NO INTERUPTION OF SERVICE TO ANY CUSTOMERS. A BY-PASS WAS CONSTRUCTED AROUND THE AREA WITH A TEMPERARY REGULATOR STATION. THE ORIGINAL GAS LOSS CALCUATION WAS ACCURATE. THE LINE WAS ALREADY SHUT DOWN AT THE TIME THE CALCULATION WAS COMPLETED. NO CALL WAS MADE AFTER IT WAS DETERMINED THAT CSX HAD ALREADY NOTIFIED THE NRC. THIS IS A CLASS 1 AREA, SEE ATTACHED DOCUMENT MAP, RURAL AREA. THERE WERE NO ADDITIONAL COSTS AVAILABLE FROM CSX. THERE WAS AN AMTRAC TRAIN DELAYED FOR SEVERAL HOURS, WHILE THE GAS WAS SHUT DOWN, BUT IT WAS NOT RE-ROUTED TO OUR KNOWLEDGE.
2025-03-31 10:13 | NO | NO | NO | 20120057 | 15520 | 2012-07-27 15:43 | SUPPLEMENTAL FINAL | 1088 | BALTIMORE GAS & ELECTRIC CO | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2012-06-28 11:21 |  |  | 2012 | 1305 RIEDEL RD | GAMBRILLS | ANNE ARUNDEL | MD | 21054 | 39.0383 | -76.6732 | [9 empty] | 2012-06-29 13:01 | 1016178 |  | NATURAL GAS |  | 2053.43 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 101 | 2012-06-28 11:21 |  |  |  | 2012-06-28 11:42 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2001 | [5 empty] | 4 | ASTMD2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 3 | 1 | [7 empty] | CLASS 3 LOCATION | 7300 | 9283.41 | 54789 | 69675.1713 | 10000 | 12717 | 0 | 0 | NONE |  | 12378 | 11174.2198731501057082452431289640591966 |  | 0 | 84467 | 48306.083910993657505285412262156448203 | 102849.8011731501057082452431289640591966 | 1 | 0 | 226 |  |  |  |  | 92 | 92 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGED, NOTIFIED BY EMERGENCY RESPONDER | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 12303726 | MISS UTILITY |  | CONTRACT LOCATOR | YES | YES | 9 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | BERNARD F SMITH | GAS SERVICE SUPERVISOR | bernard.smith@bge.com | 410-470-7106 | 410-470-7103 |  |  |  | WILLIAM H BROWN | MANAGER GAS SERVICE | 410-470-7105 | william.h.brown@bge.com | CONTRACTOR DIRECTIONAL BORING TO INSTALL CABLE MAIN AND CONDUIT DAMAGED A BGE 4 INCH PLASTIC GAS MAIN CROSSING AT 1305 RIEDEL RD. THIS 4 INCH GAS MAIN SUPPLIED A COMMUNITY OF 227 CUSTOMERS THAT WERE IMPACTED DUE TO THIS DAMAGE. EXISTING 4" MAIN WAS INCORRECTLY MARKED AND THE UTILITY GAS MAIN LOCATION RECORD INACCURATELY INDICATED THE GAS MAIN LOCATION. CONTRACTOR EXCAVATION PRACTICES WERE NOT IN ACCORDANCE WITH STATE DAMAGE PREVENTION REQUIREMENTS. INCIDENT NOTIFICATION TO THE NRC WAS BASED UPON CUMULATIVE OPERATOR EXPENSES REACHING THE FIFTY THOUSAND DOLLAR VALUE.
2025-03-31 10:13 | NO | YES | NO | 20120060 | 15634 | 2012-07-31 17:22 | SUPPLEMENTAL FINAL | 31636 | NORTHERN STATES POWER CO OF MINNESOTA | 414 NICOLLET MALL | MINNEAPOLIS | MN | 55402 | 2012-07-01 14:49 |  |  | 2012 | 15520 ZUMBRO AVENUE | SHAKOPEE |  | MN | 55379 | 44.7258 | -93.5565 | [9 empty] | 2012-07-01 17:25 | 1016411 |  | NATURAL GAS |  | 48 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2012-07-01 14:56 |  |  |  | 2012-07-01 16:07 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1990 | [5 empty] | 1.13 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.099 |  | 2406 | OTHER | [8 empty] | PE SERVICE LINE MELTED DUE TO HOUSE FIRE. | CLASS 2 LOCATION | 600000 | 763020 | 2400 | 3052.08 | 2682 | 3410.6994 | 0 | 0 |  |  | 266 | 240.131078224101479915433403805496828753 |  | 0 | 605348 | 318918.8247065539112050739957716701902748 | 769722.9104782241014799154334038054968288 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE NOT RELATED TO EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [112 empty] | PREVIOUS MECHANICAL DAMAGE NOT RELATED TO EXCAVATION | [7 empty] | 2011-10-14 | NO | [159 empty] | ELISABETH KALLBERG | PRINCIPLE PIPELINE COMPLIANCE CONSULTANT | elisabeth.m.kallberg@xcelenergy.com | 651-229-2282 |  |  |  |  | WILLIAM KAPHING | SR DIRECTOR GAS GOVERNANCE | 651-229-2435 | william.l.kaphing@xcelenergy.com | THE HOUSE FIRE CAUSED THE PE SERVICE LINE TO MELT. THE FIRE IS STILL UNDER INVESTIGATION AND NO FINAL REPORT HAS BEEN COMPLETED BY THE FIRE DEPARTMENT OR THE FIRE MARSHAL. UPDATED FEBRUARY 11, 2013: THIS UPDATE IS BASED PRIMARILY ON THE MINNESOTA STATE FIRE MARSHAL'S INVESTIGATION REPORT. WE AGREE WITH THE CONCLUSION IN THE REPORT THAT THE FIRE WAS ACCIDENTAL. THE AREA OF ORIGIN FOR THE FIRE WAS INSIDE THE RESIDENCE. THE FIRST MATERIAL THAT IGNITED WAS NATURAL GAS VAPORS THAT HAD LEECHED INTO THE RESIDENCE AFTER A GAS SERVICE LINE HAD BEEN CRACKED OR BROKEN. THE SPECIFIC LOCATION OF THE LEAK COULD NOT BE DETERMINED BECAUSE THE RISER AND A SEGMENT OF THE SERVICE WERE DESTROYED IN THE FIRE. WHILE THE EXACT IGNITION FACTOR IS NOT KNOWN, ANY APPLIANCE THAT WOULD CYCLE ON OR OFF WOULD LIKELY HAVE PROVIDED SUFFICIENT ENERGY TO IGNITE THE NATURAL GAS/AIR MIXTURE ONCE IT HAD REACHED THE LOWER EXPLOSIVE LIMIT. WITH RESPECT TO THE BROKEN OR CRACKED GAS SERVICE LINE THAT RESULTED IN THE GAS LEAK, WE KNOW THAT ON SEVERAL OCCASIONS IN THE PRECEDING 4 YEARS, THE RESIDENT HAD FILLED A SINK-TYPE OF HOLE IN THE GROUND OUTSIDE THE HOME THAT WAS ABOVE THE GAS LINE AND NEAR THE METER. THE SETTLING OF THE SOIL IN THAT HOLE COULD HAVE PUT STRESS ON THE GAS LINE. IN ADDITION, IN THE DAY (OR DAYS) BEFORE THE FIRE, A MEMBER OF THE RESIDENT'S FAMILY HAD ADDED CLASS FIVE ROCK TO THE TOP OF THE SINK HOLE AREA AND THEN PACKED IT DOWN WITH A BOBCAT, WHICH MAY HAVE ADDED TO OR CREATED STRESS ON THE GAS LINE, POSSIBLY ENOUGH TO CRACK OR BREAK IT AT THAT TIME. XCEL ENERGY DOES NOT HAVE RECORDS OF THIS CUSTOMER CONTACTING US FOR ASSISTANCE WITH THE SINK HOLE NEAR THE GAS LINE, OR MAKING US AWARE OF ANY RELATED PROBLEMS. OUR RECORDS REVEAL THAT THE METER LOCATION AT THE TIME OF THE FIRE WAS NOT THE ORIGINAL LOCATION OF THE METER. WE UNDERSTAND THAT THE METER WAS MOVED BY AN UNKNOWN PARTY, NOT XCEL ENERGY, TO MAKE ROOM FOR A GARAGE ADDITION ON THE WEST SIDE OF THE HOUSE APPROXIMATELY 2007. THE SERVICE LINE TO THIS LOCATION WILL BE RUN AT THE REQUEST OF THE CUSTOMER AFTER HOME IS REBUILT.
2025-03-31 10:13 | NO | NO | NO | 20120061 | 15491 | 2012-07-31 18:51 | ORIGINAL | 31159 | KANSAS GAS SERVICE | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2012-07-04 23:30 |  |  | 2012 | ALLEY W OF 6TH AND HEYLMAN | FORT SCOTT | BOURBON | KS | 66701-1212 | 37.8356 | -94.7185 | [9 empty] | 2012-07-10 12:09 | 1017294 |  |  |  | 3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-07-05 02:00 |  |  |  | 2012-07-05 03:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2009 | [5 empty] | 4.5 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.395 |  | 2406 | MECHANICAL PUNCTURE | 2 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1000 | 1271.7 | 52000 | 66128.4 | 0 | 0 |  |  | 23 | 20.76321353065539112050739957716701902748 |  | 0 | 53023 | 27934.3071881606765327695560253699788584 | 67420.863213530655391120507399577167019 | 0 | 0 | 200 |  |  |  |  | 1 | 1 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | WATER | YES | 12257063 |  |  | CONTRACT LOCATOR | YES | YES | 120 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | BRUCE D. KUBIE | MANAGER OF STANDARDS | bkubie@kgas.com | 785 431-4250 | 785 431-4224 |  |  |  | ROB GREEN | DIRECTOR GAS ENGINEERING | 785 431-4241 | rgreen@kgas.com | ON JULY 4TH, 2012 AT APPROXIMATELY 2330 HRS THE FORT SCOTT, KS CITY WATER DEPARTMENT WAS DIGGING TO MAKE REPAIRS ON A BROKEN WATER MAIN. WHILE DIGGING WITH LOCATED FACILITIES, THEY HIT A KGS 4" PE GAS MAIN THAT WAS OPERATING AT 10OZ. THE DAMAGE PUT A 2" BY 3" HOLE IN THE MAIN AND THE WATER FROM THE BROKEN WATER MAIN BEGAN TO FILL THE MAIN DUE TO THE WATER PRESSURE BEING GREATER THAN THE MAIN PRESSURE. THIS RESULTED IN THE DISRUPTION OF SERVICE TO SOME 200 CUSTOMERS IN A SEVERAL BLOCK AREA. THE WATER REMOVAL BEGAN THE MORNING OF JULY 5TH AND CONTINUED UNTIL ALL CUSTOMERS WERE RESTORED TO SERVICE BY LATE EVENING ON JULY 10TH.
2025-03-31 10:13 | NO | YES | NO | 20120062 | 15492 | 2012-08-02 16:17 | ORIGINAL | 31159 | KANSAS GAS SERVICE | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2012-07-09 13:36 |  |  | 2012 | 1401 N. LORRAINE AVE | WICHITA | SEDGWICK | KS | 67219 | 37.7083 | -97.3 | [9 empty] | 2012-07-10 11:40 | 1017288 |  |  |  | 2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-07-09 13:36 |  |  |  | 2012-07-09 14:36 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 |  | YES |  |  |  |  | YES | UNCASED, BORED/DRILLED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 4.5 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 700 | 890.19 | 5000 | 6358.5 | 500000 | 635850 | 0 | 0 |  |  | 30 | 27.0824524312896405919661733615221987315 |  | 0 | 505730 | 266377.2428541226215644820295983086680761 | 643125.7724524312896405919661733615221987 | 5 | 0 | 661 |  |  |  |  | 0.75 | 0.75 | 0.88 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | [7 empty] | YES | [6 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 12248973 |  |  | CONTRACT LOCATOR | YES | YES | 288 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | BRUCE D. KUBIE | MANAGER STANDARDS | bkubie@kgas.com | 785 431-4250 | 785 431-4225 |  |  |  | ROB GREEN | DIRECTOR ENGINEERING | 785 4314241 | rgreen@kgas.com | A CABLE TV CONTRACTOR STRUCK A 4 INCH PE MAIN WHILE BORING AND THEN HIT A 2" WATER MAIN WHICH FLOODED THE .5 PSIG GAS SYSTEM DUE TO THE WATER PRESSURE BEING MUCH GREATER THAN THE PRESSURE IN THE GAS MAIN. THE ENSUING FLOOD OF WATER INTO THE GAS MAIN WATERED OFF SEVERAL BLOCKS OF RESIDENTIAL HOMES FOR A TOTAL OF 666 CUSTOMERS THAT WERE SHUT OFF. ONCE THE SITUATION WAS IDENTIFIED ON 7/9 THE COMPANY SPENT UNTIL 7/20 CLEARING WATER OUT OF THE MAINS AND SERVICES AND REESTABLISHING SERVICE TO THE CUSTOMERS.
2025-03-31 10:13 | NO | YES | NO | 20120063 | 15671 | 2012-08-08 10:08 | SUPPLEMENTAL FINAL | 11713 | KEYSPAN ENERGY DELIVERY - LONG ISLAND | 175 EAST OLD COUNTRY ROAD | HICKSVILLE | NY | 11801-4257 | 2012-07-10 20:52 |  |  | 2012 | 65 FELLER DRIVE | CENTRAL ISLIP | SUFFOLK | NY | 11722-1209 | 40.8021 | -73.1972 | [9 empty] | 2012-07-27 16:20 | 1019177 |  | NATURAL GAS |  | 0.29 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 20 | 2012-07-10 20:52 |  |  |  | 2012-07-10 21:21 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | CUSTOMER PIPING | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | STILL UNDER INVESTIGATION | CLASS 4 LOCATION | 3000000 | 3815100 | 0 | 0 | 550 | 699.435 | 0 | 0 |  |  | 80 | 72.21987315010570824524312896405919661734 |  | 0 | 3000630 | 1580456.4926109936575052854122621564482 | 3815871.6548731501057082452431289640592 | 0 | 0 | 10 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO ISSUES IN THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | INCORRECT OPERATION | INCORRECT VALVE POSITION | [222 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | DAVID ANGELONE | MANAGER | david.angelone@nationalgrid.com | 718-403-3347 |  |  |  |  | DAVID ANGELONE | MANAGER | 718-403-3347 | david.angelone@nationalgrid.com | NATIONAL GRID EMPLOYEE FAILED TO FOLLOW PROCEDURE AND LEFT A 1/2 INCH VALVE, ON CUSTOMER GAS PIPING, IN THE OPEN POSITION THAT SUPPLIED GAS TO AN OPEN LINE.
2025-03-31 10:13 | YES | NO | NO | 20120065 | 16006 | 2012-08-08 21:21 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2012-07-06 19:00 |  |  | 2012 | 313 ATKINSON STREET | ROSEVILLE | PLACER | CA | 95678 | 38.7472 | -121.2994 | [9 empty] | 2012-07-06 21:30 | 1016952 |  | NATURAL GAS |  | 0.01 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2012-07-06 19:18 |  |  |  | 2012-07-06 19:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | THE DAMAGE TO THE METER AND REGULATOR ARE CONSISTENT WITH EXPOSURE TO FIRE AND EXCESSIVE HEAT. THE ROSEVILLE FIRE DEPARTMENT FOUND FIREWORKS DEBRIS AND CIGARETTE BUTTS IN THE VICINITY OF THE METER. THE ROSEVILLE FIRE DEPARTMENT HAS CLASSIFIED THE CAUSE OF THE FIRE AS UNDETERMINED. | CLASS 3 LOCATION | 100000 | 127170 | 2000 | 2543.4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 102000 | 53723.4 | 129713.4 | 0 | 0 | 1 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LAURENCE DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT APPROXIMATELY 1918 HOURS, PG&E WAS NOTIFIED BY THE ROSEVILLE FIRE DEPARTMENT OF AN UNINTENTIONAL GAS RELEASE DUE TO A HOUSE FIRE AT 313 ATKINSON ST. IN ROSEVILLE. THE FIRE DEPARTMENT HAD ALREADY SHUT OFF THE FLOW OF GAS AT THE SERVICE VALVE WHEN PG&E'S GAS SERVICE REPRESENTATIVE ARRIVED ON SITE AT 1925 HOURS. THE METER WAS PARTIALLY MELTED AND HAD CAUGHT FIRE. THE GSR REMOVED THE SERVICE METER AND REGULATOR AND CAPPED THE SERVICE OFF BY INSTALLING A PLUG DOWNSTREAM OF THE SERVICE VALVE. A SOAP TEST SHOWED FUZZ LEAKS AT THE VALVE, SO THE RISER VALVE WAS REPLACED. A LEAK SURVEY WAS PERFORMED ON THE SERVICE LINE TO THE HOME AND CONNECTION TO THE MAIN. NO LEAKS WERE DETECTED. THERE WAS NO EXPLOSION, NO FATALITIES, AND ONE PERSON SUFFERED SMOKE INHALATION, BUT WAS NOT ADMITTED TO THE HOSPITAL. FIRE DAMAGE TO THE STRUCTURE EXCEEDS $50,000 AND THE CHANNEL 10 SACRAMENTO TV WAS ON SITE. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC BECAUSE DAMAGES WERE EXPECTED TO EXCEED $50,000 FROM THE IGNITION. THE ROSEVILLE FIRE DEPARTMENT NOTED THAT THE FIRE STARTED AT A LOCATION IN CLOSE PROXIMITY TO THE METER. THE ROSEVILLE FIRE DEPARTMENT FOUND FIREWORKS DEBRIS AND CIGARETTE BUTTS IN THE VICINITY OF THE METER. THE ROSEVILLE FIRE DEPARTMENT HAS CLASSIFIED THE CAUSE OF THE FIRE AS UNDETERMINED. AS OF APPROXIMATELY 0800 HOURS ON AUGUST 13, 2012, GAS SERVICE WAS RESTORED TO 313 ATKINSON STREET.
2025-03-31 10:13 | NO | YES | NO | 20120066 | 15499 | 2012-08-10 16:14 | ORIGINAL FINAL | 11032 | LACLEDE GAS CO | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2012-07-12 14:45 |  |  | 2012 | 5559 ENRIGHT AVE | ST LOUIS | NA | MO | 63112-4514 | 38.6547 | -90.282 | [9 empty] | 2012-07-12 15:04 | 1017549 |  | NATURAL GAS |  | 1385 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 58 | 2012-07-12 14:45 |  |  |  | 2012-07-12 14:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1961 | [5 empty] | 12 | ASA A21.1 | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | RUPTURE |  |  |  | BRITTLE MAIN SEGMENT FAILURE | LONGITUDINAL |  | 6.5 | 2.5 |  | CLASS 3 LOCATION | 0 | 0 | 50467 | 64178.8839 | 33153 | 42160.6701 | 0 | 0 |  |  | 8391 | 7574.961945031712473572938689217758985201 |  | 0 | 92011 | 51049.9372980972515856236786469344608879 | 113914.5159450317124735729386892177589852 | 0 | 0 | 9 |  |  |  |  | 11.5 | 12.5 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | OPERATOR WAS WORKING AT LOCATION |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 5 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [6 empty] | YES | GRAPHITIC CORROSION |  |  | YES | YES |  |  | YES | NO |  | NO | NO | [8 empty] | NO | [22 empty] | 2011-07-26 | NO | [227 empty] | MARK D. LAUBER | SUPERINTENDENT MAINTENANCE ENGINEERING | mlauber@lacledegas.com | 314-658-5413 | 314-535-5075 |  |  |  | CRAIG R. HOEFERLIN | VICE PRESIDENT ENGINEERING AND FIELD SERVICES | 314-658-5410 | choeferlin@lacledegas.com | A CLAMP WAS BEING INSTALLED ON THE 12" CAST IRON MAIN TO REPAIR A LEAK. DURING PREPARATION FOR THE CLAMP INSTALLATION, A SEGMENT OF GRAPHITIZED MAIN DISLODGED ITSELF AT THE SIX O'CLOCK POSITION. A SPARK SUBSEQUENTLY OCCURRED FROM AN UNDETERMINED SOURCE WHICH IGNITED THE GAS.
2025-03-31 10:13 | NO | YES | NO | 20120067 | 15541 | 2012-08-15 17:04 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 200 CIVIC CENTER DR, P.O. BOX 117 | COLUMBUS | OH | 43215 | 2012-07-17 13:37 |  |  | 2012 | 10374 BRAEMAR DR | POWELL | DELAWARE | OH | 43065 | 40.1476 | -83.0964 | [9 empty] | 2012-07-17 16:04 | 1018056 | [5 empty] | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-07-17 13:37 |  |  |  | 2012-07-17 14:05 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1994 | [8 empty] | UNKNOWN | [10 empty] | LEAK |  |  | OTHER | FIRE-UNKNOWN | [5 empty] | CLASS 3 LOCATION | 305000 | 387868.5 | 1000 | 1271.7 | 1000 | 1271.7 | 2500 | 3179.25 | THIRD PARTY EXAMINATION |  | 18 | 16.2494714587737843551797040169133192389 |  | 0 | 309518 | 163028.6817124735729386892177589852008457 | 393607.3994714587737843551797040169133192 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | ROB R SMITH | OPERATIONS COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB R. SMITH | OPERATIONS COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | COLUMBIA GAS OF OHIO INVESTIGATORS AND OTHER INTERESTED PARTIES MET ON OCTOBER 11, 2012 TO PERFORM DESTRUCTIVE TESTING OF THE HEAT DAMAGED SERVICE LINE RISER AND TO SIFT THROUGH DEBRIS COLLECTED FROM THE SITE OF THE FIRE. AS A RESULT OF THAT INVESTIGATION, THE PARTIES CONCLUDED THAT THE CAUSE OF THIS FIRE CANNOT BE ASCERTAINED. COLUMBIA CONSIDERS THIS TO BE THE FINAL DETERMINATION AND THIS REPORT SHOULD BE CONSIDERED FINAL.
2025-03-31 10:13 | NO | YES | NO | 20120068 | 15532 | 2012-08-16 10:11 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2012-07-21 07:23 |  |  | 2012 | E. DUARTE & S. 2ND | ARCADIA | LOS ANGELES | CA | 91007 | 34.1304 | -118.025 | [9 empty] | 2012-07-21 22:19 | 1018655 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-07-21 07:43 |  |  |  | 2012-07-21 08:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 42 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1959 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 209000 | 265785.3 | 1000 | 1271.7 | 0 | 0 |  |  | 5 | 4.51374207188160676532769556025369978858 |  | 0 | 210005 | 110611.1754756871035940803382663847780127 | 267061.5137420718816067653276955602536998 | 20 | 0 | 437 |  |  |  |  | 39 | 39 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | W. JEFF KOSKIE | SR. PIPELINE SAFETY ADVISOR |  | 213 305-8660 | 213 244-8155 |  |  |  | W. JEFF KOSKIE | SR. PIPELINE SAFETY ADVISOR | 213 305-8660 | wkoskie@semprautilities.com | ELECTRIC TRANSFORMER FAILED, SENDING CURRENT ONTO WATER SERVICE. CURRENT ON WATER SERVICE ARCED ONTO 6' STEEL MAIN, CREATING HOLE ALLOWING WATER TO ENTER MAIN. WATER LINE AND MAIN REPAIRED. WATER REMOVAL AND RESTORATION OF 457 CUSTOMERS COMPLETE. LEAK SURVEY AND INSPECTION OF CATHODIC PROTECTION SYSTEMS IN AREA COMPLETED. NO IGNITION OR INJURIES. NO ROAD CLOSURES.
2025-03-31 10:13 | NO | NO | NO | 20120069 | 15503 | 2012-08-21 15:43 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2012-06-20 11:18 |  |  | 2012 | 748 INVERNESS | RANCHO MIRAGE | RIVERSIDE | CA | 92270 | 33.7895 | -116.4319 | [9 empty] | 2012-07-23 21:45 | 1018750 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-06-23 11:18 |  |  |  | 2012-06-23 11:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 34 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1979 | [5 empty] | 1 | ASTMD2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2306 | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 70000 | 89019 | 500 | 635.85 | 0 | 0 |  |  | 6 | 5.4164904862579281183932346723044397463 |  | 0 | 70506 | 37137.3605708245243128964059196617336152 | 89660.2664904862579281183932346723044397 | 0 | 0 | 70 |  |  |  |  | 42 | 42 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | LEAKING HIGH PRESSURE WATER SERVICE SCOURED HOLE IN PE MAIN | [154 empty] | W. JEFF KOSKIE | SR. PIPELINE SAFETY ADVISOR | wkoskie@semprautilities.com | 213 305-8660 | 213 244-8155 |  |  |  | W. JEFF KOSKIE | SR. PIPELINE SAFETY ADVISOR | 213 305-8660 | wkoskie@semprautilities.com | LEAKING HIGH PRESSURE WATER SERVICE SCOURED HOLE INTO 1' PE GAS MAIN, ALLOWING WATER TO ENTER SYSTEM. THIS RESULTED IN 50 OUTAGES AND A SIGNIFICANT WATER REMOVAL EFFORT. TOTAL COST OF WATER REMOVAL, REPAIR AND RESTORES EXCEEDED $50K, MEETING PHMSA REPORTING CRITERIA. ALTHOUGH MONITORED BY SOCALGAS SR. SAFETY ADVISOR, THIS INCIDENT WAS NOT REPORTED DUE TO AN ERROR IN INTERPRETATION OF REPORTABILITY REQUIREMENTS. USING THE PHMSA INSTRUCTIONS FOR FORM PHMSA F 7100.1 (REVISION 01-2010) GENERAL INSTRUCTIONS, PAGE 1, THE SR. SAFETY ADVISOR ASSUMED THAT ONLY COSTS ASSOCIATED WITH DAMAGE FROM ESCAPING GAS AND CONTOL OF ESCAPING GAS WERE TO BE CONSIDERED. IN THE INFORMATION RELATED TO SECONDARY IGNITION NOT NEEDING REPORTING, HE ASSUMED THAT THE ONLY COSTS REPORTABLE WOULD BE DAMAGE CAUSED BY ESCAPING GAS AND COSTS TO REPAIR ASSOCIATED LEAK. UPON FURTHER REVIEW OF INSTRUCTION, EMPLOYEE REALIZED THIS ERROR, BASED UPON PAGE 12 OF THE INSTRUCTIONS. EMPLOYEE IMMEDIATELY REVIEWED RECORDS OF INCIDENTS GOING BACK TO THE DATE OF RECEIVING THE REVISON 01-2010, AND DISCOVERED THIS SINGLE INCIDENT THAT HAD GONE UNREPORTED. WATER IN GAS INCIDENTS OCCURRING PRIOR TO REVISION 01-2010 WERE REGULARLY REPORTED WHEN ALL ASSOCIATED COSTS EXCEEDED $50K.
2025-03-31 10:13 | NO | NO | NO | 20120070 | 15504 | 2012-08-22 18:51 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2012-07-29 12:21 |  |  | 2012 | 631 S. SAN JOSE AVENUE | CLAREMONT | SAN BERNARDINO | CA | 91711 | 34.0833 | -117.7241 | [9 empty] | 2012-07-29 22:55 | 1019366 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-07-29 12:21 |  |  |  | 2012-07-29 14:51 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 37 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2002 | [5 empty] | 2 | ASTM D2513 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 75000 | 95377.5 | 1000 | 1271.7 | 0 | 0 |  |  | 6 | 5.4164904862579281183932346723044397463 |  | 0 | 76006 | 40034.2105708245243128964059196617336152 | 96654.6164904862579281183932346723044397 | 0 | 0 | 316 |  |  |  |  | 47 | 47 | 52 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HIGH PRESSURE WATER LEAK SCOURED PE SERVICE, CREATING LEAK | [154 empty] | W. JEFF KOSKIE | SR. PIPELINE SAFETY ADVISOR | wkoskie@semprautilities.com | 213 305-8660 | 213 244-8155 |  |  |  | W. JEFF KOSKIE | SR. PIPELINE SAFETY ADVISOR | 213 305-8660 | wkoskie@semprautilities.com | PRESSURE FROM LEAKING WATER MAIN SCOURED NEARBY 2" PE MAIN, CAUSING WATER TO ENTER MAIN AND DROP SERVICE TO 316 CUSTOMERS. LEAK REPAIRED, WATER REMOVED FROM MAINS AND SERVICES. MAIN HAS BEEN REPAIRED. PVC WATER LINE WAS REPLACED WITH COPPER BY WATER DEPARTMENT. NO INJURIES, NO IGNITION. BECAME REPORTABLE WHEN REPAIR/RESTORATION ESTIMATE MET $50,000 REPORTING THRESHOLD.
2025-03-31 10:13 | NO | YES | NO | 20120071 | 15505 | 2012-08-27 10:24 | ORIGINAL FINAL | 22235 | WAUKEE MUNICIPAL GAS | 805 UNVERSITY AVE | WAUKEE | IA | 50263 | 2012-05-22 08:19 |  |  | 2012 | 775 CHERRY ST | WAUKEE | DALLAS | IA | 50263 | 41.6097 | -93.8888 | [12 empty] | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 1 | 2012-05-22 08:20 |  |  |  | 2012-05-22 08:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | INSIDE RESIDENTIAL HOME |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OTHER | PRIVATE HOME | 1966 | [8 empty] | OTHER | PIPING INSIDE HOME | [9 empty] | OTHER | [8 empty] | FAILURE OF 3/8" COPPER TUBE CONNECTED TO WATER HEATER. | CLASS 3 LOCATION | 100000 | 127170 | 0 | 0 | 1000 | 1271.7 | 0 | 0 |  |  | 25 | 22.56871035940803382663847780126849894292 |  | 0 | 101025 | 53217.5773784355179704016913319238900634 | 128464.2687103594080338266384778012684989 | 0 | 0 | 1 |  |  |  |  | 20 | 20 | 20 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | FAILURE OF CUSTOMER PIPING. | [47 empty] | TIM ROYER | ASSISTANT DIRECTOR OF PUBLIC WORKS | troyer@waukee.org | 515-987-4363 | 515-987-3979 |  |  |  | TIM L. ROYER | ASST. DIRECTOR OF PUBLIC WORKS | 515-987-4363 | troyer@waukee.org | INSIDE PIPING WAS TESTED BY TECHNICAL INVESTIGATIONS INC REPRESENTING THE CITY OF WAUKEE AND INDEPENDENT FORENSIC INVESTIGATIONS CORP RETAINED BY FARM BUREAU INS REPRESENTING PROPERTY OWNER. THE GAS METER AND REGULATOR WERE TESTED AND FOUND NEGATIVE FOR OVER PRESSURE AND LEAKS. THE GAS RANGE IN KITCHEN WAS TESTED AND NO LEAKS WERE FOUND. DURING THE INSPECTION OF PIPING IN BASEMENT IT WAS FOUND NOTED THAT 3/8" SOFT COPPER TUBE PROVIDING GAS TO WATER HEATER WAS BROKEN AT THE BASE OF FLARE FITTING. IT WAS ALSO NOTED THAT FLARE FITTNG ITSELF WAS LEAKING. THE COPPER TUBING THAT BROKE FREE FROM FITTING WAS LARGELY DUE TO CORROSION. IT WAS ALSO NOTED THE WAY PIPING WAS ATTACHED TO FLOOR JOISTS IN A MANOR THAT TRANSMITS VIBRATIONS.
2025-03-31 10:13 | NO | YES | YES | 20120072 | 16087 | 2012-08-29 11:51 | SUPPLEMENTAL FINAL | 5330 | FLORIDA PUBLIC UTILITIES CO | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2012-08-28 11:16 |  |  | 2012 | 410.5 59TH ST. | WEST PALM BEACH | PALM BEACH | FL | 33407-2526 | 26.7627 | -80.0529 | [9 empty] | 2012-08-28 15:17 | 1022449 |  | NATURAL GAS |  | 0.3 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 4 | 2012-08-28 11:16 |  |  |  | 2012-08-28 11:59 |  | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | SERVICE LINE WITH CONCRETE SLAB OVER IT | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | ERW | 0.113 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 40000 | 50868 | 2500 | 3179.25 | 1000 | 1271.7 | 0 | 0 |  |  | 50 | 45.13742071881606765327695560253699788584 |  | 0 | 43550 | 22953.2047568710359408033826638477801268 | 55364.0874207188160676532769556025369979 | 0 | 0 | 2 |  |  |  |  | 18 | 20 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | ELECTRICAL ARCING BETWEEN THE GAS SERVICEA AND A CAST IRON SEWER LINE. THERE WAS LIGHTNING IN THE AREA A FEW DAYS, 8/24/12, BEFORE THE INCIDENT. THERE WERE ALSO CONDUITS FROM THE UNPERMITTED GARAGE APARTMENT IN THE GROUND AROUND THE GAS AND SEWER PIPES. THE INVESTIGATION DID NOT TURN UP A DEFINITIVE SOURCE OF THE CURRENT FOR THE ELECTRICAL ARCING. | [154 empty] | MICHAEL MCCARTY | COMPLIANCE AND MEASUREMENT MANAGER | mmccarty@fpuc.com | 863 845-7005 | 863 294-0629 |  |  |  | MICHAEL MCCARTY | COMPLIANCE AND MEASUREMENT MANAGER | 863 845-7005 | mmccarty@fpuc.com | AT APPROXIMATELY 11:15 AM ON 8/28/2012, FLORIDA PUBLIC UTILITIES WAS NOTIFIED BY WEST PALM BEACH FIRE DEPARTMENT OF AN EXPLOSION AND FIRE AT 410.5 59TH ST., WEST PALM BEACH, FL 33407-2526. THIS RESIDENCE IS A GARAGE APARTMENT BEHIND 410 59TH ST., WEST PALM BEACH, FL. THE SERVICE TECH FROM FLORIDA PUBLIC UTILTIES ARRIVED AT 11:59 AM AND FOUND THE NATURAL GAS SERVICE TO 410 59TH ST. TURNED OFF AT THE METER BY THE FIRE DEPARTMENT AS THEY WERE EXTINGUISHING THE FIRE. THE TECH FOUND THE 3/4" BARE STEEL NATURAL GAS SERVICE LEAKING UNDER A CONCRETE SLAB AT THE RESIDENCE. FLORIDA PUBLIC UTLITIES DISPATCHED A DISTRIBUTION CREW TO CUT THE SERVICE AT THE MAIN AND CAP IT AT 1:00 PM ON 8/28/12. IT WAS DETERMINED THAT AS A RESULT OF TROPICAL STORM ISAAC, THERE WERE MULTIPLE LIGHTENING STRIKES IN THE AREA OF THE RESIDENCE ON FRIDAY, 8/24/12. NEWS REPORTS STATED THAT THE RESIDENT OF 410.5 59TH ST., WEST PALM BEACH STARTED SMELLING GAS AROUND THIS TIME. HE DID NOT NOTIFY FLORIDA PUBLIC UTILITIES BUT LOOKED FOR THE SOURCE OF THE ODOR HIMSELF ON TUESDAY, 8/28/12. ATTACHED TO THIS REPORT IS A PICTURE OF A SECTION OF 3/4" BARE STEEL SERVICE THAT WAS CUT AND CAPPED AT 410 59TH ST., WEST PALM BEACH. IT APPEARS TO HAVE A HOLE CAUSED BY AN ELECTRICAL ARC. FURTHER INVESTIGATION OF THIS INCIDENT IN THE FOLLOWING WEEKS DETERMINIED THAT THE 3/4" BS GAS SERVICE WAS IN CLOSE PROXIMITY TO A CAST IRON SEWER LINE AND A GALVANIZED ELECTRICAL CONDUIT. THE ELECTRICAL CONDUIT WAS INSTALLED AT SOME POINT AFTER THE GAS SERVICE WAS INSTALLED WHEN THE GARAGE WAS CONVERTED INTO AN APARTMENT AND A CONCRETE SLAB WAS POURED OVER THEM ON THE GROUND. STRAY CURRENT EITHER FROM AN ELECTIC POWER POLE OR INDUCED UPON THE CONDUIT AND PIPING CAUSED AN ARC BETWEEN THE CONDUIT AND PIPES RESULTING IN A SMALL HOLE IN THE GAS PIPING. GAS LEAKED UNDER THE SLAB AS A RESULT OF THE ARC HOLE BEGINNING ON 8/24/12 AND VENTED INTO THE GARAGE APARTMENT. WHEN THE RESIDENT OF 410 59TH ST. BEGAN TO LOOK FOR THE SOURCE OF THE ODOR ON 8/28/12, HE LIT A CIGARETTE, IGNITING THE GAS IN THE APARTMENT. 5/28/2015 - SUPPLEMENTAL INFORMATION TO THE SUPPLEMENTAL AND FINAL REPORT FILED ON 4/28/2014. 1. THE LONGITUDE AND LATITUDE COORDINATES WERE CORRECTED FROM THE ORIGINAL COORDINATES THAT WERE OBTAINED FROM GOOGLE MAPS AND WERE SLIGHTLY INACCURATE. 2. THE CAUSE OF THE INCIDENT WAS CHANGED FROM G2 - NATURAL FORCE DAMAGE (LIGHTNING) TO G4 - OTHER OUTSIDE FORCE DAMAGE (ELECTRICAL ARCING). ALTHOUGH THERE WAS LIGHTNING IN THE AREA DAYS PRIOR TO THE INCIDENT, THE EXACT SOURCE OF THE CURRENT THAT ARCED A HOLE IN THE GAS SERVICE COULD NOT BE DEFINITIVELY DETERMINED AFTER AN INVESTIGATION. 3. TOTAL ESTIMATED PROPERTY DAMAGE WAS REVIEWED AND LEFT AS STATED. THE DAMAGE AND REMOVAL OF DEBRIS WERE CONFINED TO AN UNPERMITTED AND UNINHABITED DETACHED GARAGE THAT HAD BEEN CONVERTED INTO AN APARTMENT. THE REPAIR OF THE GAS MAIN CONSISTED OF INSTALLING A STOP FITTING AND INSERTING APPROX. 100' OF STEEL MAIN WITH PE PIPE AND RUNNING APPROX. 33' OF PE SERVICE. THE ASSESSED VALUE FOR THE ENTIRE PROPERTY AT 410 59TH ST, WEST PALM BEACH WAS $75,210 WITH A MARKET VALUE OF $92,639 IN 2012. THE MEDICAL COSTS FOR THE INJURED PARTY WERE NOT INCLUDED IN THE PROPERTY DAMAGE AMOUNT. 4. REFERENCE TO "ACTIVE LITIGATION" WAS REMOVED FROM LAST NARRATIVE. 5. CONTACT TITLE, PHONE AND FAX NUMBERS HAVE BEEN UPDATED FOR THE SUBMITTER.
2025-03-31 10:13 | NO | YES | YES | 20120073 | 15698 | 2012-09-05 17:40 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD. NE STE, 20 | ALBUQUERQUE | NM | 87109 | 2012-08-08 18:38 |  |  | 2012 | PLACITAS DE LUNA / CAMINO FRANCISCA | SANTA FE | SANTA FE | NM | 87501 | 35.7141 | -105.9445 | [9 empty] | 2012-08-08 19:40 | 1020424 |  | NATURAL GAS |  | 144 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2012-08-08 18:38 |  |  |  | 2012-08-08 18:38 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2012 | [5 empty] | 4 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | OTHER |  |  |  | UNDER INVESTIGATION |  |  |  |  | THE TYPE OF RELEASE IS INCONCLUSIVE AND UNDER INVESTIGATION. | CLASS 3 LOCATION | 61742 | 78517.3014 | 3281 | 4172.4477 | 6411 | 8152.8687 | 0 | 0 |  |  | 593 | 535.329809725158562367864693446088794926 |  | 0 | 72027 | 38119.4992164904862579281183932346723044 | 91377.9476097251585623678646934460887949 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 4 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 2012 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [7 empty] | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | YES | 2012 | 95 | [84 empty] | GARY G. ROYBAL | MANAGER | gary.roybal@nmgco.com | 505-697-3636 | 505-697-4481 |  |  |  | ED KACER | VP TECHNICAL SERVICES | 505-697-3303 | ed.kacer@nmgco.com | A 4IN PLASTIC MAINLINE WAS RELOCATED AND THE FUSION MACHINE ON THE FINAL FUSION WELD WAS IN THE PROCESS OF BEING REMOVED WHEN AN UNINTENTIONAL RELEASE OF GAS OCCURRED AND THE GAS IGNITED. THE EXACT REASONS FOR THE FAILURE CANNOT BE DETERMINED WITH CERTAINTY BECAUSE THE EVIDENCE WAS DESTROYED IN THE FIRE.
2025-03-31 10:13 | NO | YES | YES | 20120074 | 15648 | 2012-09-06 08:29 | SUPPLEMENTAL FINAL | 11296 | LAWRENCEBURG GAS DEPT, CITY OF | 403 OAK STREET | LAWRENCEBURG | TN | 38464 | 2012-08-07 18:20 |  |  | 2012 | HWY 20 @ HWY 240 | SUMMERTOWN | LAWRENCE | TN | 38483 | 35.4398 | -87.2902 | [9 empty] | 2012-08-07 21:25 | 1020313 |  |  |  | 247 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 125 | 2012-08-07 18:30 |  |  |  | 2012-08-07 19:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1990 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  |  |  |  | CLASS 3 LOCATION | 0 | 0 | 187177 | 238032.9909 | 12977 | 16502.8509 | 0 | 0 |  |  | 1145 | 1033.646934460887949260042283298097251586 |  | 0 | 201299 | 106377.2957323467230443974630021141649049 | 255569.4887344608879492600422832980972516 | 24 | 0 | 186 |  |  |  |  | 90 | 90 | 450 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | SAMUEL E. BLEVINS | D AND O OPERATOR | sblevins@lburgus.com | 931.629.9918 | 931.762.9276 |  |  |  | SAMUEL E. BLEVINS | D AND O OPERATOR | 931.629.9918 | sblevins@lburgus.com | ON AUG 7, 2012, AT APPROSIMATELY 18:20, A 2009 NISSAN SENTRA DRIVEN BY WAYNE SPENSE WAS TRAVELING EAST ON HWY 20 IN SUMMERTOWN, TN. THE VEHICLE RAN OFF OF THE LEFT SIDE OF THE ROAD, TRAVELED 500 FT., AND STRUCK A GAS REGULATOR STATION. AT APPROSIMATELY 18:30, TODD PENNINGTON, A WORKER AT SUMMERTOWN UTILITY DISTRICT CALLED SCOTT GARLAND, THE LAWRENCEBURG UTILITY SYSTEM GAS DEPT. ON CALL PERSON. TODD ADVISED THAT A CAR HAD RAN THROUGH A GAS REGULATING STATION AND WAS ON FIRE. SCOTT DID NOT KNOW IF IT WAS A LAWRENCEBURG UTILITY SYSTEM (LUS) OR EAST TENNESSEE (ETNG) STATION. SCOTT NOTIFIED RONNIE DIAL (LUS GAS FOREMAN) AND TIM DOLLAR (LUS WATER ON CALL PERSON) FOR ASSISTANCE.UPON ARRIVAL NEAR THE SCENE LUS PERSONNEL WAS DENIED ACCESS BY EMERGENCY PERSONNEL. IT WAS APPROSIMATELY 19:00 - 19:10 WHEN SCOTT ARRIVED ON THE ACCIDENT SCENE. AT APPROXIMATELY 19:20 SCOTT GARLAND AND RONNIE DIAL BEGIN TURNING OFF HIGH PRESSURE GAS VALVES. AT APPROSIMATELY 19:40 SCOTT AND RONNIE BEGIN TURNING OFF LOW PRESSURE VALVES. THE GAS DISTRIBUTION WAS BACKFEEDING INTO THE STATION AND FEEDING THE FLAMES. BY 19:50 THE GAS WAS OFF AND THE FLAMES EXTINGUISHED. THE GAS LINES WERE CAPPED. GAS VALVES WERE TURNED OFF AT THE CUSTOMERS METERS. BY 06:00 ON AUG 8, 2012 LUS WAS RELIGHTING CUSTOMERS PILOT LIGHTS. MR. SPENSE PERISHED IN THE CRASH. THE GAS REGULATING STATION WAS A COMPLETER LOSS. GAS IS CURRENTLY BEING FER TO SUMMERTOWN BY WAY OF HWY 43. FINAL: ON 01/130031/2013 BUSH CONSTRUCTION CO INSTALLED A TEMPORARY REGULATOR STATION TO HELP WITH LOW PRESSURE IN SUMMERTOWN. ON 02/28/2013 A NEW STATION WAS COMPLETED IT WAS PUT ON LINE AT APPROXIMATELY 13:15.
2025-03-31 10:13 | NO | NO | NO | 20120075 | 15512 | 2012-09-07 10:40 | ORIGINAL | 2812 | CORPUS CHRISTI, CITY OF - GAS DIV | 4225 SOUTH PORT AVENUE | CORPUS CHRISTI | TX | 78415 | 2012-08-14 10:56 |  |  | 2012 | 4619 BALDWIN BLVD | CORPUS CHRISTI | NUECES | TX | 78408-2711 | 27.7923 | -97.4473 | [9 empty] | 2012-08-14 12:40 | 1021032 |  | NATURAL GAS |  | 8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 16 | 2012-08-14 11:06 |  |  |  | 2012-08-14 11:11 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1963 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | RISER WAS SEVERED AT A THREADED CONNECTION. | CLASS 3 LOCATION | 0 | 0 | 200 | 254.34 | 700 | 890.19 | 0 | 0 |  |  | 25 | 22.56871035940803382663847780126849894292 |  | 0 | 925 | 494.907378435517970401691331923890063425 | 1167.098710359408033826638477801268498943 | 0 | 0 | 0 |  |  |  |  | 70 | 70 | 100 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JESSE M. CANTU JR | PETROLEUM SUPERINTENDENT | jessecantu@cctexas.com | (361)885-6941 | (361)853-3200 |  |  |  | DEBORAH A. MARROQUIN | DIRECTOR OF GAS SERVICES | (361)885-6924 | debbiem@cctexas.com | MAJEK DEMOLITION WAS IN THE PROCESS OF DEMOLISHING A COMMERCIAL BUILDING WITH A SMALL EXCAVATOR WHEN AN OUTSIDE WALL COLLAPSED AND FELL ON TOP OF THE METER SET BREAKING THE RISER AT A TREADED CONNECTION. THE CONTRACTOR FAILED TO NOTIFY THE CITY OF CORPUS CHRISTI FOR REMOVAL OF THE SERVICE PRIOR TO CONDUCTING THE DEMOLITION. THE RISER WAS PLUGGED TO RENDER SAFE AND THE SERVICE HAS BEEN ABANDONED FOR NON USE.
2025-03-31 10:13 | NO | NO | NO | 20120076 | 15564 | 2012-09-07 20:35 | SUPPLEMENTAL FINAL | 12876 | QUESTAR GAS COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2012-08-08 21:20 |  |  | 2012 | 905 BRIDGER DRIVE | GREEN RIVER | SWEETWATER | WY | 82935 | 41.5034 | -109.4587 | [9 empty] | 2012-08-08 22:43 | 1020434 |  | NATURAL GAS |  | 6.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2012-08-08 21:35 |  |  |  | 2012-08-08 21:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1984 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | VEHICLE HIT METER SET | [5 empty] | CLASS 3 LOCATION | 20000 | 25434 | 9200 | 11699.64 | 1000 | 1271.7 | 0 | 0 |  |  | 50 | 45.13742071881606765327695560253699788584 |  | 0 | 30250 | 15948.0947568710359408033826638477801268 | 38450.4774207188160676532769556025369979 | 1 | 0 | 0 |  |  |  |  | 35 | 35 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A METER SET THAT WAS HIT BY A VEHICLE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JEFFREY D. HANSEN | MANAGER - TECHNICAL OPERATIONS | jeff.hansen@questar.com | 801-324-3645 | 801-324-3300 |  |  |  | C. SCOTT BROWN | VICE PRESIDENT - OPERATIONS | 801-324-5172 | scott.brown@questar.com | AN ALLEGEDLY DRUNKEN DRIVER WAS TRAVELLING SOUTH ON WEST TETON DRIVE IN GREEN RIVER, WYOMING, WHEN SHE MADE AN ABRUPT 90 DEGREE TURN (EAST) AND CROSSED THE PARK STRIP, OVER AN ASPHALT DRIVE THAT IS PART OF THE PARKING LOT, JUMPED THE CURB AROUND THE LAWN AREA AND PROCEEDED ALONG THE BUILDLING STRIKING THE METER SET FROM THE WEST SIDE. THE INLET PIPING TO THE METER SET WAS BROKEN OFF ABOVE THE SHUT-OFF VALVE DUE TO THE IMPACT FROM THE VEHICLE. THE RELEASE OF GAS WAS IGNITED AND DESTROYED THE VEHICLE THAT HIT THE METER SET AND THE FIRE DAMAGED A SIGN ON THE SIDE OF THE BUILDING. THE DRIVER OF THE VEHICLE WAS TREATED AT THE SCENE AND ARRESTED. NO OTHER INJURIES WERE REPORTED. THE BUILDING WAS A GROCERY STORE AND THE STORE WAS EVACUATED. THE ACTUAL NUMBER OF PEOPLE EVACUATED IS NOT KNOWN.
2025-03-31 10:13 | NO | YES | NO | 20120077 | 15514 | 2012-09-18 15:07 | ORIGINAL | 14330 | ORANGE & ROCKLAND UTILITY INC | ONE BLUE HILL PLAZA | PEARL RIVER | NY | 10965 | 2012-06-21 16:28 |  |  | 2012 | BROADWAY & 1ST ST | NYACK | ROCKLAND | NY | 10960 | 41.0907 | -73.9179 | [12 empty] | NATURAL GAS |  | 31 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2012-06-21 16:28 |  |  |  | 2012-06-21 16:28 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 12 | API 5L GRADE B | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.375 | [6 empty] | OTHER | [8 empty] | CONTRACTOR CUTTING PIPE WITH A TORCH OVERHEATED BAGS CAUSING BAG STOPPERS TO FAIL AND IGNITION TO OCCUR. | CLASS 3 LOCATION | 100000 | 127170 | 0 | 0 | 200000 | 254340 | 0 | 0 |  |  | 124 | 111.940803382663847780126849894291754757 |  | 0 | 300124 | 158113.5517970401691331923890063424947146 | 381621.9408033826638477801268498942917548 | 80 | 0 | 305 |  |  |  |  | 0.33 | 0.33 | 0.44 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE TO PIPELINE WITH COMPANY CREWS IMMEDIATLY ON SITE. | [12 empty] | YES | 1 | 0 | YES | 3 | 0 | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | CONTRACTOR WAS FLAME CUTTING 12" STEEL AND EXPOSED 12" BAG STOPPERS TO EXCESSIVE HEAT CAUSING THE BAG STOPPERS TO FAIL. | [47 empty] | JOE MANDARA | SECTION MANAGER GAS OPERATIONS | mandaraj@oru.com | 845-577-3011 | 845-577-3166 |  |  |  | ANTHONY ADINOLFI | GM GAS OPERATIONS | 845-577-3515 | adinolfia@oru.com | CONTRACTOR RAINES & WELSH (R&W) WAS AWARDED THE CONTRACT TO UPGRADE THE LOW PRESSURE SYSTEM TO HIGH PRESSURE GAS MAINS AND SERVICES IN NYACK. THE WORK INCLUDED RETIRING AND IN SOME CASES REMOVING THE EXISTING LOW PRESSURE FACILITIES. R&W BEGAN WORK ON THE PROJECT IN SEPTEMBER 2011. ON THE DAY OF THE INCIDENT R&W WAS RETIRING A SECTION OF 12 INCH LOW PRESSURE STEEL GAS MAIN ON BROADWAY AT 1ST STREET IN WEST NYACK. THE 12 INCH MAIN RUNS NORTH AND SOUTH ON BROADWAY AND HAD A RADIAL 4 INCH LOW PRESSURE STEEL MAIN COMING OFF TO THE WEST ON 1ST ST. R&W EXCAVATED AND EXPOSED THE 12 INCH AND 4 INCH MAIN. THE BALLOON STOPPERS WERE INFLATED TO 4 PSI TESTED FOR LEAKAGE AND HELD PRESSURE FOR OVER ONE HOUR BEFORE BEING USED. THEY INSTALLED TWO TAPPING TEES AND FOUR LOW PRESSURE BALLOON STOPPERS INTO THE 12 INCH PIPE AT THE LOCATIONS SHOWN ON THE SKETCH. THE 4 INCH MAIN HAD PREVIOUSLY BEEN DEAD ENDED WITH A CAP FURTHER WEST ALONG 1ST STREET AND DID NOT REQUIRE ANY STOPPERS. R&W THEN PERFORMED A FLOW TEST TO CONFIRM THAT GAS WAS BEING SUPPLIED TO THE MAIN NORTH AND SOUTH OF THE ISOLATED SECTION. THE PRESSURE GAUGES ON THE BALLOON STOPPERS WERE CHECKED TO CONFIRM THAT THE STOPPERS WERE HOLDING AND THAT THE SECTION WAS EFFECTIVELY ISOLATED. R&W CUT THE 12 INCH PIPE ON THE NORTH END OF THE EXCAVATION WITH A REED 4 WHEEL PIPE CUTTER. THEY THEN MADE TWO CUTS WITH A DEMO SAW ON THE 4 INCH STEEL MAIN, REMOVING A 4 INCH RING. R&W USED AN ORBITAL CUTTER AND TORCH TO BEVEL CUT THE SOUTH SIDE OF THE 12 INCH MAIN. THE CREW MADE A SECOND CUT AND REMOVED ABOUT A 4 INCH RING AT THE SOUTHERLY END OF THE 12 INCH PIPE. WHEN THE RINGS WERE CUT R&W HAD SUFFICIENT CLEARANCE AND THE CUT OUT SECTION WAS REMOVED FROM THE EXCAVATION. R&W SET UP THE ORBITAL CUTTER TO BEVEL THE ROUGH CUT ON THE NORTH END OF THE 12 INCH MAIN. THE CONTRACTOR'S WELDER AND CREW FOREMAN WERE IN THE EXCAVATION AND BEGAN TO MAKE THE BEVEL CUT. AT 16:28, WHEN THEY HAD FLAME CUT APPROXIMATELY 8 INCHES OF THE CIRCUMFERENCE, THE NORTHERLY BALLOON STOPPERS FAILED AND THE LEAKING GAS IGNITED. BOTH MEN EXITED THE EXCAVATION AND WERE NOT INJURED BY THE IGNITION OR THE ENSUING GAS FED FIRE. THE THREE REGULATOR STATIONS SUPPLYING THE AFFECTED AREA WERE TURNED OFF AND THE RESIDUAL GAS BURNED OFF. APPROXIMATELY 385 GAS SERVICES WERE INTERRUPTED. OVERHEAD ELECTRIC FACILITIES IN THE AREA WERE DE-ENERGIZED INTERRUPTING APPROXIMATELY 650 SERVICES. ELECTRIC SERVICE WAS RESTORED AT APPROXIMATELY 20:40 THAT EVENING. GAS CONSTRUCTION INSTALLED COMPRESSION CAPS ON THE 12 INCH OPEN ENDS AND A WOODEN PLUG IN THE DEAD 4 INCH MAIN. O&R SERVICE MECHANICS ALONG WITH CECONY GDS CREWS WORKED AROUND-THE-CLOCK TO RESTORE GAS SERVICE TO THE AFFECTED CUSTOMERS. GAS SERVICE WAS FULLY RESTORED AT 18:00 ON 6/24/12
2025-03-31 10:13 | YES | NO | NO | 20120078 | 15531 | 2012-09-21 13:26 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2012-08-24 06:05 |  |  | 2012 | 81944 HIGHWAY 111 | INDIO | RIVERSIDE | CA | 92201 | 33.7076 | -116.2427 | [9 empty] | 2012-08-24 07:30 | 1022067 |  | NATURAL GAS |  | 42 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-08-24 06:05 |  |  |  | 2012-08-24 06:32 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1986 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 3 LOCATION | 0 | 0 | 1000 | 1271.7 | 500 | 635.85 | 0 | 0 |  |  | 250 | 225.687103594080338266384778012684989429 |  | 0 | 1750 | 998.823784355179704016913319238900634249 | 2133.237103594080338266384778012684989429 | 5 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | W. JEFF KOSKIE | SR. PIPELINE SAFETY ADVISOR | wkoskie@semprautilities.com | 213-305-8660 | 213-244-8155 |  |  |  | W. JEFF KOSKIE | SR. PIPELINE SAFETY ADVISOR | 213-305-8660 | wkoskie@semprautilities.com | ON AUGUST 24, 2012, A FIRE ERUPTED WITHIN A COMMERCIAL COMPLEX, ULTIMATELY SPREADING THROUGHOUT THE COMPLEX, CAUSING A BURNING WALL TO FALL ONTO A NATURAL GAS METER SET ASSEMBLY WHOSE COMPONENT(S) MELTED AND IGNITED. SINCE THE FIRE INVOLVED PROPERTY DAMAGE EXCEEDING $50,000, THIS INCIDENT WAS REPORTED TO PHMSA AND CPUC. FURTHER INVESTIGATION DETERMINED THAT THE FIRE WAS STARTED AWAY FROM THE METER LOCATION, AND THAT IGNITIED GAS DID NOT CONTRIBUTE TO PROPERTY DAMAGE OR HINDER FIREFIGHTING EFFORTS. REPAIRS HAVE BEEN COMPLETED, AND RESTORATION WILL TAKE PLACE ONCE COMMERCIAL FACILITIES ARE REPAIRED AND/OR REBUILT.
2025-03-31 10:13 | YES | NO | NO | 20120079 | 15569 | 2012-09-24 20:48 | SUPPLEMENTAL FINAL | 4483 | ENSTAR NATURAL GAS CO | 3000 SPENARD ROAD | ANCHORAGE | AK | 99503 | 2012-08-30 04:35 |  |  | 2012 | 39395 HALLELUJAH TRAIL | SOLDOTNA | KENAI PENINSULA BOROUGH | AK | 99669 | 60.4998 | -150.923 | [9 empty] | 2012-08-30 06:00 | 1022635 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2012-08-30 04:35 |  |  |  | 2012-08-30 05:11 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1999 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 0.5 | 0.5 |  | CLASS 3 LOCATION | 250000 | 317925 | 3000 | 3815.1 | 2000 | 2543.4 | 0 | 0 |  |  | 100 | 90.27484143763213530655391120507399577167 |  | 0 | 255100 | 134392.0095137420718816067653276955602537 | 324373.7748414376321353065539112050739958 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | DAVID BREDIN | DIRECTOR OF OPERATIONS | dave.bredin@enstarnaturalgas.com | 907-264-3745 | 907-562-0053 |  |  |  | DAVID W. BREDIN | DIRECTOR OF OPERATIONS | 907-264-3745 | dave.bredin@enstarnaturalgas.com | ENSTAR NATURAL GAS COMPANY EMPLOYEES RESPONDED TO A CALL THAT A RESIDENTIAL STRUCTURE WAS ON FIRE AT 39395 HALLELUJAH TRAIL, SOLDOTNA, AK ON 8/30/12. THE METER SET WAS ON FIRE AS THE HDPE SERVICE LINE TUBING INSIDE THE RISER HAD MELTED AND RELEASED NATURAL GAS. THE SERVICE LINE WAS DUG UP AND PINCHED OFF TO STOP THE FLOW OF NATURAL GAS. THE STRUCTURE SUFFERED EXTENSIVE DAMAGE. THE GAS REGULATOR AND METER WERE SEVERELY BURNED AND UNRECOVERABLE. A JOINT INVESTIGATION WAS CONDUCTED BY THE LOCAL FIRE INVESTIGATOR, AN INVESTIGATOR FROM THE HOMEOWNER'S INSURANCE COMPANY AND A PRIVATE INVESTIGATOR HIRED BY ENSTAR. WHILE THE FIRE STARTED NEAR THE GAS METER, IT'S ORIGIN APPEARED TO BE ELECTRICAL IN NATURE. A NON GFCI ELECTRICAL OUTLET WAS LOCATED OUTSIDE THE STRUCTURE, NEAR THE GAS METER. PLUGGED INTO THE OUTLET WAS AN UNUSED EXTENSION CORD. ALSO PLUGGED INTO THE OUTLET WAS A PHOTO VOLTAIC TIMER, A 6 RECEPTACLE POWER STRIP, A SMALL EXTENSION CORD, A STRING OF DECORATIVE PATIO LIGHTS AND A DECORATIVE WATER FOUNTAIN. IT APPEARS ONE OF THE ELECTRICAL COMPONENTS FAILED AND STARTED BURNING PLASTIC AND SILK DECORATIVE FLOWERS THAT HAD BEEN PLACED AROUND THE GAS METER. THIS APPEARS TO BE A FIRE FIRST INCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20120080 | 15645 | 2012-09-26 15:11 | SUPPLEMENTAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2012-08-28 12:30 |  |  | 2012 | 341 MONTROSE AVENUE | SOUTH ORANGE | ESSEX | NJ | 07079-9998 | 40.7499 | -74.2435 | [9 empty] | 2012-08-28 16:25 | 1022459 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2012-08-28 13:05 |  |  |  | 2012-08-28 13:25 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1935 | [5 empty] | 2 | API5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | LEAK |  |  | OTHER | CORROSION HOLE | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 0.25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | NO | COAL TAR | [21 empty] | 2011-10-02 | NO | [227 empty] | FRANKY CORIANO | PRINCIPAL REGULATORY SPECIALIST | franky.coriano@pseg.com | 609-421-8025 | 609-695-6737 |  |  |  | MICHAEL J. GAFFNEY | DIRECTOR GAS DISTRIBUTION FIELD CONSTRUCTION | 973-365-5300 | michael.gaffney@pseg.com | ON TUESDAY, AUGUST 28, 2012, AT APPROXIMATELY 12:30 PM A CREW WAS WORKING ON REPLACING A SCHEDULED 2-INCH BARE STEEL UTILIZATION PRESSURE SERVICE FROM MAIN TO CURB AT 341 MONTROSE AVENUE IN SOUTH ORANGE. A UTILITY MECHANIC WAS EXCAVATING WITH A LEAK (PRY) BAR TO UNCOVER THE SERVICE TEE AT THE MAIN IN ACCORDANCE TO THE CONSTRUCTION STANDARDS WHEN GAS LEAKING FROM A CORROSION HOLE IGNITED. A FLASH FIRE ENSUED CAUSING THE EMPLOYEE TO SUSTAIN BURNS TO HIS FACE AND BOTH ARMS. THE EMPLOYEE WAS NOT WEARING PROPER PPE WHILE WORKING IN A GASEOUS ATMOSPHERE. THE EMPLOYEE IS OQ QUALIFIED AND WAS RECENTLY OQ QUALIFIED ON JULY 12, 2012. THE FIRE WAS EXTINGUISHED BY THE STREET LEADER WITH A FIRE EXTINGUISHER THAT WAS AVAILABLE ALONGSIDE THE EXCAVATION. SUPERVISION WAS NOTIFIED AND ARRIVED TO THE SCENE AT 1:25 PM AND TRANSPORTED THE EMPLOYEE TO AN EMERGENCY MEDICAL FACILITY. AT 1:30 PM THE GAS SERVICE WAS MADE SAFE AND REPLACED BY A RELIEF CREW THAT WAS DISPATCHED TO THE SCENE. AFTER MULTIPLE ASSESSMENTS, DR. E. HANI MANSOUR DETERMINED THE EMPLOYEE HAD SUSTAINED SECOND AND THIRD DEGREE BURNS AND ADMITTED HIM FOR OBSERVATION AND TREATMENT. THE EMPLOYEE WAS DISCHARGED ON SEPTEMBER 3, 2012, AND HE IS RECEIVING THERAPY FOR HIS INJURIES.
2025-03-31 10:13 | NO | NO | NO | 20120081 | 15794 | 2012-09-27 15:36 | SUPPLEMENTAL FINAL | 2812 | CORPUS CHRISTI, CITY OF - GAS DIV | 4225 SOUTH PORT AVENUE | CORPUS CHRISTI | TX | 78415 | 2012-08-29 14:15 |  |  | 2012 | 1045 HAMLIN DR | CORPUS CHRISTI | NUECES | TX | 78411 | 27.7341 | -97.3841 | [9 empty] | 2012-08-29 15:55 | 1022577 |  | NATURAL GAS |  | 89 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 1 | 2012-08-29 14:15 |  |  |  | 2012-08-29 14:19 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1956 | [5 empty] | 2.375 | API 5L | UNKNOWN | STEEL |  | SEAMLESS | SEAMLESS | 0.375 | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1000 | 1271.7 | 200 | 254.34 | 0 | 0 |  |  | 300 | 270.824524312896405919661733615221987315 |  | 0 | 1500 | 882.568541226215644820295983086680761099 | 1796.864524312896405919661733615221987315 | 0 | 0 | 15 |  |  |  |  | 10 | 10 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | [7 empty] | YES | [6 empty] | CONTRACTOR | AUGER | POLE | YES | 122281249 | TEXAS 811 |  | UTILITY OWNER | YES |  |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | JESSE M. CANTU JR | PETROLEUM SUPERINTENDENT | jessecantu@cctexas.com | (361)885-6941 | (361)853-3200 |  |  |  | JESSE M. CANTU JR. |  | (361)885-6941 | No Email Address | THE 2 INCH STEEL MAIN WAS MARKED BY THE LINE LOCATOR APPROXIMATELY 4 FEET FROM THE ACTUAL LOCATION OF THE LINE. THE LINE WAS PUNCTURED BY AN AUGER DURING THE INSTALLATION OF A POWER POLE. THE LINE IS A SHORT SEGMENT AND WAS INITIALLY CLAMPED AND RETURNED TO SERVICE. FINAL REPAIRS WERE COMPLETED ON AUGUST 29TH, 2012 BY CUTTING OUT AND REPLACING 5 FEET OF PIPE.
2025-03-31 10:13 | NO | YES | YES | 20120082 | 15534 | 2012-10-03 12:28 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2012-09-09 03:45 |  |  | 2012 | 11412 VENTURA BLVD. | STUDIO CITY | LOS ANGELES | CA | 91604 | 34.1397 | -118.3793 | [9 empty] | 2012-09-09 07:00 | 1023817 |  | NATURAL GAS |  | 22 |  | YES | 0 | 0 | 0 | 0 | 3 | 3 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-09-09 03:45 |  |  |  | 2012-09-09 04:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1986 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 10000 | 12717 | 3000 | 3815.1 | 400 | 508.68 | 0 | 0 |  |  | 125 | 112.843551797040169133192389006342494715 |  | 0 | 13525 | 7162.166892177589852008456659619450317125 | 17153.6235517970401691331923890063424947 | 2 | 0 | 0 |  |  |  |  | 35 | 35 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | W. JEFF KOSKIE | SR. PIPELINE SAFETY ADVISOR | wkoskie@semprautilities.com | 213-305-8660 | 213-244-8155 |  |  |  | W. JEFF KOSKIE | SR. PIPELINE SAFETY ADVISOR | 213-305-8660 | wkoskie@semprautilities.com | VEHICLE CARRYING THREE ADULTS TRAVELING AT HIGH SPEED LOST CONTROL, JUMPED CURB AND HIT TWO TREES, RISER, AND BUILDING AT A STRIP MALL. RAN THROUGH METER GUARD AND STRUCK MSA. RISER BENT AND VEHICLE CAUGHT ON FIRE. FD SHUT METER OFF AND GAS WAS UNDER CONTROL AT 4:20 AM. METER INCIDENT WAS REPORTABLE BASED ON THE 3 FATALITIES AND MULTIPLE NEWS MEDIA OUTLETS ON SCENE.
2025-03-31 10:13 | YES | NO | NO | 20120085 | 15528 | 2012-10-11 08:11 | SUPPLEMENTAL FINAL | 18104 | CPS ENERGY | 500 MCCULLOUGH | SAN ANTONIO | TX | 78215 | 2012-09-16 02:25 |  |  | 2012 | 4215 TIMBERHILL DRIVE | SAN ANTONIO | BEXAR | TX | 78296 | 29.4745 | -98.6262 | [9 empty] | 2012-09-18 08:51 | 1024763 |  |  |  | 81.9 |  | YES | 0 | 0 | 0 | 0 | 2 | 2 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-09-16 04:00 |  |  |  | 2012-09-16 05:10 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | 1975 | [8 empty] | STEEL |  | OTHER | SMLS | 0.179 | [6 empty] | OTHER | [8 empty] | NATURAL GAS RELEASE RESULTED FROM A VEHICLE CRASHING THROUGH THE RESIDENTIAL GAS METER AND REGULATOR SETTING. THE GAS SERVICE RISER WAS SHEARED OFF CAUSING A RELEASE OF GAS. | CLASS 3 LOCATION | 190000 | 241623 | 300 | 381.51 | 571 | 726.1407 | 0 | 0 |  |  | 245 | 221.173361522198731501057082452431289641 |  | 0 | 191116 | 100736.3540086680761099365750528541226216 | 242951.8240615221987315010570824524312896 | 0 | 0 | 1 |  |  |  |  | 9 | 9 | 33 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BECAUSE THE RELEASE OF NATURAL GAS IN THE DISTRIBUTION SYSTEM WAS NOT LARGE ENOUGH FOR THE SCADA SYSTEM TO DETECT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | ANTHONY BROWN | GAS ENGINEER | abrown@cpsenergy.com | (210) 353-6092 | (210) 353-2072 |  |  |  | TORRY HURT | SUPERVISOR - GAS CODES AND STANDARDS | (210) 353-6132 | tlhurt@cpsenergy.com | THE PRIMARY CAUSE OF THE INCIDENT WAS DUE TO OTHER OUTSIDE FORCE DAMAGE. A VEHICLE LOST CONTROL AND CRASHED THROUGH A RESIDENTIAL HOME SHEARING THE GAS METER AND REGULATOR SETTING AT THE INITIAL POINT OF IMPACT. AS A RESULT, THE PRIMARY IGNITION SOURCE WAS THE GASOLINE FROM THE VEHICLE WHICH STARTED THE HOUSE FIRE. THE HOUSE FIRE THEN IGNITED THE NATURAL GAS RELEASED FROM THE DAMAGED GAS RISER CAUSING A SECONDARY FUEL SOURCE DURING THE INCIDENT. THE TWO DEATHS THAT OCCURED WHERE NOT ATTRIBUTED TO THE RELEASE OF NATURAL GAS.
2025-03-31 10:13 | NO | YES | YES | 20120086 | 15524 | 2012-10-11 14:26 | ORIGINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2012-09-07 17:09 |  |  | 2012 | 272 REOCK AVENUE | ORANGE | ESSEX | NJ | 07050-3510 | 40.7705 | -74.2299 | [9 empty] | 2012-09-07 19:38 | 1023710 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | NO | 0 | 2012-09-07 17:09 |  |  |  | 2012-09-07 17:27 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | METER-BAR | [9 empty] | OTHER | [8 empty] | THEFT OF GAS METER AND ASSOCIATED PIPING BY VANDALS | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 0.25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | UTILIZATION PRESSURE NOT REQUIRING CONTROL ROOM MONITORING | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | THEFT OF EQUIPMENT | [156 empty] | FRANKY CORIANO | PRINCIPAL REGULATORY SPECIALIST | franky.coriano@pseg.com | 609-421-8025 | 609-695-6737 |  |  |  | MICHAEL J. GAFFNEY | DIRECTOR GAS DISTRIBUTION FIELD CONSTRUCTION | 973-365-5300 | michael.gaffney@pseg.com | ON FRIDAY SEPTEMBER 7, 2012, PSE&G RESPONDED TO A GAS EMERGENCY CALL INVOLVING A GAS IGNITION. THE INITIAL CALL CAME IN FROM THE ORANGE FIRE DEPARTMENT AT 17:09, AS A HOUSE FIRE AT 272 REOCK AVE, ORANGE; THE FIRE CHIEF STATED GAS WAS NOT INVOLVED, AND THE FIRE WAS CAUSED BY SQUATTERS. SUBSEQUENT INVESTIGATION OF THE INCIDENT REVEALED THAT THE FIRE WAS CAUSED WHEN ONE OF THE SQUATTERS LIT A MATCH, WHICH IGNITED LEAKING GAS, ORIGINATING FROM GAS PIPING REMOVED FROM THE HEAD OF AN INSIDE METER SET. THE GAS METER, INLET VALVE AND ASSOCIATED PIPING WERE ALL REMOVED BY AN UNKNOWN PERSON, ON AN UNKNOWN DATE, PRIOR TO THE FIRE. AN APPLIANCE SERVICE TECH RESPONDED AND SHUT THE GAS OFF AT THE CURB AT 17:40 ON SEPTEMBER 7, 2012. A STREET CREW WAS DISPATCHED, AND THE GAS SERVICE TO 272 REOCK AVE WAS CUT AT THE CURB AT 19:00. TWO PEOPLE, (NAMES UNKNOWN) SQUATTERS, WERE INJURED, ONE BY THE FIRE, ONE WAS INJURED JUMPING OUT A WINDOW TO ESCAPE THE FIRE. THE HOME IN QUESTION WAS VACATED BY THE OWNER, AND THE INJURED PARTIES WERE TRESPASSING ON THE PROPERTY AT THE TIME OF THE INCIDENT. PSE&G HAS BEEN UNABLE TO CONFIRM ANY INFORMATION ON THE STATUS OF THEIR INJURIES DUE TO PATIENT CONFIDENTIALITY LAWS.
2025-03-31 10:13 | NO | NO | NO | 20120087 | 15544 | 2012-11-02 12:06 | SUPPLEMENTAL FINAL | 31159 | KANSAS GAS SERVICE | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2012-09-25 13:50 |  |  | 2012 | 3200 BLOCK OF KANSAS AVE | TOPEKA | SHAWNEE | KS | 66611 | 39.0108 | -95.6819 | [9 empty] | 2012-10-05 15:30 | 1026557 |  | NATURAL GAS |  | 101 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-09-25 14:02 |  |  |  | 2012-09-25 14:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1992 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 12000 | 15260.4 | 38500 | 48960.45 | 2500 | 3179.25 | 0 | 0 |  |  | 500 | 451.374207188160676532769556025369978858 |  | 0 | 53500 | 28332.6475687103594080338266384778012685 | 67851.4742071881606765327695560253699789 | 0 | 0 | 24 |  |  |  |  | 45 | 45 | 58 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | BRUCE D. KUBIE | MANAGER OF STANDARDS | bkubie@kgas.com | (785) 431-4250 | (785) 431-4224 |  |  |  | ROB GREEN | DIRECTOR ENGINEERING | (785) 431-4241 | rgreen@kgas.com | AN AUTOMBILE TRAVELING NORTH ON S. KANSAS AVE., THAT WAS DRIVEN BY A DRUG OR ALCOHOL IMPAIRED INDIVIDUAL AND AT A HIGH RATE OF SPEED, LEFT THE ROAD AND COLLIDED WITH A KANSAS GAS SERVICE REGULATOR STATION. THE FORCE FROM THE COLLISION SEVERED THE INLET REGULATOR STATION PIPING ABOVE GROUND AND THE ENSUING RELEASE OF GAS CAUGHT FIRE. THE SOURCE OF IGNITION IS NOT KNOWN. THERE WAS A BARRICADE AROUND THE REGULATOR STATION. THE DRIVER OF THE CAR WAS EVACUATED FROM THE VEHICLE WITH THE HELP OF BY-STANDERS AND WAS UNHARMED. ONCE THE GAS CAUGHT FIRE THE OVERHEAD ELECTRIC LINES WERE ALSO BURNED. THE GAS WAS SHUT OFF USING AN UPSTREM VALVE AND EFFECTED ABOUT 24 CUSTOMERS. REPAIRS WERE COMPLETED ON 9/28/2012 WITH GAS BEING REINTRODUCED TO THE MAIN AT THAT TIME. GAS SERVICE TO EFFECTED CUSTOMERS WAS RESTORED AS THEIR SERVICE LINES WERE REPLACED. SUPPLEMENTAL DATA ADDED 11/26/2012; PART E - MAOP WAS CHANGED FROM 45 LBS. TO 58 LBS. BDK
2025-03-31 10:13 | NO | YES | YES | 20120088 | 15539 | 2012-11-02 18:19 | ORIGINAL FINAL | 1640 | BOSTON GAS CO | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2012-10-03 10:45 |  |  | 2012 | 27 LAKE WARREN DRIVE | LITTLETON | MIDDLESEX | MA | 01460-1506 | 42.534 | -71.5016 | [9 empty] | 2012-10-03 15:20 | 1026348 |  | NATURAL GAS |  | 37 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 7 | 2012-10-03 10:45 |  |  |  | 2012-10-03 11:03 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | FITTINGS | 2009 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | CUSTOMER TAMPERED WITH COMPANY PIPING, THE 3/4" STEEL END CAP WITH A 3/4" STEEL NIPPLE. | CLASS 4 LOCATION | 100000 | 127170 | 0 | 0 | 6317 | 8033.3289 | 0 | 0 |  |  | 119 | 107.427061310782241014799154334038054968 |  | 0 | 106436 | 56096.5402213530655391120507399577167019 | 135310.755961310782241014799154334038055 | 0 | 0 | 1 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS THE RESULT OF THE CUSTOMER TAMPERING WITH COMPANY OWNED PIPING. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | OTHER | THE HOMEOWNER TAMPERED WITH COMPANY PIPING BY REMOVING 3/4" STEEL END CAP WITH A 3/4" STEEL NIPPLE ON THE TEE WAS REMOVED WHICH CAUSED THE GAS LEAK IN THE BASEMENT AND RESULTED IN A FLASH FIRE. THE MOST LIKELY SOURCE OF IGNITION WAS THE WATER HEATER. THE HOMEOWNER DIED IN THE INCIDENT | [155 empty] | KATHLEEN MCNAMARA | MANAGER NE DISPATCH AND SCHEDULING | kathleen.mcnamara@nationalgrid.com | 508-421-7450 | 508-421-7586 |  |  |  | GARY BENNETT | DIRECTOR DISPATCH AND SCHEDULING | 617-839-7208 | gary.bennett@nationalgrid.com | THE HOMEOWNER TAMPERED WITH COMPANY PIPING BY REMOVING 3/4" STEEL END CAP WITH A 3/4" STEEL NIPPLE ON THE TEE WAS REMOVED WHICH CAUSED THE GAS LEAK IN THE BASEMENT AND RESULTED IN A FLASH FIRE. THE MOST LIKELY SOURCE OF IGNITION WAS THE WATER HEATER. THE HOMEOWNER DIED IN THE INCIDENT
2025-03-31 10:13 | NO | NO | NO | 20120089 | 15542 | 2012-11-14 12:58 | ORIGINAL FINAL | 12408 | MICHIGAN CONSOLIDATED GAS CO (MICHCON) | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2012-10-18 02:17 |  |  | 2012 | 866 SCENIC DRIVE | NORTH MUSKEGON | MUSKEGON | MI | 49445-8629 | 43.2676 | -86.3611 | [9 empty] | 2012-10-18 18:59 | 1027752 |  | NATURAL GAS |  | 35 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-10-18 02:17 |  |  |  | 2012-10-18 02:59 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1994 | [5 empty] | 2.375 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | RUPTURE |  |  |  |  | LONGITUDINAL |  | 3 | 1 |  | CLASS 3 LOCATION | 700 | 890.19 | 55080 | 70045.236 | 12000 | 15260.4 | 0 | 0 |  |  | 180 | 162.494714587737843551797040169133192389 |  | 0 | 67960 | 35850.0431247357293868921775898520084567 | 86358.3207145877378435517970401691331924 | 4 | 0 | 34 |  |  |  |  | 52 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | JOHN D LUEDERS | SUPERVISOR CODES AND STANDARDS | luedersj@dteenergy.com | 6166322646 | 6166322687 |  |  |  | ROBERT H FRECKELTON | MANAGER CODES AND STANDARDS | 3133897755 | freckeltonr@dteenergy.com | A TREE BRANCH BROKEN DURING A WINDY RAIN STORM FELL ONTO A POLE-MOUNTED ELECTRICITY DISTRIBUTION CONDUCTOR, WHICH FELL TO THE GROUND AND CONTINUED TO ARC AND SPARK FOR A LENGTHY PERIOD OF TIME. INVESTIGATION REVEALED THE COPPER LOCATING WIRE INSTALLED ADJACENT TO THE 2-INCH PLASTIC GAS MAIN BECAME ENERGIZED, GENERATING INTENSE LOCALIZED HEAT WHICH MELTED THE PLASTIC. NATURAL GAS AT APPROX 52 PSIG WAS RELEASED AND WAS IGNITED BY AN UNKNOWN SOURCE, ALTHOUGH IT HAS BEEN SPECULATED THAT THE ARCING ELECTRIC CONDUCTOR WAS THE SOURCE. A MICHCON CREW RESPONDED BY PINCHING THE 2-INCH PLASTIC PIPE UPSTREAM OF THE RUPTURE, STOPPING THE LEAK AND INTERRUPTING SERVICE TO 38 CUSTOMERS. THE LEAKING MAIN WAS REPAIRED USING A 60-INCH LENGTH OF PRE-TESTED POLYETHYLENE PLASTIC. AN AIR TEST AT 54 PSIG WAS APPLIED TO THE MAIN AND SERVICE LINES DOWNSTREAM OF THE PINCH, BUT THE TEST DID NOT HOLD AND THE DEAD-END SYSTEM TO THE SOUTH OF THE PINCH REMAINED OUT OF SERVICE. A LEAK SURVEY OF THE GAS DISTRIBUTION SYSTEM UPSTREAM OF THE PINCH FOUND LEAKS AT ANOTHER 20 LOCATIONS, SOME NEARLY 2 MILES FROM THE ORIGINAL MAIN LEAK AT 866 SCENIC DRIVE. ARC BURNS AND PERFORATIONS OF POLYETHYLENE PLASTIC SERVICE LINE TUBING WERE FOUND ALONG SCENIC DRIVE, ON WEST GILES ROAD AS FAR EAST AS 4175 W GILES, AND NORTH OF W GILES AT 1680 BENJAMIN ROAD IN LAKETON TOWNSHIP. ALL 20 LEAKS WERE ELIMINATED BY REPLACEMENT OF VARIOUS LENGTHS OF NEW SERVICE LINE TUBING. THE EVENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER AT 18:59 ON OCTOBER 18, 2012, WHEN MICHCON REALIZED THE COST OF REPAIRS ALREADY MADE AND OTHER LEAKS THAT MAY HAVE REMAINED TO BE FOUND AND REPAIRED WOULD LIKELY EXCEED THE THRESHOLD FOR REPORTING AS AN INCIDENT. ON FRIDAY, OCTOBER 19, 2012, MICHCON RE-ESTABLISHED GAS SERVICE TO THE MAINS AND SERVICE LINES SOUTH (DOWNSTREAM) OF THE PINCH ALONG SCENIC DRIVE AND FENNER ROAD. THE MAINS AND SERVICE LINES WERE SURVEYED FOR LEAKS; EIGHT MORE LEAKS WERE FOUND AND REPAIRED. THE EVENT WAS DECLARED FINISHED AT 22:45 ON OCTOBER 19, 2012.
2025-03-31 10:13 | NO | YES | NO | 20120090 | 15632 | 2012-11-16 11:20 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2012-05-06 03:26 |  |  | 2012 | 707 8 AVE S.E. | MINNEAPOLIS | HENNEPIN | MN | 55414 | 44.9868 | -93.2417 | [9 empty] | 2012-05-06 13:35 | 1010706 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2012-05-06 03:26 |  |  |  | 2012-05-06 03:57 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1974 | [5 empty] | 3 | AA | UNKNOWN | PLASTIC |  |  |  |  | OTHER |  |  |  | UNKNOWN |  | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 33144 | 42149.2248 | 55409 | 70463.6253 | 12068 | 15346.8756 | 0 | 0 |  |  | 20 | 18.05496828752642706131078224101479915433 |  | 0 | 100641 | 53013.7826027484143763213530655391120507 | 127977.7806682875264270613107822410147992 | 0 | 0 | 12 |  |  |  |  | 8 | 8 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIN HOLE LEAKS DID NOT CAUSE A PRESSURE CHANGE THAT WOULD HAVE ALERTED GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [218 empty] | CHRISTE H SINGLETON | GAS OPERATIONS | christe.singleton@centerpointenergy.com | 612-321-5203 |  |  |  |  | CHRISTE SINGLETON | GAS OPERATIONS | 612-321-5203 | christe.singleton@centerpointenergy.com | LIGHTNING STRUCK AN ELECTRICAL TRANSFORMER, LINES FELL AND STARTED MULTIPLE CAR FIRES, THE PAVEMENT WAS SOFTENED AND HEAT REACHED THE MAIN. THE HEAT TRANSFERRED TO THE TRACER WIRE AND BURNED HOLES IN THE PLASTIC MAIN WHERE IT WAS TOUCHING.
2025-03-31 10:13 | NO | YES | NO | 20120092 | 15546 | 2012-11-27 15:23 | ORIGINAL FINAL | 4350 | ELIZABETHTOWN GAS CO | 520 GREEN LANE | UNION | NJ | 07083 | 2012-10-30 00:40 |  |  | 2012 | 11 NOE ST | CARTERET | MIDDLESEX | NJ | 07008-2905 | 40.5802 | -74.2199 | [9 empty] | 2012-10-30 04:50 | 1028698 |  | NATURAL GAS |  | 26 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2012-10-30 00:47 |  |  |  | 2012-10-30 03:17 |  | NO | PRIVATE PROPERTY | TRANSITION AREA | OTHER | SEE PART H, NARRATIVE DESCRIPTION |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1966 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 1000000 | 1271700 | 2500 | 3179.25 | 7989 | 10159.6113 | 0 | 0 |  |  | 92 | 83.05285412262156448202959830866807610994 |  | 0 | 1010581 | 532301.3850526427061310782241014799154334 | 1285121.91415412262156448202959830866808 | 0 | 0 | 3 |  |  |  |  | 23 | 23 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | NOTIFICATION FROM 911 OPERATOR |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | HURRICANE SANDY COASTAL STORM SURGE PUSHED A 3 FOOT HIGH FLOOD THRUST AGAINST THE HOUSE UPPER FOUNDATION WALL FACING THE BAY. THIS ACTION BROKE APART THE EXPOSED PORTION OF THE WALL AND DROVE THE SHATTERED CINDER BLOCKS, ALONG WITH THE ATTACHED OUTSIDE METER SET DOWN INTO THE BASEMENT. THE PULLED AND TWISTED SERVICE PIPE SEPARATED RESULTING IN THE OPEN END BLOWING INTO THE BASEMENT. | YES | YES | [217 empty] | PHILIP SALVATORE | COMPLIANCE ENGINEER | psalvato@aglresources.com | 908 662 8306 | 908 351 5127 |  |  |  | RICHARD LONN | DIRECTOR OF COMPLIANCE | 404 584 3552 | rlonn@aglresources.com | HURRICANE SANDY COASTAL STORM SURGE PUSHED A 3 FOOT HIGH FLOOD THRUST AGAINST THE HOUSE UPPER FOUNDATION WALL FACING THE BAY. THIS ACTION BROKE APART THE EXPOSED PORTION OF THE WALL AND DROVE THE SHATTERED CINDER BLOCKS, ALONG WITH THE ATTACHED OUTSIDE METER SET, DOWN INTO THE BASEMENT. THE PULLED AND TWISTED SERVICE PIPE SEPARATED LEAVING AN OPEN END BLOWING INTO THE BASEMENT. THE GAS THEN IGNITED RESULTING IN THE GAS EXPLOSION AND FIRE. THE SOURCE OF THE IGNITION COULD NOT BE IDENTIFIED. THE HIGH HURRICANE WINDS AND FLOODS IN PLACE AT THAT TIME ACCELERATED THE BLAZE AND HAMPERED EMERGENCY RESPONSE. THUS, THE FIRE SPREAD AND DESTROYED TWO ADDITIONAL HOUSES AND CAUSED HEAT DAMAGE TO A FOURTH HOUSE (13, 15 AND 17 NOE STREET). THESE HOMES WERE NOT OCCUPIED AT THE TIME OF THE INCIDENT. THE OCCUPANTS HAD BEEN ORDERED TO EVACUATE IN ANTICIPATION OF COASTAL STORM FLOODING.
2025-03-31 10:13 | NO | NO | NO | 20120093 | 15547 | 2012-11-28 08:59 | ORIGINAL FINAL | 2652 | NSTAR GAS COMPANY | 157 CORDAVILLE ROAD | SOUTHBOROUGH | MA | 01772 | 2012-10-28 01:14 |  |  | 2012 | 15 GRANT CT | MARLBOROUGH |  | MA | 01752 | 42.3473 | -71.5496 | [9 empty] | 2012-10-28 03:30 | 1028549 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 1 | 2012-10-28 01:14 |  |  |  | 2012-10-28 01:36 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | ON CUSTOMER SIDE OF METER | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | OPEN FUEL LINE ON CUSTOMER PIPING OF PREVIOUSLY SHUTOFF AND LOCKED METER | CLASS 3 LOCATION | 82000 | 104279.4 | 1500 | 1907.55 | 10000 | 12717 | 0 | 0 |  |  | 8 | 7.22198731501057082452431289640591966173 |  | 0 | 93508 | 49253.1307610993657505285412262156448203 | 118911.1719873150105708245243128964059197 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [156 empty] | JOHN DUSTIN | PRINCIPAL ENGINEER | john.dustin@nstar.com | 781-441-8443 | 781-441-3486 |  |  |  | PAUL ZOHORSKY | VP GAS ENGINEERING SALES | 781-441-8440 | paul.zohorsky@nstar.com | A SERVICE TECH WAS CALLED AT 1:15 AM SUNDAY MORNING TO RESPOND TO THE MARLBORO FIRE DEPARTMENT AT AN APPARENT EXPLOSION AND HOUSE FIRE. THE TECH ARRIVED AND CALLED FOR ADDITIONAL RESOURCES. HE THEN BEGAN TO CHECK FOR MIGRATING GAS IN THE SURROUNDING BUILDINGS, ALONG THE SERVICE TO THE HOUSE, AND IN THE STREET. NO GAS READINGS WERE DETECTED. THE DISTRIBUTION AND SERVICE ON CALL PERSONNEL ARRIVED AND BEGAN CALLING IN ADDITIONAL COMPANY RESOURCES TO ASSIST IN THE RESPONSE EFFORT AND CONTROLLING THE INCIDENT. A DISTRIBUTION CREW WAS CALLED IN TO SHUT OFF AND CUT THE SERVICE. ADDITIONAL SERVICE TECHS WERE CALLED IN TO ASSIST IN CHECKING THE SURROUNDING BUILDINGS AND IN THE STREETS AT CATCH BASINS AND MANHOLES AROUND THE ENTIRE BLOCK. GAS SUPPLY PERSONNEL WERE CALLED IN AND DISPATCHED TO TAKE ODORANT SAMPLES IN THE HOUSES DIRECTLY ACROSS FROM 15 GRANT CT. THAT HAD ACTIVE GAS SERVICE. GAS SURVEY CREWS WERE CALLED IN TO SURVEY GRANT ST., AND THE TWO PARALLEL STREETS, MCENELLY ST. AND WASHINGTON CT. ALONG WITH THE PORTION OF WASHINGTON ST. IN BETWEEN THESE STREETS. THE METER AND METER BAR ASSEMBLY WERE TAKEN BY THE INVESTIGATORS AS EVIDENCE. THE SERVICE WAS PRESSURE TESTED TO THE RISER WHICH WAS WITNESSED BY A REPRESENTATIVE OF THE DPU. THE SERVICE WAS CUT OFF AT THE MAIN. AFTER THE INVESTIGATORS COMPLETED GATHERING EVIDENCE AT THE SCENE THEY GAVE PERMISSION TO BEGIN CLEANING UP THE SITE. THERE WAS A TENANT HOME AT THE TIME OF THE EXPLOSION WHO WAS CONSCIOUS AND WALKING AROUND WHEN THE FIRE DEPARTMENT ARRIVED. HE WAS TAKEN TO THE HOSPITAL AND REPORTS ARE THAT HE SUSTAINED 2ND AND 3RD DEGREE BURNS ON PORTIONS OF HIS BODY.
2025-03-31 10:13 | NO | YES | YES | 20120094 | 15909 | 2012-11-28 16:28 | SUPPLEMENTAL FINAL | 11713 | KEYSPAN ENERGY DELIVERY - LONG ISLAND | 175 EAST OLD COUNTRY ROAD | HICKSVILLE | NY | 11801 | 2012-10-29 19:49 |  |  | 2012 | 15 KENWOOD ROAD | GARDEN CITY | NASSAU | NY | 11530 | 40.7343 | -73.629 | [9 empty] | 2012-10-29 20:46 | 1028677 |  | NATURAL GAS |  | 12 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 1 | 2012-10-29 19:55 |  |  |  | 2012-10-29 19:55 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1936 | [5 empty] | 1.25 | BARE STEEL | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | TREE WAS UPROOTED AND SERVICE WAS PULLED OUT AT HOUSE FOUNDATION WALL CAUSING GAS TO ESCAPE. | CLASS 4 LOCATION | 750000 | 953775 | 784 | 997.0128 | 150 | 190.755 | 0 | 0 |  |  | 36 | 32.4989429175475687103594080338266384778 |  | 0 | 750970 | 395547.0012249471458773784355179704016913 | 954995.2667429175475687103594080338266385 | 0 | 0 | 1 |  |  |  |  | 0.22 | 0.2 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | OFFICE OF EMERGENCY MANAGEMENT |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY NATURAL FORCES IN CONJUNCTION WITH A HURRICANE. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE | [5 empty] | YES |  |  |  | YES | SUPER STORM SANDY | [213 empty] | RICHARD VERDERAME | LEAD SUPERVISOR DISPATCH AND SCHEDULING | richard.verderame@nationalgrid.com | 718 403-3105 |  |  |  |  | RICHARD VERDERAME | LEAD SUPERVISOR DISPATCH AND SCHEDULING | 718 403-3105 | richard.verderame@nationalgrid.com | A REPORT OF A DISTURBANCE AND FIRE WAS RECEIVED FOR 15 KENWOOD ROAD, GARDEN CITY, NY. (NOTE: NATIONAL GRID ORGINALLY REPORTED THAT THIS EVENT OCCURED AT 16 KENWOOD ROAD, GARDEN CITY, NY AS THAT WAS HOW IT WAS REPORTED TO NATIONAL GRID). DUE TO THE EFFECTS OF SUPERSTORM SANDY, A LARGE TREE WAS UPROOTED WHICH PULLED THE GAS SERVICE FROM FROM INTERIOR GAS PIPING OF THE STRUCTURE. GAS SERVICE WAS SHUT OFF AT THE CURB VALVE. THE INCIDENT RESULTED IN SIGNIFICANT DAMAGE TO THE STRUCTURE WITH ONE INJURY REPORTED.
2025-03-31 10:13 | NO | YES | NO | 20120095 | 15979 | 2012-11-29 16:15 | SUPPLEMENTAL FINAL | 11713 | KEYSPAN ENERGY DELIVERY - LONG ISLAND | 175 EAST OLD COUNTRY ROAD | HICKSVILLE | NY | 11801 | 2012-10-30 00:27 |  |  | 2012 | 96 FOREST AVENUE | MASSAPEQUA | NASSAU | NY | 11709 | 40.6774 | -73.4068 | [9 empty] | 2012-10-30 09:05 | 1028714 | [5 empty] | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2012-10-30 06:10 |  |  |  | 2012-10-30 06:10 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | UNKNOWN |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | SEE #5 RESPONSE. | UNKNOWN | [8 empty] | OTHER | SEE #5 RESPONSE. | [9 empty] | OTHER | [8 empty] | NO INDICATION OF NATIONAL GRID FACILITIES INVOLVED IN THE INCIDENT. | CLASS 4 LOCATION | 400000 | 508680 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 400000 | 210680 | 508680 | 0 | 0 | 1 |  |  |  |  | 53 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | NO | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NEAREST SCADA COMMUNICATION POINT WAS DOWN DUE TO HURRICANE. PRESSURE WAS TAKEN AT A NEIGHBORING STATION IN THE AREA THAT WAS FEEDING THE SAME OPERATING SYSTEM. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | R. VERDERAME | SUPERVISOR CMS | richard.verderame@nationalgrid.com | 516 783-2140 |  |  |  |  | R. DE MARINIS | VP MAINTENANCE AND CONSTRUCTION NY GAS | 516 545-4337 | robert.demarinis@nationalgrid.com | A REPORT OF A DISTURBANCE AND FIRE WAS RECEIVED FOR 96 FOREST AVENUE, MASSAPEQUA, NEW YORK. GAS SERVICE WAS SHUT OFF AT THE CURB VALVE, THE INCIDENT RESULTED IN DAMAGE TO THE STRUCTURE. NO INJURIES WERE REPORTED. THE INCIDENT OCCURRED DURING SUPERSTORM SANDY. A CLAIMS INVESTIGATOR ARRIVED AT THE SCENE A DAY OR TWO AFTERWARDS, AT WHICH TIME ALL THAT REMAINED OF THE PROPERTY, WHICH IS LOCATED ON A CANAL AND IS BELIEVED TO HAVE BEEN UNDERWATER AT THE TIME OF THE STORM, WAS AN EMPTY LOT.
2025-03-31 10:13 | NO | YES | YES | 20120097 | 15980 | 2012-11-29 16:55 | SUPPLEMENTAL FINAL | 11713 | KEYSPAN ENERGY DELIVERY - LONG ISLAND | 175 EAST OLD COUNTRY ROAD | HICKSVILLE | NY | 11801 | 2012-10-30 05:33 |  |  | 2012 | 122 SAINT MARKS AVENUE | FREEPORT | NASSAU | NY | 11520 | 40.6408 | -73.5912 | [9 empty] | 2012-10-30 08:45 | 1028712 | [5 empty] | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 4 | 4 | YES |  |  |  |  | YES | 4 | 2012-10-30 05:46 |  |  |  | 2012-10-30 05:46 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | UNKNOWN |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | SEE #5 RESPONSE. | UNKNOWN | [8 empty] | OTHER | SEE #5 RESPONSE. | [9 empty] | OTHER | [8 empty] | NO INDICATION OF NATIONAL GRID FACILITIES INVOLVED IN THE INCIDENT. | CLASS 4 LOCATION | 275000 | 349717.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 275000 | 144842.5 | 349717.5 | 0 | 0 | 1 |  |  |  |  | 55.5 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM WAS OPERATING WITHIN MAOP. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | R. VERDERAME | SUPERVISOR CMS | richard.verderame@nationalgrid.com | 516 783-2140 |  |  |  |  | R. DE MARINIS | VP MAINTENANCE AND CONSTRUCTION NY GAS | 516 545-4337 | robert.demarinis@nationalgrid.com | A REPORT WAS RECEIVED BY THE FREEPORT FIRE DEPARTMENT OF A DISTURBANCE AT 122 ST. MARKS AVENUE, FREEPORT, N.Y. GAS SERVICE WAS SHUT OFF AT THE CURB VALVE. THE INCIDENT RESULTED IN DAMAGE TO THE STRUCTURE AND REPORTED INJURIES TO FOUR PEOPLE. A LEAK INVESTIGATION WAS PERFORMED AT THE SUBJECT LOCATION. NO NATURAL GAS READINGS WERE OBTAINED.
2025-03-31 10:13 | NO | YES | YES | 20120098 | 34473 | 2012-12-02 20:05 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2012-11-23 17:25 |  |  | 2012 | 453 WORTHINGTON STREET | SPRINGFIELD | HAMPDEN | MA | 01105 | 42.1067 | -72.5894 | [9 empty] | 2012-11-23 18:23 | 1031399 |  | NATURAL GAS |  | 26 |  | NO | [5 empty] | 0 | YES | 2 | 0 | 12 | 1 | 2 | 17 | YES |  |  |  |  | YES | 20 | 2012-11-23 17:30 |  |  |  | 2012-11-23 17:30 |  | NO | PRIVATE PROPERTY | TRANSITION AREA | WALL SLEEVE |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1993 | [5 empty] | 1.25 | ASTM 02513 | PHILLIPS OR PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.121 |  | 3408 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 2 LOCATION | 1000000 | 1271700 | 100000 | 127170 | 10000 | 12717 | 200000 | 254340 | RESIDUAL STRUCTURE GLASS DAMAGE |  | 300 | 270.824524312896405919661733615221987315 |  | 0 | 1310300 | 690227.5285412262156448202959830866807611 | 1666197.82452431289640591966173361522199 | 1 | 0 | 0 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS HUMAN ERROR AND ISOLATED TO DAMAGE ON SERVICE | [12 empty] | YES | 6 | 0 | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  | YES |  |  |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | MEGGAN BIRMINGHAM | MANAGER COMPLIANCE GAS OPERATIONS | meggan.pena@eversource.com |  | 508.468.9956 |  |  |  | MEGGAN BIRMINGHAM | MANAGER COMPLIANCE GAS OPERATIONS | 508.468.9956 | meggan.pena@eversource.com | OPERATOR EMPLOYEE RESPONDED TO ODOR CALL IN BASEMENT OF 453 WORTHINGTON ST. AFTER OBTAINING ZERO LEVELS INSIDE OF BUILDING, EMPLOYEE BEGAN INVESTIGATION OUTSIDE. USING PROBE BAR EMPLOYEE STRUCK AND PUNCTURED SERVICE LINE CAUSING GAS TO ENTER BUILDING. RELEASED GAS ULTIMATELY IGNITED, CAUSING EXPLOSION.
2025-03-31 10:13 | NO | YES | NO | 20120099 | 15556 | 2012-12-06 11:17 | ORIGINAL | 5200 | FITCHBURG GAS & ELECTRIC LIGHT CO | 357 ELECTRIC AVE | LUNENBURG | MA | 01462 | 2012-11-09 13:45 |  |  | 2012 | 425 WATER ST | FITCHBURG | WORCESTER | MA | 01420 | 42.5742 | -71.7903 | [9 empty] | 2012-11-09 20:00 |  |  | NATURAL GAS |  | 20 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 15 | 2012-11-09 13:45 |  |  |  | 2012-11-09 13:55 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | CONTRACTOR PULLED VALVE OFF END OF PIPE | CLASS 3 LOCATION | 80000 | 101736 | 12000 | 15260.4 | 8000 | 10173.6 | 0 | 0 |  |  | 10000 | 9027.484143763213530655391120507399577167 |  | 0 | 110000 | 61020.95137420718816067653276955602537 | 136197.4841437632135306553911205073995772 | 0 | 0 | 0 |  |  |  |  | 90 | 90 | 99.9 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 20123811642 |  |  | UTILITY OWNER | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO UNLOCATABLE FACILITY | [170 empty] | DANIEL | MANAGER GAS DISTRIBUTION | golden@unitil.com | 978-833-1227 |  |  |  |  | DANIEL GOLDEN | MANAGER GAS DISTRIBUTION | 978-833-1227 | golden@unitil.com | CONTRACTOR (LUDLOW CONSTRUCTION WAS EXCAVATING IN THE VICINITY OF BIRCH ST AND WATER ST IN FITCHBURG TO INSTALL A DRAIN LINE. THE CONTRACTOR ASSUMED THAT A 6" STEEL LINE THAT THEY UNCOVERED WAS DEAD, AND THEY PULLED ON THE LINE. THE GAS LINE WAS AN UNKNOWN 6" STUB THAT WAS DEAD ENDED FOR FUTURE USE.
2025-03-31 10:13 | NO | YES | YES | 20120100 | 15781 | 2012-12-06 11:58 | SUPPLEMENTAL FINAL | 13840 | NORTHWEST NATURAL GAS CO | 250 SW TAYLOR ST | PORTLAND | OR | 97204 | 2012-11-06 13:11 |  |  | 2012 | 2, 477 ' W OF WALLACE CREEK RD, HWY 222, MP 4.52 | JASPER | LANE | OR | 97438 | 44.0057 | -122.9104 | [9 empty] | 2012-11-06 13:25 | 1030415 |  | NATURAL GAS |  | 367 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO |  |  |  |  | NO | 0 | 2012-11-06 13:11 |  |  |  | 2012-11-06 13:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1970 | [5 empty] | 4 | API5L GRADE B | UNKNOWN | STEEL |  | OTHER | ERW | 0.237 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | 0 | 0 | 1000 | 1271.7 | 300 | 381.51 | 0 | 0 |  |  | 2526 | 2280.342494714587737843551797040169133192 |  | 0 | 3826 | 2794.160317124735729386892177589852008457 | 3933.552494714587737843551797040169133192 | 0 | 0 | 0 |  |  |  |  | 375 | 375 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSED BY TRAFFIC ACCIDENT. CONTROL ROOM WAS NOTIFIED IMMEDIATELY BY LOCAL 911. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ANDREA SCOTT | COMPLIANCE SPECIALIST | a3s@nwnatural.com | 503-226-4211 |  |  |  |  | KERRY SHAMPINE | MANAGER CODE COMPLIANCE | 503-226-4211 | kfs@nwnatural.com | AT APPROXIMATELY 1:11 PM ON NOVEMBER 6, 2012, NW NATURAL WAS NOTIFIED THAT A MOTORCYCLIST SLID AND TORE OUT THE SQUARE FRAME AND COVER FOR A 4' PLUG VALVE LOCATED BETWEEN 36538 AND 36600 JASPER ROAD, JASPER, OR. BOTH TEST RISERS WERE BENT AND ONE WAS LEAKING BELOW THE THREADS RESULTING IN THE RELEASE OF NATURAL GAS. NWN FIRST RESPONDER ARRIVED ON SITE AT APPROXIMATELY 1:35 PM AND FOUND THAT THE POLICE DEPARTMENT HAD ESTABLISHED THE PERIMETER, CLOSED HWY 222 AND UNION PACIFIC RAILROAD. THE CYCLIST WAS INJURED AND TRANSPORTED TO SACRED HEART MEDICAL CENTER AT RIVER BEND. GAS WAS CONTROLLED AT 2:45 PM. UNION PACIFIC RAILROAD WAS OPENED BY 3:30 PM AND REPAIRS WERE COMPLETED AND HWY 222 WAS REOPENED FOR TRAFFIC AT APPROXIMATELY 6:30 PM. THE INCIDENT WAS REPORTED TO THE NRC (NATIONAL REPORTING CENTER) ON NOVEMBER 12, 2012, DUE TO PERSONAL INJURY NECESSITATING IN-PATIENT HOSPITALIZATION. NW NATURAL RECEIVED CONFIRMATION OF THE HOSPITALIZATION ON NOVEMBER 12, 2012 FROM THE LANE COUNTY SHERIFF'S DEPARTMENT.
2025-03-31 10:13 | NO | YES | YES | 20120101 | 15560 | 2012-12-10 16:10 | ORIGINAL FINAL | 13062 | NATIONAL FUEL GAS DISTRIBUTION CORP - NEW YORK | 6363 MAIN ST. | WILLIAMSVILLE | NY | 14221 | 2012-11-11 17:10 |  |  | 2012 | 34 GLEN ST. | ALFRED | ALLEGANY | NY | 14802-1015 | 42.2629 | -77.7888 | [9 empty] | 2012-11-12 08:20 | 1030352 |  | NATURAL GAS |  | 1.5 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 14 | 2012-11-11 17:39 |  |  |  | 2012-11-11 18:10 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 20 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1987 | [5 empty] | 1.125 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 12.5 |  |  | 2406 | MECHANICAL PUNCTURE | 1.2 | 0.3 | [7 empty] | CLASS 3 LOCATION | 500000 | 635850 | 500 | 635.85 | 2500 | 3179.25 | 0 | 0 |  |  | 12 | 10.8329809725158562367864693446088794926 |  | 0 | 503012 | 264940.1211416490486257928118393234672304 | 639675.9329809725158562367864693446088795 | 1 | 0 | 0 |  |  |  |  | 35 | 35 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | REGULATOR STATIONS FEEDING DISTRIBUTION SYSTEM ARE MANUALLY SET. SYSTEM IS NOT MONITORED BY SCADA. CONTROLLERS' ACTIONS WOULD NOT HAVE AFFECTED OUTCOME. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | FENCING | NO |  |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED | YES | 9999 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | ANDREW D. EMHOF | JUNIOR ENGINEER | emhofa@natfuel.com | 716-857-7630 | 716-857-7469 |  |  |  | BRIAN A. KEMPSKI | SUPERINTENDENT | 716-827-2131 | kempskib@natfuel.com | AT APPROXIMATELY 5:10PM ON SUNDAY, NOVEMBER 11TH, 2012, THE APARTMENT COMPLEX AT 34 GLEN STREET, ALFRED, NY 14802 SUFFERED AN EXPLOSION. THERE WERE NO FATALITIES. THERE WAS 1 INJURY AND 14 RESIDENTS WERE EVACUATED. FURTHER INVESTIGATION INDICATED A WOODEN LANDSCAPING STAKE TO BE USED FOR SNOW FENCING PUNCTURED THE NATURAL GAS PLASTIC SERVICE LATERAL 15 FEET FROM THE BUILDING WALL. GAS MAY HAVE MIGRATED INTO THE BUILDING THROUGH AN ADJACENT UNDERGROUND ELECTRICAL SERVICE FEED WHERE IT IGNITED. THE LOCAL ONE-CALL CENTER (DIG SAFELY NEW YORK) WAS NOT NOTIFIED OF THE EXCAVATION ACTIVITY. AT THE LOCATION OF THE PUNCTURE, THE SERVICE LINE WAS APPROXIMATELY 20" DEEP. SUBSEQUENT TO THE EVENT, THE SERVICE LINE INVOLVED IN THIS INCIDENT WAS CUT OFF AT THE MAIN AND ABANDONED.
2025-03-31 10:13 | NO | YES | NO | 20120102 | 15572 | 2012-12-12 17:20 | SUPPLEMENTAL FINAL | 22476 | ATMOS ENERGY CORPORATION - KY/MID-STATES (KENTUCKY) | 5430 LBJ FREEWAY | DALLAS | TX | 75240 | 2012-11-17 14:40 |  |  | 2012 | N. JACKSON STREET | CAMPBELLSVILLE | TAYLOR | KY | 42718 | 37.3335 | -85.3335 | [9 empty] | 2012-11-17 15:30 | 1030930 |  | NATURAL GAS |  | 0.15 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-11-17 14:45 |  |  |  | 2012-11-17 15:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | VEHICLE RAN OVER METER SET AND PIPING BROKE OFF ABOVE METER STOP BELOW REGULATOR | CLASS 3 LOCATION | 200000 | 254340 | 1000 | 1271.7 | 1000 | 1271.7 | 0 | 0 |  |  | 0 | 0 |  | 0 | 202000 | 106393.4 | 256883.4 | 1 | 0 | 0 |  |  |  |  | 45 | 45 | 58 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | GEORGE TUCKER | COMPLIANCE MANAGER | george.tucker@atmosenergy.com | 270-685-8137 | 270-685-8025 |  |  |  | GEORGE TUCKER | COMPLIANCE MANAGER | 270-685-8137 | george.tucker@atmosenergy.com | OPERATOR OF VEHICLE WAS TRAVELING NORTH ON SOUTH JACKSON STREET. OPERATOR LOST CONTROL OF VEHICLE DUE TO POSSIBLE MEDICAL EPISODE. THE VEHICLE TRAVELED INTO THE REAR OF A BP GAS STATION/CONVENIENCE STORE, STRIKING GAS METER AND CAUSING VEHICLE AND BUILDING TO CATCH FIRE.THE OPERATOR OF THE VEHICLE WAS TREATED AND RELEASED AT TAYLOR REGIONAL HOSPITAL FOR INJURIES; 4 OTHER PASSENGERS WERE NOT INJURED. EMERGENCE RESPONDERS WERE ABLE TO SHUT OFF METER SET AT THE METER STOP UPON ARRIVAL. ATMOS ENERGY WORKERS SHUT OFF THE SERVICE AT THE TAP ON THE MAIN 30 MINUTES AFTER ARRIVAL, AROUND 3:30 PM. POLICE REPORTS INDICATED THAT POSSIBLE ARRESTS WERE PENDING AND VEHICLE WAS IMPOUNDED.
2025-03-31 10:13 | NO | YES | NO | 20120103 | 34474 | 2012-12-18 15:09 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE SUITE 250 | WESTBOROUGH | MA | 01581 | 2012-06-24 06:05 |  |  | 2012 | 390 FALL RIVER AVE | SEEKONK | BRISTOL | MA | 02771 | 41.8171 | -71.3353 | [9 empty] | 2012-06-29 12:20 | 1016169 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-06-24 06:05 |  |  |  | 2012-06-24 06:21 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 4 LOCATION | 300000 | 381510 | 5000 | 6358.5 | 10000 | 12717 | 0 | 0 |  |  | 400 | 361.099365750528541226215644820295983087 |  | 0 | 315400 | 166244.5380549682875264270613107822410148 | 400946.5993657505285412262156448202959831 | 1 | 0 | 20 |  |  |  |  | 60 | 99 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MEGGAN BIRMINGHAM | MANAGER COMPLIANCE GAS OPERATIONS | meggan.pena@eversource.com |  | 508.468.9956 |  |  |  | MEGGAN BIRMINGHAM | MANAGER COMPLIANCE GAS OPERATIONS | 508.468.9956 | meggan.pena@eversource.com | TRACTOR TRAILER ROLL-OVER AT 06:00 ON SUNDAY JUNE 24, 2012, STRIKING ABOVE GROUND METER CAUSING RELEASE AND IGNITION OF NATURAL GAS AND FIRE DAMAGE TO THE RESTAURANT LOCATED AT 390 FALL RIVER AVE, SEEKONK. SERVICE VALVE WAS UNABLE TO BE ACCESSED DUE TO FIRE, VEHICLE AND EMERGENCY VEHICLES. ISOLATION OF GAS FACILITIES WAS ACHIEVED VIA ALTERATE VALVES IN DISTRIBUTION SYSTEM. THERE WAS A BREAKDOWN IN THE NOTIFICATION PROCESS WHICH RESULTED IN A DELAYED NRC CALL BEING MADE.
2025-03-31 10:13 | NO | YES | NO | 20120104 | 15654 | 2012-12-18 19:25 | SUPPLEMENTAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION AVENUE | SPOKANE | WA | 99220 | 2012-11-19 13:31 |  |  | 2012 | 5TH STREET BETWEEN BEACHEY AND DIKE BYPASS (NORTH OF RR TRACKS) | LEWISTON | NEZ PERCE COUNTY | ID | 83501-0000 | 46.4237 | -117.027 | [9 empty] | 2012-11-19 15:11 | 1031098 |  | NATURAL GAS |  | 411 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 30 | 2012-11-19 13:35 |  |  |  | 2012-11-19 13:51 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 60 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1956 | [5 empty] | 4.5 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 1 | 12.6 | [7 empty] | CLASS 3 LOCATION | 237000 | 301392.9 | 1050 | 1335.285 | 4320 | 5493.744 | 6380 | 8113.446 | ELECTRIC FACILITIES OWNED/OPERATED BY AVISTA UTILITIES |  | 1483 | 1338.775898520084566596194503171247357294 |  | 0 | 250233 | 132255.0710887949260042283298097251585624 | 317674.1508985200845665961945031712473573 | 1 | 0 | 0 |  |  |  |  | 289 | 289 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | APPARENT CAUSE WAS AN EXCAVATOR DIG-IN | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 2012420218 | NA |  | CONTRACT LOCATOR | NO | YES | 218 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | SETH R. SAMSELL | NATURAL GAS DISTRIBUTION ENGINEER | seth.samsell@avistacorp.com | 509-495-4883 | 509-777-9855 |  |  |  | JODY MOREHOUSE | GAS COMPLIANCE MANGER | 509-495-2760 | jody.morehouse@avistacorp.com | ON 11/19/2012 AT APPROXIMATELY 1331-HOURS (PACIFIC STANDARD TIME) ML ALBRIGHT & SONS CONSTRUCTION DUG INTO AND SEVERED A 4-INCH STEEL HIGH-PRESSURE NATURAL GAS PIPE WITHIN 5TH STREET, BETWEEN THE INTERSECTIONS OF BEACHEY AND DIKE BYPASS, IN LEWISTON, ID. THE MAINLINE, OWNED AND OPERATED BY AVISTA UTILITIES, WAS OPERATING AT 289 PSIG (300 PSIG - SYSTEM MAOP) AT THE TIME OF THE INCIDENT. THE EXCAVATOR DIG-IN RESULTED IN BLOWING GAS THAT IGNITED IN EXPLOSION, WHICH IS BELIEVED TO HAVE BEEN CAUSED BY AN EXCAVATOR BACKFIRE. THE RESULTING FIRE TOTALED THE EXCAVATOR EQUIPMENT INVOLVED IN THE INCIDENT AND CAUSED ADDITIONAL DAMAGE TO A RAILROAD CROSS-ARM, AN ADJACENT WAREHOUSE STRUCTURE AND LOCAL ELECTRIC DISTRIBUTION FACILITIES (ALSO OWNED AND OPERATED BY AVISTA UTILITIES). IT IS AVISTA'S UNDERSTANDING THAT THE CONTRACTOR WAS OPERATING USING LOCATES FROM A ONE-CALL TICKET THAT HAD EXPIRED 14-DAYS PRIOR TO THE INCIDENT AND MARKS WERE NO LONGER FULLY VISIBLE. AVISTA DISPATCH WAS NOTIFIED OF THE INCIDENT AT APPROXIMATELY 1335-HOURS. AVISTA PERSONNEL WERE EN-ROUTE BY 1338-HOURS AND ON LOCATION BY 1351-HOURS. GAS FLOW WAS ISOLATED AT 1355-HOURS BY CLOSING THREE SYSTEM EOP VALVES (AVISTA VALVE #S LEC 128, LEC 130 & LEC 542) WITHIN CLOSE VICINITY TO THE AREA. AT THIS TIME LOCAL FIRE DEPARTMENT RESPONDERS WERE ABLE TO CONTAIN THE FIRE. POLICE ALSO RESPONDED AND LOCAL MEDIA FOLLOWED THE INCIDENT CLOSELY. THERE WERE NO DEATHS AND ONLY MINOR INJURIES (NO HOSPITALIZATION REQUIRED) AS A RESULT OF THE EVENT. AVISTA GAS CONSTRUCTION CREWS WORKED TO REPAIR DAMAGED GAS FACILITIES OVER THE NEXT 9-DAYS FOLLOWING THE DIG-IN. THE SYSTEM WAS REPAIRED, RE-TESTED AND RESTORED TO FULL OPERATION BY 1530-HOURS ON 11/28/2012. ONLY ONE AVISTA NATURAL GAS CUSTOMER LOST SERVICE AS A RESULT OF THESE EVENTS. THE RESULTING OPERATOR AND NON-OPERATOR DAMAGE COSTS FROM THE EVENT ARE ESTIMATED TO EXCEED $50,000 WHICH IS THE REASON FOR THIS REPORTABLE. THE DETAILS RELATED TO THESE COSTS HAVE BEEN PROVIDED BASED UPON THE BEST AVAILABLE INFORMATION AT THIS TIME. WE PLAN TO REPORT SUPPLEMENTAL INFORMATION IF NECESSARY WHEN IT BECOMES AVAILABLE.
2025-03-31 10:13 | NO | YES | NO | 20130001 | 15949 | 2013-01-04 15:26 | SUPPLEMENTAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2012-12-08 14:50 |  |  | 2012 | 872 BLUE BELL DRIVE | MINOT | WARD | ND | 58701 | 48.1961 | -101.3044 | [9 empty] | 2012-12-12 18:08 | 1033061 |  | NATURAL GAS |  | 2.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2012-12-08 14:50 |  |  |  | 2012-12-08 14:59 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1999 | [8 empty] | STEEL | [10 empty] | OTHER | [8 empty] | SHEARED THE METER SET PIPING OFF ABOVE THE METER STOP VALVE DUE TO THE VEHICLE IMPACT. | CLASS 3 LOCATION | 120000 | 152604 | 200 | 254.34 | 150 | 190.755 | 0 | 0 |  |  | 40 | 36.10993657505285412262156448202959830867 |  | 0 | 120390 | 63421.7488054968287526427061310782241015 | 153085.2049365750528541226215644820295983 | 0 | 0 | 1 |  |  |  |  | 20 | 20 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DARYL ANDERSON | DIRECTOR OF DISTRIBUTION ENGINEERING | daryl.anderson@mdu.com | 701-222-7994 | 701-222-7994 |  |  |  | DARYL ANDERSON | DIRECTOR OF DISTRIBUTION ENGINEERING | 701-222-7994 | daryl.anderson@mdu.com | A 1-TON TRUCK WAS WESTBOUND ON A STRAIGHT STRETCH OF 37TH AVE, IT LEFT THE ROADWAY CROSSING TRAFFIC JUMPED THE CURB WHEN THROUGH A TREE ROW AND COLLIDED WITH A HOUSE ON PRIVATE PROPERTY. THE EMERGENCY RESPONSE OFFICIALS, THE FIRE DEPARTMENT, SHUT OFF THE GAS AT THE METER STOP VALVE SHORTLY AFTER ARRIVING AT THE SCENE. AN INVESTIGATION OF AN ADDITIONAL DAMAGE TO GAS FACILITIES OR EMERGENCY CONDITIONS WERE CHECKED AND RESULTED IN NO ADDITOIN DAMAGES OR DANGERS IDENTIFED. THE DRIVER OF THE VEHICLE WAS TAKEN TO THE HOSPITAL, CHECKED, AND RELEASE TO POLICE CUSTODY. METER SET WAS REBUILT SEVERAL DAYS AFTER THE ACCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20130002 | 15577 | 2013-01-10 14:09 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2012-12-12 19:10 |  |  | 2012 | 121 OBION RD | HOUSTON | HARRIS | TX | 77076 | 29.2124 | -95.3989 | [9 empty] | 2012-12-12 23:00 | 1033081 |  | NATURAL GAS |  | 155 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2012-12-12 19:10 |  |  |  | 2012-12-12 19:10 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1951 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 1.38 | [6 empty] | OTHER | [8 empty] | LOCK WING VALVE SEPARATED FROM RISER. | CLASS 3 LOCATION | 150000 | 190755 | 2500 | 3179.25 | 5000 | 6358.5 | 0 | 0 |  |  | 921 | 831.431289640591966173361522198731501057 |  | 0 | 158421 | 83724.3726215644820295983086680761099366 | 201124.1812896405919661733615221987315011 | 0 | 0 | 1 |  |  |  |  | 48 | 48 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM OR CONTROLLERS ACTIONS WERE NOT RESPONSIBLE FOR THIS RELEASE | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | LOCK WING VALVE INADVERTENTLY SEPARATED FROM RISER WHILE ATTEMPTING TO REMOVE BUSHING. |  |  |  | YES | LOCK WING VALVE INADVERTENTLY SEPARATED FROM RISER WHILE ATTEMPTING TO REMOVE BUSHING. | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | LESLIE J. DAVENPORT | ADVANCED OPERATIONS COORDINATOR | leslie.davenport@centerpointenergy.com | 7139677325 | 7139677307 |  |  |  | STEVE YARBROUGH | DIRECTOR OF OPERATIONS | 7132075100 | steve.yarbrough@centerpointenergy.com | WHILE ATTEMPTING TO REMOVE A 1 1/4" X 1" STEEL BUSHING FROM AN 1 1/4" X 1 1/4" LOCK WING VALVE, SAID VALVE BECAME SEPARATED FROM SERVICE RISER AND ESCAPING GAS WAS IGNITED BY UNKNOWN IGNITION SOURCE CAUSING DAMAGE TO (2) SINGLE FAMILY DWELLINGS.
2025-03-31 10:13 | NO | YES | NO | 20130003 | 15578 | 2013-01-10 16:10 | ORIGINAL FINAL | 11248 | LAS VEGAS NATURAL GAS SYSTEM | 905 12TH ST. P.O. BOX 179 | LAS VEGAS | NM | 87701 | 2011-02-09 04:15 |  |  | 2011 | 1925 CURCH STREET | LAS VEGAS | SAN MIGUEL | NM | 87701 | 35.5934 | -105.2128 | [9 empty] | 2011-02-09 14:27 | 966986 |  |  |  | 1000 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 10 | 2011-02-09 05:15 |  |  |  | 2011-02-09 06:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | PVC | UNKNOWN | OTHER | PVC | [9 empty] | OTHER | [8 empty] | CRACK ON PVC LINE | CLASS 3 LOCATION | 100000 | 129501.0183299389 | 10000 | 12950.10183299389 | 5000 | 6475.050916496945 | 0 | 0 | NO OTHER COST |  | 1500 | 1137.655417406749555950266429840142095915 |  | 0 | 116500 | 62733.1514327160338632326820603907637655 | 150063.8264968364845559502664298401420959 | 0 | 0 | 10 |  |  |  |  | 34 | 34 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | KENNY LUCERO | GAS SYTEMS MANAGER | klucero@ci.las-vegas.nm.us | 5054263209 | 5054541632 |  |  |  | KEN GARCIA | UTILITIES DIRECTOR | 5054263310 | kgarcia@ci.las-vegas.nm.us | GAS SERVICEMAN ON CALL WAS CALLED OUT BY POLICE DEPT. ON FEBRUARY 9, 2011 ABOUT 4:15 A.M. THAT THERE WAS A HOUSE FIRE AT 1925 CHURCH STREET. AFTER RESPONDING AND INSPECTING, HE ADVISED THAT THE STREET WAS ON FIRE AND THAT THE FIRE WAS COMING OUT OF THE WATER METER CAN. A GAS VALVE WAS LOCATED AT VALENCIA ST. AND WAS TURNED OFF. THE RESIDENCE WERE EVACUATED AND GAS METERS TURNED OFF. GAS CREW WERE CALLED OUT. PRC WAS CONTACTED AND WERE NOTIFIED. A CRACK ON THE 2" PVC MAIN WAS DISCOVERED. CREW CAPPED 2" PVC WAS DONE ALONG SIDE THE PIPELINE WHICH WAS RESTORED. CUSTOMERS APPLIANCES WERE THEN RE-LIT. NOTE: THE PVC GAS LINE HAS BEEN REPLACED WITH PE GAS LINE THRU ENTIRE BLOCK.
2025-03-31 10:13 | NO | NO | NO | 20130004 | 15787 | 2013-01-14 14:31 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2012-12-18 12:54 |  |  | 2012 | 2100 E BALL ROAD | ANAHEIM | ORANGE | CA | 92806 | 33.8178 | -117.8873 | [9 empty] | 2012-12-20 13:16 | 1933841 |  | NATURAL GAS |  | 162 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2012-12-18 12:54 |  |  |  | 2012-12-18 16:01 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1979 | [5 empty] | 2 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 35000 | 44509.5 | 35000 | 44509.5 | 1000 | 1271.7 | 0 | 0 |  |  | 1000 | 902.748414376321353065539112050739957717 |  | 0 | 72000 | 38230.795137420718816067653276955602537 | 91193.4484143763213530655391120507399577 | 3 | 0 | 0 |  |  |  |  | 44 | 44 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [8 empty] | YES |  |  |  | POOR CONSTRUCTION/INSTALLATION PROCEDURES |  |  | YES | 2013 | 100 | [84 empty] | W. JEFF KOSKIE | PIPELINE SAFETY AND COMPLIANCE MANAGER | wkoskie@semprautilities.com | 213 305-8660 | 213 244-8223 |  |  |  | W. JEFF KOSKIE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 213 305-8660 | wkoskie@semprautilities.com | ON DECEMBER 18, 2012, SOUTHERN CALIFORNIA GAS COMPANY RECEIVED NOTICE FROM A RESTAURANT THAT 2 FLASHES AT GRILLE HAD OCCURRED OVER A 2 WEEK PERIOD. UPON NOTIFICATION, A CHECK WAS PERFORMED ON CUSTOMER FACILITIES, AND NO LEAKAGE WAS FOUND. FURTHER INVESTIGATION UNCOVERED UNDERGROUND LEAKAGE THAT WAS DETERMINED TO BE COMING FROM A CRACK ON 2' PE PIPING AT A COUPLING FUSION. FLASHES CAUSED MINOR BURNS TO 2 RESTAURANT CUSTOMERS. DUE TO SATURATION OF SOIL, AREA COULD NOT BE CLEARED OF A FLAMMABLE MIXTURE, AND RESTAURANT WAS CLOSED. IT WAS ANTICIPATED THAT RESTAURANT WOULD BE ABLE TO REOPEN ON 12/20. HOWEVER, NATURAL GAS INDICATIONS WERE STILL IN THE VICINITY, AND RESTAURANT WAS NOT ABLE TO REOPEN. THIS SECOND DAY OF LOSS OF BUSINESS PUT THE ESTIMATED INCIDENT COST AT OVER $50K, TRIGGERING DOT NOTIFICATION. A GAS EXTRACTION SERVICE WAS SUBSEQUENTLY BROUGHT IN, AND UNDERGROUND GAS READINGS DISSIPATED. REPAIRS COMPLETED AND ALL CUSTOMERS PUT BACK INTO SERVICE.
2025-03-31 10:13 | NO | YES | NO | 20130005 | 15581 | 2013-01-14 16:31 | ORIGINAL | 18440 | SOUTH JERSEY GAS CO | 101 SOUTH LINCOLN PLACE | ATLANTIC CITY | NJ | 08401 | 2012-12-21 00:10 |  |  | 2012 | 35 W. BROOKLINE DRIVE | LAUREL SPRINGS | CAMDEN | NJ | 08021 | 39.824 | -75.053 | [9 empty] | 2012-12-21 11:44 | 1033908 |  | NATURAL GAS |  | 100 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 15 | 2012-12-21 00:10 |  |  |  | 2012-12-21 00:33 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1985 | [5 empty] | 0.75 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 233600 | 297069.12 | 5000 | 6358.5 | 81000 | 103007.7 | 0 | 0 |  |  | 1000 | 902.748414376321353065539112050739957717 |  | 0 | 320600 | 169168.415137420718816067653276955602537 | 407338.0684143763213530655391120507399577 | 0 | 0 | 8 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | TREE ROOT CRACKED PLASTIC SERVICE TEE PIECE | NO | [218 empty] | DAVID NEWMAN | MANAGER COMPLIANCE AND QUALITY ASSURANCE | dnewman@sjindustries.com | 609-561-9000 | 609-704-1802 |  |  |  | DAVID NEWMAN | MANAGER COMPLIANCE AND QUALITY ASSURANCE | 609-561-9000 | dnewman@sjindustries.com | A TREE ROOT CRACKED THE PLASTIC SERVICE TEE SERVING 36 W. BROOKLINE DRIVE. THE CRACKED PLASTIC SERVICE TEE AND ATTACHED PIPING WAS SENT TO AN INDEPENDENT TESTING LABORATORY FOR ANALYSIS.
2025-03-31 10:13 | NO | YES | NO | 20130006 | 15587 | 2013-01-18 09:22 | SUPPLEMENTAL FINAL | 4060 | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2010-02-13 06:30 |  |  | 2010 | 2816 CENTER RD | POLAND | MAHONING | OH | 44514-2154 | 41.0237 | -80.5988 | [9 empty] | 2010-02-13 15:25 | 931209 |  | NATURAL GAS |  | 62 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2010-02-13 06:45 |  |  |  | 2010-02-13 07:11 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | THE SOURCE OF IGNITION COULD NOT BE DETERMINED | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | TYPE OF RELEASE INVOLVED COULD NOT BE DETERMINED | CLASS 3 LOCATION | 100000 | 132110.949511739 | 0 | 0 | 10000 | 13211.0949511739 | 0 | 0 |  |  | 355 | 245.283171521035598705501618122977346278 |  | 0 | 110355 | 60414.9337067153218770226537216828478964 | 145567.3276344339355987055016181229773463 | 0 | 0 | 1 |  |  |  |  | 25 | 25 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | AARON MCCOY | TECHNICAL SPECIALIST | aaron.m.mccoy@dom.com | 330-458-9186 | 330-478-3760 |  |  |  | AARON MCCOY | TECHNICAL SPECIALIST | 330-458-9186 | aaron.m.mccoy@dom.com | ON SATURDAY, FEBRUARY 13, 2010 AT APPROXIMATELY 6:30 A.M. A SINGLE-FAMILY HOME AT 2816 CENTER RD, POLAND, OH WAS INVOLVED IN AN EXPLOSION/FIRE. THE GAS SERVICE LINE WAS SHUT-OFF AT APPROXIMATELY 9:30 A.M. A LEAK SURVEY OF THE MAIN LINE AND SURROUNDING SERVICE LINES FROM 2776 CENTER RD TO 2842 CENTER RD REVEALED NO INDICATION OF GAS LEAKS. THE SERVICE LINE TO 2816 CENTER RD WAS AIR TESTED AT OPERATING PRESSURE WITH NO PRESSURE LOSS. AN ODORANT TEST WAS CONDUCTED AT A NEIGHBORING HOUSE, 2806 CENTER RD. THE RESULTS OF THE ODORANT TEST REVEALED ODORANT LEVELS WELL WITHIN DOT COMPLIANCE LEVELS. DOMINION EAST OHIO CONDUCTED A THOROUGH INVESTIGATION OF THE PROPERTY WITH THE POLAND FIRE DEPARTMENT AND THE STATE FIRE MARSHALL. IT WAS DETERMINED THAT THE WATER HEATER WAS LEAKING GAS AND WAS RED-TAGGED BY DOMINION ON WEDNESDAY, FEBRUARY 10, 2010. THE CUSTOMER, DESPITE THE RED TAG, OPERATED THE WATER HEATER PRIOR TO REPAIRS. TESTING OF THE WATER HEATER PERFORMED AFTER THE INCIDENT, AND WITNESSED BY ALL INTERESTED PARTIES, CONFIRMED THE WATER HEATER WAS STILL LEAKING. THE HOUSE LINE PIPING DOWNSTREAM OF THE SERVICE REGULATOR AND THE METER SET WAS DAMAGED DURING THE EXPLOSION AND WERE NOT ABLE TO BE TESTED. PER THE POLAND FIRE DEPARTMENT, STATE FIRE MARSHALL, AND THE DOMINION INCIDENT RESPONSE TEAM'S INVESTIGATION, THE CAUSE/ORIGIN OF THE INCIDENT COULD NOT TO BE DETERMINED.
2025-03-31 10:13 | NO | YES | NO | 20130007 | 15695 | 2013-01-26 00:18 | SUPPLEMENTAL FINAL | 25000 | ZIA NATURAL GAS CO | 101 DIVISION ST | WORLAND | WY | 82401 | 2012-12-26 15:32 |  |  | 2012 | 4420 OVERLOOK LN | LAS CRUCES | DONA ANA | NM | 88007-0000 | 32.3488 | -106.8312 | [9 empty] | 2012-12-26 16:45 | 1034209 |  | NATURAL GAS |  | 2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2012-12-26 15:33 |  |  |  | 2012-12-26 15:33 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1983 | [8 empty] | OTHER | ANODELESS RISER/ SERVICE VALVE | [9 empty] | OTHER | [8 empty] | THERE WAS AN INTENTIONAL RELEASE OF GAS WHILE THE SERVICE LINE VALVE WAS BEING CHANGED LIVE. THE OPERATION TECHNICIAN CHECKED AND DID NOT IDENTIFY ANY POTENTIAL IGNITION SOURCES, BUT THE GAS IGNITED AND CAUSED THE INCIDENT. | CLASS 3 LOCATION | 446000 | 567178.2 | 2000 | 2543.4 | 500 | 635.85 | 0 | 0 |  |  | 8 | 7.22198731501057082452431289640591966173 |  | 0 | 448508 | 236231.6307610993657505285412262156448203 | 570364.6719873150105708245243128964059197 | 0 | 0 | 1 |  |  |  |  | 30 | 30 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | INCIDENT OCCURRED DUE TO RELEASE OF GAS RESULTING FROM MAINTENANCE REPLACEMENT OF SERVICE LINE VALVE ON AN ANODELESS RISER. | YES |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | LESLIE GRAHAM | GENERAL MANAGER | lgraham@zngc.com | 575-378-4277 | 575-378-7011 |  |  |  | LESLIE GRAHAM | GENERAL MANAGER | 575-378-4277 | lgraham@zngc.com | THERE WAS AN INTENTIONAL RELEASE OF GAS WHILE THE SERVICE LINE VALVE WAS BEING CHANGED LIVE. THE OPERATION TECHNICIAN CHECKED AND DID NOT IDENTIFY ANY POTENTIAL IGNITION SOURCES, BUT THE GAS IGNITED AND CAUSED THE INCIDENT. ZIA NATURAL GAS COMPANY HAS IMPLEMENTED A SPECIFIC WRITTEN PROCEDURE FOR CHANGING SERVICE LINE VALVES AND HAS RETRAINED EMPLOYEES ON PROPERLY IDENTIFYING POTENTIAL SOURCES OF IGNITION. INCIDENT HAS BEEN INVESTIGATED BY THE NEW MEXICO PUBLIC REGULATION COMMISSION, PIPELINE SAFETY BUREAU. THE FINDINGS AND COMPLIANCE ACTIONS HAVE BEEN DOCUMENTED IN NOTICE OF PROBABLE VIOLATION CASE #12-122612-11-PD.
2025-03-31 10:13 | NO | YES | NO | 20130008 | 15593 | 2013-01-31 09:38 | ORIGINAL FINAL | 11296 | LAWRENCEBURG GAS DEPT, CITY OF | 2009 LIBERTY AVE | LAWRENCEBURG | TN | 38464 | 2013-01-10 15:05 |  |  | 2013 | 2126 BALER DR. | LAWRENCEBURG | LAWRENCE | TN | 38464 | 35.2742 | -87.3272 | [9 empty] | 2013-01-10 16:20 | 1035362 |  | NATURAL GAS |  | 0.174 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-01-10 15:08 |  |  |  | 2013-01-10 15:15 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1993 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  |  | 1 |  | CLASS 1 LOCATION | 500000 | 624423.0580379065 | 4502 | 5622.305214573310126 | 604 | 754.303054109791052 | 0 | 0 |  |  | 7 | 6.125 |  | 0 | 505113 | 261263.969234122170699049180327868852459 | 630805.791306589601178 | 1 | 0 | 0 |  |  |  |  | 48 | 48 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | SAMUEL E. BLEVINS | D AND O OPERATOR | sblevins@lburgus.com | 931.629.9918 | 931.762.9276 |  |  |  | SAMUEL E. BLEVINS | D AND O OPERATOR | 931.629.9918 | sblevins@lburgus.com | ON THURSDAY, JAN 10, 2013 AT APPROXIMATELY 15:05, THE DRIVER OF A TRUCK OWNED BY J. W. GARLAND (AMERICAN DOOR AND MILLWORKS), WAS RETURNING A KEY TO THE SOLID WASTE SERVICES OFFICE. WHEN THE DRIVER TRIED TO STOP AT THE BUILDING THE BRAKES WERE UNRESPONSIVE. THE TRUCK HIT A NATURAL GAS METER AND THEN THE BUILDING. THE GAS DID NOT IGNITE IMMEDIATELY BUT DID IGNITE AFTER SEVERAL SECONDS. THE DISPATCHER FOR LAWRENCEBURG UTILITY SYSTEM CALLED AT 15:08. I ARRIVED ON THE SCENE AT 15:15. SCOTT GARLAND AND WILLIE RICHARDSON HAD ALSO JUST ARRIVED. THE FIRE HAD ENGULFED THE FRONT OF THE TRUCK AND THE OFFICES OF THE BUILDING. AT 15:22 THE GAS HAD BEEN SHUT OFF AND THE FIRE WAS EXTINGUISHED BY 13:25. I NOTIFIED LARRY BORUM WITH TRA AT 16:10 AND THE NATIONAL RESPONSE CENTER AT 16:20. AS A PRECAUTION A SQUEEZE OFF TOOL WAS INSTALLED ON THE SERVICE LINE BY SAM BLEIVNS AND KEN BOND. ON 1/11/13 WE DUG OUT THE SERVICE LINE AND INSTALLED A STAB PLUG UNTIL GAS LINE COULD BE REINSTATED. THE METER WAS REINSTALLED AND GAS WAS BACK ON ON 1/16/2013.
2025-03-31 10:13 | NO | YES | YES | 20130009 | 16380 | 2013-02-01 09:20 | SUPPLEMENTAL FINAL | 7685 | HUNTSVILLE GAS SYSTEM | P.O. BOX 2048 | HUNTSVILLE | AL | 35804 | 2013-01-15 22:18 |  |  | 2013 | 851 WASHINGTON STREET | HUNTSVILLE | MADISON | AL | 35801-5400 | 34.7423 | -86.5893 | [9 empty] | 2013-01-16 01:12 | 1035819 |  | NATURAL GAS |  | 8 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES |  |  |  |  | YES | 14 | 2013-01-15 22:18 |  |  |  | 2013-01-15 22:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OTHER | CUSTOMER FUEL LINE | UNKNOWN | [8 empty] | OTHER | BLACK IRON PIPE | [9 empty] | OTHER | [8 empty] | CORROSION | CLASS 3 LOCATION | 40000 | 49953.84464303252 | 6831 | 8530.867818913878603 | 352 | 439.593832858686176 | 0 | 0 |  |  | 37 | 32.375 |  | 0 | 47220 | 24434.6292182969732496885245901639344262 | 58956.681294805084779 | 0 | 0 | 191 |  |  |  |  | 47 | 48 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER CAN ONLY MONITOR THE OPERATOR'S SYSTEM VIA SCADA. CONTROLLERS WORK EIGHT HOUR SHIFTS SO FATIGUE WAS NOT DETEMINED TO BE A FACTOR. A MORE APPROPRIATE TERM FOR THESE EMPLOYEES IS "DISPATCHERS", AS THAT IS THEIR JOB TITLE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JIMMIE L. BUTLER | GAS AND WATER OPERATIONS MANAGER | jimmie.butler@hsvutil.org | 256-535-1240 | 256-532-8346 |  |  |  | JIMMIE L. BUTLER | GAS AND WATER OPERATIONS MANAGER | 256-535-1240 | jimmie.butler@hsvutil.org | AT APPROXIMATLEY 2218 (10:18PM CST) ON JANUARY 15, 2013, HUNTSVILLE UTILITIES (HU) DISPATCH CENTER RECEIVED A TELEPHONE CALL FROM HUNTVILLE FIRE DEPARTMENT (HPD) REQUESTING EMERGENCY RESPONSE FROM THE HU GAS DEPARTMENT AT 850 WASHINGTON WHERE A STRUCTURE FIRE WAS IN PROGRESS. HFD DISPATCHER ADVISED THAT THEY RECEIVED A REPORT OF A "BOOM" FOLLOWED BY FIRE. GAS WAS SMELLED IN THE AREA AND OUR CREWS WERE URGENTLY REQUESTED. OPERATOR EMERGENCY RESPONDERS FROM HU GAS DEPARTMENT ARRIVED ON SITE AT 2230 (10:30PM CST) ON JANUARY 15, 2013. HFD AND THE HUNTSVILLE POLICE DEPARTMENT (HPD) WERE ON SITE AND HAD EXTINGUISHED A FIRE AT THE PUBLIC HOUSING DWELLING UNIT AT 851 UNIT C WASHINGTON ST AND SECURED THE AREA. UPON SMELLING NATURAL GAS THE EMERGENCY RESPONDERS CALLED FOR ADDITIONAL HELP TO LOCATE THE SOURCE OF THE APPARENT GAS LEAK. CREWS WERE CALLED IN AND WERE SUCCESSFUL IN SHUTTING OFF THE SUPPLY OF GAS TO THE ENTIRE PUBLIC HOUSING PROJECT AT 0230 (2:30AM CST) ON JANUARY 16, 2013. IT WAS DISCOVERED THAT AN UNDERGROUND STEEL DISTRIBUTION VALVE, 2 INCH IN DIAMETER, HAD A CRACKED FLANGE. THIS LEAK WAS REPAIRED BY REMOVING THE VALVE ALONG WITH ANOTHER SIMILIAR VALVE AND REPLACING IT WITH COATED STEEL PIPE. THE LEAK WAS TWENTY FEET AWAY FROM THE DWELLING AT 851 WASHINGTON ST. GAS SERVICE WAS THEN RESTORED TO THE AREA AT 0745 (7:45AM CST) ON JANUARY 16, 2013. AFTER THE LEAK WAS REPAIRED HU GAS DEPARTMENT CREWS BEGAN TO CONDUCT A NUMBER OF TESTS IN THE VICINTY OF 851 WASHINGTON ST. THESE TESTS INCLUDED A LEAK SURVEY, CATHODIC PROTECTION PIPE TO SOIL READINGS, BAR HOLE TEST AND A PRESSURE TEST OF ALL THREE GAS SERVICE LINES TO 851 WASHINGTON ST., AS THIS BUILDING WAS A TRI-PLEX COMPRISED OF UNITS A, B, AND C. ALL THREE GAS SERVICES HELD THE TEST PRESSURE OF APPROXIMATLY +125 PSIG WITH NO LEAKS INDICATED. A TEST OF THE FUEL LINE (CUSTOMER PIPING) AT UNIT C FAILED, INDICATING A LEAK INSIDE THE UNIT. AN INVESTIGATION INTO THE CAUSE OF THE INCIDENT IS ON GOING. CONTRIBUTING FACTOR(S) MAY HAVE BEEN THE LEAK ON THE FUEL LINE, THE UNDERGROUND GAS LEAK OR SOME OTHER FACTOR. THE LOCAL WEATHER CONDITIONS AT THE TIME OF THE INCIDENT WERE A TEMPERATURE OF 37 DEGREES FARENHEIT, THE WIND SPEED WAS 5 MPH, NO WIND GUSTS, WIND DIRECTION WAS 300 (GENERALLY OUT OF THE NORTHWEST). IT WAS OVERCAST WITH A LIGHT RAINFALL. A SUPPLEMENTAL OR SUPPLEMENTAL PLUS FINAL REPORT WILL BE FILED AS SOON AS NEW, UPDATED AND/OR CORRECTED INFORMATION IS KNOWN. SEPTEMBER 8, 2016-THIS IS A SUPPLEMENTAL REPORT RELATED TO THIS INCIDENT. EXPERT WITNESSES DETERMINED THAT SOMETHING HEAVY LIKE A VEHICLE RAN OVER A VALVE BOX CAUSING DOWNWARD PRESSURE ON A 2 INCH FLANGED ROCKWELL FIGURE 143 VALVE CAUSING THE VALVE TO CRACK IN A FLANGE. GAS THEN MIGRATED ALONG A DITCH LINE INTO THE DWELLING CAUSING AN EXPLOSION AND FIRE.
2025-03-31 10:13 | NO | YES | NO | 20130010 | 15612 | 2013-02-01 09:57 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS CO | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2013-01-03 15:20 |  |  | 2013 | 9208 SOUTH VILLA AVENUE | OKLAHOMA CITY | CLEVELAND | OK | 73159 | 35.3741 | -97.5569 | [9 empty] | 2013-01-03 19:00 | 1034760 |  | NATURAL GAS |  | 218 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 14 | 2013-01-03 15:22 |  |  |  | 2013-01-03 16:00 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1972 | [5 empty] | 2 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2513 | MECHANICAL PUNCTURE | 0.3 | 5.5 | [7 empty] | CLASS 3 LOCATION | 260000 | 324699.99017971138 | 78 | 97.409997053913414 | 6859 | 8565.835510164001367 | 0 | 0 |  |  | 1105 | 966.875 |  | 0 | 268042 | 138963.470191600297846049180327868852459 | 334330.110686929294781 | 0 | 0 | 24 |  |  |  |  | 46 | 46 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS KNOWN AT THE ONSET THAT THIS DAMAGE WAS THE RESULT OF A THIRD PARTY AND DID NOT WARRANT AN INVESTIGATION OF CONTROL ROOM OR CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | BORING | CABLE TV | YES | 13010207380135 |  |  | CONTRACT LOCATOR | YES | YES | 5 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | JAY SULLIVAN | AREA OPERATIONS MANAGER | jay.sullivan@oneok.com | 4053662455 | 4053662440 |  |  |  | BRYAN BREWSTER | DIRECTOR - DIVISION OPERATIONS | 4055516653 | bbrewster@ong.com | THIRD PARTY ARZO INC. DAMAGED ONG'S 2" MAIN DURING A BORING OPERATION TO INSTALL FIBER OPTIC CABLE IN A RESIDENTIAL AREA. THE THIRD PARTY DID REQUEST A LOCATE, WHICH WAS PERFORMED TIMELY AND ACCURATELY. DAMAGE OCCURED AS A RESULT OF FAILURE TO MAINTAIN CLEARANCE BETWEEN THE BORING HEAD AND ONG'S PIPELINE. PART A, 16. THE EVACUATION VALUE IS AN ESTIMATE PROVIDED FROM THE FIRE DEPARTMENT REPORT. PART D, 2A. THE ESTIMATED COST OF PUBLIC AND NON-OPERATOR PRIVATE PROPERTY DAMAGE WAS DEVELOPED AFTER A REVIEW OF THE FIRE DEPARTMENT REPORT AND COUNTY ASSESSOR RECORDS. PART C, 3D. WE ARE UNABLE TO DETERMINE THE DATE OF MANUFACTURE, HOWEVER IT IS LIKELY BETWEEN THE YEARS OF 1969 AND 1972. PART C, 5. THE PUNCUTURE DIMENSIONS HAVE BEEN CORRECTED FROM THE ORIGINAL REPORT AS 2.0" X 2.0".
2025-03-31 10:13 | NO | NO | NO | 20130011 | 15636 | 2013-02-04 16:29 | SUPPLEMENTAL FINAL | 6243 | THE GAS COMPANY | 515 KAMAKEE STREET | HONOLULU | HI | 96814 | 2013-01-06 22:17 |  |  | 2013 | 87-2135 HELELUA PLACE, UNITS 3 & 4 | WAIANAE |  | HI | 96792 | 21.3864 | -158.1486 | [9 empty] | 2013-01-17 11:00 | 1035025 |  | PROPANE GAS |  | 5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-01-06 22:17 |  |  |  | 2013-01-06 23:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PETROLEUM GAS DISTRIBUTION |  | SERVICE RISER |  | UNKNOWN | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | NIPPLE ON THE UPSTREAM SIDE OF THE SERVICE VALVE WAS CRACKED. | CLASS 4 LOCATION | 35000 | 43709.614062653455 | 1500 | 1873.2691741137195 | 200 | 249.7692232151626 | 0 | 0 |  |  | 700 | 612.5 |  | 0 | 37400 | 19549.1084264516756049180327868852459016 | 46445.1524599823371 | 0 | 0 | 2 |  |  |  |  | 5 | 5 | 5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | NIPPLE CRACKED DUE TO STRESS CAUSED BY KIDS CLIMBING ON THE METER SET TO JUMP TO A FENCE. | [154 empty] | EDWIN SAWA | INTEGRITY MANAGEMENT PROGRAM ENGINEER | esawa@hawaiigas.com | 8085945661 | 8085945630 |  |  |  | CHARLES CALVET | DIRECTOR OAHU OPERATIONS | 8085945570 | ccalvet@hawaiigas.com | HAWAI`IGAS' DISPATCHER RECEIVED A CALL FROM THE HONOLULU FIRE DEPARTMENT (HFD) INFORMING US OF A FIRE AT 87-2135 HELELUA PLACE, UNITS 3 & 4. WE SENT OUT OUR SERVICE TECHNICIAN TO RESPOND. THE SERVICE TECHNICIAN FOUND THE METER SET LEANING TO THE LEFT SIDE. THE 3/4" NIPPLE ON THE UPSTREAM SIDE OF THE SERVICE COCK WAS CRACKED. THE FIRE DEPARTMENT HAD EXTINGUISHED THE FIRE PRIOR TO THE SERVICE TECHNICIAN ARRIVING. THE SERVICE TECHNICIAN REMOVED THE METER AND INSTALLED A RUBBER STOPPER ON THE RISER TO STOP THE GAS LEAK. THE METER SET WAS INSTALLED ON THE EXTERIOR OF THE WATER HEATER ENCLOSURE. THE FIRE DESTROYED THE WATER HEATER ENCLOSURE AND BURNED THE EXTERIOR SIDING ON THE 2ND FLOOR. AS A RESULT OF HFD EXTINGUISHING THE FIRE, 2 UNITS SUSTAINED WATER DAMAGE. BYSTANDERS REPORTED SEEING KIDS STANDING ON THE METER SET AND JUMPING TO THE FENCE. THIS WOULD BE A PLAUSIBLE EXPLANATION WHY THE METER SET WAS LEANING TO THE LEFT SIDE AND COULD BE THE CAUSE OF THE CRACKED NIPPLE. THE 3/4" GALVANIZED RISER WAS IN GOOD CONDITION WITH NO NOTICABLE CORROSION. ACCORDING TO THE HONOLULU FIRE DEPARTMENT'S INCIDENT REPORT (2013-0001443-000), THE ESTIMATED PROPERTY DAMAGE IS $35,000. THE REPORT ALSO NOTES THE PROBABLE CAUSE WAS SOMEONE STEPPED ONTO THE LEFT SIDE OF THE METER ASSEMBLY TRYING TO GET OVER A 6 FOOT WOODEN FENCE. THE WEIGHT OF THE PERSON CAUSED THE RIGHT SIDE OF THE PIPING TO CRACK OPEN, WHICH CREATED A LARGE GAS LEAK. THE PROPANE FILLED THE SURROUNDING AREA AND EVENTUALLY REACHED THE PILOT LIGHT OF THE GAS WATER HEATERIN THE CLOSET AND IGNITED.
2025-03-31 10:13 | NO | YES | YES | 20130012 | 15600 | 2013-02-08 17:49 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY | DALLAS | TX | 75240 | 2013-01-11 12:15 |  |  | 2013 | 520 E. MAIN | LEWISVILLE | DENTON | TX | 75057 | 33.0463 | -96.9891 | [9 empty] | 2013-01-11 13:52 | 103545 |  | NATURAL GAS |  | 515 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 12 | 2013-01-11 12:15 |  |  |  | 2013-01-11 12:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 70 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1998 | [5 empty] | 4 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 6 | 2 | [7 empty] | CLASS 3 LOCATION | 150000 | 187326.91741137195 | 27510 | 34355.75665324561563 | 0 | 0 | 0 | 0 |  |  | 2433 | 2128.875 |  | 0 | 179943 | 93783.649051255484492950819672131147541 | 223811.54906461756563 | 6 | 0 | 6 |  |  |  |  | 28 | 28 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DID NOT AFFECT MEASUREMENT | [12 empty] | YES | 7 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | AUGER | POLE | YES | 1235209328 | TEXAS EXCAVATION SAFETY SYSTEM, INC. |  | CONTRACT LOCATOR | YES | YES | 29 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | STEVEN ROPER | OPERATIONS SUPERVISOR | steven.roper@atmosenergy.com | 972-360-4411 | 972-360-4420 |  |  |  | MARC CHAPMAN | COMPLIANCE DIRECTOR | 214-206-2875 | marcus.chapman@atmosenergy.com | EXCAVATOR DRILLING TO INSTALL A UTILITY POLE DRILLED INTO AN ACCURATELY MARKED 4" POLY MAIN WITH AN AUGER. HOUSE EXPLODED BEFORE HAZARDOUS CONDITION WAS ELIMINATED.
2025-03-31 10:13 | NO | NO | NO | 20130013 | 15835 | 2013-02-08 19:04 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2013-01-11 14:24 |  |  | 2013 | S TACOMA WAY AND SPRAGUE ST | TACOMA | PIERCE | WA | 98409 | 47.2321 | -122.4631 | [9 empty] | 2013-02-08 12:25 | 1037945 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2013-01-11 14:24 |  |  |  | 2013-01-11 14:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2007 | [5 empty] | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 46100 | 57571.8059510949793 | 29867 | 37299.286948836306871 | 0 | 0 |  |  | 100 | 87.5 |  | 0 | 76067 | 39373.7039899350162511311475409836065574 | 94958.592899931286171 | 4 | 0 | 0 |  |  |  |  | 41 | 41 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS CAUSED BY FALLING DEMOLITION DEBRIS | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | FALLING CONSTRUCTION DEBRIS FROM ELEVATED ROADWAY DEMOLITION | [154 empty] | ANTOINETTE IMAD | CONSULTING ENGINEER | antoinette.imad@pse.com | 425 213 6219 | 425 462 3770 |  |  |  | CHERYL MCGRATH | MANAGER COMPLIANCE AND REGULATORY AUDITS - GAS | 425 462 3207 | cheryl.mcgrath@pse.com | ON JANUARY 1ST, 2013, A LARGE CONCRETE SECTION OF SR-16 UNDER DEMOLITION BY WSDOT AT THE TIME, FELL ONTO THE PAVEMENT AT THE INTERSECTION OF S. TACOMA WAY AND SPRAGUE STREET. AS A RESULT, A LEAK OCCURED ON AN UNDERGROUND GAS LINE AT THIS LOCATION. THE EVENT WAS REPORTED TO THE WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION FOR A GAS RELEASE EXCEEDING 2 HOURS. ON FEBRUARY 8TH AND AT ABOUT 12:00PM, FOLLOWING A REVIEW OF THE COST OF THIS INCIDENT, PSE DISCOVERED THAT THE COST OF THIS EVENT EXCEEDED $50,000 AND TELEPHONICALY REPORTED IT TO NRC.
2025-03-31 10:13 | NO | NO | NO | 20130014 | 15602 | 2013-02-11 18:50 | ORIGINAL FINAL | 38906 | LIBERTY ENERGY (MID-STATES) CORP D/B/A LIBERTY UTILITIES - CENTRAL | 2751 NORTH HIGH STREET | JACKSON | MO | 63755 | 2013-01-15 06:20 |  |  | 2013 | MT. MISSION RD. | METROPOLIS | MASSAC | IL | 62960 | 37.1911 | -88.7597 | [9 empty] | 2013-01-15 10:30 | 1035738 |  | NATURAL GAS |  | 1.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-01-15 06:45 |  |  |  | 2013-01-15 07:10 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1980 | [8 empty] | CAST/WROUGHT IRON | [10 empty] | OTHER | [8 empty] | FISHER 630 REGULATOR FAILED AT THE SAME TIME 1805P-167AR PILOT FAILED TO RELIEVE. | CLASS 3 LOCATION | 0 | 0 | 85000 | 106151.919866444105 | 1000 | 1248.846116075813 | 0 | 0 |  |  | 3 | 2.625 |  | 0 | 86003 | 44484.6044546681065901639344262295081967 | 107403.390982519918 | 0 | 1 | 27 |  |  |  |  | 270 | 70 | 80 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  | YES | [73 empty] | RONALD SNIDER | COMPLIANCE MANAGER | ronald.snider@libertyutilities.com | 573-225-7834 | 573-471-1363 |  |  |  | MICHAEL D. BEATTY | SR. MANAGER - ENGINEERING AND COMPLIANCE | 573-979-0220 | mike.beatty@libertyutilities.com | A FISHER 630 REGULATOR FAILED AND THE FISHER 1805P-167AR RELIEF VALVE FAILED TO RELIEVE. THIS RESULTED IN 270 PSIG BEING PLACED ON THE EXISTING PLASTIC PE DISTRIBUTION SYSTEM (SYSTEM). THE SYSTEM WAS SHUT DOWN. A 15PSI AIR TEST WAS PLACED ON THE SYSTEM THEN THE SYSTEM WAS RE-PRESSURIZED WITH NATURAL GAS TO 15 PSIG, LEAK SURVEYED AND THEN TEMPORARILY PLACED BACK INTO SERVICE UNTIL THE ENTIRE SYSTEM WAS REPLACED. DURING THE REPLACEMENT THE EXISTING SYSTEM WAS LEAK SURVEYED EACH DAY UNTIL ALL CUSTOMERS WERE BACK IN SERVICE. THE HOUSE PIPING WAS AIR TESTED TO ENSURE ALL THEIR PIPING WAS SAFE ALONG WITH VISUAL INSPECTING ALL ACCESSIBLE PIPING. TOTAL PIPE REPLACEMENT - 8,102 FT OF 2" POLY AND 28 POLY SERVICES (5,193').
2025-03-31 10:13 | NO | YES | YES | 20130018 | 30721 | 2013-02-18 11:47 | SUPPLEMENTAL FINAL | 20110 | DUKE ENERGY KENTUCKY | 139 EAST FOURTH STREET PO BOX 960 - ROOM 460-ANNEX | CINCINNATI | OH | 45202 | 2013-01-25 04:39 |  |  | 2013 | 1615 WATER WORKS ROAD | NEWPORT | CAMPBELL | KY | 41071 | 39.0919 | -84.4623 | [9 empty] | 2013-01-25 06:33 | 1036545 |  | NATURAL GAS |  | 35 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 0 | 2013-01-25 05:09 |  |  |  | 2013-01-25 05:09 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2005 | [5 empty] | 1.5 | UNKNOWN | UNKNOWN | OTHER | STEEL RISER/ALUMINUM METER |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | GAS METER WAS DAMAGED DURING THE FIRE/EXPLOSION WHICH MELTED THE DIAL FACE OF THE METER CAUSING AN UNINTENTIIONAL RELEASE OF GAS. STEEL RISER DID NOT MELT. | CLASS 3 LOCATION | 89200 | 111397.0735539625196 | 45 | 56.198075223411585 | 1500 | 1873.2691741137195 | 0 | 0 |  |  | 142 | 124.25 |  | 0 | 90887 | 47051.3929093490844994262295081967213115 | 113450.790803299650685 | 0 | 0 | 1 |  |  |  |  | 16.8 | 19 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DUKE-ENERGY DETEMINED THAT THE ACTIONS OF THE CONTROLLER(S) AND THE CONTROL ROOM SYSTEMS DID NOT INFLUENCE THE INCIDENT. | [12 empty] | YES | 1 | 0 | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | DUKE ENERGY KENTUCKY HAS DETERMINED THE CAUSE OF THIS INCIDENT IS UNKNOWN. DUKE ENERGY KENTUCKY AND SEA CONDUCTED PRESSURE TESTS ON THE SERVICE LINE AND THE HOUSELINE. DUKE ENERGY KENTUCKY HAS DETERMINED THAT THERE ARE SEVERAL POSSIBLE CAUSES INCLUDING BUT NOT LIMITED TO A LEAKING COUPLING ON THE RISER BEFORE THE METER AND SEVERAL LEAKING UNIONS IN THE HOUSELINE. THE CAUSE OF THIS INCIDENT MAY REMAIN UNKNOWN AND COULD HAVE BEEN AN ACT OF GOD. | NO | [218 empty] | JEROME HUMPHRIES | COMPLIANCE SPECIALIST | jerome.humphries@duke-energy.com | 513-373-9769 |  |  |  |  | DENNIS WESTENBERG | MANAGER OF REGULATORY COMPLIANCE | 513-287-5330 | dennis.westenberg@duke-energy.com | DUKE ENERGY KENTUCKY HAS DETERMINED THE CAUSE OF THIS INCIDENT IS UNKNOWN. ALL OF THE CUSTOMER OWNED PIPING AND APPLIANCES WERE REMOVED AND ARE IN THE POSSESSION OF SEA LIMITED ('SEA') IN COLUMBUS OHIO. SEA IS AN AGENT OF METROPOLITAN LIFE INSURANCE COMPANY, THE HOMEOWNERS INSURANCE CARRIER. DUKE ENERGY KENTUCKY AND SEA CONDUCTED PRESSURE TESTS ON THE SERVICE LINE AND THE HOUSELINE. DUKE ENERGY KENTUCKY HAS DETERMINED THAT THERE ARE SEVERAL POSSIBLE CAUSES INCLUDING BUT NOT LIMITED TO A LEAKING COUPLING ON THE RISER BEFORE THE METER AND SEVERAL LEAKING UNIONS IN THE HOUSELINE. THE CAUSE OF THIS INCIDENT MAY REMAIN UNKNOWN. NO FURTHER TESTING IS SCHEDULED BY SEA. THE CAUSE COULD HAVE BEEN AN ACT OF GOD.
2025-03-31 10:13 | NO | NO | NO | 20130019 | 15608 | 2013-02-19 11:09 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2013-01-22 19:11 |  |  | 2013 | 3210 HWY 31W | WHITE HOUSE | SUMNER | TN | 37188-8972 | 36.4691 | -86.652 | [9 empty] | 2013-01-22 20:50 | 1036328 |  | NATURAL GAS |  | 14 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-01-22 19:46 |  |  |  | 2013-01-22 19:50 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1984 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | MALLEABLE FITTING BROKEN UPON IMPACT. | CLASS 3 LOCATION | 50000 | 62442.30580379065 | 1516 | 1893.250711970932508 | 0 | 0 | 0 | 0 | FIRE DEPARTMENT'S DAMAGE ESTIMATE WAS $35,000. BELIEVED TO BE HIGHER. |  | 347 | 303.625 |  | 0 | 51863 | 26926.7289002645087542950819672131147541 | 64639.181515761582508 | 1 | 0 | 0 |  |  |  |  | 45 | 60 | 75 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM WAS OPERATING NORMALLY AT TIME OF INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | FARRIS BERRY | MANAGER - OPERATIONS PERFORMANCE | farris.berry@piedmontng.com | 704-731-4618 |  |  |  |  | JAMES THWEATT | OPERATIONS MANAGER - OPERATIONS AND MAINTENANCE | 615-872-2370 | jim.thweatt@piedmontng.com | A VEHICLE WHICH HAD BEEN OBSERVED DRIVING ERRATICALLY LEFT THE ROAD AND STRUCK THE METER SET OF A STRUCTURE, CAUSING THE RELEASE AND IGNITION OF NATURAL GAS. THE VEHICLE AND PORTIONS OF THE STRUCTURE WERE BURNED. THE DRIVER WAS PRONOUNCED DEAD AT THE SCENCE. THE POLICE REPORT (ATTACHED) INDICATES THE VEHICLE STRUCK THE BUILDING AT 95 MPH AND 67% THROTTLE. THE MEDICAL EXAMINER REPORTED THAT THE DRIVER DIED FROM BLUNT FORCE TRAUMA TO THE HEAD. OPERATOR IS NOT REPORTING THE DEATH IN SECTION A SINCE MEDICAL EXAMINER'S REPORT INDICATES DRIVER DIED FROM CAUSES UNRELATED TO THE RELEASE AND IGNITION OF NATURAL GAS.
2025-03-31 10:13 | NO | NO | NO | 20130020 | 15729 | 2013-02-22 10:05 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2013-01-23 01:02 |  |  | 2013 | 60TH STREET AND OAK AVE | ALTOONA | BLAIR | PA | 16602 | 40.4767 | -78.4359 | [9 empty] | 2013-01-23 11:21 | 1036357 | [5 empty] | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-01-23 01:02 |  |  |  | 2013-01-23 01:50 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1970 | [8 empty] | OTHER | STEEL BODY RELIEF DEVICE | [9 empty] | OTHER | [8 empty] | SYSTEM OVER PRESSURE | CLASS 3 LOCATION | 0 | 0 | 14315 | 17877.232151625263095 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 14315 | 7404.213394873810655 | 17877.232151625263095 | 0 | 0 | 0 |  |  |  |  | 205 | 145 | 150 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  | YES | [73 empty] | MICHAEL L. SMITH | COMPLIANCE PROCESS MANAGER | michael.l.smith@peoples-gas.com | 1-412-244-2605 |  |  |  |  | KENNETH M. JOHNSTON | SR. VICE PRESIDENT CHIEF OPERATING OFFICER | 1-412-208-7930 | kenneth.m.johnston@peoples-gas.com | ON 1/23/2013 AT 1:03 AM PNG GAS CONTROL RECEIVED AN OVER PRESSURE ALARM FORM SYSTEM 217, 60TH STREET DISTRICT REGULATOR STATION (LS 1723) IN ALTOONA, PA. AT 1:10 AM A GAS MEASUREMENT AND REGULATION TECHNICIAN WAS DISPATCHED AND ARRIVED ON SITE AT 1:50 AM. AFTER ACCESSING THE SITUATION, THE TECHNICIAN MANUALLY THROTTLED BACK INLET VALVES AND HAD THE SYSTEM BACK TO 150# MAOP BY 2:13 AM. POST INCIDENT EVALUATION OF REGULATOR REVEALED A BOOT FAILURE IN THE SYSTEM AND RELIEFS THAT DID NOT RESPOND TO TESTED SET POINT. FOLLOW UP ACTIONS TAKEN INCLUDE LEAK SURVEY OF ALL MAINS AND SERVICES WITHIN OVER PRESSURED SYSTEM BY 9:00 PM ON 1/23/2013. GAS MEASUREMENT AND REGULATOR TECHNICIANS CONTINUOUSLY MONITORED SYSTEM AND ON 1/24/2013, A WORKER-MONITOR SYSTEM WITH RELIEF WAS INSTALLED TO REPLACE EXISTING WORKER-RELIEF SET UP. ALL DOWNSTREAM REGULATING EQUIPMENT ON SYSTEM 217 WAS INSPECTED ON 1/25/2013. A SECOND FOLLOW UP LEAK SURVEY WAS CONDUCTED OF ALL MAINS AND SERVICES OF SYSTEM 217 ON 2/1/2013. A STANDBY REGULATOR RUN, LOCKED OUT OF SERVICE FROM TIME OF INCIDENT, WAS ALSO REVISED ON 8/19/2013 FROM WORKER/RELIEF TO WORKER/MONITOR PLUS RELIEF ON 8/21/2013, AND PLACED BACK INTO OPERATION. A FIELD TEST OF SYSTEM RELIEF VALVES WAS CONDUCTED ON 9/5/2013, CONFIRMING OVERPROTECTION CAPABILITIES UNDER LOAD.
2025-03-31 10:13 | NO | YES | NO | 20130021 | 15611 | 2013-02-22 17:36 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY | DALLAS | TX | 75240 | 2013-01-24 07:00 |  |  | 2013 | 221 TENNIE | GAINESVILLE | COOKE | TX | 76241 | 33.6189 | -97.1479 | [9 empty] | 2013-01-24 08:22 | 103643 |  | NATURAL GAS |  | 31 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | YES | 50 | 2013-01-24 07:00 |  |  |  | 2013-01-24 07:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 40 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1 | UNKNOWN | UNKNOWN | STEEL |  |  |  | 0.125 | [6 empty] | OTHER | [8 empty] | EXTERNAL FORCES PULLED A STEEL SERVICE LINE OUT OF TAP | CLASS 3 LOCATION | 100000 | 124884.6116075813 | 500 | 624.4230580379065 | 5000 | 6244.230580379065 | 0 | 0 |  |  | 150 | 131.25 |  | 0 | 105650 | 54689.6649410058330081967213114754098361 | 131884.5152459982715 | 0 | 0 | 3 |  |  |  |  | 25 | 25 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM WAS OPERATING PROPERLY | [12 empty] | YES | 6 | 0 | YES | 1 | 0 | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JACKY THOMAS | OPERATIONS SUPERVISOR | jacky.thomas@atmosenergy.com | 903-891-4251 | 903-891-4239 |  |  |  | MARC CHAPMAN | COMPLIANCE DIRECTOR | 214-206-2875 | marcus.chapman@atmosenergy.com | WHILE ATMOS ENERGY WAS RESPONDING TO AN EMERGENCY LINE LOCATE FOR THE CITY OF GAINESVILLE TO REPAIR A MAJOR WATER LEAK, THE WATER REPAIR CREW WAS SETTING UP TO PREPARE TO EXCAVATE THE WATER LEAK. DURING THIS PROCESS, THE CITY'S DUMP TRUCK FELL THROUGH THE STREET ON TOP OF THE GAS SERVICE LINE, CAUSING A LEAK.
2025-03-31 10:13 | NO | NO | NO | 20130022 | 15800 | 2013-02-26 12:15 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2013-01-29 12:13 |  |  | 2013 | SWENSON STREET AND COLBY AVENUE | LAS VEGAS | CLARK COUNTY | NV | 89119 | 36.0972 | -115.1458 | [9 empty] | 2013-01-29 17:20 | 1037011 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-01-29 12:13 |  |  |  | 2013-01-29 12:13 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 38 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | SOLVENT CEMENT FITTING | 1980 | [8 empty] | PLASTIC |  |  |  |  | POLYVINYL CLORIDE (PVC) |  |  | 0.117 |  |  | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 291 | 363.414219778061583 | 70223 | 87697.720809191816299 | 0 | 0 |  |  | 0 | 0 |  | 0 | 70514 | 36472.281056663072618 | 88061.135028969877882 | 122 | 0 | 904 |  |  |  |  | 38 | 38 | 43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | [197 empty] | THREADED CONNECTION FAILURE | [12 empty] | OTHER | THREADED FITTING CAP | [69 empty] | RENEE EGGE | COMPLIANCE SPECIALIST | renee.egge@swgas.com | 702.365-2080 | 702.221-4116 |  |  |  | PHIL ANDREW | DIRECTOR OF GAS OPERATIONS FOR SOUTHERN NEVADA | 702.630-8188 | phil.andrew@swgas.com | A CONTRACTED LEAK SURVEYOR WORKING FOR SOUTHWEST GAS DISCOVERED A GRADE 1 LEAK ON A TWO-INCH PVC MAIN IN THE INTERSECTION OF SWENSON STREET AND COLBY AVENUE IN CLARK COUNTY. SERVICE TO 1026 ACTIVE CUSTOMERS WAS DISCONTINUED AT 15:10 UNTIL REPAIRS TO THE MAIN WERE COMPLETED.
2025-03-31 10:13 | NO | NO | NO | 20130023 | 15614 | 2013-02-26 20:27 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 200 CIVIC CENTER DR | COLUMBUS | OH | 43215 | 2013-01-28 10:23 |  |  | 2013 | 21 HARRISON ST. | TIFFIN | SENECA | OH | 44831-1552 | 41.1204 | -83.1767 | [9 empty] | 2013-01-28 12:15 | 1036809 | [5 empty] | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2013-01-28 10:23 |  |  |  | 2013-01-28 10:32 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | UNKNOWN | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN | CLASS 3 LOCATION | 0 | 0 | 1000 | 1248.846116075813 | 1500 | 1873.2691741137195 | 1000 | 1248.846116075813 | PAVING RESTORATION |  | 0 | 0 |  | 0 | 3500 | 1810.3211234410295 | 4370.9614062653455 | 0 | 0 | 1 |  |  |  |  | 0.44 | 0.44 | 0.54 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | ROB R.SMITH | OPERATIONS COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB R.SMITH | OPERATIONS COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | COLUMBIA GAS OF OHIO INVESTIGATORS AND OTHER INTERESTED PARTIES MET ON JANUARY 28, 2013 TO PERFORM AN INVESTIGATION REGARDING THE INCIDENT. AS A RESULT OF THIS INVESTIGATION, THE PARTIES CONCLUDED THAT THE CAUSE OF THIS EXPLOSION CANNOT BE ASCERTAINED. THE BUILDING'S COMPROMISED STRUCTURAL CONDITION LIMITED ANY INTERNAL BUILDING INVESTIGATION. THE BUILDING WAS DEMOLISHED THE SAME DAY AS A RESULT OF ITS UNSAFE CONDITION. DURING THE COLUMBIA GAS OF OHIO SERVICE LINE TEST FOR 21 HARRISON ST., A MINUTE, NON-CAUSAL LEAK WAS DISCOVERED 34 FEET FROM THE BUILDING FOUNDATION THAT COULD NOT HAVE BEEN THE SOURCE OF THE EXPLOSION. A SECTION OF SERVICE PIPE, INCLUDING A COUPLING AND CURB VALVE, WAS REMOVED, IN THE AREA OF THIS LEAK, AND A SUBSEQUENT LAB TEST WAS PERFORMED ON FEBRUARY 6, 2012. THE RESULTS OF THE TEST CONFIRMED A MINUTE, NON-CAUSAL LEAK. OUR POST-INCIDENT LEAKAGE INVESTIGATION DID NOT REVEAL ANY MIGRATION OF NATURAL GAS TOWARDS THE VICINITY OF THE BUILDING'S FOUNDATION. COLUMBIA CONSIDERS THIS TO BE THE FINAL DETERMINATION AND THIS REPORT SHOULD BE CONSIDERED FINAL.
2025-03-31 10:13 | NO | NO | NO | 20130024 | 34475 | 2013-03-04 18:35 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2013-02-09 19:20 |  |  | 2013 | 71 SUCH DRIVE | ATTLEBORO | BRISTOL | MA | 02703 | 41.9102 | -71.2657 | [9 empty] | 2013-02-09 21:04 | 1038045 |  | NATURAL GAS |  | 60 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 40 | 2013-02-09 19:22 |  |  |  | 2013-02-09 19:55 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1972 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | DAMAGED THREADED FITTING | [5 empty] | CLASS 2 LOCATION | 80000 | 99907.68928606504 | 3000 | 3746.538348227439 | 3000 | 3746.538348227439 | 0 | 0 |  |  | 650 | 568.75 |  | 0 | 86650 | 45008.303225159909868852459016393442623 | 107969.515982519918 | 0 | 0 | 2 |  |  |  |  | 80 | 80 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS RELEASE RATE WAS INSIGNIFICANT. WOULD NOT HAVE AFFECTED SCADA READINGS OR CAUSED ALARMS | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | DAMAGE WAS IDENTIFIED ON THE METER SET HOWEVER UNABLE TO IDENTIFY HOW THE METER WAS DAMAGED. | [154 empty] | MEGGAN BIRMINGHAM | MANAGER COMPLIANCE GAS OPERATIONS | meggan.pena@eversource.com | 508.468.9956 |  |  |  |  | MEGGAN BIRMINGHAM | MANAGER COMPLIANCE GAS OPERATIONS | 508.468.9956 | meggan.pena@eversource.com | OUTSIDE METER SET ON RESIDENCE, 71 SUCH DRIVE, ATTLEBORO, MA. SHOWED DAMAGE RESULTING FROM OUTSIDE FORCE HOWEVER NO VEHICLE OR EQUIPMENT THAT COULD HAVE CAUSED THE DAMAGE WAS ON SITE DURING THE INCIDENT. THE FORCE CAUSED THE THREADED FITTING TO SPLIT AND RELEASE GAS. GAS THEN IGNITED AND CAUSED RESIDENCE TO SUFFER EXTENSIVE DAMAGE. THE COMPANY AND FIRE MARSHAL (MSP 2013-117-0182) WERE UNABLE TO DETERMINE THE CAUSE OF THE FIRE AND THE SOURCE THAT CAUSED THE DAMAGE TO THE METER SET.
2025-03-31 10:13 | NO | YES | NO | 20130025 | 16542 | 2013-03-07 17:09 | SUPPLEMENTAL FINAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2013-02-08 19:28 |  |  | 2013 | 8 MARPLE RD | POUGHKEEPSIE | DUTCHESS | NY | 12603 | 41.7036 | -73.902 | [9 empty] | 2013-02-08 23:32 | 1037974 |  | NATURAL GAS |  | 6.2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 9 | 2013-02-08 19:29 |  |  |  | 2013-02-08 19:48 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1931 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.28 | [6 empty] | LEAK |  |  | OTHER | WELD FAILURE | [5 empty] | CLASS 3 LOCATION | 285000 | 355921.143081606705 | 14246 | 17791.061769616031998 | 5548 | 6928.598251988610524 | 0 | 0 |  |  | 95 | 83.125 |  | 0 | 304889 | 157726.9002055418916665245901639344262295 | 380723.928103211347522 | 0 | 0 | 2 |  |  |  |  | 0.27 | 0.3 | 0.43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | MATERIAL FAILURE OF PIPE OR WELD | BUTT WELD | [146 empty] | BUTT WELD |  |  | FABRICATION | [35 empty] | YES | INCOMPLETE WELD PENETRATION | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | LENORE J CLARKE | SECTION ENGINEER GAS SYSTEM SAFETY AND COMPLIANCE | lclarke@cenhud.com | 845 486 5521 | 845 486 5697 |  |  |  | LARRY CAMBALIK | MANAGER OF GAS AND MECHANICAL ENGINEERING | 845 486 5741 | lcambalik@cenhud.com | CENTRAL HUDSON WAS NOTIFIED OF A STRUCTURE FIRE AT 8 MARPLE ROAD FROM THE DUTCHESS COUNTY 911 CENTER, FRIDAY, FEBRUARY 8TH AT 19:28. A CENTRAL HUDSON SERVICE TRUCK ARRIVED ON SITE AT 19:48. THE ELECTRIC SERVICE WAS DROPPED AND THE GAS METER SHUT OFF TO 8 MARPLE ROAD AT 19:59. A COMMERCIAL REPRESENTATIVE ARRIVED ON SITE AT 20:02 AND SMELT AN ODOR OF GAS IN THE AIR. ASSISTANCE OF ADDITIONAL COMMERCIAL REPRESENTATIVES WAS REQUESTED UPON HIS ARRIVAL. READINGS WERE TAKEN AND FOUND IN THE STORM DRAINS, IN THE STREET AND INSIDE THE HOME ACROSS THE STREET AT 9 MARPLE RD. RESIDENTS WERE EVACUATED AT 9 MARPLE ROAD, IN ADDITION TO THE INDIVIDUALS AT 8 MARPLE RD. ON SITE PERSONNEL AT 20:18 REQUESTED A GAS CREW AND SUPERVISION TO BE DISPATCHED TO THE SCENE. THE POUGHKEEPSIE WATER DEPARTMENT WAS ALSO ON SITE AND ASSISTED CENTRAL HUDSON PERSONNEL IN LOCATING MAN HOLES IN THE AREA TO OPEN AND VENT. CENTRAL HUDSON GAS CREWS IDENTIFIED A LEAK IN THE STREET BETWEEN THE TWO EVACUATED HOMES OVER THE 6" LOW PRESSURE STEEL MAIN. UPON EXCAVATION, A 3/16" SEPARATION IN A JOINT WAS FOUND AND A 6" LEAK REPAIR CLAMP WAS INSTALLED TO REPAIR THE LEAK AT 01:30 ON FEBRUARY 9TH. THE ONSITE COMMERCIAL REPRESENTATIVES CONTINUED TO MONITOR HOMES AND DRAINS FOR READINGS WHILE THE REPAIR WORK WAS TAKING PLACE. FRIDAY, FEBRUARY 9TH AT 03:48 9 MARPLE ROAD WAS CLEARED TO RE-OCCUPY AND ALL SERVICES WERE RESTORED. THE SERVICE TO 8 MARPLE ROAD WAS RETIRED. CENTRAL HUDSON PERSONNEL REMAINED ONSITE AERATING THE GROUND THROUGH FEBRUARY 10TH UNTIL 0% READINGS OF GAS WERE RECEIVED. CENTRAL HUDSON HAS RECEIVED THE RESULTS OF THE LABORATORY TESTING OF THE SECTION OF PIPE THAT CONTRIBUTED TO THIS INCIDENT. THE EXTERIOR OF THE PIPE WAS FOUND TO BE IN VERY GOOD CONDITION. THE ANALYSIS SHOWS THE FAILURE OF THE CIRCUMFERENTIAL GROOVE WELD TO BE THE RESULT OF EXTERNAL LOADS EXCEEDING THE CAPABILITIES OF A WELD JOINT THAT EXHIBITED COMPLETE LACK OF PENETRATION SINCE ITS INSTALLATION IN 1931. EXTERNAL CORROSION WAS NOT A FACTOR, SINCE NONE WAS OBSERVED, INDICATING THE WRAPPING AND CATHODIC PROTECTION OF THIS PIPE WERE SATISFACTORY. THE ROOT CAUSE OF THE FAILURE WAS INCOMPLETE PENETRATION OF THE WELD METAL JOINING THE TWO PIPES. HOWEVER, THE WELD WAS SUFFICIENTLY STRONG TO REMAIN IN SERVICE FOR OVER 80 YEARS.
2025-03-31 10:13 | NO | YES | NO | 20130026 | 15617 | 2013-03-08 07:55 | ORIGINAL | 24015 | YANKEE GAS SERVICES CO | 107 SELDEN STREET | BERLIN | CT | 06037 | 2013-01-30 15:40 |  |  | 2013 | 166 MOUNT PLEASANT TERRACE | NEWTOWN | FAIRFIELD | CT | 06470 | 41.4175 | -73.3686 | [9 empty] | 2013-01-30 17:33 | 1037102 |  | NATURAL GAS |  | 600 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-01-30 15:40 |  |  |  | 2013-01-30 15:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 26 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1992 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 54000 | 67437.690268093902 | 125000 | 156105.764509476625 | 0 | 0 |  |  | 1205 | 1054.375 |  | 0 | 180205 | 93560.3532053986000491803278688524590164 | 224597.829777570527 | 50 | 0 | 549 |  |  |  |  | 35 | 35 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK VOLUME BELOW LEVELS DETECTABLE BY SCADA. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | PIPE SADDLE |  |  |  |  | YES |  |  |  |  | YES |  |  |  | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | GARRY DAIGLE | PRINCIPAL ENGINEER | garry.daigle@nu.com | 203-596-3149 | 203-596-3130 |  |  |  | BRET FACTORA | MANAGER - ENGINEERING-GIS | 203-596-3071 | bret.factora@nu.com | NEWTOWN FIRE DEPARTMENT REPORTED GAS LEAK AT 166 MOUNT PLEASANT TERRACE, NEWTOWN. COMPANY RESPONDERS ARRIVED AND EVALUATED LEAK SITE. IT WAS DETERMINED THAT THE NEAREST OPERABLE VALVE WOULD BE USED TO SHUTDOWN THE DISTRIBUTION SYSTEM FEEDING THE LEAK LOCATION. THE SHUTDOWN RESULTED IN THE INTERRUPTION OF 599 CUSTOMERS.
2025-03-31 10:13 | NO | YES | NO | 20130027 | 15715 | 2013-03-08 18:27 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2013-02-09 23:28 |  |  | 2013 | 5479 JAY ROAD | BOULDER | BOULDER | CO | 80301-3038 | 40.0511 | -105.2258 | [9 empty] | 2013-02-11 13:00 | 1038193 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2013-02-09 23:44 |  |  |  | 2013-02-10 00:30 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 17 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1967 | [5 empty] | 0.375 | ASTM D 2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYVINYL CLORIDE (PVC) |  |  | 0.062 |  |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 180000 | 224792.30089364634 | 1000 | 1248.846116075813 | 1990 | 2485.20377099086787 | 0 | 0 |  |  | 15 | 13.125 |  | 0 | 183005 | 94660.9020730066195808196721311475409836 | 228539.47578071302087 | 0 | 0 | 1 |  |  |  |  | 54 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURES AND FLOWS REMAINED WITHIN EXPECTED VALUES. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [56 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | SUBSIDENCE |  |  |  |  | NO | [218 empty] | DIANE JACQUEZ | SENIOR INVESTIGATOR | diane.m.jacquez@xcelenergy.com | 303-294-2552 | 303-294-2311 |  |  |  | JOHN KARTUS | MANAGING INVESTIGATOR | 303-294-2665 | john.j.kartus@xcelenergy.com | INVESTIGATION REVEALED PVC SERVICE CRACKED IN A LOCATION WHERE GROUND MOVEMENT WAS LIKELY.
2025-03-31 10:13 | NO | YES | NO | 20130029 | 15707 | 2013-03-12 15:10 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2013-02-12 13:25 |  |  | 2013 | INTERSECTION OF 50TH ST. AND BROAD AVE. | ALTOONA |  | PA | 16601 | 40.4821 | -78.4247 | [9 empty] | 2013-02-12 19:05 | 1038323 |  | NATURAL GAS |  | 12538 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2013-02-12 13:25 |  |  |  | 2013-02-12 13:25 |  | NO | PUBLIC PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | VALVE 12 INCH | 1959 | [8 empty] | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 14500 | 18108.2686830992885 | 182571 | 228003.084258077255223 | 21770 | 27187.37994697044901 | 0 | 0 |  |  | 45638 | 39933.25 |  | 0 | 264479 | 150132.7328265688924842131147540983606557 | 313231.982888146992733 | 0 | 0 | 2 |  |  |  |  | 143 | 143 | 150 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM WAS OPERATING NORMALLY. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | WHILE ATTEMPTING TO REPAIR FLANGE SEAL LEAK, REPAIR CREW DID NOT TIGHTEN FLANGE BOLTS IN PROPER SEQUENCE. |  |  | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | MICHAEL L. SMITH | COMPLIANCE PROCESS MANAGER | michael.l.smith@peoples-gas.com | 1-412-244-2605 |  |  |  |  | KENNETH M. JOHNSTON | SR. VICE PRESIDENT CHIEF OPERATING OFFICER | 1-412-208-7930 | kenneth.m.johnston@peoples-gas.com | ON FEBRUARY 12, 2013 AT 1:25 PM A PNG CREW WAS IN THE PROCESS OF REPAIRING A FLANGE LEAK AT THE GASKET SURFACE OF A 12 INCH GATE VALVE LOCATED IN A CEMENT PIT AT THE INTERSECTION OF 50TH STREET AND BROAD AVENUE. AFTER TIGHTENING A SERIES OF BOLTS ON THE FLANGE, THE CREW HEARD A POPPING SOUND AND OBSERVED A CRACK IN THE VALVE BODY. THIS MAIN LINE VALVE IS LOCATED NEAR THE SOLE SOURCE OF SUPPLY FOR THE ENTIRE ALTOONA SYSTEM, SERVING APPROXIMATELY 30,000 CUSTOMERS AND OPERATES WITH 150 POUND MAOP. IMMEDIATE RESPONSE INCLUDED VENTING, CONTINUOUS SURVEY OF SURROUNDING AREA IN COOPERATION WITH 911 RESPONDERS, GATHERING MATERIALS, PNG MANPOWER, AND OUTSIDE CONTRACTOR SUPPORT TO INSTALL A BYPASS AND SET 20 INCH AND 12 INCH STOPPLES. A BYPASS WAS INSTALLED AND STOPPLE EQUIPMENT WAS SET, ACHIEVING SHUT DOWN OF BLOWING GAS ON FEBRUARY 14, 2013 AT 12:18 PM. FINAL REPAIRS INCLUDED REPLACEMENT OF CRACKED VALVE WITH 12 INCH FLANGED SPOOL PIECE. THE VALVE WAS SENT TO DET NORSKE VERITAS FOR METALLURGICAL ANALYSIS REVEALING COMPOSITION OF VALVE TO BE CAST IRON. FURTHER TESTING CONCLUDED THAT FAILURE WAS CAUSED BY OVERSTRESSING, ORIGINATING AT THE EXTERNAL SURFACE OF THE VALVE. PEOPLES NATURAL GAS IS IDENTIFYING AND INSTALLING WARNING TAGS TO ALL VALVES MANUFACTURED BY DARLING, VALVES OF KNOWN CAST IRON MATERIAL, AND THOSE OF UNKNOWN COMPOSITION. THESE WARNING DEVICES ARE TO REMIND OPERATORS TO EXERCISE CAUTION WHEN OPERATING OR REPAIRING CAST IRON VALVES OR VALVES OF UNKNOWN MATERIAL ORIGIN. PART F -DRUG AND ALCOHOL TESTING INFORMATION WAS REVISED IN FINAL REPORT TO REFLECT NO EMPLOYEES TESTED. PNG DID SEND TWO EMPLOYEES FOR POST INCIDENT TESTING, COMPLETING THE DRUG ASPECT WITHIN THE PRESCRIBED TIMEFRAME, BUT MISSED THE TIME DEADLINE ON THE ALCOHOL TEST REQUIREMENT. ADDITIONAL TRAINING ON VALVE REPAIR AND POST INCIDENT PROCEDURES WILL BE PERFORMED.
2025-03-31 10:13 | NO | YES | YES | 20130031 | 30415 | 2013-03-21 18:07 | SUPPLEMENTAL | 30769 | MISSOURI GAS ENERGY | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2013-02-19 18:02 |  |  | 2013 | NEAR 910 W 48TH ST | KANSAS CITY | JACKSON | MO | 64112 | 39.0407 | -94.5981 | [9 empty] | 2013-02-19 18:57 | 1038907 |  | NATURAL GAS |  | 180 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 1 | 0 | 0 | 2 | 1 | 4 | YES |  |  |  |  | YES | 2 | 2013-02-19 16:55 |  |  |  | 2013-02-19 17:16 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 38 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2000 | [5 empty] | 2 | ASTM. D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1.5 | [7 empty] | CLASS 3 LOCATION | 19566000 | 24434923.107139357158 | 85454 | 106718.896003142524102 | 75587 | 94396.531375822477231 | 0 | 0 |  |  | 1000 | 875 |  | 0 | 19728041 | 10204317.71916872249063831147540983606557 | 24636913.534518322159333 | 2 | 0 | 0 |  |  |  |  | 25 | 25 | 58 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 5 | 0 | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 130370903 |  |  | CONTRACT LOCATOR | YES | YES |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | RANDY WILSON | MANAGER PIPELINE SAFETY AND COMPLIANCE | randy.wilson@spireenergy.com | 205-326-2987 |  |  |  |  | CRAIG R. HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@thelacledegroup.com | ON FEBRUARY 19, 2013, HEARTLAND MIDWEST, LLC, WAS INSTALLING CABLE NEAR 910 W 48TH STREET, KANSAS CITY, MO FOR TIME WARNER CABLE VIA A VERMEER D9X13 SERIES II HORIZONTAL DIRECTIONAL DRILL WHEN IT TORE A HOLE IN MGE'S TWO-INCH GAS MAIN THAT WAS APPROXIMATELY 38 INCHES DEEP. USIC LOCATING, INC. PERFORMED ONE-CALL LOCATING FOR THE CITY OF KANSAS CITY, MGE AND OTHER UNDERGROUND FACILITY OWNERS. USIC MARKED THE PRESENCE OF ONE UNDERGROUND ELECTRICAL LINE FOR THE STREETLIGHTS AND ONE UNDERGROUND GAS LINE ABOUT A FOOT TO THE SOUTH OF THE ELECTRICAL LINE. HOWEVER, THERE ACTUALLY WERE TWO ELECTRICAL LINES AT THAT LOCATION, NOT ONE, ALONG WITH THE GAS LINE ABOUT A FOOT TO THE SOUTH OF THE TWO ELECTRICAL LINES. HEARTLAND PERSONNEL DUG ONE POTHOLE BETWEEN THE SINGLE RED BROKEN PAINT LINE FOR ONE ELECTRICAL LINE AND THE SINGLE BROKEN YELLOW PAINT LINE FOR THE GAS LINE MARKED ON THE SURFACE AND FOUND TWO CONDUITS. HEARTLAND CONCLUDED THEY HAD EXPOSED THE ELECTRICAL LINE AND THE GAS LINE THAT USIC HAD MARKED. IN REALITY, HEARTLAND HAD EXPOSED TWO ELECTRICAL CONDUITS AND HAD NOT EXPOSED THE GAS MAIN. HEARTLAND THEN DIRECTED THE DRILL TO A DEPTH ABOUT A FOOT BELOW THE CONDUITS AND STRUCK THE GAS MAIN. HEARTLAND FAILED TO EXTEND THE POTHOLE TO THE DEPTH OF THE PLANNED BORE WHERE THE DRILL COULD BE OBSERVED PASSING BELOW THE CONDUITS. THE GAS LINE WAS STRUCK BETWEEN 16:00 AND 16:30, BUT HEARTLAND PERSONNEL DID NOT NOTIFY EMERGENCY PERSONNEL UNTIL THEY CALLED 911 AT 16:54. MGE DISPATCH WAS NOTIFIED AT 16:55. IN REFERENCE TO PART A, QUESTION 16, MGE GAVE EVACUATION ORDERS TO TWO STRUCTURES (906 AND 910 W 48TH STREET) PRIOR TO THE EXPLOSION. THE EXPLOSION AT JJ'S RESTAURANT, 910 W. 48TH STREET, KANSAS CITY, MO, OCCURRED AT 18:02. THE TWO-INCH VALVE AT THE NW CORNER OF 48TH AND ROANOKE WAS CLOSED AT 19:20. THE TWO-INCH GAS MAIN WAS PINCHED OFF AT THE SE CORNER OF 48TH AND BELLEVIEW AT 20:00. AFTER THE GAS FLOW WAS STOPPED, THE GAS MAIN ON 48TH STREET WAS CUT AND CAPPED AT THE NE CORNER OF 48TH AND BELLEVIEW AND JUST WEST OF THE TWO-INCH VALVE AT THE NW CORNER OF 48TH AND ROANOKE. THEN, THE GAS MAIN ON BELLEVIEW WAS RE-ENERGIZED TO ALLOW GAS FLOW TO CUSTOMERS ON BELLEVIEW BETWEEN 48TH AND 47TH STREETS. THE GAS MAIN ON 48TH STREET BETWEEN BELLEVIEW AND ROANOKE IS STILL INACTIVE. ONE FATALITY AND MULTIPLE INJURIES RESULTED, INCLUDING MGE'S FIRST RESPONDER, AND EMPLOYEES OF HEARTLAND AND JJ'S RESTAURANT. THERE WAS SIGNIFICANT PROPERTY DAMAGE, BUT THE TOTAL ESTIMATED PROPERTY DAMAGE IS UNKNOWN AT THIS TIME, IN PART BECAUSE LITIGATION CONTINUES INVOLVING THREE BUILDINGS IN THE VICINITY AND ONE ISSUE IN EACH CASE IS THE EXTENT OF THE DAMAGES RESULTING FROM THE EXPLOSION. MGE HAD SIX EMPLOYEES ON SITE AT THE TIME OF THE EXPLOSION. AS MGE WAS UNABLE TO COMPLETE A FULL INVESTIGATION ON THE NIGHT OF THE INCIDENT TO DETERMINE WHETHER ANY OF ITS ON-SITE EMPLOYEES CONTRIBUTED TO THE INCIDENT, FIVE OF THE SIX EMPLOYEES WERE SENT TO THE HOSPITAL LATER THAT EVENING FOR DOT POST-ACCIDENT DRUG AND ALCOHOL TESTING. THE HOSPITAL WAS INSTRUCTED TO ADMINISTER DOT POST-ACCIDENT DRUG AND ALCOHOL TESTING FOR ALL FIVE EMPLOYEES. DRUG AND ALCOHOL TESTS WERE ADMINISTERED TO FOUR OF THE EMPLOYEES, WITH NO POSITIVE RESULTS. A DRUG TEST WAS ADMINISTERED TO THE FIFTH EMPLOYEE WITH NO POSITIVE RESULTS. THE HOSPITAL WAS INSTRUCTED TO ADMINISTER AN ALCOHOL TEST TO THE FIFTH EMPLOYEE, BUT DID NOT. THE SIXTH EMPLOYEE, MGE'S FIRST RESPONDER, WAS TESTED FOR ALCOHOL AND DRUGS AFTER THE INCIDENT IN THE COURSE OF THE TREATMENT FOR HIS INJURIES AT ST. LUKE'S HOSPITAL, AND THAT THE RESULTS WERE NEGATIVE. MGE DOES NOT BELIEVE ITS EMPLOYEES' PERFORMANCE CONTRIBUTED TO THE INCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20130033 | 15656 | 2013-03-28 13:52 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2013-02-27 17:07 |  |  | 2013 | 4232 COOPER AVENUE | ROYAL OAK | OAKLAND | MI | 48073 | 42.5271 | -83.1931 | [9 empty] | 2013-02-27 19:01 | 1039624 |  | NATURAL GAS |  | 231.8 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 75 | 2013-02-27 17:07 |  |  |  | 2013-02-27 17:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1948 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  |  |  | 0.113 | [6 empty] | MECHANICAL PUNCTURE | 1.2 | 0.5 | [7 empty] | CLASS 3 LOCATION | 750000 | 936634.58705685975 | 1000 | 1248.846116075813 | 19336 | 24147.688500441920168 | 3000 | 3746.538348227439 | HOTEL ACCOMODATIONS FOR EVACUATED CUSTOMERS |  | 2133 | 1866.375 |  | 0 | 775469 | 401722.6479525101234385573770491803278689 | 967644.035021604922168 | 2 | 0 | 36 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | OPERATOR PERSONNEL FELT EXPLOSION FROM NEARBY ROYAL OAK SERVICE CENTER |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 7 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | YES | YES | CITY STREET |  |  | YES | [9 empty] | UTILITY | BORING | NATURAL GAS | YES | 30380079 |  |  | UTILITY OWNER | YES | YES | 51 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | CREWS DID NOT FOLLOW PROCEDURES. | [169 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 |  |  |  |  | TRACY A. GOBLE | REGULATORY AND COMPLIANCE MANAGER | 517-768-3187 | tracy.goble@cmsenergy.com | AT APPROXIMATELY 1707 HOURS (5:07 PM) ON FEBRUARY 27, 2013, AN EXPLOSION OCCURRED AT 4232 COOPER AVENUE, ROYAL OAK, MICHIGAN. CONSUMERS ENERGY MANAGEMENT AND FIELD PERSONNEL ARRIVED AT THE SITE AT VARIOUS TIMES BETWEEN 1715 AND 1809 IN RESPONSE TO THE INCIDENT. WORKING WITH LOCAL POLICE AND FIRE DEPARTMENTS, CONSUMERS ENERGY EXCAVATED AND SHUT OFF THE GAS SUPPLY TO 4232 COOPER AVE AT 1836 HOURS. INFORMATION OBTAINED FROM THE INCIDENT REVIEW AND INVESTIGATION DETERMINED THAT THE CREWS DID NOT FOLLOW COMPANY BORING PROCEDURES DURING INSTALLATION OF A NEW MAIN ALONG COOPER AVENUE. AS A RESULT, THE OPERATION CAUSED DAMAGE TO THE STEEL GAS SERVICE LOCATED AT 4232 COOPER AVENUE IN ROYAL OAK, MICHIGAN, RESULTING IN POSSIBLE BELOW-GRADE GAS MIGRATION INTO THE STRUCTURE. INVESTIGATION ESTABLISHED THAT CREWS DID NOT FOLLOW CONSUMERS ENERGY PROCEDURAL REQUIREMENTS TO EXCAVATE AND EXPOSE ALL ACTIVE SERVICES PRIOR TO PERFORMING BORING OPERATIONS. THESE CREWS ALSO FAILED TO FOLLOW COMPANY GAS LEAK RESPONSE STANDARDS. NOTE (5/15/2013 SUPPLEMENTAL REPORT): DESPITE THE NEARBY FACILITIES BEING STAKED CORRECTLY (PART G3-12) AND LOCATE MARKS BEING VISIBLE WITHIN THE VICINITY OF THE BORING AREA (PART G3-11), FOLLOWING THE INCIDENT THERE WAS MINIMAL OBSERVATION OF STAKING FLAGS OR PAINT MARKING AT SOME SERVICE LOCATIONS ALONG COOPER AVENUE. THAT MARKING WAS NOT IMMEDIATELY APPARENT DURING POST-INCIDENT OBSERVATIONS MAY BE DUE IN PART TO LARGE AMOUNTS OF DEBRIS IN THE AREA (AS WELL AS RECENT SNOWFALL) PARTIALLY OBSTRUCTING DIRECT OBSERVATION OF ALL FACILITY STAKING ALONG COOPER AVENUE.
2025-03-31 10:13 | NO | YES | NO | 20130034 | 16290 | 2013-03-31 13:12 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2013-03-30 07:56 |  |  | 2013 | 1ST STREET & BROADWAY | GARY | LAKE | IN | 46402 | 41.6059 | -87.3372 | [9 empty] | 2016-03-30 09:33 | 1042503 |  | NATURAL GAS |  | 10150 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-03-30 07:56 |  |  |  | 2013-03-30 07:59 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1948 | [5 empty] | 14 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 6 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 15000 | 18732.691741137195 | 2500 | 3122.1152901895325 | 0 | 0 |  |  | 63673 | 55713.875 |  | 0 | 81173 | 60590.2019286805573360655737704918032787 | 77568.6820313267275 | 20 | 1 | 0 |  |  |  |  | 160 | 160 | 170 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS CAUSED BY A TRAIN DERAILMENT, THE TRAIN PUNCTURED THE PIPELINE AFTER LEAVING THE TRACKS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LUKE SELKING | MANAGER PIPELINE SAFETY AND COMPLIANCE | leselking@nisource.com | 260-433-6115 | 260-422-9151 |  |  |  | LUKE SELKING | MANAGER PIPELINE SAFETY AND COMPLIANCE | 260-433-6115 | leselking@nisource.com | TRAIN DERAILED FROM TRACKS AND PUNCTURED A BURIED 14" NATURAL GAS PIPELINE. THE PIPELINE SHUTDOWN WAS DELAYED DUE TO COORDINATION WITH INDUSTRIAL CUSTOMER PROCESS. THE CUSTOMER HAD TO SWITCH OVER TO ALTERNATIVE FUEL BEFORE THE PIPELINE WAS SHUTDOWN. AFTER THE PIPELINE WAS SHUTDOWN, THE DERAILED TRAINS WERE REMOVED, AND 60 FEET OF PIPE WAS REPLACED. THE PIPELINE WAS PURCHASED FROM THE US GOVMT IN MARCH OF 1948. ORIGINAL PIPE INFORMATION IS UNKNOWN.
2025-03-31 10:13 | NO | NO | NO | 20130036 | 16090 | 2013-04-04 11:49 | SUPPLEMENTAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2013-03-04 18:30 |  |  | 2013 | 1501 A STREET | AURORA | HAMILTON | NE | 68818 | 40.8581 | -97.998 | [9 empty] | 2013-03-04 22:10 | 1040076 |  | NATURAL GAS |  | 192 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 8 | 2013-03-04 18:53 |  |  |  | 2013-03-04 19:46 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1971 | [5 empty] | 1 | ASTM D2513 | DUPONT ALDYL A | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 75000 | 93663.458705685975 | 3600 | 4495.8460178729268 | 2000 | 2497.692232151626 | 0 | 0 |  |  | 200 | 175 |  | 0 | 80800 | 41850.9945457150615442622950819672131148 | 100831.9969557105278 | 1 | 0 | 0 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | CONSTRUCTION | NO | [50 empty] | NATHAN STEWART | COMPLIANCE SPECIALIST | nathan.stewart@blackhillscorp.com | 402-437-1734 | 402-437-6734 |  |  |  | NATHAN STEWART | COMPLIANCE SPECIALIST | 402-437-1734 | nathan.stewart@blackhillscorp.com | AT APPROXIMATELY 1722 AURORA VOLUNTEER FIRE DEPARTMENT (AVFD) WAS CALLED TO 1501 'A' STREET IN AURORA NE FOR A FIRE. THIS IS A HAMILTON COUNTY HIGHWAY DEPARTMENT COMPLEX. FIRE LOCATED WITHIN THE 'BRIDGE BUILDING' AVFD EXTINGUISHED THE FIRE AND DURING OVERHAUL DISCOVERED VAPOR ESCAPING THROUGH CRACKS IN THE FLOOR OF STRUCTURE. THE GAS OPERATOR BLACK HILLS ENERGY (BHE) WAS CONTACTED REGARDING FIRE AT 1853 HOURS. STATE FIRE MARSHAL INVESTIGATOR DETERMINED THE PRODUCT TO BE NATURAL GAS AT 1915 HOURS THE GAS OPERATOR WAS INFORMED OF PROBABLE INVOLVEMENT OF NATURAL GAS AT 1936 AND TO STOP THE FLOW OF NATURAL GAS TO AREA. FIRST BHE PERSONNEL ARRIVED AT LOCATION 1946 HOURS ADDITIONAL BHE PERSONNEL RESPONDED TO LOCATION AND EXCAVATED THE SERVICE LINE, EXPOSING THE SERVICE LINE, CUT AND CAPPED THE SERVICE LINE. GAS FLOW STOPPED AT 2245 HOURS. IT WAS DISCOVERED THAT NATURAL GAS FROM A FAILED UNDERGROUND PIPE HAD VENTED ITSELF INSIDE THE STRUCTURE. NATURAL GAS LEVELS INSIDE THE STRUCTURE INCREASED TO AN IGNITABLE LEVEL, IGNITION WAS PROVIDED BY A GAS FIRED OVERHEAD UNIT HEATER WITH STANDARD SAFETY PILOT. THE NATURAL GAS FLASHED ACROSS THE ROOM AND BACK TO THE CRACKS IN THE FLOOR WHERE IT CONTINUED TO BURN, IGNITING COMBUSTIBLE MATERIALS BELOW WORK BENCHES ALONG THE EAST AND WEST WALLS. ON 3/5/13 GAS DEPARTMENT CREW EXCAVATED AN AREA NEAR A TEE JUNCTION IN THE SERVICE LINE REVEALING A MECHANICAL FITTING. VISUALLY APPARENT WAS THE FACT THAT A SEGMENT OF 3/4' DUPONT ALDYL-A PE PIPING HAD PULLED OUT OF THE MECHANICAL FITTING APPROXIMATELY 3/4', ALLOWING GAS TO FLOW UNRESTRICTED UNDERGROUND. THE MECHANICAL FITTING WAS REMOVED AND REMAINING PIPE SEGMENTS AIR TESTED AND DETERMINED TO BE LEAK FREE. NATURAL GAS UNDERGROUND PIPING WITHIN THE COMPLEX WAS REPLACED.
2025-03-31 10:13 | NO | YES | NO | 20130037 | 15631 | 2013-04-04 16:10 | ORIGINAL | 5200 | FITCHBURG GAS & ELECTRIC LIGHT CO | 357 ELECTRIC AVE | LUNENBURG | MA | 01462 | 2013-02-05 17:30 |  |  | 2013 | 214 LUNENBURG ST | FITCHBURG | WORCESTER | MA | 01420 | 42.5849 | -71.7894 | [9 empty] | 2013-02-05 20:30 | [6 empty] | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | YES | 2 | 2013-02-05 17:30 |  |  |  | 2013-02-05 17:35 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 28 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 600000 | 749307.6696454878 | 6500 | 8117.4997544927845 | 10500 | 13112.8842187960365 | 15000 | 18732.691741137195 | HOTEL ROOMS FOR RESIDENTS THAT HAD TO LEAVE THEIR HOMES |  | 0 | 0 |  | 0 | 632000 | 326892.271432780184 | 789270.745359913816 | 0 | 0 | 1 |  |  |  |  | 0.5 | 0.5 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS IS A LOW PRESSURE CAST IRON MAIN THAT WAS NOT MONITORED OR CONTROLLED BY CONTROL ROOM STAFF | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [56 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | OTHER |  |  |  | FROST CONDITIONS TO THE DEPTH OF THE MAIN | NO | [218 empty] | DANIEL GOLDEN | MANAGER GAS DISTRIBUTION | golden@unitil.com | 978-353-3245 | 978-353-3345 |  |  |  | DANIEL GOLDEN | MANAGER GAS DISTRIBUTION | 978-353-3245 | golden@unitil.com | EXPLOSION OCCURRED AT 214 LUNENBURG ST IN FITCHBURG MASS ON FEBRUARY 5, 2013. UNITIL FIRST RESPONDERS RESPONDED TO THE SCENE AND BEGAN LEAK INVESTIGATION AND FOUND A CRACKED 4" CAST IRON MAIN THAT THEY REPAIRED AND THE CAUSE WAS DETERMINED TO BE FROM FROST CONDITIONS DOWN TO THE TOP OF THE MAIN.
2025-03-31 10:13 | NO | YES | YES | 20130038 | 15633 | 2013-04-05 16:03 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2013-03-09 12:10 |  |  | 2013 | 9614 SALTILLO ST | HOUSTON | HARRIS | TX | 77013 | 29.8 | -95.2581 | [9 empty] | 2013-03-09 17:18 | 1040561 |  | NATURAL GAS |  | 15 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 2 | 2013-03-09 12:10 |  |  |  | 2013-03-09 12:10 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1971 | [5 empty] | 2 | ASTM D2513 - 2" | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | 2306 | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1.5 | 0.5 |  | CLASS 3 LOCATION | 12000 | 14986.153392909756 | 10000 | 12488.46116075813 | 14000 | 17483.845625061382 | 4000 | 4995.384464303252 | FENCE REPLACEMENT, STORAGE BUILDING AND LANDSCAPING |  | 100 | 87.5 |  | 0 | 40100 | 20770.3268908482996721311475409836065574 | 50041.34464303252 | 0 | 0 | 28 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF SYSTEM | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | IMPROPER CONSTRUCTION PRACTICES (BACKFILLING) BY CONTRACTORS WORKING IN AREA ON SEWER SYSTEM. | [154 empty] | LESLIE J. DAVENPORT | ADVANCED OPERATIONS COORDINATOR | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | DIRECTOR OF OPERATIONS | 713-207-5700 | steve.yarbrough@centerpointenergy.com | GAS ESCAPED FROM MAIN AND COMMUNICATED THROUGH SOIL INTO STRUCTURE RESULTING IN FLASH FIRE BY UNKNOWN/UNDETERMINED IGNITION SOURCE AND INJURING (1) MALE ADULT REQUIRING HOSPITALIZATION.
2025-03-31 10:13 | NO | YES | NO | 20130039 | 15635 | 2013-04-11 00:45 | ORIGINAL FINAL | 11713 | KEYSPAN ENERGY DELIVERY - LONG ISLAND | 175 EAST OLD COUNTRY ROAD | HICKSVILLE | NY | 11801 | 2013-03-12 19:28 |  |  | 2013 | 4 CHOATE AVENUE | SELDEN | SUFFOLK | NY | 11784 | 40.8748 | -73.0568 | [9 empty] | 2013-03-12 21:14 | 1040884 |  | NATURAL GAS |  | 12000 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-03-12 19:47 |  |  |  | 2013-03-12 19:47 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | GALVANIZED STEEL GAS PIPE | [9 empty] | OTHER | [8 empty] | OUTSIDE METER/REGULATOR SET SUSTAINED VEHICULAR DAMAGE. | CLASS 4 LOCATION | 100000 | 124884.6116075813 | 400 | 499.5384464303252 | 150 | 187.32691741137195 | 0 | 0 |  |  | 25 | 21.875 |  | 0 | 100575 | 52028.1753591649952680327868852459016393 | 125593.35197142299715 | 1 | 0 | 0 |  |  |  |  | 57.5 | 57.9 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT INVOLVED A MEMBER OF THE PUBLIC DRIVING THEIR VEHICLE OFF THE ROAD AND INTO THE SIDE OF A STRUCTURE AT THE POINT OF THE GAS METER. NO ACTIONS, INDICATIONS OR MEASUREMENT TO THE CONTROLLER WOULD HAVE HELPED. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | RICHARD VERDERAME | LEAD SUPERVISOR | richard.verderame@nationalgrid.com | 516 545 5767 | 516 545 4193 |  |  |  | RICHARD VERDERAME | LEAD SUPERVISOR | 516 545 5767 | richard.verderame@nationalgrid.com | A MEMBER OF THE PUBLIC LOST CONTROL OF THEIR VEHICLE AND CRASHED INTO THE GAS METER AND REGULATOR SET. THE GAS IGNITED AND THE STRUCTURE SUSTAINED SIGNIFICANT DAMAGE. IT WAS MADE SAFE BY CLOSING THE CURB VALVE.
2025-03-31 10:13 | NO | YES | NO | 20130040 | 15637 | 2013-04-12 21:11 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2013-03-12 14:45 |  |  | 2013 | 1710 MARTIN LUTHER KING WAY | BERKELEY | ALAMEDA | CA | 94704 | 37.8755 | -122.2737 | [9 empty] | 2013-03-13 17:20 | 1040980 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2013-03-12 14:45 |  |  |  | 2013-03-12 14:55 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1987 | [5 empty] | 1 | UNKNOWN | DUPONT | PLASTIC |  |  |  |  | OTHER | ALDYL A |  |  | UNKNOWN |  | OTHER | [8 empty] | THIRD PARTY STRUCK AND CRACKED THE PIPE | CLASS 3 LOCATION | 100000 | 124884.6116075813 | 1200 | 1498.6153392909756 | 1000 | 1248.846116075813 | 0 | 0 |  |  | 20 | 17.5 |  | 0 | 102220 | 52877.5653290682253344262295081967213115 | 127649.5730629480886 | 0 | 0 | 2 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA ON THIS PART OF THE SYSTEM | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | OCCUPANT | HAND TOOLS | SEWER (SANITARY/STORM) | NO |  |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED | YES | 192 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CHERYL DIZON | GAS ENGINEER | c1dz@pge.com | 925-974-4378 | 925-974-4232 |  |  |  | FRANCES YEE | REGULATORY COMPLIANCE AND SUPPORT DIRECTOR | 925-974-4316 | fsc2@pge.com | ON MARCH 12, 2013 AT APPROXIMATELY 1445 HOURS, PACIFIC GAS AND ELECTRIC (PG&E) WAS NOTIFIED THAT A THIRD PARTY DAY LABORER HIRED BY A HOMEOWNER, STRUCK A 1/2-INCH PLASTIC GAS DISTRIBUTION SERVICE LINE. THE DAY LABORER WAS USING A PICK IN THE HOMEOWNER'S FRONT YARD TO EXCAVATE FOR THE SEWER LINE, WHEN HE STRUCK THE GAS LINE AND CAUSED A RELEASE OF GAS. THE HOMEOWNER AND THE LABORER DID NOT NOTIFY USA PRIOR TO DIGGING. THE GAS IGNITED AND CAUSED OVER $50,000 WORTH OF DAMAGE TO A NEARBY FOUR-PLEX PROPERTY. PG&E'S GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SCENE AT 1455 HOURS AND THE FLOW OF GAS WAS STOPPED AT 1550 HOURS BY DIGGING AND SQUEEZING THE 1/2-INCH PLASTIC LINE. TWO CUSTOMERS EXPERIENCED GAS SERVICE INTERRUPTION AT THIS BRANCH SERVICE LOCATION AND WERE RESTORED BY MARCH 16, 2013 AT 1527 HOURS. THERE WERE NO INJURIES, NO FATALITIES AND LESS THAN 3 MILLION CUBIC FEET OF GAS WAS RELEASED. THIS INCIDENT WAS REPORTED TO THE CPUC AND DOT BECAUSE THE COST OF DAMAGES IS GREATER THAN $50,000 AND MAJOR BAY AREA NEWS MEDIA WAS PRESENT ON SCENE.
2025-03-31 10:13 | NO | YES | NO | 20130042 | 15642 | 2013-04-18 08:34 | ORIGINAL | 24015 | YANKEE GAS SERVICES CO | 107 SELDEN STREET | BERLIN | CT | 06037 | 2013-03-18 11:00 |  |  | 2013 | 55-61 PROCTOR STREET | WATERBURY | NEW HAVEN | CT | 06706 | 41.5376 | -73.0244 | [9 empty] | 2013-03-18 01:32 | 1041385 |  | NATURAL GAS |  | 3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 15 | 2013-03-18 11:33 |  |  |  | 2013-03-18 11:54 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | CRAWLSPACE BENEATH BUILLDING |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1960 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | PIPE WAS CUT BY USE OF AN ELECTRICALLY POWERED RECIPROCATING SAW. | CLASS 3 LOCATION | 750000 | 936634.58705685975 | 3903 | 4874.246391043898139 | 3909 | 4881.739467740353017 | 0 | 0 |  |  | 24 | 21 |  | 0 | 757836 | 391986.0180001063245653114754098360655738 | 946411.572915644001156 | 0 | 0 | 80 |  |  |  |  | 58 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR RELEASE OF GAS NOT DETECTABLE BY SCADA. | [12 empty] | NO |  |  | YES | 1 | 0 | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | VENDOR EMPLOYEE CUT PIPE THAT WAS ASSUMED TO BE OUT OF SERVICE. | [47 empty] | GARRY DAIGLE | PRINCIPAL ENGINEER | garry.daigle@nu.com | 203-596-3149 | 203-596-3130 |  |  |  | BRET FACTORA | MANAGER ENGINEERING GIS | 203-596-3071 | bret.factora@nu.com | VENDOR EMPLOYEE WAS REMOVING ABOVEGROUND ABANDONED PIPE AS PART OF PIPELINE REPLACEMENT PROJECT. PIPING WAS LOCATED IN CRAWL SPACE OF THE BUILDING. THE VENDOR BEGAN CUTTING THE PIPE AT THIS LOCATION AND REALIZED THAT THE PIPE WAS STILL ACTIVE. BUILDING OCCUPANTS WERE EVACUATED, BUILDING CAUGHT FIRE AND WAS DAMAGED AND SUBSEQUENTLY WAS DEMOLISHED.
2025-03-31 10:13 | NO | YES | YES | 20130043 | 15643 | 2013-04-18 14:28 | ORIGINAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2013-03-19 11:40 |  |  | 2013 | 1752 N 7TH ST | GRAND JUNCTION | MESA | CO | 81501- | 39.0836 | -108.5606 | [9 empty] | 2013-03-19 13:35 | 1041528 |  | NATURAL GAS |  | 34 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES |  |  |  |  | YES | 285 | 2013-03-19 11:53 |  |  |  | 2013-03-19 12:11 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 58 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1952 | [5 empty] | 6 | API 5L | UNKNOWN | STEEL |  | OTHER | ASSUMED ERW | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 525000 | 655644.210939801825 | 27133 | 33884.941667485034129 | 27133 | 33884.941667485034129 | 173080 | 216150.28577040171404 | OPERATOR'S RESTORATION AND RELIGHTING |  | 138 | 120.75 |  | 0 | 752484 | 389251.0882300620683495409836065573770492 | 939685.130045173607298 | 3 | 0 | 110 |  |  |  |  | 150 | 150 | 150 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE MONITORED BY SCADA WITH NO APPRECIABLE DIFFERENTIAL PRESSURE DETECED | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TRAFFIC SIGNAL | YES | 307200051 |  |  | CONTRACT LOCATOR | YES | YES | 72 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | MARIO LOPEZ | INVESTIGATOR | mario.e.lopez@xcelenergy.com | 303-294-2848 | 303-294-2311 |  |  |  | JOHN KARTUS | MANAGER CLAIMS SERVICES | 303-294-2665 | john.j.kartus@xcelenergy.com | DAMAGE RESULTED WHEN THIRD PARTY CONTRACTOR STRUCK GAS MAIN WITH DIRECTIONAL DRILLING EQUIPMENT
2025-03-31 10:13 | NO | YES | NO | 20130044 | 15644 | 2013-04-19 13:52 | ORIGINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2013-03-20 08:45 |  |  | 2013 | 511 EWING STREET | PRINCETON TOWNSHIP | MERCER | NJ | 08540 | 40.3675 | -74.6567 | [9 empty] | 2013-03-20 10:10 | 1041596 |  | NATURAL GAS |  | 206.643 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-03-20 08:45 |  |  |  | 2013-03-20 09:10 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 8 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | DRIP RISER | 1968 | [8 empty] | STEEL |  |  |  | 0.133 | [6 empty] | OTHER | [8 empty] | DAMAGE | CLASS 3 LOCATION | 750000 | 936634.58705685975 | 5000 | 6244.230580379065 | 10000 | 12488.46116075813 | 0 | 0 |  |  | 1125 | 984.375 |  | 0 | 766125 | 396595.0786317360263114754098360655737705 | 956351.653797996945 | 0 | 0 | 5 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | MILLING EQUIPMENT | MILLING | YES | 130701758 | N/A |  | UTILITY OWNER | NO | YES | 7 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | FRANKY CORIANO | PRINCIPLE REGULATORY SPECIALIST | franky.coriano@pseg.com | 609.421.8008 |  |  |  |  | RICHARD F. LEWIS | DIRECTOR GAS SYSTEMS OPS AND TEHNICAL SERVICES | 973-430-7049 | richard.lewis@pseg.com | ON MARCH 20, 2013 AT APPROXIMATELY 8:45 A.M., TOP LINE CONSTRUCTION CORP. WORKFORCES WERE EXCAVATING THE EXISTING ROAD SURFACE ON EWING STREET, PRINCETON TOWNSHIP WITH A MILLING MACHINE, AS PART OF AN ONGOING ROAD RECONSTRUCTION PROJECT FOR PRINCETON TOWNSHIP. DURING THE PERFORMANCE OF THIS WORK STRUCK AN UNMARKED GAS MAIN 3/4 INCH DRIP RISER THAT WAS BURIED AND PAVED OVER WITH THE MILLING MACHINE'S DRUM. THE MILLING MACHINE IGNITED AS A RESULT OF THE CONTACT AND BURNED FOR SEVERAL HOURS, UNTIL PUBLIC SERVICE ELECTRIC AND GAS COMPANY ("PSE&G") ISOLATED THE MAIN AND SHUT-OFF THE GAS. AS A RESULT, FIVE RESIDENCES WERE WITHOUT SERVICE UNTIL THE MILLING MACHINE COULD BE REMOVED AND GAS FACILITIES REPAIRED. GAS SERVICE WAS RESTORED AT APPROXIMATELY 9:00 P.M. AT NIGHT.
2025-03-31 10:13 | NO | YES | YES | 20130045 | 15967 | 2013-04-22 10:56 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2013-03-26 18:56 |  |  | 2013 | 299 PEARL STREET | NEW YORK | NEW YORK | NY | 10038-1847 | 40.708 | -74.0035 | [9 empty] | 2013-03-26 20:10 | 1042181 | [5 empty] | NO | [5 empty] | 0 | YES | 0 | 2 | 0 | 0 | 0 | 2 | NO |  |  |  |  | NO | 0 | 2013-03-26 18:56 |  |  |  | 2013-03-26 18:56 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 27 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1961 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | CAUSE OF INCIDENT UNDER INVESTIGATION. | CLASS 4 LOCATION | 0 | 0 | 5000 | 6244.230580379065 | 500 | 624.4230580379065 | 500 | 624.4230580379065 | MATERIALS |  | 20 | 17.5 |  | 0 | 6020 | 3119.596164774785934426229508196721311475 | 7510.576696454878 | 0 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER | 718-319-2350 | dadariov@coned.com | ON MARCH 26, 2013 AT 18:56, A MANHATTAN GAS OPERATIONS (MGO) PLANNER REPORTED TO THE GAS EMERGENCY RESPONSE CENTER THAT HALLEN CONSTRUCTION MAINTENANCE MECHANIC DEAN LEWIS, #C0083 AND SAFEWAY INC. LABORER VEVAKANAND HARRICHARAN, #C3162, WERE TAKEN BY AMBULANCE TO CORNELL HOSPITAL WITH BURNS TO THEIR FACE AND HANDS SUSTAINED WHEN AN ELECTRIC FEEDER OVER THE GAS MAIN FLASHED AS THEY WERE WORKING TO REPAIR A TYPE 1 GAS LEAK. THE CONTRACTORS WERE WORKING FOR MANHATTAN GAS OPERATIONS AND ASSIGNED TO TYPE 1 LEAK (ML13001012), WHICH WAS INITIALLY REPORTED ON FEBRUARY 7, 2013, DUE TO POSITIVE READING IN ELECTRIC MANHOLE M60941 AT THIS LOCATION. THE CONTRACTOR CREWS WERE WORKING TO EXPOSE AND ENCAPSULATE A COMPRESSION COUPLING ON AN 8" LOW PRESSURE STEEL MAIN, LOCATED BELOW ELECTRIC FEEDER 40M34, WHEN THE FEEDER "OPENED-AUTO". BOTH CONTRACTOR EMPLOYEES WERE ADMITTED TO CORNELL HOSPITAL. MR. LEWIS SUSTAINED A BURN TO HIS FOREHEAD AND A SIGNIFICANT BURN TO HIS RIGHT HAND. MR. HARICHARIN SUSTAINED DEBRIS IN HIS LEFT EYE AND IS EXPECTED TO MAKE A FULL RECOVERY. ON MARCH 27, 2013 AT 08:52, MANHATTAN ELECTRIC CONTROL CENTER ISSUED AN ORDER PREVENTING ANYONE FROM WORKING IN THE OPEN EXCAVATION. MGO WORKED AROUND-THE-CLOCK TO RELOCATE THE GAS SERVICE TO BUILDING 6 OF SOUTHBRIDGE TOWERS, A HOUSING COMPLEX AT THIS LOCATION. THE GAS SERVICE WAS RELOCATED AND THE LOW PRESSURE STEEL MAIN INVOLVED WITH THIS INCIDENT WAS CUT AND CAPPED FOR SAFETY. ELECTRIC OPERATIONS MADE THE NECESSARY REPAIRS TO RETURN THE FEEDER TO OPERATION. THE INCIDENT INVESTIGATION DETERMINED THERE WAS NO GAS IGNITION. THE HALLEN CONTRACTOR WAS WORKING TO LOCATE A GAS LEAK, PIERCED AN ELECTRIC CONDUCT AND HIT AN ENERGIZED ELECTRIC CABLE. HALLEN CONSTRUCTION MECHANIC LEWIS WAS HOSPITALIZED DUE TO THE INJURIES SUSTAINED. THE US DOT, NYS PSC & NYC DEP WERE NOTIFIED. THE PSC INQUIRED ABOUT THIS INCIDENT AND OSHA AND THE PSC RESPONDED TO THE LOCATION.
2025-03-31 10:13 | NO | YES | NO | 20130046 | 15786 | 2013-04-22 12:27 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2013-03-24 09:45 |  |  | 2013 | 6455 EL CAMINO ROAD | ATASCADERO | SAN LUIS OBISPO COUNTY | CA | 93422 | 35.4877 | -120.6691 | [9 empty] | 2013-03-24 15:00 | 1041990 |  | NATURAL GAS |  | 150 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-03-24 09:45 |  |  |  | 2013-03-24 09:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 21 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1952 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | ERW | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 0.7 | [7 empty] | CLASS 3 LOCATION | 25000 | 31221.152901895325 | 470000 | 586957.67455563211 | 5000 | 6244.230580379065 | 0 | 0 |  |  | 1000 | 875 |  | 0 | 501000 | 259426.7295782266967213114754098360655738 | 625298.0580379065 | 50 | 0 | 700 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HIGH PRESSURE WATER LEAK SCOURED HOLE IN 2" STEEL NATURAL GAS MAIN | [154 empty] | W. JEFF KOSKIE | PIPELINE SAFETY AND COMPLIANCE MANAGER | wkoskie@semprautilities.com | 213 305-8660 | 213 244-8155 |  |  |  | W. JEFF KOSKIE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 213 305-8660 | wkoskie@semprautilities.com | PRESSURE FROM LEAKING WATER MAIN SCOURED NEARBY 2" STEEL MAIN, CAUSING WATER TO ENTER MAIN AND DROP SERVICE TO 701 CUSTOMERS. GAS MAIN REPAIRED, WATER REMOVED FROM MAINS AND SERVICES. WATER LINE REPAIRED BY WATER DEPARTMENT. NO INJURIES, NO IGNITION. BECAME REPORTABLE WHEN REPAIR/RESTORATION ESTIMATE MET $50,000 REPORTING THRESHOLD.
2025-03-31 10:13 | NO | YES | NO | 20130047 | 15649 | 2013-04-24 16:02 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2013-03-15 02:56 |  |  | 2013 | 1300 EAST SHAW AVENUE | FRESNO | FRESNO | CA | 93710 | 36.8094 | -119.7661 | [10 empty] | 1041175 |  | NATURAL GAS |  | 1690 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2013-03-15 02:56 |  |  |  | 2013-03-15 03:10 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 87 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1950 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | 3RD PARTY BORING FOR FIBER OPTIC STRUCK STEEL GAS LINE AND PUNCTURED THREE SMALL HOLES IN THE PIPE | CLASS 3 LOCATION | 1000 | 1248.846116075813 | 292000 | 364663.065894137396 | 5000 | 6244.230580379065 | 0 | 0 |  |  | 2000 | 1750 |  | 0 | 300000 | 155754.7652548526194426229508196721311475 | 373906.142590592274 | 2 | 0 | 0 |  |  |  |  | 195 | 195 | 204 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE IS NO SCADA ON THIS PORTION OF THE SYSTEM | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | CABLE TV | NO |  |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED | YES | 90 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CHERYL DIZON | GAS ENGINEER | c1dz@pge.com | 925-974-4378 | 925-974-4232 |  |  |  | FRANCES YEE | REGULATORY COMPLIANCE AND SUPPORT DIRECTOR | 925-974-4316 | fsc2@pge.com | ON MARCH 15, 2013, AT APPROXIMATELY 0256 HOURS, PACIFIC GAS AND ELECTRIC (PG&E) WAS NOTIFIED THAT A THIRD PARTY EXCAVATOR, ATAZZ TECHNICAL SERVICES, WAS BORING UNDER EAST SHAW AVENUE IN FRESNO AND STRUCK A 6-INCH STEEL GAS DISTRIBUTION FEEDER MAIN (DFM) 1202-09, RESULTING IN A RELEASE OF GAS. PG&ES GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SITE AT 0310 HOURS AND GAS SERVICE WAS SHUT OFF TO TWO NEARBY COMMERCIAL CUSTOMERS. PG&E CREWS STOPPED THE FLOW OF GAS AT 0349 HOURS ON MARCH 16, 2013 BY WELDING TWO PRESSURE CONTROL FITTINGS ONTO THE 6-INCH LINE. THE EXCAVATOR WAS OPERATING UNDER AN EXPIRED USA TICKET (#037122) AND DID NOT REQUEST A PG&E STANDBY FOR THE EXCAVATION WORK. PERMANENT REPAIRS TO THE DFM WERE COMPLETED BY REMOVING THE DAMAGED SECTION AND WELDING ON A NEW PUP. THE PIPE WAS PUT INTO SERVICE AT APPROXIMATELY 1430 HOURS ON MARCH 16, 2013 AND THE TWO CUSTOMERS WHO EXPERIENCED SERVICE INTERRUPTION WERE RESTORED AT 1111 HOURS ON MARCH 18, 2013. OUT OF AN ABUNDANCE OF CAUTION, THE AREA WAS BLOCKED OFF, NEIGHBORING BUILDINGS WERE EVACUATED AND EAST SHAW AVE WAS CLOSED TO TRAFFIC. THERE WERE NO INJURIES, NO FATALITIES AND NO IGNITION AS A RESULT OF THIS INCIDENT. THE VOLUME OF GAS UNINTENTIONALLY RELEASED WAS LESS THAN 3 MILLION CUBIC FEET. THIS INCIDENT WAS REPORTED TO THE CPUC AND DOT BECAUSE THE COST OF DAMAGES IS IN EXCESS OF $50,000.
2025-03-31 10:13 | YES | NO | NO | 20130048 | 15831 | 2013-04-26 17:48 | SUPPLEMENTAL FINAL | 12876 | QUESTAR GAS COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2013-03-29 11:37 |  |  | 2013 | 7245 SOUTH HWY 165 | HYRUM | CACHE | UT | 84328 | 41.6008 | -111.836 | [9 empty] | 2013-04-02 16:36 | 1042750 |  | NATURAL GAS |  | 32 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2013-03-29 12:19 |  |  |  | 2013-03-29 12:47 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2003 | [8 empty] | OTHER | AMERICAN METER AC250, METER ID 46012106 | [9 empty] | OTHER | [8 empty] | METER MELTED IN HOUSE FIRE | CLASS 1 LOCATION | 100000 | 124884.6116075813 | 500 | 624.4230580379065 | 1000 | 1248.846116075813 | 0 | 0 |  |  | 150 | 131.25 |  | 0 | 101650 | 52620.7265142160850081967213114754098361 | 126889.1307816950195 | 0 | 0 | 1 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | JEFFREY D. HANSEN | MANAGER | jeff.hansen@questar.com | 801-324-3645 |  |  |  |  | VAUGHN W. SHOSTED | GENERAL MANAGER | 801-324-3384 | vaughn.shosted@questar.com | HOME OWNER WAS COOKING OUTSIDE IN THE CARPORT WITH A PROPANE FUELED BARBECUE. THE HOME CAUGHT ON FIRE. THE CAUSE OF THE FIRE IS UNDETERMINED. THE GAS METER WAS NEARBY AND WAS MELTED IN THE FIRE.
2025-03-31 10:13 | YES | NO | NO | 20130049 | 15651 | 2013-05-01 10:48 | ORIGINAL FINAL | 17360 | RICHMOND, CITY OF | 730 E. BROAD STREET | RICHMOND | VA | 23219 | 2013-04-07 09:45 |  |  | 2013 | 2832 DOVER HUNT PLACE | HENRICO |  | VA | 23233 | 37.6327 | -77.5859 | [9 empty] | 2013-04-07 11:28 | 1043186 | [5 empty] | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-04-07 09:45 |  |  |  | 2013-04-07 10:22 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1995 | [5 empty] | 1 | D2513 | YELLOWSTRIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 3408 | OTHER | [8 empty] | METER & REGULATOR DESTROYED IN FIRE | CLASS 3 LOCATION | 0 | 0 | 23 | 28.723460669743699 | 100 | 124.8846116075813 | 600 | 749.3076696454878 | ADDITIONAL |  | 0 | 0 |  | 0 | 723 | 373.960620642246951 | 902.915741922812799 | 0 | 0 | 1 |  |  |  |  | 20.8 | 22 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | CARL V. JAMES | GAS MAINTENANCE OPERTIONS MANAGER | carl.james@richmondgov.com | 804-646-8321 | 804-646-8399 |  |  |  | CARL V. JAMES |  | 804-646-8399 | No Email Address | THIS IS A FOLLOW-UP TO THE TELEPHONE CALL PLACED ON APRIL 7, 2013. INCIDENT REPORT #1043186, WHICH OCCURRED AT 2832 DOVER HUNT PL., HENRICO, VA. A FIRE, UNRELATED TO NATURAL GAS, WAS THE PRIMARY CAUSE OF THE INCIDENT. THE ORIGIN OF THE FIRE WAS ELECTRICAL IN NATURE. THE CITY OF RICHMOND PERFORMED A SERIES OF TESTS WHICH INCLUDED A LEAK SURVEY OF THE OUTER PERIMETER OF THE BUILDING, BAR HOLE TEST, AND A PRESSURE TEST OF THE GAS SERVICE. DURING THE FIRE,THE METER & REGULATOR WAS DESTROYED, A PRESSURE TEST REVEALED NO LEAK DETECTEDON THE SERVICE LINE. ALSO, THE CITY OF RICHMOND, DEPARTMENT OF PUBLIC UTILITIES, HAD AN ODOROMETER TEST PERFORMED BY THE SUPERVISOR OF PRESSURE CONTROL AND FOUND THE ODORANT TO BE IN THE ACCEPTABLE RANGE.
2025-03-31 10:13 | NO | YES | NO | 20130050 | 15833 | 2013-05-09 18:38 | SUPPLEMENTAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2013-04-12 08:03 |  |  | 2013 | 1118 E. BRIDGEPORT AVE | SPOKANE | SPOKANE | WA | 99207-2811 | 47.6883 | -117.3931 | [9 empty] | 2013-04-12 11:26 | 1043770 |  | NATURAL GAS |  | 39.22 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2013-04-12 08:03 |  |  |  | 2013-04-12 08:25 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 28 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2005 | [5 empty] | 0.75 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | OTHER | [8 empty] | FULLY SEVERED PIPE. | CLASS 3 LOCATION | 105000 | 131128.842187960365 | 1900 | 2372.8076205440447 | 350 | 437.09614062653455 | 40000 | 49953.84464303252 | COST OF RENTAL EXCATION EQUIPMENT |  | 99 | 86.625 |  | 0 | 147349 | 76242.9290329189097254098360655737704918 | 183979.21559216346425 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, BUT THE INVESTIGATION OF THE CONTROL ROOM AND/OR CONTROLLER ACTIONS HAS NOT YET BEEN COMPLETED BY THE OPERATOR (SUPPLEMENTAL REPORT REQUIRED) | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 13081658 | ONE CALL CONCEPTS |  | CONTRACT LOCATOR | NO | YES | 5 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | JODY MOREHOUSE | MANAGER PIPELINE INTEGRITY AND COMPLIANCE | jody.morehouse@avistacorp.com | 509-495-2760 | 509-777-5625 |  |  |  | JODY MOREHOUSE | MANAGER PIPELINE INTEGRITY AND COMPLIANCE | 509-495-2760 | jody.morehouse@avistacorp.com | A CONTRACTOR INSTALLING A SEWER LINE AT A RESIDENTIAL HOME STRUCK A 3/4" PE NATURAL GAS SERVICE OPERATING AT APPROXIMATELY 55 PSIG. THE RELEASE OF NATURAL GAS CAUGHT THE MINI BACKHOE ON FIRE WHICH THEN CAUGHT THE HOUSE ON FIRE. THE CONTRACTOR HAD A VALID LOCATE TICKET. WHETHER OR NOT THE SERVICE WAS LOCATED PROPERLY IS UNDER DISPUTE. THE GAS METER WAS LESS THAN 10 FEET FROM THE POINT OF DAMAGE AND VISIBLE ABOVE GROUND FROM THE POINT OF DAMAGE. NO INJURIES RESULTED FROM THE FIRE. SERVICE WAS TEMPORARILY LOST TO ONE CUSTOMER.
2025-03-31 10:13 | NO | NO | NO | 20130051 | 15714 | 2013-05-14 17:31 | SUPPLEMENTAL FINAL | 13360 | ENTERGY NEW ORLEANS, INC | 3700 TULANE AVENUE L-TUL-111 | NEW ORLEANS | LA | 70119 | 2013-04-14 17:03 |  |  | 2013 | 1811 N GALVEZ STREET | NEW ORLEANS | ORLEANS | LA | 70119 | 29.9782 | -90.0653 | [9 empty] | 2013-04-14 19:15 | 1043932 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-04-14 17:40 |  |  |  | 2013-04-14 17:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | CUSTOMER PIPING | UNKNOWN | [8 empty] | OTHER | FLEX-TUBING BEHIND RANGE. | [9 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 75000 | 93663.458705685975 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 75000 | 38792.595502307775 | 93663.458705685975 | 0 | 0 | 1 |  |  |  |  | 80 | 80 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | DOG BROKE FLEX TUBING CONNECTION BEHIND RANGE. LEAKING GAS FOUND AN IGNITION SOURCE CAUSING A FLASH FIRE THAT DESTROYED THE RESIDENCE. | [47 empty] | LEON T HINSON | SR. ENGINEER - COMPLIANCE COORDINATOR | lhinson@entergy.com | 504-595-3722 | 504-593-3440 |  |  |  | DAVID B PETERSON | MANAGER - ENGINEERING AND PLANNING | 504-595-3725 | dpeter4@entergy.com | ON SUNDAY APRIL 14, 2013 DISPATCH RECEIVED FIRE CALL FROM FIRE DEPARTMENT AT 17:03. FIRE CALL TICKET WAS GENERATED AND SENT TO SERVICE TECHNICIAN WHO ARRIVED ON THE SCENE AT 17:10. AT THIS TIME ENTERGY DID NOT KNOW IF GAS WAS INVOLVED IN THE FIRE. AT 17:40 SERVICE TECH WAS ALLOW TO APPROACH METER AN TURN OFF GAS. THIS IS THE TIME WE CONSIDER FIRST KNOWLDEGE OF GAS INVOLVEMENT. PHMSA STATE PARTNER LA DEPT OF NATURAL RESOURCES, OFFICE OF CONSERVATION, PIPELINE DIVISION WAS CONTACTED AT 18:17; NRC WAS NOTIFIED AT 19:15. AT APPROXIMATELY 18:13,DUTY SUPERVISOR RECEIVED A CALL FROM THE GAS DISPATCHER REGARDING A GAS EXPLOSION LOCATED AT 1811 N. GALVEZ ST.DUTY SUPERVISOR ARRIVED AT THE SCENE AT 18:40. UPON ARRIVAL,HE OBSERVED THAT THE FIRE HAD BEEN CONTAINED. HE SPOKE TO THE FIRE CHIEF TO GET A SUMMARY OF WHAT HE HAD OBSERVED. FIRE CHIEF REPORTED THAT THE INITIAL FIRE STARTED IN THE KITCHEN BY THE FAMILY'S DOG. THE FIRE CHIEF REPORTED THAT THE DOG HIT THE FLEX LINE THAT WAS CONNECTED TO THE STOVE; THIS IS WHAT CAUSED THE POSSIBLE EXPLOSION AND THE FIRE. DURING HIS INVESTIGATION, DUTY SUPERVISOR DISCOVERED THAT THE HOME OWNERS TAMPERED WITH ENTERGY'S GAS EQUIPMENT. A REGULATOR WAS COMING OUT OF THE GROUND WITH A NIPPLE ATTACHED TO IT. THE NIPPLE WAS GOING THROUGH THE HOME OWNER'S WALL. DUTY SUPERVISOR ALSO DISCOVERED A FLEX LINE CONNECTED TO THE NIPPLE WHICH WENT TO THE GAS METER HEADER. THIS ILLEGALLY SUPPLIED THE HOME WITH GAS. DUTY SUPERVSISOR CALLED OUT FOR A REPAIR CREW APPROXIMATELY 19:00 TO CUT THE GAS SERVICE OFF. THE CREW ARRIVED ON THE SCENE AT 19:49. DUTY SUPERVISOR ALSO PLACED A CALL OUT TO MEASUREMENT TO PERFORM AN ODOROMETER TEST. TECHNICIAN ARRIVED ON THE SCENE AT 20:33. TECHNICIAN REPORTED THAT THERE WAS A 1.5 ODORANT LEVEL IN THE PIPE. AT 19:04 HOMEOWNER STATED HER SON WAS IN THE KITCHEN WHEN THE FIRE STARTED.THE SON ATTEMPTED TO PUT THE FIRE OUT WITH A FIRE EXTINGUISHER. HOWEVER, HE WAS UNSUCCESSFUL AT CONTAINING THE FIRE. HOMEOWNER WAS TOLD BY HER SON THAT AFTER BEING UNSUCCESSFUL AT CONTAINING THE FIRE, HE DECIDED TO JUMP OUT OF THE WINDOW. HOMEOWNER ALSO REPORTED THAT HER DOG PERISHED IN THE FIRE. IN CONCLUSION, AT 19:12 DUTY SUPERVISOR SOPE FIRE DEPARTMENT CAPTAIN ON THE SCENE. DUTY SUPERVISOR ASKED CAPTAIN TO WITNESS (ENTERGY) REMOVE THE REGULATOR AND THE NIPPLE WHICH WAS CONNECTED TO THE FLEX LINE. CAPTAIN WAS ALSO ASKED TO WITNESS (ENTERGY) CRACK THE VALVE OPEN TO DETERMINE IF THE SMELL OF GAS WAS PRESENT. CA0PTAIN REPORTED THAT THE SMELL OF GAS WAS PRESENT.
2025-03-31 10:13 | NO | NO | NO | 20130052 | 15658 | 2013-05-22 06:14 | ORIGINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2010-11-12 09:52 |  |  | 2010 | 490 HUNTS POINT AVENUE | BRONX |  | NY | 10474-7012 | 40.8104 | -73.881 | [9 empty] | 2010-11-12 10:25 |  |  | NATURAL GAS |  | 17 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 16 | 2010-11-12 09:52 |  |  |  | 2010-11-12 10:04 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | DAMAGE BY VEHICLE/EQUIPMENT | CLASS 4 LOCATION | 0 | 0 | 1200 | 1585.331394140868 | 4174 | 5514.31103261998586 | 0 | 0 | 0 |  | 100 | 69.09385113268608414239482200647249190939 |  | 0 | 5474 | 3004.374822907485589527508090614886731392 | 7168.736277893539944142394822006472491909 | 0 | 0 | 0 |  |  |  |  | 280 | 280 | 350 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | KEVIN FAGAN | MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2310 | dadariov@coned.com | ON NOVEMBER 12, 2010, AT 09:52 THE NEW YORK CITY FIRE DEPTARTMENT (FDNY) REPORTED A CONTRACTOR DAMAGE AT 490 HUNTS POINT AVE., BRONX, NEW YORK TO THE GAS EMERGENCY RESPONSE CENTER (GERC). THE FDNY STATED THAT THEY WERE EVACUATING SURROUNDING PROPERTIES. A CODE MURRE (MULTIPLE RESOURCE RESPONSE EVENT) WAS INITIATED AND THE GERC DISPATCHED GAS DISTRIBUTION SERVICES (GDS), GAS EMERGENCY RESPONSE GROUP (ERG), CONSTRUCTION EMERGENCY RESPONSE FORCE (ERF) AND BRONX GAS OPERATIONS SUPERVISION. A THIRD PARTY FORK LIFT (OPERATED BY LUIS MEJIA, AN EMPLOYEE OF HERNANDEZ PRODUCTS CORPORATION) HIT A TRANSMISSION PRESSURE GAUGE POST CAUSING A LEAK AT TRANSMISSION PRESSURE ON A 1" STEEL GAUGE LINE. GDS SHUT MAIN VALVE 7735 (4" TRANSMISSION INLET VALVE TO REGULATOR STATION GR-184) AT 10:04 HRS. TO SECURE THE LEAK. THE FDNY EVACUATED 10 PEOPLE FROM THE SIGNATURE SAVINGS BANK AT 423 HUNTS POINT AVE. AND 6 PEOPLE FROM HERNANDEZ PRODUCTS CORPORATION AT 490 HUNTS POINT AVE. PRIOR TO GDS' ARRIVAL, AND THE EVACUATION ENDED AT 10:18. GDS, CONSTRUCTION AND PRESSURE CONTROL RESPONDED TO LOCATION. CONSTRUCTION CUT AND CAPPED THE LINE, WELDERS SECURED THE PIPING, REPAIRS WERE MADE AND X-RAYED, AND THE STATION AND EFFECTED PIPELINE WERE PLACED BACK IN SERVICE AT 17:03 HOURS. THIS INCIDENT HAD NO IMPACT ON THE TRANSMISSION OR DISTRIBUTION SYSTEMS. THERE WERE NO REPORTED INJURIES, NO OUTAGES, AND NO MEDIA ATTENTION.THE US DOT, NYS PSC AND NYC DEP WERE NOTIFIED. THIS WAS AN UPGRADED LEVEL INCIDENT. NOTE--THIS GAS DISTRIBUTION INCIDENT REPORT WAS CREATED IN PLACE OF RESCINDED GAS TRANSMISSION INCIDENT REPORT #20100094-15866.
2025-03-31 10:13 | NO | YES | NO | 20130053 | 15659 | 2013-05-22 15:22 | ORIGINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2010-11-02 10:29 |  |  | 2010 | 426 EAST 4 STREET | MOUNT VERNON | WESTCHESTER | NY | 10553-1619 | 40.9068 | -73.8194 | [9 empty] | 2010-11-02 15:46 | 958763 |  | NATURAL GAS |  | 0.16 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-11-02 15:36 |  |  |  | 2010-11-02 15:36 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 72 |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1957 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 221614 | 292776.35965094526746 | 1485 | 1961.84760024932415 | 42141 | 55672.87523374193199 | MATERIALS |  | 100 | 69.09385113268608414239482200647249190939 |  | 0 | 265340 | 145193.6769213908249535275080906148867314 | 350480.1763360692096841423948220064724919 | 0 | 0 | 0 |  |  |  |  | 191 | 191 | 230 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | [197 empty] | NON-THREADED CONNECTION FAILURE | [14 empty] | OTHER | COUPLING ON DRIP RISER LEAKING AT SEAL | [67 empty] | KEVIN FAGAN | MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2310 | dadariov@coned.com | ON TUESDAY, NOVEMBER 2, 2010, THE PUBLIC REPORTED AN OUTSIDE ODOR COMPLAINT AT # 426 E 4 ST (MT. VERNON) TO THE GAS EMERGENCY RESPONSE CENTER. GAS DISTRIBUTION SERVICES (GDS) RESPONDED AND OBTAINED A 60% GAS-IN-AIR READING AT THE 20' LINE OF #426 E 4 ST. THE LEAK WAS CLASSIFIED TYPE-1 DUE TO THE PROXIMITY TO THE 24" TRANSMISSION MAIN (230 PSI). GAS CONSTRUCTION CREWS AND SUPERVISION RESPONDED, INVESTIGATED AND AT 1536 HRS IT WAS DETERMINED THE LEAK MAY BE COMING FROM THE TRANSMISSION MAIN. THE 12" 1957 STEEL TRANSMISSION INLET TO GAS REGULATOR GR-514 WAS BELIEVED TO BE THE SOURCE OF THE LEAK IN THE VICINITY OF A DRIP POT AND RISER. GR-514 WAS VALVED OFF AND THE LEAK EXCAVATED AFTER PRESSURE WAS BLED DOWN. THE EXCAVATION DETERMINED THE ACTUAL SOURCE OF THE LEAK WAS ON A 1" COUPLING IN THE DRIP RISER AT THE INLET PIPING TO GR-514. PRESSURE CONTROL, GAS CONTROL AND GAS ENGINEERING DETERMINED THERE WOULD NOT BE ANY NEGATIVE SYSTEM IMPACT DUE TO THE LOSS OF THIS TRANSMISSION PRESSURE TO HIGH PRESSURE REGULATOR STATION. TRANSMISSION VALVES 25960 AND 28563 WERE CLOSED AT 1705 HRS AND PRESSURE REDUCTION THROUGH GR-514. THE LEAKING COUPLING WAS REMOVED AND A WELDED CAP INSTALLED ON THE DRIP POT WHERE THE RISER CONNECTS TO THE DRIP POT, REMOVING THE HAZARD. THE REGULATOR STATION REMAINED OFFLINE WHILE ADDITIONAL PLANNED WORK REPLACING 70' OF THE AFFECTED SECTION OF INLET PIPING TO THE REGULATOR STATION WAS COMPLETED. THE PIPELINE WORK WAS COMPLETED, AND THE MAIN RESTORED TO FULL SERVICE ON NOVEMBER 9, 2010 AT 23:01 HRS. THE US DOT AND NYS PSC WERE NOTIFIED. NOTE--THIS GAS DISTRIBUTION INCIDENT REPORT IS GENERATED TO REPLACE RECINDED GAS TRANSMISSION INCIDENT REPORT 20100094-15867
2025-03-31 10:13 | NO | NO | NO | 20130054 | 15661 | 2013-05-22 15:38 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-10-15 08:46 |  |  | 2011 | BRONX STREET AND HAMILTON AVENUE | WHITE PLAINS | WESTCHESTER | NY | 10606 | 41.0369 | -73.7789 | [9 empty] | 2011-10-16 07:36 | 992682 |  | NATURAL GAS |  | 100 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-10-15 08:46 |  |  |  | 2011-10-15 08:46 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 60 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | ONSHORE PIPELINE, INCLUDING VALVE SITES | 1948 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 19715 | 25531.125763747454135 | 1697 | 2197.632281059063133 | 1400 | 1813.0142566191446 | MATERIALS |  | 100 | 75.84369449378330373001776198934280639432 |  | 0 | 22912 | 12305.4759475171137015488454706927175844 | 29617.6159959194451717300177619893428064 | 0 | 0 | 0 |  |  |  |  | 237 | 237 | 245 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS DETECTED BY GOUND PATROL/LEAK SURVEY. NO CONTROL ROOM FUNCTION IS RELATED TO LEAK DETECTION AS IT APPLIES TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | [197 empty] | NON-THREADED CONNECTION FAILURE | [14 empty] | OTHER | COMPRESSION COUPLING LEAK | [67 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON SATURDAY OCTOBER 15, 2011 AT 08:46 HRS A LEAK SURVEY CREW REPORTED TO THE GAS EMERGENCY RESPONSE CENTER (GERC) A TYPE-1 LEAK ALONG THE ROUTE OF THE TRANSMISSION SYSTEM AT 200' NORTH OF HAMILTON AVE ON BRONX ST., WHITE PLAINS. THE ONLY MAIN AT THIS LOCATION IS A 12" 1948 TRANSMISSION PRESSURE MAIN OPERATING AT 237 PSI AT THE TIME OF DISCOVERY. ALL CONTINGENCY VALVES WERE IDENTIFIED AND BRONX GAS OPERATIONS ASSISTED IN MANNING THESE VALVES. WESTCHESTER GAS DISTRIBUTION SERVICES, GAS CONSTRUCTION, GAS CONTROL, PRESSURE CONTROL AND CENTRAL OPERATIONS RESPONDED. OPERATIONAL PLANNING INVOLVING ALL OPERATING AREAS, PRESSURE CONTROL, GAS CONTROL, LEAK SURVEY, TRANSMISSION ENGINEERING AND MAJOR PROJECTS WAS CONDUCTED. GAS CONSTRUCTION INVESTIGATED AND IDENTIFIED THE LOCATION OF THE LEAK. GAS CONTROL REDUCED OPERATING PRESSURE TO 68 PSI. GAS CONSTRUCTION EXCAVATED AND EXPOSED A 12" COMPRESSION COUPLING LEAKING AT BOTH END RINGS. THE COUPLING WAS TIGHTENED TO TEMPORARILY SECURE THE LEAK. GAS CONSTRUCTION INSTALLED A PRE-FABRICATED WELDED REPAIR SLEEVE. WELDING OPERATIONS WERE COMPLETED ON OCTOBER 16, 2011 AT 09:15 HRS. THE REPAIR SLEEVE WAS PRESSURE TESTED AND FOUND OK . CORROSION OPERATIONS INSPECTED THE MAIN AND SAME WAS CLEANED AND COATED. LEAK SURVEY CONDUCTED A MOBILE SURVEY OF ISOLATED SECTION OF MAIN AND NO LEAKS WERE FOUND. GAS CONTROL RETURNED ROV-32717 TO THE FULLY OPENED POSITION AT 108 HRS AND PRESSURE RETURNED TO 234 PSI. AT 14:04 HRS., VALVES 25978 AND 25979 WERE FULLY OPENED. LEAK SURVEY COMPLETED THEIR SURVEY OF THE AREA AND DETECTED NO LEAKS. BACKFILLING OPERATIONS STARTED AT 14:58 HRS AND THE INCIDENT COMMAND STRUCTURE WAS TERMINATED. THE NYS PUBLIC SERVICE COMMISSION AND THE US DEPARTMENT OF TRANSPORTATION WERE NOTIFIED. THE NATIONAL TRANSPORTATION SAFETY BOARD CALLED FOR INFORMATION. THIS WAS A SERIOUS LEVEL INCIDENT. NOTE--THIS GAS DISTRIBUTION INCIDENT REPORT IS GENERATED TO REPLACE RESCINDED GAS TRANSMISSION INCIDENT REPORT 20110381-15383
2025-03-31 10:13 | NO | NO | NO | 20130055 | 15662 | 2013-05-22 15:50 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-04-19 10:03 |  |  | 2011 | LINCOLN AVENUE AND BROOKSIDE WAY | TOWN OF HARRISON | WESTCHESTER | NY | 10573 | 41.0192 | -73.6939 | [9 empty] | 2011-04-19 13:26 | 973442 |  | NATURAL GAS |  | 0.16 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-04-19 10:03 |  |  |  | 2011-04-19 10:03 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1970 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 20943 | 27121.398268839103827 | 0 | 0 | 1000 | 1295.010183299389 | WELDED ALEEVES & WELDER |  | 100 | 75.84369449378330373001776198934280639432 |  | 0 | 22043 | 11839.3839923236312485488454706927175844 | 28492.2521466322761307300177619893428064 | 0 | 0 | 0 |  |  |  |  | 212 | 212 | 245 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | NO | NO | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | [197 empty] | NON-THREADED CONNECTION FAILURE | [14 empty] | OTHER | MECHANICAL COUPLING ON DRIP RISER LEAKING AT SEAL | [67 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON APRIL 18, 2011 A WESTCHESTER GAS DISTRIBUTION SERVICES (GDS) MECHANIC PERFORMED A TRANSMISSION DRIP INSPECTION SURVEY AND DETECTED 35% GAS-IN-AIR READING IN THE REGULATOR MANHOLE OF STATION GR-498 LOCATED AT LINCOLN AVENUE AND BROOKSIDE WAY, HARRISON. THE GAS EMERGENCY RESPONSE CENTER (GERC) DISPACTHED GAS CONSTRUCTION CREWS AND SUPERVISORS TO THE LOCATION. THE LEAK WAS INVESTIGATED AND A 1" LUBRICATING VALVE ON A DRIP RISER WAS DETERMINED TO BE THE SOURCE OF THE LEAK. THE VALVE WAS SERVICED AND THE LEAK SECURED. THE AREA OF WORK WAS LEFT PLATED AND SECURED OVERNIGHT. ON APRIL 19, 2011, THE LOCATION WAS SURVEILLED DURING AN INSPECTION OF THE PIPING AND A LEAK CONDITION WAS FOUND. AN OPERATIONAL PLAN WHICH WAS PREVIOUSLY DEVELOPED WAS IMPLEMENTED AFTER A LEAK ON A 1" DRIP RISER COMPRESSION COUPLING AT THE INLET OF THIS REGULATOR STATION WAS DETECTED. THE PLAN CALLED FOR ISOLATION OF THE FIRST STAGE OF GR-498 (212 PSI INLET) WHICH SUPPLIES A 60 PSI HIGH PRESSURE DISTRIBUTION SYSTEM. THE EFFECTED SECTION OF TRANSMISSION PRESSURE PIPE WAS ISOLATED, DEPRESSURIZED AND THE LEAK CONDITION ELIMINATED. THERE WAS NO REDUCTION IN PRESSURE OF THE HIGH PRESSURE SYSTEM, OR LOSS OF CUSTOMERS, AS A RESULT OF THESE ACTIONS. GAS CONSTRUCTION, GDS, PRESSURE CONTROL AND TRANSMISSION ENGINEERING REMAINED ON LOCATION UNTIL WORK WAS COMPLETED FOR THE REMOVAL OF THE STANDPIPE AND COUPLING AND THE INSTALLATION OF A WELDED HIGH-HAT. GR-498-L1 WAS PLACED BACK IN NORMAL SERVICE UPON COMPLETION OF ALL WORK AT 23:49 HRS ON APRIL 19, 2011. THE US DOT AND NYS PSC WERE NOTIFIED. THIS IS A SERIOUS LEVEL EVENT. NOTE--THIS GAS DISTRIBUTION INCIDENT REPORT IS GENERATED TO REPLACE RESCINDED GAS TRANSMISSION INCIDENT REPORT 20110048-15869
2025-03-31 10:13 | NO | YES | NO | 20130056 | 15663 | 2013-05-22 16:19 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2011-01-19 05:53 |  |  | 2011 | WEST 135 STREET AND AMSTERDAM AVENUE | NEW YORK |  | NY | 10031 | 40.8192 | -73.9523 | [9 empty] | 2011-01-19 06:07 | 965080 |  | NATURAL GAS |  | 9.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2011-01-19 05:53 |  |  |  | 2011-01-19 20:32 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 57 |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1980 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 129395 | 167567.842668024439655 | 3704 | 4796.717718940936856 | 0 | 0 |  |  | 67 | 50.81527531083481349911190053285968028419 |  | 0 | 133166 | 71435.2385711908130855577264653641207815 | 172415.3756622762113244991119005328596803 | 0 | 0 | 0 |  |  |  |  | 288 | 288 | 350 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | VALVE | MATERIAL/WELD/EQUIP FAILURE | VALVE | EQUIPMENT FAILURE | VALVE | [197 empty] | VALVE | [16 empty] | OTHER | ELASTOSEAL VALVE LEAK WHICH COULD NOT BE REPAIRED; REQUIRED REPLACEMENT | [65 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON 1-17-11 THE GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A REPORT OF AN OUTSIDE GAS ODOR COMPLAINT AT W 135 ST. AND AMSTERDAM AVE. FROM THE PUBLIC. A GAS DISTRIBUTION SERVICES (GDS) CREW WAS DISPATCHED AND UPON INVESTIGATING THE COMPLAINT RECEIVED 50% GAS-IN-AIR READING IN THE MAIN VALVE BOX FOR V-3530 WHICH IS A 4" TRANSMISSION PRESSURE INLET VALVE THAT SUPPLIES REGULATOR STATION GR-80. THE MAIN VALVE BOX WAS VENTED AND THE 50% READING DISSIPATED. THIS VALVE IS AN ELASTOSEAL VALVE WHICH COULD NOT BE SERVICED AND NEEDED TO BE REPLACED. AN OPERATIONAL PLAN WAS DEVELOPED FOR THE REPLACEMENT OF V-3530 AND CONTINGENCY PLANS WERE PUT IN PLACE TO MAINTAIN SUPPLY TO THE MANHATTAN HIGH PRESSURE SYSTEM IN THE UNLIKELY EVENT THE 30" TRANSMISSION MAIN, SUPPLYING THE 4" INLET TO GR-80, WOULD HAVE TO BE SHUTDOWN. THE CONTINGENCY PLAN CALLED FOR THE 59 ST. GENERATING STATION AS WELL AS INTERRUPTIBLE GAS CUSTOMERS TO CEASE GAS USAGE. THE AREA OF THE INLET PIPING TO GR-80 WAS EXCAVATED AND A CONTROL FITTING AND VARIOUS FITTINGS WERE WELDED, TAPPED AND THE 4" INLET MAIN STOPPED-OFF SUCCESSFULLY. THE 4" MAIN WAS DEPRESSURIZED AND V-3530 WAS EXCAVATED AND THE VALVE AND ASSOCIATED PIPING WERE CUT AND REMOVED. THE 5' REPLACEMENT SECTION (INCLUDING NEW INLET VALVE) WAS SUCCESSFULLY WELDED AND X-RAYED. WELDED HIGH-HATS WERE INSTALLED AND SUCCESSFULLY MAG-PARTICLE TESTED OVER VARIOUS FITTINGS. AT 20:32 HRS 1-19-11, THE TRANSMISSION MAIN WAS PLACED BACK IN SERVICE. REGULATOR STATION GR-80 WAS PLACED BACK IN SERVICE AT 2000 HRS. THIS WAS A SERIOUS LEVEL INCIDENT. NOTE--THIS GAS DISTRIBUTION INCIDENT REPORT IS GENERATED TO REPLACE RESCINDED GAS TRANSMISSION INCIDENT REPORT 20110013-15868
2025-03-31 10:13 | NO | NO | NO | 20130057 | 15664 | 2013-05-22 16:29 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2010-11-18 13:48 |  |  | 2010 | 144 BRADHURST AVENUE | MOUNT PLEASANT | WESTCHESTER | NY | 10532-1625 | 41.0956 | -73.8028 | [9 empty] | 2010-11-18 14:19 | 960220 |  | NATURAL GAS |  | 105 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2010-11-18 13:48 |  |  |  | 2010-11-18 13:48 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 42 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | ONSHORE PIPELINE, INCLUDING VALVE SITES | 1949 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 15147 | 20010.84552254310633 | 3168 | 4185.27488053189152 | 1400 | 1849.553293164346 | MATERIALS |  | 100 | 69.09385113268608414239482200647249190939 |  | 0 | 19815 | 10851.2527576675141035275080906148867314 | 26114.7675473720299341423948220064724919 | 0 | 0 | 0 |  |  |  |  | 215 | 215 | 245 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | [197 empty] | NON-THREADED CONNECTION FAILURE | [14 empty] | OTHER | MECHANICAL COMPRESSION COUPLING LEAK | [67 empty] | KEVIN FAGAN | MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPT. MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2310 | dadriov@coned.com | ON 11-18-10 AT 12:39 HRS LEAK SURVEY NOTIFIED THE GAS EMERGENCY RESPONSE CENTER (GERC) OF A STRONG ODOR AT 144 BRADHURST AVE., MT. PLEASANT. A CODE MURRE WAS INITIATED AND THE MT. PLEASANT FIRE DEPT. (MPFD), GAS DISTRIBUTION SERVICES (GDS), GAS CONSTRUCTION AND WESTCHESTER GAS OPERATIONS SUPERVISION WERE DISPATCHED. ALL BUILDINGS IN THE AREA CHECKED WERE FOUND TO BE FREE OF GAS READINGS (AKA- CLEAR) WITH THE ASSIST OF MPFD, AND SUBSURFACE STRUCTURES IN THE AREA WERE ALSO CLEAR. AFTER INVESTIGATING OVER THE 12" HIGH PRESSURE PE MAIN AND THE 12" TRANSMISSION STEEL MAIN IT WAS DETERMINED THE LEAK WAS ON THE TRANSMISSION MAIN WHICH SUPPLIES REGULATOR STATION GR-484 AT BRIGHTON AND NEWMAN AVES. REGULATOR STATIONS GR-519, 673 AND 483 WERE RAISED TO COMPENSATE FOR LOSS OF GR-484. GDS CREWS WERE DISPATCHED TO V-31585. GAS CONTROL, PRESSURE CONTROL WERE NOTIFIED, AND WESTR GENERAL MGR. THAKER & CHIEF TRANSMISSION ENGINEER PAYNE WERE ADVISED AND RESPONDED. V-31585 WAS CLOSED AT 1426 HRS AND GAS CONTROL REPORTED NO SYSTEM IMPACT. V-31587 WAS CLOSED AS A CONTINGENCY AND NO SYSTEM IMPACT RESULTED. TRANSMISSION PRESSURE WAS REDUCED TO HIGH PRESSURE (60 PSI) AND THE TRANSMISSION MAIN WAS EXCAVATED OVER THE HIGHEST READING. CONSTRUCTION FOUND A LEAK ON A 12" COMPRESSION COUPLING AND A WELDED REPAIR SLEEVE WAS INSTALLED OVER THE COUPLING. THE SLEEVE WAS INSTALLED ON 11-19-10 AND AT 14:16 HRS MV-31587 WAS FULLY OPENED, AT 1459 MV-31585 WAS FULLY OPENED AND REGULATOR STATION GR-484 WAS PLACED BACK IN SERVICE BY PRESSURE CONTROL. THE US DOT AND NYS PSC WERE NOTIFIED. THIS WAS A SERIOUS LEVEL EVENT. NOTE--THIS GAS DISTRIBUTION INCIDENT REPORT IS GENERATED TO REPLACE RESCINDED GAS TRANSMISSION INCIDENT REPORT 20100100-15165
2025-03-31 10:13 | NO | NO | NO | 20130058 | 15665 | 2013-05-22 20:39 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2013-04-18 10:00 |  |  | 2013 | MCKEE ROAD AND N CLAREMONT | SAN JOSE | SANTA CLARA | CA | 95127 | 37.3782 | -121.831 | [9 empty] | 2013-04-18 15:38 | 1044397 |  | NATURAL GAS |  | 820 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2013-04-18 10:00 |  |  |  | 2013-04-18 10:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 75 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | UNKNOWN | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 5000 | 6244.230580379065 | 47500 | 59320.1905136011175 | 0 | 0 | 0 | 0 |  |  | 2500 | 2187.5 |  | 0 | 55000 | 29178.3824253859343032786885245901639344 | 67751.9210939801825 | 0 | 0 | 47 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA ON THIS PART OF THE SYSTEM | [12 empty] | YES | 2 | 0 | YES | 2 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 63983 | USA NORTH |  | UTILITY OWNER | YES | YES | 8 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | DATA NOT COLLECTED | [169 empty] | CHERYL DIZON | GAS COMPLIANCE ENGINEER | c1dz@pge.com | 925-974-4378 | 925-974-4232 |  |  |  | FRANCES YEE | REGULATORY COMPLIANCE AND SUPPORT DIRECTOR | 925-974-4316 | fsc2@pge.com | ON APRIL 18, 2013 A PACIFIC GAS AND ELECTRIC (PG&E) CREW WAS WORKING ON AN ALDYL A MAIN REPLACEMENT. AT APPROXIMATELY 1000 HOURS, THE CREW WAS EXCAVATING UNDER A NEARBY 4-INCH STEEL MAIN, WHEN THE SOIL PUSHED ON THE PIPE ASSEMBLY CAUSING A TRANSITION FITTING BETWEEN THE ADJACENT 2-INCH STEEL MAIN AND A 2-INCH PLASTIC MAIN TO BECOME UN-COUPLED RESULTING IN A RELEASE OF GAS. THE USA TICKET (#063983) FOR THE AREA WHERE THE MAIN WAS STRUCK IS VALID, AND THE GAS FACILITIES WERE PROPERLY LOCATED AND MARKED. THE BACKHOE OPERATOR AND THE UTILITY WORKER INVOLVED IN THE INCIDENT WERE ADMINISTERED POST-ACCIDENT TESTS FOR DRUGS AND ALCOHOL. THE ALCOHOL AND DRUG TESTS FOR BOTH EMPLOYEES WERE RETURNED WITH NEGATIVE RESULTS. THE PG&E INVESTIGATION ON THE CAUSE OF THE INCIDENT IS ONGOING. THERE WERE NO INJURIES, NO FATALITIES, NO IGNITION AND NO MEDIA ON SITE AS A RESULT OF THIS INCIDENT. OUT OF AN ABUNDANCE OF CAUTION, THE POLICE DEPARTMENT REROUTED TRAFFIC ON MCKEE ROAD, BLOCKED OFF THE AREA, AND EVACUATED 12 RESIDENTS. THE VOLUME OF GAS RELEASED IS LESS THAN THREE MILLION CUBIC FEET, HOWEVER THE COST OF DAMAGES DUE TO THE RELEASE OF GAS IS ESTIMATED TO BE GREATER THAN $50,000. THUS, THIS INCIDENT WAS REPORTED TO THE DEPARTMENT OF TRANSPORTATION AT 1538 HOURS AND TO THE CPUC AT 1550 HOURS WHEN THE COST OF DAMAGES WAS ESTIMATED TO EXCEED $50,000.
2025-03-31 10:13 | NO | YES | NO | 20130059 | 15666 | 2013-05-22 22:26 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2013-04-22 08:22 |  |  | 2013 | ALTA VISTA AND LINDEN AVENUE | BAKERSFIELD | KERN | CA | 93305 | 35.4048 | -118.9913 | [10 empty] | 1044707 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2013-04-22 08:22 |  |  |  | 2013-04-22 08:50 |  | NO | PUBLIC PROPERTY | UNDERGROUND |  |  | 4 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1938 | [5 empty] | 3 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | [9 empty] | CLASS 3 LOCATION | 750000 | 936634.58705685975 | 3000 | 3746.538348227439 | 0 | 0 | 0 | 0 |  |  | 200 | 175 |  | 0 | 753200 | 389639.5440890717003442622950819672131148 | 940556.125405087189 | 0 | 0 | 12 |  |  |  |  | 48 | 48 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE IS NO SCADA ON THIS PORTION OF THE SYSTEM | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | GRADER/SCRAPER | ROAD WORK | YES | 140210 | USA NORTH |  | UTILITY OWNER | YES | YES | 12 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CHERYL DIZON | COMPLIANCE ENGINEER | c1dz@pge.com | 925-974-4378 |  |  |  |  | FRANCES YEE | REGULATORY COMPLIANCE AND SUPPORT DIRECTOR | 925-974-4316 | fsc2@pge.com | ON APRIL 22, 2013 AT APPROXIMATELY 0822 HOURS, PACIFIC GAS AND ELECTRIC (PG&E) WAS NOTIFIED THAT A THIRD PARTY CONTRACTOR WAS PERFORMING ROAD PAVEMENT ACTIVITIES WHEN THE OPERATOR OF A ROAD GRINDER STRUCK A 3-INCH STEEL GAS DISTRIBUTION MAIN, CAUSING A RELEASE OF GAS. THE GAS IGNITED AND THE ROAD GRINDER CAUGHT FIRE RESULTING IN OVER $50,000 OF DAMAGE TO THE EXCAVATOR'S EQUIPMENT. PG&E ARRIVED ON SCENE AT 0850 HOURS AND STOPPED THE FLOW OF GAS AT 1111 HOURS BY DIGGING AND ISOLATING THE STEEL MAIN WITH PRESSURE CONTROL FITTINGS. THE CONTRACTOR HELD A VALID USA TICKET (#140210) FOR THE AREA WHERE THE MAIN WAS STRUCK AND THE GAS FACILITIES WERE PROPERLY LOCATED AND MARKED, BUT THE CONTRACTOR FAILED TO HAND DIG, EXPOSE AND PROTECT THE GAS MAIN PRIOR TO DIGGING WITH MECHANICAL EQUIPMENT. THERE WERE NO INJURIES AND NO FATALITIES AS A RESULT OF THIS INCIDENT. OUT OF AN ABUNDANCE OF CAUTION, THE FIRE DEPARTMENT EVACUATED SEVEN HOMES AND 12 CUSTOMERS EXPERIENCED GAS SERVICE INTERRUPTION. GAS SERVICE TO ALL AFFECTED CUSTOMERS WAS RESTORED BY 2345 HOURS. THIS INCIDENT WAS REPORTED TO THE CPUC AND DOT BECAUSE THE COST OF DAMAGES IS ABOVE $50,000.
2025-03-31 10:13 | NO | YES | NO | 20130061 | 15668 | 2013-05-29 06:59 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-06-29 12:06 |  |  | 2012 | TARRYTOWN ROAD AND YELLOWSTONE AVENUE | TOWN OF GREENBURGH | WESTCHESTER | NY | 10607 | 41.0434 | -73.8015 | [9 empty] | 2012-06-29 12:25 | 1016170 |  | NATURAL GAS |  | 144 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-06-29 12:06 |  |  |  | 2012-06-29 12:06 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 65 |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1954 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 1500000 | 1907550 | 8640 | 10987.488 | 0 | 0 | INCLUDES MATERIALS (PIPE, NEW ROV, VAULT, ETC) |  | 288 | 259.991543340380549682875264270613107822 |  | 0 | 1508928 | 794841.1953995771670190274841437632135307 | 1918797.47954334038054968287526427061311 | 0 | 0 | 0 |  |  |  |  | 236 | 236 | 245 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR LEAK ON DISTRIBUTION LINE OPERATING ABOVE 125 PSIG | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | [197 empty] | NON-THREADED CONNECTION FAILURE | [14 empty] | OTHER | SEAL PACKING. SMALL LEAK ON ORIFICE METER FITTINGS | [67 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON JUNE 28, 2012 WESTCHESTER GAS DISTRIBUTION SERVICES (GDS) WAS PERFORMING A FOLLOW UP LEAK INSPECTION AT THIS LOCATION AND DISCOVERED 17% IN A MANHOLE APPROXIMATELY 43' WEST OF 12" TRANSMISSION PRESSURE V-25873 LOCATED AT TARRYTOWN ROAD AND YELLOWSTONE AVENUE IN GREENBURGH, WESTCHESTER COUNTY, NY. THE MANHOLE CONTAINED A 12" ORIFICE METER AND ASSOCIATED FITTINGS. A 16" HIGH PRESSURE MAIN IS LOCATED 6' NORTH OF THE TRANSMISSION MAIN, AND DIRT AND MATERIALS IN THE MANHOLE NEEDED TO BE REMOVED TO INVESTIGATE THE SOURCE OF THE LEAK. A CONTINGENCY CASE WAS INITIATED AND ISOLATION VALVES WERE IDENTIFIED AND STAFFED. THE MANHOLE WAS VENTED AND A VACUUM TRUCK WAS ASSIGNED TO REMOVE MATERIALS IN THE MANHOLE. THE SEGMENT OF MAIN WAS ISOLATED AFFECTING SUPPLY TO GR-519 AND GR-516. THE PRESSURE WAS REDUCED IN THE AFFECTED SEGMENT TO 60 PSI WITHOUT INCURRING ANY INTERRUPTIONS OR SYSTEM IMPACT. GDS MONITORED THE LOCATION OVERNIGHT AND NO READINGS WERE OBTAINED, AND NO ODOR WAS PRESENT. ON JUNE 29, 2012 OPERATIONAL PLANNING CONTINUED AND ADDITIONAL VALVE CLOSURES WERE SUCCESSFUL IN ISOLATING THE SEGMENT OF TRANSMISSION MAIN. PRESSURE CONTROL SUCCESSFULLY REDUCED PRESSURE TO 30 PSI, AND AT 12:06 (2) MINOR LEAKS WERE CONFIRMED ON THE TRANSMISSION MAIN IN THE MANHOLE ON ORIFICE METER FITTINGS. THE PRESSURE WAS FURTHER REDUCED TO APPROXIMATELY 8 PSI AND THEN AGAIN TO APPROXIMATELY 1 PSI. OPERATIONAL PROCEDURE MPC-12-21 WAS DEVELOPED AND A TOTAL OF 210' OF NEW TRANSMISSION MAIN AND A NEW 12" ROV-59278 WERE INSTALLED. ON JULY 19, 2012 AT 03:48 THE TRANSMISSION SYSTEM WAS RETURNED TO NORMAL OPERATING CONDITIONS. THE NYS PSC AND US DOT WERE NOTIFIED. THIS WAS A SERIOUS LEVEL INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20130062 | 15669 | 2013-05-29 07:12 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-03-07 10:03 |  |  | 2012 | 1060 KNOLLWOOD ROAD | TOWN OF GREENBURGH | WESTCHESTER | NY | 10607 | 41.0694 | -73.8002 | [9 empty] | 2012-03-07 10:15 | 1005004 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-03-07 10:03 |  |  |  | 2012-03-07 10:03 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | ONSHORE PIPELINE, INCLUDING VALVE SITES | 1947 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 25000 | 31792.5 | 5000 | 6358.5 | 1400 | 1780.38 | MATERIALS |  | 30 | 27.0824524312896405919661733615221987315 |  | 0 | 31430 | 16563.4328541226215644820295983086680761 | 39958.4624524312896405919661733615221987 | 0 | 0 | 0 |  |  |  |  | 204 | 204 | 245 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NORMAL SYSTEMS CONDITIONS PRESENT; NO ABNORMAL OCCURENCES AT TIME OF DISCOVERY | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | [197 empty] | NON-THREADED CONNECTION FAILURE | [14 empty] | OTHER SEAL OR PACKING | [68 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON MARCH 6, 2012 AT 08:18 HRS A LEAK SURVEY CREW PERFORMING THEIR MOBILE SURVEY REPORTED TO THE GAS EMERGENCY RESPONSE CENTER (GERC) THEY RECEIVED 94% AT THE CURB LINE IN THE VICINITY OF A 12" 245 PSI RATED, COUPLED TRANSMISSION MAIN INSTALLED IN 1947 IN FRONT OF 1060 KNOLLWOOD ROAD, GREENBURGH. THE PRESSURE AT THE TIME OF DISCOVERY OF THE LEAK WAS 204 PSI. ADDITIONALLY, THERE ARE (2) HIGH PRESSURE (60 PSI) DISTRIBUTION MAINS IN THE VICINITY. A 16" HIGH PRESSURE STEEL (HP STL) MAIN INSTALLED IN 1999 IS LOCATED 3' WEST OF THE TRANSMISSION MAIN, AND APPROXIMATELY 30 FEET EAST OF THE TRANSMISSION MAIN, ON THE OPPOSITE SIDE OF THE STREET IS A 2" HIGH PRESSURE POLYETHYLENE MAIN WHICH WAS ALSO INSTALLED IN 1999. WESTCHESTER GAS CONSTRUCTION AND ADDITIONAL CREWS RESPONDED AND CONTINGENCY VALVES WERE LOCATED. THE LEAK WAS INVESTIGATED AND TWO EXCAVATIONS OVER THE PARALLEL 16" HP STEEL DISTRIBUTION MAIN REVEALED NO LEAKS. THE CONSTRUCTION SUPERVISOR REPORTED THAT IN THE SECOND EXCAVATION VISIBLE WATER BUBBLING FROM THE DIRECTION OF THE TRANSMISSION MAIN 30' NORTH OF THE NORTH BUILDING LINE OF # 1060 KNOLLWOOD RD. INDICATED A PROBABLE LEAK ON THE TRANSMISSION MAIN. CREWS CEASED EXCAVATING, AND THE LEAK DID NOT POSE AN IMMEDIATE HAZARD TO LIFE OR PROPERTY. CONTINGENCY VALVES WERE STAFFED THROUGHOUT THE NIGHT, AND THE EXCAVATION MONITORED FOR SAFETY. AN OPERATIONAL PLAN WAS DEVELOPED WHICH INVOLVED PRESSURE REDUCTION, ISOLATION OF THE AFFECTED SECTION AND SUBSEQUENT HAND EXCAVATION TO DETERMINE THE LOCATION OF THE LEAK. AN OPERATIONAL PLAN WAS DEVELOPED TO IDENTIFY THE NECESSARY STEPS TO ISOLATE THE TRANSMISSION MAIN TO REPAIR THE LEAK. ON MARCH 7, 2012 AT 10:03 HRS., THE TRANSMISSION MAIN WAS ISOLATED VIA SHUTDOWN AND PRESSURE REDUCTION BEGAN. AT 10:34 HRS., PRESSURE WAS REDUCED TO 60 PSI. THE MAIN WAS EXCAVATED AND AT 15:55 HRS. A VISUAL LEAK ON A 12" COMPRESSION COUPLING WAS CONFIRMED TO BE THE SOURCE OF THE LEAK. THE MAIN WAS ABATED AND A WELDED REPAIR SLEEVE WAS INSTALLED TO SECURE THE LEAK. ALL TESTING OF THE SLEEVE WERE SUCCESSFUL. ON MARCH 8, 20112, PRESSURE RESTORATION IN THIS SEGMENT OF MAIN BEGAN AT 03:00 HRS. THE MAIN PRESSURE WAS RESTORED INCREMENTALLY AND LEAK SURVEY CHECKED THE SEGMENT OF MAIN INVOLVED AT EACH PRESSURE INCREASE. NO LEAKS WERE FOUND. AT 07:18 HRS. GAS CONTROL REPORTED PRESSURE IN AFFECTED SEGMENT OF MAIN WAS 227 PSI. PRESSURE CONTROL RETURNED REGULATOR GR-483 TO OPERATION. THERE WERE NO INJURIES OR EVACUATIONS REPORTED AND THE N.Y.S. PSC AND U.S. DOT WERE NOTIFIED. THIS WAS A SERIOUS LEVEL INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20130063 | 15785 | 2013-05-29 10:11 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2013-05-01 03:05 |  |  | 2013 | 9411 TUDOR LANE | GARDEN GROVE | ORANGE | CA | 92841 | 33.7882 | -117.9687 | [9 empty] | 2013-05-01 04:45 | 104565 |  | NATURAL GAS |  | 11 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2013-05-01 03:05 |  |  |  | 2013-05-01 03:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1974 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 50000 | 62442.30580379065 | 600 | 749.3076696454878 | 200 | 249.7692232151626 | 0 | 0 |  |  | 66 | 57.75 |  | 0 | 50866 | 26328.9401513773405836065573770491803279 | 63499.1326966513004 | 0 | 0 | 2 |  |  |  |  | 41 | 44 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JEFF KOSKIE | PIPELINE SAFETY AND COMPLIANCE MANAGER | wkoskie@semprautilities.com | 213 305-8660 | 213 244-8155 |  |  |  | JEFF KOSKIE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 213 305-8660 | wkoskie@semprautilities.com | ON MAY 1, 2013 AT 3:05 AM, THE GAS COMPANY WAS INFORMED OF A GAS LEAK AT THE ADDRESS OF 9411 TUDOR LANE IN GARDEN GROVE. THE LEAK WAS FROM A GAS RISER AT THE GAS METER SET ASSEMBLY. THE CAUSE OF THE LEAK WAS A VEHICLE THAT HAD STRUCK THE METER SET ASSEMBLY SEVERING THE RISER. ESCAPING GAS IGNITED, DAMAGING HOUSE. GAS COMPANY PERSONNEL RESPONDED AND PINCHED GAS SERVICE. AFTER THE VEHICLE AND OTHER DEBRIS WERE CLEARED AND THE STRUCTURAL DAMAGE TO THE RESIDENCE WAS SAFELY SUPPORTED, THE PINCHED SERVICE WAS RETURNED TO SERVICE. THE DRIVER OF THE VEHICLE WAS TRANSPORTED TO THE HOSPITAL, DUE TO INJURIES FROM CRASHING INTO HOUSE. THE ESTIMATED DAMAGE TO THE PRIVATE PROPERTY OF THE HOUSE AT 9411 TUDOR LANE IS IN EXCESS OF $50,000.
2025-03-31 10:13 | NO | NO | NO | 20130064 | 15672 | 2013-05-29 15:05 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-03-07 09:55 |  |  | 2012 | BRADHURST AVE & STEVENS AVE | TOWN OF MT. PLEASANT | WESTCHESTER | NY | 10607 | 41.0964 | -73.8024 | [9 empty] | 2012-03-07 12:53 | 1005004 |  | NATURAL GAS |  | 13 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-03-07 09:55 |  |  |  | 2012-03-07 09:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 45 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1949 | [5 empty] | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 20000 | 25434 | 5000 | 6358.5 | 1400 | 1780.38 | MATERIALS |  | 40 | 36.10993657505285412262156448202959830867 |  | 0 | 26440 | 13938.2838054968287526427061310782241015 | 33608.9899365750528541226215644820295983 | 0 | 0 | 0 |  |  |  |  | 231 | 231 | 245 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | MINOR LEAK UNDER REDUCED PRESSURE DISCOVERED BY MOBILE LEAK SURVEY CREWS | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | [197 empty] | NON-THREADED CONNECTION FAILURE | [14 empty] | OTHER SEAL OR PACKING | [68 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-579-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-579-2350 | dadariov@coned.com | ON MARCH 7, 2012 AT 09:55 A LEAK SURVEY CREW REPORTED A T-1 LEAK AT BRADHURST AVENUE AND STEVENS AVENUE, MT. PLEASANT, ALONG THE ROUTE OF THE TRANSMISSION MAIN AT THIS LOCATION AS PART OF A BASELINE SURVEY ASSOCIATED WITH THE PRESSURE REDUCTION TO HP RELATED TO THE LEAK AT 1060 KNOLLWOOD RD (TG) {SEE PHMSA REPORT 20120033-15480} ON THE 12" 245 PSI TRANSMISSION MAIN. GAS CONSTRUCTION AND SUPERVISION WERE DISPATCHED IMMEDIATELY AND THE LEAK INVESTIGATION INDICATED A PROBABLE TRANSMISSION MAIN LEAK. AN OPERATIONAL PLAN WAS DEVELOPED AND UPON EXCAVATING OVER THE 12" TRANSMISSION MAIN (AT 55 PSI) A COUPLING WAS FOUND LEAKING AT BOTH COMPRESSION ENDS AT 22:11 HRS. A WELDED REPAIR SLEEVE WAS INSTALLED OVER THE LEAKING COUPLING AND THE REPAIR WAS TESTED AND PASSED. TRANSMISSION PRESSURE WAS RESTORED INCREMENTALLY AND ON MARCH 8, 2012 AT 17:59 TRANSMISSION PRESSURE WAS FULLY RESTORED TO 231 PSI. GR-484 WAS RETURNED TO SERVICE. THE N.Y.S. PSC AND U.S. DOT WERE NOTIFIED. THERE WERE NO INJURIES OR EVACUATIONS ASSOCIATED WITH THIS EVENT. THIS WAS A SERIOUS LEVEL INCIDENT.
2025-03-31 10:13 | YES | NO | NO | 20130065 | 15881 | 2013-05-29 16:27 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2013-05-02 06:58 |  |  | 2013 | 685 EAST 226 STREET | BRONX | BRONX | NY | 10467 | 40.8889 | -73.8607 | [9 empty] | 2013-05-02 08:00 | 1045761 |  |  |  | 2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2013-05-02 07:00 |  |  |  | 2013-05-02 07:18 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | 1978 | [8 empty] | OTHER | ALUMINUM METERS | [9 empty] | OTHER | [8 empty] | METERS MELTED/DESTROYED PER FDNY FIRE MARSHAL'S REPORT OF SECONDARY IGNITION ASSOCIATED WITH 4 ALARM BUILDING FIRE. | CLASS 4 LOCATION | 250000 | 312211.52901895325 | 5000 | 6244.230580379065 | 500 | 624.4230580379065 | 500 | 624.4230580379065 | MATERIALS |  | 20 | 17.5 |  | 0 | 256020 | 132428.2478391340359344262295081967213115 | 319722.105715408128 | 12 | 0 | 19 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY REPSONSE CENTER | 718-319-2350 | dadariov@coned.com | ON MAY 2, 2013 AT 06:58 GAS ENGINEERING REPORTED A BUILDING FIRE IN THE BRONX AT AN UNKNOWN LOCATION TO THE GAS EMERGENCY REPSONSE CENTER (GERC) PER NEWS REPORTS. THE GERC CONTACTED THE FDNY WHO CONFIRMED A 4 ALARM FIRE IN-PROGRESS AT 685 E 226 ST. GAS DISTRIBUTION SERVICES (GDS), THE ELECTRIC EMERGENCY DEPARTMENT, GAS CONSTRUCTION, GAS EMERGENCY RESPONSE GROUP (ERG) AND SUPERVISION WERE DISPATCHED. UPON INITIAL INVESTIGATION AT 07:23 GDS REPORTED A POSSIBLE GAS FED FIRE IN A LAUNDROMAT AT 3985 WHITE PLAINS RD. ADDITIONAL CONSTRUCTION CREWS, THE LAW DEPARTMENT., AND A PHOTOGRAPHER WERE DISPATCHED. THE FIRE EXTENDED TO ALL THE BUILDINGS ON THE WEST SIDE OF WHITE PLAINS ROAD BETWEEN E 225 ST & E 226 ST. AND AT 07:46 THE FIRE DEPARTMENT OF NEW YORK (FDNY) DECLARED A 5 ALARM CONDITION. AT 07:51 GDS CLOSED A 6" LOW PRESSURE POLYETHYLENE (LPPE) VALVE 8987 TO ISOLATE THE SOUTHERN GAS SUPPLY FROM E 225 ST. AT 09:49 IT WAS REPORTED PER FDNY CHIEF ESPOSITO THE FIRE APPEARED TO BE GAS FED IN BUILDINGS # 3983 AND #3985 WHITE PLAINS RD. GAS CONSTRUCTION EXCAVATED IN FRONT OF 4013 WHITE PLAINS ROAD AND 674 E 226 ST AND INSTALLED STOPPERS IN THE 6" LP GAS MAINS TO ISOLATE THE NORTHERN GAS SUPPLY. THIS ISOLATION INTERRUPTED 15 SERVICES ; 31 CUSTOMERS AT 09:55. MULTIPLE MEDIA OUTLETS RESPONDED TO LOCATION. THE FDNY FIRE MARSHAL INVESTIGATED AND REPORTED THE FIRE BEGAN IN A DETACHED GARAGE TO BUILDING 685 E 225 ST. AND SPREAD TO THE ADJACENT ROW OF STORES; THE PRIMARY CAUSE OF THE FIRE WAS NOT ATTRIBUTED TO NATURAL GAS. THE REPORTED GAS IGNITION WAS SECONDARY IGNITION ONLY, AFTER THE GAS METERS WERE DESTROYED BY THE FIRE. THERE WERE NO REPORTS OF INJURIES AND THE REPORTED PROPERTY DAMAGE WAS WELL IN EXCESS OF $50,000. THE US DOT, NYS PSC AND NYC DEP WERE NOTIFIED AND THE PSC RESPONDED TO LOCATION. THIS WAS AN UPGRADED LEVEL INCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20130066 | 15700 | 2013-05-30 16:28 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 200 CIVIC CENTER DR | COLUMBUS | OH | 43215 | 2013-05-03 11:45 |  |  | 2013 | 816 UTAH ST. | TOLEDO | LUCAS | OH | 43065 | 41.6356 | -83.5274 | [9 empty] | 2013-05-03 12:43 | 1045929 |  | NATURAL GAS |  | 4.8 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 4 | 2013-05-03 11:45 |  |  |  | 2013-05-03 11:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | OTHER | LOCALIZED CORROSION PITTING | [5 empty] | CLASS 3 LOCATION | 2075 | 2591.355690857311975 | 498 | 621.925365805754874 | 2000 | 2497.692232151626 | 0 | 0 |  |  | 13 | 11.375 |  | 0 | 4586 | 2375.836397410985958377049180327868852459 | 5722.348288814692849 | 0 | 0 | 4 |  |  |  |  | 0.45 | 0.45 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | YES | 2 | 0 | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | ROB R. SMITH | OPERATIONS COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB R. SMITH | OPERATIONS COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | A TWO PERSON REPAIR CREW WAS REPAIRING A LEAK ON A 4" WROUGHT IRON MAIN LINE IN AN OPEN EXCAVATION. A WATER PUMP WAS BEING USED TO REMOVE EXCESS WATER WHILE THE CREW BEGAN REMOVING SCALE OFF THE STEEL MAIN LINE WITH A PNEUMATIC SCALER TO INSTALL A LEAK CLAMP WHEN THE NATURAL GAS PRESENT IN THE EXCAVATION IGNITED. ONLY ONE INDIVIDUAL WAS IN THE OPEN EXCAVATION AT THE TIME OF THE IGNITION. THE FIRE WAS IMMEDIATELY EXTINGUISHED BY THE SECOND CREW MEMBER. THE CREW MEMBER SUBJECTED TO THE IGNITION IMMEDIATELY EXITED THE EXCAVATION. HE THEN REMOVED HIS NOMEX HOOD AND OTHER FIRE RESISTANT CLOTHING AND SAFETY APPAREL. HE WAS GIVEN FIRST AID AND 911 WAS CALLED. AN INVESTIGATION INTO THE CAUSE OF INCIDENT HAS BEEN CONDUCTED AND CAN NOT ASCERTAIN THE CAUSE WITH ANY REASONALBLE DEGREE OF CERTAINTY. COLUMBIA GAS OF OHIO'S THIRD PARTY CAUSE AND ORIGIN INVESTIGATORS WERE ABLE TO DETERMINE THAT THERE WERE TWO POTENTIAL SOURCES OF IGNITION IN THE EXCAVATION AT THE TIME OF THE INCIDENT; A PNEUMATIC SCALER AND AN ELECTRIC WATER PUMP. THE DAMAGE TO THE ELECTRIC WATER PUMP'S WIRING AND PROTECTIVE BOOT ALLOWED ARCING WHICH IS LIKELY THE IGNITION SOURCE OF THIS INCIDENT. THERE IS PHYSICAL EVIDENCE THAT SUGGESTS THE CONDITION OF THE PROTECTIVE BOOT WAS COMPROMISED PRIOR TO THE INCIDENT. IN ORDER TO ELIMINATE THE POTENTIAL FOR RECURRENCE COLUMBIA GAS OF OHIO INC. HAS PROHIBITED THE USE OF THESE WATER PUMPS BY ALL REPAIR CREWS AND IS ACTIVELY SEEKING A REPLACEMENT WATER PUMP WHICH IS NOT ELECTRICALLY DRIVEN. IN ADDITION, WHILE THE INVESTIGATION DID NOT INDICATE THAT THE INCIDENT WAS NOT CAUSED BY THE SCALER, COLUMBIA IS ALSO ISSUING A SAFETY BULLETIN TO OUR MAINTENANCE CREWS ADVISING THEM TO ENSURE A COBALT PISTONS ARE BEING UTILIZED. PLEASE CONSIDER THIS COLUMBIA'S FINAL REPORT ON THIS INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20130067 | 15675 | 2013-06-03 10:07 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2013-03-20 10:00 |  |  | 2013 | BRONX STREET AND HAMILTON AVENUE | WHITE PLAINS | WESTCHESTER | NY | 10606 | 41.0332 | -73.7755 | [9 empty] | 2013-03-22 10:45 | 1041813 |  | NATURAL GAS |  | 9.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-03-21 08:41 |  |  |  | 2013-03-21 08:41 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 51 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1948 | [5 empty] | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 25000 | 31221.152901895325 | 5000 | 6244.230580379065 | 1500 | 1873.2691741137195 | MATERIALS |  | 10 | 8.75 |  | 0 | 31510 | 16300.9843732643474672131147540983606557 | 39347.4026563881095 | 0 | 0 | 0 |  |  |  |  | 214 | 214 | 245 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK ON A COMPRESSION COUPLING | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | BOLTED |  | COUPLING |  | DRESSER |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | COMPRESSION COUPLING LEAK AT SEAL | [7 empty] | NO | [86 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON WEDNESDAY, MARCH 20, 2013 LEAK SURVEY DETECTED 35% AT THE CURB LINE AND 25% IN A BAR-HOLE IN THE VICINITY OF A GAS TRANSMISSION MAIN TO THE GAS EMERGENCY RESPONSE CENTER (GERC). GAS DISTRIBUTION SYSTEM (GDS), GAS CONSTRUCTION AND SUPERVISION WERE NOTIFIED AND RESPONDED. GAS CONSTRUCTION CONDUCTED A LEAK INVESTIGATION SURVEY OVER THE ROUTE OF THE 1948 12" STEEL TRANSMISSION MAIN (245 PSI SYSTEM) AND THE 16" MEDIUM PRESSURE CAST IRON (MPCI) MAIN IN THE AREA. ALL SUBSURFACE STRUCTURES IN THE AREA WERE CHECKED AND FOUND CLEAR; THERE WERE NO BUILDINGS IN THE AREA. GAS CONTROL WAS NOTIFIED AND CONTINGENCY CASE 39-A WAS INITIATED. ISOLATION VALVES 25977 AND 25976 WERE STAFFED AND GAS CONTROL CONFIRMED COMMUNICATION WITH REMOTE OPERATED VALVE (ROV) 32717. GAS CREWS CONTINUED TO AERATE, PINPOINT AND MONITOR THE AREA. ON THURSDAY, MARCH 21, 2013 AT 08:41 THE INVESTIGATION IDENTIFIED A PROBABLE TRANSMISSION MAIN LEAK APPROXIMATELY 175' SOUTH OF THE TRANSCONTINENTAL GAS PIPELINE (TGPL) WHITE PLAINS GATE STATION LOCATED AT BRONX STREET AND MOTT STREET (WP).TRANSMISSION ENGINEERING, DISTRIBUTION ENGINEERING, GAS CONTROL, MAJOR PROJECTS, TECHNICAL OPERATIONS, GERC AND WESTCHESTER GAS OPERATIONS PARTICIPATED IN OPERATIONAL PLANNING TO IDENTIFY THE ACTIONS REQUIRED TO MAINTAIN SUPPLY TO THE DISTRIBUTION SYSTEM AS WELL AS THE ACTIONS REQUIRED TO REPAIR THE SUSPECTED 12" COUPLING BELIEVED TO BE THE SOURCE OF THE LEAK. REPAIR PROCEDURE MPC-13-09 WAS INITIATED AND ON FRIDAY, MARCH 22, 2013 AT 10:16 THE SEGMENT OF TRANSMISSION MAIN WAS ISOLATED AND PRESSURE REDUCED FROM 214 PSI TO 62 PSI. REPAIR OPERATIONS CONTINUED AROUND-THE-CLOCK AND A VISIBLE LEAK WAS CONFIRMED ON A 12" COMPRESSION COUPLING. A WELDED REPAIR SLEEVE WAS INSTALLED TO SECURE THE LEAK. A SECOND WELDED REPAIR SLEEVE WAS INSTALLED ON A COUPLING NOT LEAKING BUT IN CLOSE PROXIMITY AS A PRECAUTION. ON SATURDAY, MARCH 23, 2013 A PRELIMINARY MOBILE LEAK SURVEY WAS PERFORMED IN ADVANCE OF PRESSURE RESTORATION AND (2) LEAKS WERE FOUND ALONG THE ROUTE OF THE TRANSMISSION MAIN. THE LEAKS WERE INVESTIGATED AND IT WAS DETERMINED THE TRANSMISSION MAIN WAS NOT THE SOURCE OF THE READINGS DETECTED. A THIRD T-1 WAS DETECTED DURING PRESSURE RESTORATION AND A 16" MPCI HUB WAS FOUND TO BE THE SOURCE OF THAT LEAK. ON MONDAY, MARCH 25, 2013 AT 02:00 THE ISOLATED SEGMENT WAS RETURNED TO NORMAL OPERATING PRESSURE. GAS CONTROL AND PRESSURE CONTROL ARE RETURNING THE REGULATOR STATIONS INVOLVED IN THIS PROCEDURE TO NORMAL SETTINGS. THERE WERE NO OUTAGES AS A RESULT OF THIS OPERATIONAL PLAN. NO EVACUATIONS, INJURIES OR MEDIA ATTENTION WERE REPORTED AS A RESULT OF THIS EVENT. THE WHITE PLAINS FIRE DEPARTMENT (WPFD) WAS NOTIFIED AND THE WPFD RESPONDED PER THE TRANSMISSION LEAK NOTIFICATION PROTOCOL AND REPAIR OPERATIONS WERE REVIEWED. THE US DOT AND NYS PSC WERE NOTIFIED AND THE PSC RESPONDED TO LOCATION. THIS WAS A SERIOUS LEVEL INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20130068 | 15676 | 2013-06-03 10:28 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-08-16 12:54 |  |  | 2012 | BAYCHESTER AVENUE AND NEREID AVENUE | BRONX | BRONX | NY | 10475-4572 | 40.899 | -73.8462 | [9 empty] | 2012-08-16 15:39 | 1021260 |  | NATURAL GAS |  | 65 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-08-16 12:54 |  |  |  | 2012-08-16 12:54 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 32 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2007 | [5 empty] | 4 | UNKNOWN | CAMERON | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 25000 | 31792.5 | 1500 | 1907.55 | 0 | 0 |  |  | 130 | 117.357293868921775898520084566596194503 |  | 0 | 26630 | 14066.1123678646934460887949260042283298 | 33817.4072938689217758985200845665961945 | 0 | 0 | 0 |  |  |  |  | 178 | 178 | 245 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK ON 4" VALVE PACKING | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | VALVE | MATERIAL/WELD/EQUIP FAILURE | VALVE | EQUIPMENT FAILURE | VALVE | [197 empty] | VALVE | [16 empty] | OTHER | LEAK AT SEAL PACKING | [65 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON AUGUST 16, 2012 AT 12:54 PRESSURE CONTROL REPORTED TO THE GAS EMERGENCY RESPONSE CENTER (GERC) AN OUTSIDE LEAK AT 4" TRANSMISSION INLET V-43662 WHILE PERFORMING AN INSPECTION OF REGULATOR STATION GR-149 AT BAYCHESTER AVE. AND NEREID AVE. IN BRONX, NEW YORK. GAS DISTRIBUTION SERVICES (GDS) RESPONDED AND INVESTIGATED THE AREA. CONTINGENCY CASE 16-A WAS INITIATED AND 4" REMOTE INLET V-6423 AND 24" V-6408 WERE INSPECTED FOR CONTINGENCY. A BAR-HOLE SURVEY WAS COMPLETED AND AT 15:02 V-6423 WAS CLOSED ISOLATING APPROXIMATELY 30' OF 178 PSI INLET PIPING TO GR-149. GAS CONTROL REPORTED GR-174 AND GR-141 WERE ALSO SUPPORTING THE AREA AND THERE WAS NO SYSTEM IMPACT FROM ISOLATING GR-149. PRESSURE IN THE AFFECTED SEGMENT WAS REDUCED TO APPROXIMATELY 90 PSI. GAS CONSTRUCTION EXCAVATED AND AT 16:56 A VISIBLE LEAK ON THE BODY OF V-43662 WAS REPORTED. ADDITIONAL RESEARCH WAS PERFORMED TO DETERMINE IF A REPAIR CAN BE MADE OR IF THE VALVE WILL BE REPLACED. THE MAIN PRESSURE IN THE AFFECTED SEGMENT WAS REDUCED TO 5 PSI AND THERE WAS A MINOR LEAK WHICH GDS SURVEILLED UNTIL A REPAIR WAS COMPLETED. MULTIPLE REPAIR ATTEMPTS WITH THE CAMERON VALVE REPRESENTATIVE PRESENT WERE UNSUCCESSFUL. ON 8-29-12 IT WAS DETERMINED THE VALVE WAS TO BE CUT-OUT AND REPLACED. ON 9-2-12, V-43662 WAS CUT OUT ON PROCEDURE MPC-12-25 AND REPLACEMENT V-59674 WAS INSTALLED. TRANSMISSION PRESSURE WAS RETURNED TO THE AFFECTED SEGMENT OF PIPING AND AT 01:30 ON 9-3-12 THE SERIOUS LEVEL STATUS WAS TERMINATED. THERE WERE NO INJURIES, EVACUATIONS OR SYSTEM IMPACT REPORTED. THE US DOT, NYS PSC, NYC DEP AND FDNY WERE NOTIFIED AND THE PSC RESPONDED TO LOCATION. THIS WAS A SERIOUS LEVEL INCIDENT. NOTE--GAS DISTRIBUTION INCIDENT REPORT WAS GENERATED TO REPLACE GAS TRANSMISSION INCIDENT REPORT 20120092-15812
2025-03-31 10:13 | NO | YES | NO | 20130069 | 15677 | 2013-06-03 10:55 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-11-21 13:18 |  |  | 2012 | POPHAM AVENUE AND SOUTH CHURCH LANE | SCARSDALE | WESTCHESTER | NY | 10583-3709 | 40.9888 | -73.8087 | [9 empty] | 2012-11-21 13:38 | 1031262 |  | NATURAL GAS |  | 29 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-11-21 13:18 |  |  |  | 2012-11-21 13:18 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 72 |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1925 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 360000 | 457812 | 1000 | 1271.7 | 0 | 0 |  |  | 38 | 34.30443974630021141649048625792811839323 |  | 0 | 361038 | 190170.4336152219873150105708245243128964 | 459118.0044397463002114164904862579281184 | 0 | 0 | 0 |  |  |  |  | 212 | 212 | 245 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK AT VALVE PACKING RESULTING IN NO PRESSURE LOSS OR INCREASED FLOW | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | VALVE | MATERIAL/WELD/EQUIP FAILURE | VALVE | EQUIPMENT FAILURE | VALVE | [197 empty] | VALVE | [16 empty] | OTHER | LEAK AT DARLING VALVE OPERATING HEAD | [65 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON WEDNESDAY NOVEMBER 21, 2012 AT 09:16 WESTCHESTER GAS CONSTRUCTION REPORTED A POSSIBLE TRANSMISSION LEAK AT 8" V-28871 LOCATED AT THE INLET TO REGULATOR STATION GR-510 (TRANS-HP) AT POPHAM AVENUE AND SOUTH CHURCH LANE, SCARSDALE. A READING OF 3% WAS DETECTED UPSTREAM OF THE VALVE. A CODE MURRE (MULTIPLE RESOURCE RESPONSE EVENT) WAS INITIATED, AND GAS DISTRIBUTION SERVICES (GDS), THE EMERGENCY RESPONSE GROUP (ERG), PRESSURE CONTROL, TRANSMISSION ENGINEERING AND GAS CONTROL WERE NOTIFIED. AN OPERATIONAL PLAN WAS DEVELOPED AND 24" V-26005 AND ROV 25934 WERE CLOSED AT 13:18 TO ISOLATE THE AFFECTED 212 PSI SEGMENT (245 PSI RATED). PRESSURE WAS REDUCED VIA GR-510 TO 65 PSI AT 15:12. THE LOCATION WAS MONITORED AND AROUND-THE-CLOCK OPERATIONS COMMENCED FRIDAY NOVEMBER 23, 2012 AT 06:00 HRS. GAS CONTROL DECLARED A CONDITION YELLOW AND ISSUED A LIMIT WORK ORDER TO ENSURE GAS SYSTEM SUPPLY. AT 17:10 ON NOVEMBER 23, 2012, A VISUAL LEAK WAS CONFIRMED ON THE BURIED DARLING GATE VALVE DIRECTLY UPSTREAM OF V-28871. AN OPERATIONAL PLAN WAS DEVELOPED FOR THE REPLACEMENT OF THE DARLING VALVE, V-28871 AND THE 1.5" PURGE RISER ALL ASSOCIATED WITH THE 8" SUPPLY TO GR-510. A NEW REMOTE INLET VALVE AND ASSOCIATED 8" PIPE TOTALING 25' WAS FABRICATED AND THE PSC-WITNESSED TEST PASSED ON TUESDAY NOVEMBER 27, 2012. REPLACEMENT OF THE SEGMENT WAS COMPLETED AT 07:00 ON WEDNESDAY NOVEMBER 28, 2012. THE AFFECTED SEGMENT WAS RE-ENERGIZED INCREMENTALLY AND LEAK SURVEY CHECKED THE AREA AT EACH PRESSURE INCREASE AND NO LEAKS WERE DETECTED. AT 09:19 GAS CONTROL REPORTED THE TRANSMISSION SYSTEM WAS AT 219 PSI AND HAS RETURNED TO NORMAL OPERATING CONDITIONS. THE SCARSDALE FIRE DEPT. WAS ADVISED AND VISITED LOCATION FOR AN OPERATIONAL OVERVIEW. THE US DOT AND NYS PSC WERE NOTIFIED AND THE NTSB INQUIRED ABOUT THIS INCIDENT. THERE WERE NO INJURIES OR EVACUATIONS REPORTED. THIS WAS A SERIOUS LEVEL INCIDENT. NOTE--THIS GAS DISTRIBUTION INCIDENT REPORT WAS GENERATED TO REPLACE GAS TRANSMISSION INCIDENT REPORT 20120126-15817.
2025-03-31 10:13 | NO | NO | NO | 20130070 | 15678 | 2013-06-03 11:27 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2012-09-11 09:05 |  |  | 2012 | 1218 NOBLE AVENUE | BRONX | BRONX | NY | 10472-4510 | 40.8302 | -73.8696 | [9 empty] | 2012-09-11 16:49 | 1024109 |  | NATURAL GAS |  | 11 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2012-09-11 09:05 |  |  |  | 2012-09-11 09:05 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 65 |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2006 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 31720 | 40338.324 | 2500 | 3179.25 | 0 | 0 |  |  | 22 | 19.86046511627906976744186046511627906977 |  | 0 | 34242 | 18042.0460930232558139534883720930232558 | 43537.4344651162790697674418604651162791 | 0 | 0 | 0 |  |  |  |  | 183 | 183 | 245 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK ON 4" VALVE PACKING | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | VALVE | MATERIAL/WELD/EQUIP FAILURE | VALVE | EQUIPMENT FAILURE | VALVE | [197 empty] | VALVE | [16 empty] | OTHER | LEAK AT VALVE PACKING SEAL | [65 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON TUESDAY SEPTEMBER 11, 2012 AT 09:05 LEAK SURVEY REPORTED TO THE GAS EMERGENCY RESPONSE CENTER A 15% GAS READING WAS DETECTED AT 4" TRANSMISSION MAIN VALVE #12082 OPPOSITE 1218 NOBLE AVE, BRONX, NEW YORK. VALVE #12082 IS THE INLET VALVE TO TRANSMISSION-LOW PRESSURE REGULATOR STATION GR-191. A CODE MURRE (MULTIPLE RESOURCE RESPONSE EVENT) WAS INITIATED AND GAS CONSTRUCTION, PRESSURE CONTROL AND SUPERVISION WERE DISPATCHED. AT 12:45, CONTINGENCY CASE 13B WAS ACTIVATED AND ISOLATION VALVES WERE IDENTIFIED AND INSPECTED. A VACUUM TRUCK WAS ASSIGNED AND USED TO EXCAVATE AROUND THE VALVE. AT 16:18, IT WAS REPORTED A LEAK ON VALVE #12082 WAS CONFIRMED. GAS CONTROL WAS NOTIFIED AND PRESSURE CONTROL CLOSED REMOTE INLET V-6947 TO ISOLATE LEAKING V-12082. THE AFFECTED SEGMENT OF 4" 245 PSI RATED PIPING WAS APPROXIMATELY 82' IN TOTAL AND WAS DEPRESSURIZED THROUGH GR-191. THERE WERE NO SYSTEM IMPACT OR CUSTOMER OUTAGES AS A RESULT OF GR-191 OUT OF SERVICE. AN OPERATIONAL PLAN WAS IDENTIFIED AND PROCEDURE MP-12-27 WAS DEVELOPED FOR THE REPLACEMENT OF THE LEAKING VALVE AND ASSOCIATED PIPING. ON FRIDAY SEPTEMBER 14, 2012 THE PROCEDURE WAS INITIATED AND NEW VALVE #59783 AND PIPING TOTALING 5'2" WAS INSTALLED. PRESSURE CONTROL RETURNED GR-191 TO SERVICE AND AT 19:38 THE SERIOUS LEVEL INCIDENT WAS TERMINATED. THE US DOT, NYS PSC, NYC DEP AND FDNY WERE NOTIFIED. NOTE--THIS GAS DISTRIBUTION INCIDENT REPORT WAS GENERATED TO REPLACE GAS TRANSMISSION INCIDENT REPORT 20120102-15825
2025-03-31 10:13 | NO | YES | NO | 20130071 | 15731 | 2013-06-03 11:46 | SUPPLEMENTAL FINAL | 31159 | KANSAS GAS SERVICE | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2013-05-04 13:05 |  |  | 2013 | INTERSECTION OF 13TH AND FOUNTAIN | WICHITA | SEDGWICK | KS | 67208 | 37.7083 | -97.288 | [9 empty] | 2013-05-04 15:55 | 1046039 |  | NATURAL GAS |  | 1252 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 42 | 2013-05-04 13:05 |  |  |  | 2013-05-04 13:27 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 84 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 2012 | [5 empty] | 4 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 4 | [7 empty] | CLASS 3 LOCATION | 100000 | 124884.6116075813 | 13392 | 16724.547186487287696 | 4278 | 5342.563684572328014 | 0 | 0 |  |  | 7143 | 6250.125 |  | 0 | 124813 | 66644.7277274644609703278688524590163934 | 153201.84747864091571 | 0 | 0 | 21 |  |  |  |  | 48 | 48 | 58 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 13164876 | N/A |  | CONTRACT LOCATOR | YES | YES | 7 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO ABANDONED FACILITY | [170 empty] | BRUCE D. KUBIE | MANAGER OF STANDARDS | bkubie@kgas.com | 785 431 4250 | 785 431 4224 |  |  |  | ROB GREEN | DIRECTOR ENGINEERING | 785 431 4241 | rgreen@kgas.com | A CONTRACTOR EXCAVATING TO COMPLETE SEWER REPLACEMENT WORK HIT A 4" PE MAIN OPERATING AT 48 LBS WITH A TRACKHOE. THE GAS IGNITED AND THE TRACKHOE CAUGHT FIRE. THE OPERATOR OF THE EQUIPMENT HEARD THE NOISE CAUSED BY BLOWING GAS AND ABANDONED THE TRACKHOE. AS SOON AS HE WAS CLEAR OF THE EQUIPMENT IT CAUGHT FIRE. LOCATES WERE ACCURATE AND UP-TO-DATE AND THE CONTRACTOR HAD POT HOLED EXPOSING AN ABANDONED BARE STEEL AND A PE MAIN. THE ACTIVE 4" PE WAS LOCATED AT A GREATER DEPTH AND WAS STRUCK BY THE TRACKHOE. 21 HOMES WERE EVACUATED. NO INJURIES OR FATALITIES OCCURRED AS A RESULT OF THIS RELEASE. 09/18/2013 - LATITIUDE AND LONGITUDE COORDINATES WERE UPDATED IN PART A TO MORE ACCURATE REFLECT THE LOCATION OF THE INCIDENT. BDK
2025-03-31 10:13 | NO | YES | NO | 20130072 | 15680 | 2013-06-03 11:51 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2013-01-07 14:02 |  |  | 2013 | 1119 LONGWOOD AVENUE | BRONX | BRONX | NY | 10474-5712 | 40.8147 | -73.894 | [9 empty] | 2013-01-07 14:10 | 1035007 |  | NATURAL GAS |  | 2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-01-07 14:02 |  |  |  | 2013-01-07 14:02 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 54 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | VALVE RISER CONNECTION | 2010 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 400000 | 499538.4464303252 | 1250 | 1561.05764509476625 | 5000 | 6244.230580379065 | MATERIALS |  | 10 | 8.75 |  | 0 | 406260 | 210134.6532331288632172131147540983606557 | 507352.48465579903125 | 0 | 0 | 0 |  |  |  |  | 303 | 303 | 350 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK ON 1" FITTING AT BOTTOM OF 36" MAIN LINE VALVE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | VALVE | MATERIAL/WELD/EQUIP FAILURE | VALVE | EQUIPMENT FAILURE | VALVE | [197 empty] | VALVE | [16 empty] | OTHER | BODY BLEED RISER CONNECTION | [65 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON MONDAY JANUARY 7, 2013 AT 10:56, LEAK SURVEY REPORTED A TYPE 1 GAS READING OF 10% IN TRANSMISSION MAIN VALVE 43940 IN FRONT OF 1119 LONGWOOD AVE. SUPERVISION AND GAS CONSTRUCTION WERE DISPATCHED. AT 12:45 HRS GAS CONSTRUCTION REPORTED THAT THEY PERFORMED A LEAK INVESTIGATION AND DETERMINED A PROBABLE LEAK WAS ON TRANSMISSION VALVE 43940. GAS CONTROL WAS NOTIFIED AND VALVE 46630 WAS IDENTIFIED TO ISOLATE THE SECTION OF 36" TRANSMISSION MAIN. A CODE MURRE (MULTIPLE RESOURCE RESPONSE EVENT) WAS INITIATED AND GAS DISTRIBUTION SERVICES (GDS) RESPONDED AND LOCATED VALVE 46630 AS CONTINGENCY. AT 14:02, GAS CONTROL GAVE PERMISSION TO GDS TO CLOSE VALVE 46630. APPROXIMATELY 2,400 FEET OF 36", 303 PSI MAIN WAS AFFECTED AND NO REPORTED SYSTEM IMPACT RESULTED FROM THIS SECTION OF MAIN BEING ISOLATED. AN OPERATIONAL PLAN WAS DEVELOPED AND THE SEGMENT OF TRANSMISSION MAIN WAS REDUCED FROM 303 PSI TO APPROXIMATELY 60 PSI THROUGH A PRESSURE CONTROL TEMPORARY REGULATOR CONNECTION TO A 6" LPPE DISTRIBUTION MAIN AT TIFFANY ST. AND OAK POINT AVE. ON JANUARY 10, 2013 THE VALVE WAS EXCAVATED AND A VISUAL LEAK WAS CONFIRMED ON THE BODY BLEED RISER'S WELDED CONNECTION AT THE BOTTOM OF THE VALVE BODY. THE VALVE MANUFACTURER'S REPRESENTATIVE WAS CONTACTED AND RESPONDED TO THE LOCATION TO REVIEW REPAIR OPTIONS WITH ENGINEERING AND GAS OPERATIONS' PERSONNEL. ON JANUARY 14, 2013, THE PRESSURE WAS REDUCED FURTHER TO LOW PRESSURE AND THE LEAKING CONNECTION WAS CUT, REMOVED AND A WELDED HIGH HAT INSTALLED. THE HIGH HAT WAS TESTED AND ALL TESTS PASSED. ON JANUARY 16, 2013 A NEW RISER WAS INSTALLED AND RESTORATION OPERATIONS WERE INITIATED AT 12:39. LEAK SURVEY MONITORED THE SEGMENT AS PRESSURE WAS RESTORED IN 60 PSI INCREMENTS. AT 19:56, THE SEGMENT OF ISOLATED MAIN WAS RETURNED TO NORMAL OPERATING PRESSURE OF 295 PSI. THE SERIOUS LEVEL ICS STRUCTURE WAS TERMINATED AT 20:18. US DOT, NYS PSC, NYC DEP AND FDNY WERE NOTIFIED. THE DOT-PHMSA OFFICE INQUIRED ABOUT THE LEAK. THERE WERE NO REPORTS OF ANY INJURY, EVACUATION OR MEDIA ATTENTION ASSOCIATED WITH THIS INCIDENT. NOTE--THIS GAS DISTRIBUTION INCIDENT REPORT WAS GENERATED TO REPLACE GAS TRANSMISSION INCIDENT REPORT 20130010-15729
2025-03-31 10:13 | NO | NO | NO | 20130073 | 15884 | 2013-06-04 07:57 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2013-01-13 22:28 |  |  | 2013 | 1060 KNOLLWOOD ROAD | TOWN OF GREENBURGH | WESTCHESTER | NY | 10523 | 41.0702 | -73.8001 | [9 empty] | 2013-01-14 13:18 | 1035662 |  | NATURAL GAS |  | 14.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-01-14 12:51 |  |  |  | 2013-01-14 12:51 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER A BUILDING |  | 28 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | ONSHORE PIPELINE, INCLUDING VALVE SITES | 1948 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 47993 | 59935.871648826493309 | 745 | 930.390356476480685 | 1500 | 1873.2691741137195 | MATERIALS |  | 30 | 26.25 |  | 0 | 50268 | 26009.1149581510859076393442622950819672 | 62765.781179416693494 | 0 | 0 | 0 |  |  |  |  | 205 | 205 | 245 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK ON COMPRESSION COUPLING RESULTING IN NO PRESSURE DROP OR INCREASED FLOW ON SCADA | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | BOLTED |  | COUPLING |  | DRESSER |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | 12" COMPRESSION COUPLING SEAL PACKING LEAK | [7 empty] | NO | [86 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-597-5463 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON JANUARY 13, 2013 AT 22:28 THE RESIDENT AT 1060 KNOLLWOOD RD (TG) REPORTED AN OUTSIDE ODOR AND GAS DISTRIBUTION SERVICES (GDS) RESPONDED, INVESTIGATED AND DETECTED 10% OVER THE 12" 1948 245 PSI TRANSMISSION MAIN. GAS CONSTRUCTION -EMERGENCY RESPONSE FORCE (ERF) RESPONDED AND INVESTIGATED, DETECTING 95% DIRECTLY OVER THE MAIN. THE 95% READING OVER THE TRANSMISSION MAIN WAS AERATED AND 70% QUICKLY RETURNED. CONTINGENCY CASE 40-C-1 WAS IDENTIFIED AND (2) TRANSMISSION VALVES WERE INITIALLY STAFFED. AN OPERATIONAL PLAN WAS DEVELOPED TO ENSURE NO SYSTEM IMPACT OR CUSTOMER LOSS RESULTED AS A RESULT OF THE PLANNED ISOLATION OF REGULATOR STATIONS GR-484 AND GR-483. AT 12:51 ON JANUARY 14, 2013, TRANSMISSION V-40427 WAS CLOSED ISOLATING THE EFFECTED SEGMENT OF TRANSMISSION MAIN. PRESSURE WAS REDUCED TO APPROX 60 PSI AND EXCAVATION OPERATIONS WERE INITIATED. AROUND-THE-CLOCK OPERATIONS CONTINUED AND ADDITIONAL INVESTIGATION AND EXCAVATION WAS COMPLETED. APPROXIMATELY 21' SOUTH OF THE HIGHEST READING AND INITIAL EXCAVATION, A SECOND EXCAVATION OVER A 12" COMPRESSION COUPLING WAS COMPLETED AND INVESTIGATION CONTINUED. THE COUPLING WAS FOUND NOT LEAKING. A WELDED REPAIR SLEEVE AND (2) HIGH HATS WERE INSTALLED. ON JANUARY 16, 2013 RESTORATION OPERATIONS WERE INITIATED AT 12:39 AND LEAK SURVEY MONITORED THE SEGMENT AS PRESSURE WAS RESTORED IN 60 PSI INCREMENTS AND NO LEAKS WERE FOUND. THE SEGMENT OF ISOLATED MAIN WAS RETURNED TO NORMAL OPERATING CONDITION AT AT 205 PSI. INVESTIGATION CONTINUED AND AT 14:27 A VISIBLE LEAK ON A 12" TRANSMISSION COUPLING WAS CONFIRMED AT THE COMPRESSION END SEAL. AN OPERATIONAL PLAN WAS DEVELOPED AND THE LEAK WAS MONITORED AROUND-THE-CLOCK UNTIL SYSTEM CONDITIONS WERE FAVORABLE FOR ISOLATION. THERE WAS NO MIGRATION TOWARD BUILDINGS AND ALL SUBSURFACE STRUCTURES REMAINED GAS FREE DURING THIS PERIOD. ON JANUARY 19, 2013, THE SEGMENT OF MAIN FROM V-40427 TO GR-484 WAS ISOLATED AND PRESSURE REDUCED. THE LEAK WAS FULLY EXCAVATED AND A WELDED REPAIR SLEEVE WAS INSTALLED ON THE LEAKING COUPLING. THE WELDS WERE TESTED AND ALL TESTS PASSED. RESTORATION OPERATIONS WERE INITIATED AT 18:38, AND AT 21:31 THE SEGMENT OF MAIN FROM V-40427 TO GR-484 WAS RESTORED TO FULL LINE PRESSURE AFTER INCREMENTAL INCREASES. NO OTHER TRANSMISSION LEAKS WERE FOUND. THE SUPPLY TO GR-483 WAS RESTORED AT 22:39 AFTER V-34589 WAS OPENED AND LEAK SURVEY DETECTED NO LEAKS. REGULATOR STATION GR-483 WAS RETURNED TO SERVICE. THE US DOT AND NYS PSC WERE NOTIFIED. THIS WAS A SERIOUS LEVEL INCIDENT. NOTE--THIS GAS DISTRIBUTION INCIDENT REPORT WAS GENERATED TO REPLACE GAS TRANSMISSION INCIDENT REPORT 20130011-15731.
2025-03-31 10:13 | NO | YES | NO | 20130074 | 15919 | 2013-06-14 14:35 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2013-05-15 06:24 |  |  | 2013 | HIGHWAY 280 AT THIRD AVENUE | MOUNT VERNON | MONTGOMERY | GA | 30445 | 32.1909 | -82.6237 | [9 empty] | 2013-05-15 09:50 | 1047186 |  | NATURAL GAS |  | 26075.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-05-15 06:24 |  |  |  | 2013-05-15 07:13 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | 6-INCH POSI-HOLD COUPLING | 2012 | [8 empty] | OTHER | 6-INCH POSI-HOLD COUPLING | [9 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | 0 | 0 | 48000 | 59944.613571639024 | 226675 | 283082.193361484911775 | 0 | 0 |  |  | 215000 | 188125 |  | 0 | 489675 | 316098.0549388808030569672131147540983607 | 531151.806933123935775 | 442 | 11 | 1899 |  |  |  |  | 250 | 280 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSE OF INCIDENT WAS DUE TO 6-INCH POSI-HOLD COUPLING SEPARATED FROM MAIN | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | OTHER COMPRESSION TYPE FITTING | STYLE 700 POSI-HOLD |  |  | DRESSER |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | SEE PART H | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@aglresources.com | 4045843733 | 4045844710 |  |  |  | RICHARD R. LONN | MANAGING DIRECTOR COMPLIANCE AND PIPELINE RISK MAN | 4045843552 | rlonn@aglresources.com | A 6-INCH HP STEEL MAIN WITH A BULL PLUG END CONNECTED BY A STYLE 700 POSI-HOLD COMPRESSION COUPLING SEPARATED FROM THE MAIN.
2025-03-31 10:13 | NO | NO | NO | 20130075 | 15686 | 2013-06-20 08:22 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2013-05-22 08:49 |  |  | 2013 | HIGHWAY 84 AT CHURCH STREET | PATTERSON | PIERCE | GA | 31557 | 31.3893 | -82.1381 | [9 empty] | 2013-05-22 11:15 | 1047943 |  | NATURAL GAS |  | 6756.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 200 | 2013-05-22 08:52 |  |  |  | 2013-05-22 09:14 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 84 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1965 | [5 empty] | 8.625 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 1 | 5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 25550 | 31908.01826573702215 | 39500 | 49329.4215849946135 | 0 | 0 |  |  | 1980 | 1732.5 |  | 0 | 67030 | 35248.7751000945063581967213114754098361 | 82969.93985073163565 | 4 | 0 | 5 |  |  |  |  | 238 | 240 | 250 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSE OF INCIDENT WAS DUE TO 3RD PART DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY | 2011-06-23 | NO |  |  | YES | YES | [8 empty] | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | NO | 4083400032 |  |  | CONTRACT LOCATOR | YES | YES | 6 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@aglresources.com | (404) 584-3733 | (404) 584-4807 |  |  |  | RICHARD R. LONN | DIRECTOR COMPLIANCE ASSURANCE | (404) 584-3552 | rlonn@aglresources.com | A CONTRACTOR RUPTURED AN 8-INCH HP STEEL NATURAL GAS MAIN WHILE BORING UNDERNEATH THE STREET TO INSTALL TELEPHONE CABLE. THE GAS MAIN WAS CORRECTLY MARKED BUT WAS NOT SPOTTED BY THE EXCAVATOR.
2025-03-31 10:13 | NO | NO | NO | 20130076 | 15790 | 2013-06-21 19:34 | SUPPLEMENTAL FINAL | 32013 | AMERIGAS PROPANE LP | 500 N. GULPH RD. | KING OF PRUSSIA | PA | 19406 | 2013-06-18 17:30 |  |  | 2013 | MERRIDIAN BLVD | MAMMOTH LAKES |  | CA | 93546 | 37.6607 | -118.8884 | [9 empty] | 2013-06-20 21:07 | 1051169 |  | PROPANE GAS |  | 10.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-06-18 17:30 |  |  |  | 2013-06-18 18:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | OTHER | PROPANE | MAIN |  | UNKNOWN | [5 empty] | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 4 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 2500 | 3122.1152901895325 | 1000 | 1248.846116075813 | 0 | 0 |  |  | 275 | 240.625 |  | 0 | 3775 | 2032.913336555783598360655737704918032787 | 4611.5864062653455 | 4 | 0 | 0 |  |  |  |  | 18 | 18 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  | YES | [6 empty] | NO |  |  |  |  | YES | [9 empty] | UTILITY | BORING | TELECOMMUNICATIONS | NO |  |  |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | JEFF PAHLOW | DISTRICT MANAGER | pahlowj@amerigas.com | 7608736371 | 7608735346 |  |  |  | JEFF PAHLOW | DISTRICT MANAGER | 7608736371 | pahlowj@amerigas.com
2025-03-31 10:13 | NO | NO | NO | 20130077 | 15874 | 2013-06-24 14:38 | SUPPLEMENTAL FINAL | 6760 | GREENSBORO MUNICIPAL GAS SYSTEM, CITY OF | 212 NORTH MAIN STREET | GREENSBORO | GA | 30642 | 2013-06-04 09:02 |  |  | 2013 | LOVE SPRINGS REGULATOR STATION | GREENSBORO | GREENE | GA | 30642 | 33.5762 | -83.1759 | [9 empty] | 2013-06-04 11:02 | 1049322 |  | NATURAL GAS |  | 430 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 5 | 2013-06-04 09:02 |  |  |  | 2013-06-04 09:04 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | LEAK ON FLANGE ASSEMBLY | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 20000 | 24976.92232151626 | 14000 | 17483.845625061382 | 0 | 0 |  |  | 2500 | 2187.5 |  | 0 | 36500 | 19609.5422014833498032786885245901639344 | 44648.267946577642 | 146 | 118 | 709 |  |  |  |  | 400 | 400 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 2 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | CONTRACTOR WAS PREPARING PIPE TO APPLY EXTERIOR COATING. CONTRACTOR USED PROPANE TORCH TO DRIVE PIPE CAUSING FAILURE ON FLANGE WHICH CAUSED GAS TO LEAK AND CAUSED GAS TO INGNITE. |  | YES |  |  |  | OTHER MAINTENANCE | YES | NO, THEY WERE NOT QUALIFIED FOR THE TASK(S) NOR WERE THEY PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | ANTHONY WOODRUFF | GAS SUPERINTENDANT | awoodruff@greensboroga.gov | 706-453-7967 | 706-453-2912 |  |  |  | LARRY POSTELL | CITY MANAGER | 706-453-7967 | larrypostell@greensboroga.gov | ON JUNE 4, 2013 AN EXTERNAL CONTRACTOR WAS CLEANING PIPE TO INSTALL POWDER COATING ON REGULATOR STATION. CITY OF GREENSBORO PERSONNEL CHECKED STATION FOR LEAKS AND NON WERE FOUND. IMMEDIATLY AFTER TESTING, THE CREW BEGAN HEATING THE PIPE WITH A PROPANE TORCH TO APPROXIMATLEY 110 DEGREES. A LEAK BEGAN AT THE INLET FILTER ASSEMBLEY FLANGE OF THE 400 POUND LINE, , CAUSING A FIRE. THE CONTRACTOR ATTEMPTED TO EXTINGUISH THE FIRE BUT WAS UNSUCCESFUL. THIS FIRE LED TO A COMPLETE MELT DOWN OF THE REGULATOR STATION, WHICH RESULTED IN A SHUT DOWN OF THE COMPLETE GAS SYSTEM OF THE CITY OF GREENSBORO.
2025-03-31 10:13 | NO | YES | NO | 20130078 | 15885 | 2013-06-25 16:04 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2013-05-29 06:02 |  |  | 2013 | INTERSECTION OF CASTLE HILL AND WESTCHESTER AVENUES | NEW YORK | BRONX | NY | 10462-4807 | 40.8342 | -73.8517 | [9 empty] | 2013-05-30 04:04 | 1048708 |  | NATURAL GAS |  | 3.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-05-29 06:02 |  |  |  | 2013-05-29 06:02 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1971 | [5 empty] | 20 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.375 | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 600000 | 749307.6696454878 | 2500 | 3122.1152901895325 | 0 | 0 |  |  | 10 | 8.75 |  | 0 | 602510 | 311641.9447975008744672131147540983606557 | 752438.5349356773325 | 0 | 0 | 0 |  |  |  |  | 200 | 200 | 245 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK ON VALVE CONNECTION DID NOT RESULT IN PRESSURE DROP OR INCREASED FLOW. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | VALVE | MATERIAL/WELD/EQUIP FAILURE | VALVE | EQUIPMENT FAILURE | VALVE | [197 empty] | VALVE | [16 empty] | OTHER | LEAK AT BOLTED CONNECTION ON 20" VALVE BODY | [65 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-597-5463 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | AT 06:02 ON MAY 29, 2013 PROCEDURE MPC 13-19 WAS INITIATED DUE TO THE INVESTIGATION OF LEAK (XL13001342) IN THE VICINITY OF THE TRANSMISSION SYSTEM AT THIS LOCATION. IN ADDITION TO THE 20" TRANSMISSION MAIN (OPERATING AT LESS THAN 20% SMYS), LOCATED IN THIS VICINITY IS THE 12" TRANSMISSION STRADDLE CONNECTIONS SUPPLYING TP-HP-MP GR-102, (3) TRANSMISSION VALVES AND ASSOCIATED FITTINGS AS WELL AS 12" LOW PRESSURE POLYETHYLENE (LPPE) AND 12" LOW PRESSURE CAST IRON DISTRIBUTION MAINS AND SERVICES. CONTINGENCY B13-044; CASE 20 & 21-A WAS PLACED IN EFFECT. AT 09:16 ISOLATION OF THE AFFECTED SEGMENT WAS ACHIEVED AND PRESSURE WAS REDUCED FROM 200 PSI TO 60 PSI PER THIS PROCEDURE AND EXCAVATION OPERATIONS BEGAN. THE (3) VALVES AT THIS LOCATION (20" MAIN LINE V-7583 AND 12" INLETS V-7584/7585) WERE INVESTIGATED FOR A POSSIBLE SOURCE OF THE SUSPECTED LEAK AND A VISIBLE LEAK ON THE BLEED CONNECTION TO THE VALVE BODY OF 12" INLET V-7585. ADDITIONALLY, A VISIBLE LEAK ON A .5" RELIEF VALVE BOTTOM OF THE BODY OF 20" V-7583 WAS LOCATED UNDER THE GEAR BOX. THIS VALVE'S OUTER FLANGES WERE ABATED AND VISIBLE LEAKS WERE LOCATED ON BOLTS OF THE SOUTH FLANGE AT THE 6-8 O'CLOCK POSITION. ATTEMPTS TO REPAIR THE LEAKS WERE NOT SUCCESSFUL AND AN OPERATIONAL PLAN WAS IDENTIFIED FOR THE REPLACEMENT OF THE 20" MAIN LINE VALVE, (2) 12" INLET VALVES TO GR-102 AND ASSOCIATED PIPING. PRESSURE REDUCTION IN THE AFFECTED SEGMENT OF TRANSMISSION MAIN WAS ACHIEVED AND THE OPERATIONAL PLAN CONTINUED AROUND-THE-CLOCK. ON JUNE 9, 2013 INSTALLATION OF APPROXIMATELY 12' OF 20'' PIPE AND 8' OF 12" PIPE ASSOCIATED WITH THE (3) REPLACEMENT VALVES WAS COMPLETED. ALL WELDING WAS TESTED AND PASSED SUCCESSULLY. LEAK SURVEY MONITORED THE ISOLATED SEGMENT OF MAIN AS PRESSURE WAS RESTORED INCREMENTALLY AND NO LEAKS WERE DETECTED. AT 14:53 NORMAL SYSTEM CONDITIONS RESUMED. THERE WAS NO MIGRATION BEYOND THE OPEN EXCAVATION; ALL SUBSURFACE STRUCTURES REMAINED GAS FREE DURING THIS OPERATION. THERE WERE NO REPORTED OUTAGES OR NEGATIVE SYSTEM IMPACT AS A RESULT OF THIS PROCEDURE. THERE WERE NO INJURIES, EVACUATIONS OR MEDIA ATTENTION REPORTED. THE US DOT, PSC, DEP WAS NOTIFIED AND THE FDNY WAS NOTIFIED UNDER THE TRANSMISSION LEAK NOTIFICATION PROTOCOL. THE SERIOUS LEVEL INCIDENT WAS TERMINATED.
2025-03-31 10:13 | NO | NO | NO | 20130079 | 15690 | 2013-06-26 13:40 | ORIGINAL FINAL | 11713 | KEYSPAN ENERGY DELIVERY - LONG ISLAND | 175 EAST OLD COUNTRY ROAD | HICKSVILLE | NY | 11801 | 2013-06-11 06:11 |  |  | 2013 | 527 BEACH 64TH STREET | ARVERNE | QUEENS | NY | 11801 | 40.5957 | -73.7935 | [9 empty] | 2013-06-11 15:00 | 1050052 | [5 empty] | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-06-11 06:11 |  |  |  | 2013-06-11 06:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 42 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6 | CAST IRON | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | THERE WAS NO RELEASE | CLASS 4 LOCATION | 0 | 0 | 25373 | 31686.972503191603249 | 15259 | 19056.142885200830567 | 18626 | 23261.007758028092938 | TRANSPORTATION 20% OF LABOR,ROBOTICS CAMERA CREW AND PAVING |  | 0 | 0 |  | 0 | 59258 | 30650.288323676721746 | 74004.123146420526754 | 0 | 0 | 140 |  |  |  |  | 0.23 | 0.21 | 0.43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | OTHER | ALARM AT SYSTEM LP INTO GSO |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR RECEIVED A LOW PRESSURE ALARM AND REMOTELY RAISED QD1 TO HOLD UP SYSTEM. ALL PROTOCOLS WERE FOLLOWED IN GAS CONTROL. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | HEAVY RAIN ON COASTAL AREA CAUSED WATER INTRUSION INTO THE LOW PRESSURE MAIN. | YES |  |  |  | YES | HEAVY RAIN THAT BROUGHT 4-6 INCHES OF RAIN IN A 12 HOUR PERIOD | [213 empty] | DEBORAH MAIFORTH | LEAD SUPERVISOR | deborah.maiforth@nationalgrid.com | 5165454986 | 5165454193 |  |  |  | ROBERT DE MARINIS | VP MAINTENANCE AND CONSTRUCTION NY GAS | 5165454337 | robert.demarinis@nationalgrid.com | GSO RECEIVED A LOW PRESSURE ALARM OF 4" WC FROM A LOW POINT LOCATED ON 64TH ST AND THURSBY AVE IN ARVERNE. THE GAS SYSTEM OPERATOR REMOTELY RAISED THE FEEDING REGULATORS QD-1 & QD-1 WHICH CAUSE THE LOW POINT TO RETURN ABOVE 5" WC. GSO CONTATCED SHIFT CREW AND DISPATCH TO INVESTIGATE FURTHER. JOE SASSO WENT OUT TO THE LOCATION TO PUMP THE DRIPS IN THE AREA AND INVESTIGATE THE ROOT CAUSE OF THE WATER INTRUTION. DISPATCH DID RECEIVE NO GAS CALLS IN THE AREA AS A RESULT OF THE WATER INTRUSION. GSO TRENDED THE SYSTEM TO ENSURE THE PRESSURES HELD UP DURING THE FIELD OPERATIONS INVESTIGATION.
2025-03-31 10:13 | NO | NO | NO | 20130080 | 15691 | 2013-06-27 10:22 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 200 CIVIC CENTER DR | COLUMBUS | OH | 43215 | 2013-05-17 14:14 |  |  | 2013 | UPTON AND W. CENTRAL | TOLEDO | LUCAS | OH | 43606 | 41.6789 | -83.5892 | [9 empty] | 2013-05-29 12:10 | 1048644 |  | NATURAL GAS |  | 2.37 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 6 | 2013-06-17 14:14 |  |  |  | 2013-06-17 14:17 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1969 | [5 empty] | 16 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 2.19 | [6 empty] | MECHANICAL PUNCTURE | 2.5 | 5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 55000 | 68686.536384169715 | 5000 | 6244.230580379065 | 0 | 0 |  |  | 6630 | 5801.25 |  | 0 | 66630 | 36400.5723034855642622950819672131147541 | 80732.01696454878 | 0 | 0 | 6 |  |  |  |  | 53 | 53 | 58 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | YES | [7 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | GRADER/SCRAPER | ROAD WORK | YES | 313403046 | OHIO UTILITY PROTECTION SERVICE |  | CONTRACT LOCATOR | NO | YES | 16 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | ROB R. SMITH | OPERATIONS COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB R.SMITH | OPERATIONS COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | ON MAY 17, 2013, AT APPROXIMATELY 2:14 PM A THIRD PARTY EXCAVATOR STRUCK AND DAMAGED A 16-INCH STEEL MEDIUM PRESSURE DISTRIBUTION PIPELINE AS A RESULT OF A LARGE ROADWAY IMPROVEMENT ACTIVITY. THE 16-INCH STEEL PIPELINE WAS NOT MARKED UNDER THE ACTIVE "ONE CALL TICKET". THE THIRD PARTY EXCAVATION COMPANY HAD BEEN NOTIFIED OF THE FACILITIES LOCATION VIA MAPS THAT WERE PROVIDED DURING THE DESIGN PHASE OF THIS PROJECT. IN ADDITION, THE LOCATOR HAD MET WITH THE EXCAVATOR, EXCHANGED CONTACT INFORMATION, AND MARKED THE FACILITY PREVIOUSLY THROUGHOUT THE COURSE OF CONSTRUCTION. COLUMBIA GAS OF OHIO INC. (COLUMBIA) RESPONDED TO THE DAMAGE IMMEDIATELY AND COORDINATED WITH THE FIRE DEPARTMENT TO ENSURE THAT A PERIMETER WAS SET AND THAT NO SECONDARY DAMAGE HAD OCCURRED, TO PROTECT LIFE AND PROPERTY. AT APPROXIMATELY 4:45 PM THREE (3) CRITICAL VALVES WERE CLOSED, ISOLATING AND SHUTTING OFF NATURAL GAS TO THE DAMAGED PIPELINE, MAKING THE AREA SAFE. AS A RESULT OF THIS ACTION, SIX(6) RESIDENTIAL CUSTOMERS HAD THEIR NATURAL GAS SERVICE INTERRUPTED. SERVICE RESTORATION TO THE SIX(6) RESIDENTIAL CUSTOMERS BEGAN AT 8:00 AM, SATURDAY, MAY 18, 2013 FOLLOWING A TEMPORARY REPAIR. COLUMBIA GAS HAD BEEN MONITORING THE COSTS ASSOCIATED WITH THE PERMANENT REPAIRS SINCE THE INITIAL DAMAGE DATE. PERMANENT REPAIR TO THE 16-INCH PIPELINE WERE PLANNED AND IMPLEMENTED. ON MAY 29, 2013, IT WAS DETERMINED THAT THE COST OF THE PERMANENT REPAIRS EXCEEDED THE $50,000 REPORTING CRITERIA AS DEFINED IN CFR PART 191.3(1)(II).
2025-03-31 10:13 | NO | NO | NO | 20130081 | 15761 | 2013-07-01 14:58 | SUPPLEMENTAL FINAL | 4060 | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2013-06-01 06:06 |  |  | 2013 | 14115 SAINT CLAIR AVE | CLEVELAND | CUYAHOGA | OH | 44110-3425 | 41.5503 | -81.5837 | [9 empty] | 2013-06-01 15:32 | 1048968 |  | NATURAL GAS |  | 1727 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 4 | 2013-06-01 06:46 |  |  |  | 2013-06-01 06:46 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1948 | [5 empty] | 20 | API 5L | YOUNGSTOWN SHEET AND TUBE | STEEL |  | LONGITUDINAL ERW - LOW FREQUENCY | LF-ERW | 0.375 | [6 empty] | RUPTURE |  |  |  | LONGITUDINAL SEAM CORROSION | LONGITUDINAL |  | 16 | 1 |  | CLASS 3 LOCATION | 0 | 0 | 60000 | 74930.76696454878 | 5000 | 6244.230580379065 | 0 | 0 |  |  | 8200 | 7175 |  | 0 | 73200 | 40257.5445173006181147540983606557377049 | 88349.997544927845 | 0 | 0 | 0 |  |  |  |  | 88 | 85 | 95 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [5 empty] | YES | [5 empty] | YES |  |  | YES | NO |  | NO | NO | [8 empty] | NO | NONE | [21 empty] | 2012-04-10 | NO | [227 empty] | AARON MCCOY | TECHNICAL SPECIALIST | aaron.m.mccoy@dom.com | 3304589186 | 3304783760 |  |  |  | AARON MCCOY | TECHNICAL SPECIALIST | 3304589186 | aaron.m.mccoy@dom.com | ON JUNE 1, 2013, A 20" INTERMEDIATE PRESSURE DISTRIBUTION MAINLINE OPERATING AT 88 PSIG LOCATED ON SAINT CLAIR AVE., CLEVELAND, OHIO FAILED AT THE SEAM THAT RESULTED IN A LEAK. AT APPROXIMATELY 6:06 A.M. ON JUNE 1, 2013, AN ODOR COMPLAINT WAS CALLED IN BY THE PUBLIC. DOMINION ARRIVED ON THE SCENE AT APPROXIMATELY 6:46 A.M. AND WAS ABLE TO PINPOINT THE LEAK. THE MAINLINE VALVES WERE SHUT AT APPROXIMATELY 3:00 P.M. TO ISOLATE THE SECTION OF PIPELINE THAT FAILED. AT APPROXIMATELY 7:00 P.M., TWO CLAMPS WERE INSTALLED ON THE PIPELINE. THE SECTION OF PIPE THAT FAILED WAS CUT OUT AND SENT TO A THIRD PARTY LABORATORY, KEIFNER & ASSOCIATES, FOR FAILURE INVESTIGATION. THE RESULT OF THE FAILURE INVESTIGATION CONCLUDED THAT THE RUPTURE ALONG THE LONGITUDINAL SEAM WELD WAS CAUSED BY SELECTIVE SEAM CORROSION (SSC). THE PIPELINE THAT FAILED WAS REPLACED IN OCTOBER 2013.
2025-03-31 10:13 | NO | YES | YES | 20130082 | 16720 | 2013-07-03 11:52 | SUPPLEMENTAL FINAL | 14330 | ORANGE & ROCKLAND UTILITY INC | ONE BLUE HILL PLAZA | PEARL RIVER | NY | 10965 | 2013-06-04 11:55 |  |  | 2013 | 177 SOUTH HIGHLAND AVENUE | NYACK | ROCKLAND | NY | 10960 | 41.0871 | -73.9317 | [9 empty] | 2013-06-04 14:03 | 1049258 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 7 | 8 | NO |  |  |  |  | YES | 0 | 2013-06-04 11:55 |  |  |  | 2013-06-04 12:05 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1969 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | PIPE PULLED FROM COUPLING | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 75000 | 93663.458705685975 | 0 | 0 |  |  | 0 | 0 |  | 0 | 75000 | 38792.595502307775 | 93663.458705685975 | 0 | 0 | 33 |  |  |  |  | 60 | 60 | 80 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY CONTRACTOR DAMAGE TO PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | GRADING | NO |  |  |  | UTILITY OWNER | NO | YES | 6 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | ALMED SEJATI | SENIOR ENGINEER | sejatia@oru.com | 845-577-3024 |  |  |  |  | GARY FULOP | PRINCIPAL ENGINEER | 845-577-3537 | fulopg@oru.com | NYACK COLLEGE IS A CAMPUS COMPRISED OF MULTIPLE BUILDINGS. ORANGE & ROCKLAND UTILITIES PROVIDES NATURAL GAS AND ELECTRIC SERVICES TO A NUMBER OF THE BUILDINGS INCLUDING 177 SOUTH HIGHLAND AVENUE KNOWN AS SKY ISLAND LODGE AND 154 SOUTH HIGHLAND AVENUE KNOWN AS BOWMAN GYMNASIUM. ON TUESDAY, JUNE 4, 2013 AT APPROXIAMATELY 1155 THE GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A CALL FROM ROCKLAND COUNTY FIRE CONTROL OF A GAS EXPLOSION AT THE SKY ISLAND LODGE. GERC IMMEDIATELY DISPATCHED ALL AVAILABLE UNITS. THE FIRST TWO RESPONDERS ARRIVED AT 1205 AND 1206 RESPECTIVELY. A STRONG ODOR OF GAS WAS PRESENT IN THE AIR AND GAS VAPORS COULD BE SEEN COMING FROM THE SEWER CLEAN OUT LOCATED ALONG THE CURBLINE OF 177 SOUTH HIGHLAND AVENUE, THE SKY ISLAND LODGE. THE O&R SERVICEMEN IMMEDIATELY BEGAN A LEAK INVESTIGATION. HIGH CONCENTRATIONS OF GAS WERE DETECTED IN THE OUTDOOR SEWER CLEAN-OUTS, CATCH BASIN AND SEWER MANHOLE. THERE WERE NO GAS READINGS IN THE TEST POINTS TAKEN IN THE EARTH. COVERS ON THE SEWER CLEAN OUTS AND MANHOLES WERE REMOVED ALLOWING THESE STRUCTURES TO VENT. AT 1211, A 7% GAS-IN-AIR READING WAS RECORDED IN ATMOSHERE INSIDE THE DAMAGED BUILDING AT 177 SOUTH HIGHLAND. THE SERVICE TO THIS BUILDING WAS IMMEDIATELY TURNED OFF AND ISOLATED. THE ELECTRIC CONTROL CENTER WAS CONTACTED TO DE-ENERGIZE THE AREA AT 1234. 258 WERE AFFECTED. GAS MAIN VALVES WERE IDENTIFIED AND CLOSED TO ISOLATE THE AREA AFFECTING 33 CUSTOMERS. UPON INVESTIGATION OF THE INCIDENT, IT WAS DISCOVERED THAT A MAINTENANCE WORKER CONTRACTED BY NYACK COLLEGE WAS PERFORMING SOME GRADING OF THE PROPERTY BEHIND 154 SOUTH HIGHLAND, THE BOWMAAN GYM THE MORNING OF THE EXPLOSION. THIS WORKER, USING A BACKHOE, PULLED ON THE 2" STEEL GAS SERVICE FOR THE BOWMAN GYM CAUSING IT TO PULL FROM A CONNECTING COUPLING CAUSING GAS TO LEAK. THE GAS THEN MIGRATED THROUGH A STORM DRAIN INTO THE SEWER SYSTEM THAT WAS CONNECTED TO THE SKY ISLAND LODGE. AN UNCAPPED, OPEN SEWER TRAP WAS DISCOVERED IN THE BASEMENT OF THE SKY ISLAND LODGE. THIS WAS DEEMED THE POINT OF ENTRY INTO THE BUILDING FOR THE GAS. THE EXPLOSION OCCURRED SHORTLY THEREAFTER.
2025-03-31 10:13 | NO | NO | NO | 20130083 | 15694 | 2013-07-15 12:06 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2013-06-19 12:33 |  |  | 2013 | 3100 TERMINAL RD S | HOUSTON | HARRIS | TX | 77032 | 29.9874 | -95.3389 | [9 empty] | 2013-06-19 16:03 | 1051010 |  | NATURAL GAS |  | 575.41 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-06-19 12:33 |  |  |  | 2013-06-19 13:28 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 168 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2013 | [5 empty] | 4 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 2411 | 3010.967985858785143 | 7137 | 8913.014730433077381 | 0 | 0 | N/A |  | 4055 | 3548.125 |  | 0 | 13603 | 8220.779385402866180918032786885245901639 | 15472.107716291862524 | 3 | 0 | 0 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  |  |  | YES | [9 empty] | CONTRACTOR | AUGER | BUILDING CONSTRUCTION | YES | 530994863 | LONESTAR NOTIFICATION CENTER |  | UTILITY OWNER | YES | YES | 3 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO ABANDONED FACILITY | [170 empty] | LESLIE J. DAVENPORT | ADVANCED OPERATIONS COORDINATOR | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | DIRECTOR OF OPERATIONS | 713-207-5700 | steve.yarbrough@centerpointenergy.com | THE EXCAVATOR (WEBER BLAKE FOUNDATION) FAILED TO CALL IN LOCATE TICKET AND WAS WORKING OFF (SPAW GLASS CIVIL CONSTRUCTION) TICKET # 530994863 AND DRILLED INTO NEW UNMARKED 4" PLASTIC GAS MAIN.
2025-03-31 10:13 | NO | NO | NO | 20130084 | 15801 | 2013-07-17 14:15 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2013-06-20 08:37 |  |  | 2013 | 4362 EAST LAKE MEAD BOULEVARD | LAS VEGAS | CLARK COUNTY | NV | 89115 | 36.1957 | -115.0787 | [9 empty] | 2013-06-20 12:40 | 1051115 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-06-20 08:37 |  |  |  | 2013-06-20 08:37 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | TRANSITION FITTING | 1968 | [8 empty] | PLASTIC |  |  |  |  | POLYVINYL CLORIDE (PVC) |  |  | 0.308 |  |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 2383 | 2976.000294608662379 | 67514 | 84314.596680742438882 | 0 | 0 |  |  | 0 | 0 |  | 0 | 69897 | 36153.147304330753989 | 87290.596975351101261 | 27 | 0 | 1502 |  |  |  |  | 40 | 40 | 43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | TWO-INCH PVC-TO-STEEL TRANSITION FITTING |  |  | YES | [11 empty] | YES |  |  |  | OTHER | CIRCUMFERENTIAL SEAM | NO | [86 empty] | RENEE EGGE | COMPLIANCE SPECIALIST | renee.egge@swgas.com | 702-365-2080 | 702-221-4116 |  |  |  | PHIL ANDREW | DIRECTOR OF GAS OPERATIONS FOR SOUTHERN NEVADA | 702-630-8188 | phil.andrew@swgas.com | DURING A LEAK SURVEY, SOUTHWEST GAS DISCOVERED A GRADE 1 LEAK ON A TWO-INCH PVC MAIN AT 4362 E. LAKE MEAD BOULEVARD IN CLARK COUNTY. SEVERAL GAS CONTROL PLANS WERE ESTABLISHED. SOUTHWEST GAS IMPLEMENTED A SECTION OF THEIR VALVE ISOLATION PLAN TO QUICKLY MITIGATE THE SITUATION AND ELIMINATE THE LEAK. FOR THIS REASON, SERVICE TO 1529 ACTIVE CUSTOMERS WAS DISCONTINUED UNTIL REPAIRS TO THE MAIN WERE COMPLETED.
2025-03-31 10:13 | YES | NO | NO | 20130085 | 16593 | 2013-07-18 12:00 | SUPPLEMENTAL | 32061 | TEXAS COMMUNITY PROPANE, LTD. | 2579 WESTERN TRAILS BLVD SUITE 230 | AUSTIN | TX | 78745 | 2012-12-27 14:42 |  |  | 2012 | 11504 BRIARCREEK LOOP | MANOR | TRAVIS | TX | 78653 | 30.3152 | -97.5367 | [9 empty] | 2013-01-03 10:00 | 1034748 |  | PROPANE GAS |  | 10 |  | NO | [5 empty] | 0 | YES | 2 | 0 | 0 | 0 | 0 | 2 | YES |  |  |  |  | YES | 0 | 2012-12-27 14:42 |  |  |  | 2012-12-27 14:42 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | BELOW COCKSTOP | 2002 | [8 empty] | OTHER | PIPE BROKEN BELOW COCKSTOP | [9 empty] | OTHER | [8 empty] | CUSTOMER BROKE COCKSTOP WHILE TAMPERING WITH GAS LINE. | CLASS 3 LOCATION | 0 | 0 | 500 | 635.85 | 1000 | 1271.7 | 5000 | 6358.5 | OPERATOR OVERTIME $6500 |  | 5000 | 4513.742071881606765327695560253699788584 |  | 0 | 11500 | 7599.025687103594080338266384778012684989 | 12779.7920718816067653276955602536997886 | 0 | 0 | 750 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | JACKIE BURGE | OFFICE MANAGER | customerservicemanager@texascommunitypropane.com | 512-272-5503 | 512-899-9333 |  |  |  | JACKIE BURGE | OFFICE MANAGER | 512-272-5503 | custoemrservicemanager@texascommunitypropane.com | OPERATOR REMOVED METER AND REGULATOR, CAPPED RISER, CUSTOMER WAS HOOKING UP A PIPE TO HOME AND STEALING GAS. THEY BROKE THE PIPE THEY HAD HOOKED UP TO RISER AND AFTER ONE HOUR OF GAS BLOWING, CALLED OPERATOR. OPERATOR DISPATCHED REPAIR CREW WHO ARRIVED AND WERE BURNED WHEN GAS IGNITED FROM INTERIOR OF HOME BY ELECTRIC DRYER, CAUSING EXPLOSION AND FIRE TO WALL OF HOME. THIS REPORT WAS CALLED IN TO PHMSA ON 01-03-13 TO MOHAMMAD ELZBIC AT 10 AM. HE STATED I DID NOT HAVE TO FILE ONLINE SINCE I REPORTED BY PHONE.
2025-03-31 10:13 | NO | YES | NO | 20130086 | 15721 | 2013-07-22 19:15 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2013-06-22 00:10 |  |  | 2013 | 397 BLUEFIELD DRIVE | SAN JOSE |  | CA | 95136 | 37.271 | -121.8489 | [10 empty] | 1051305 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2013-06-22 00:10 |  |  |  | 2013-06-22 00:35 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET | [10 empty] | STEEL | [10 empty] | OTHER | [8 empty] | VEHICLE HIT METER SET | CLASS 3 LOCATION | 800000 | 999076.8928606504 | 2500 | 3122.1152901895325 | 0 | 0 | 0 | 0 |  |  | 200 | 175 |  | 0 | 802700 | 415242.6571205948318442622950819672131148 | 1002374.0081508399325 | 0 | 0 | 2 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA ON THIS PART OF THE SYSTEM | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | CHERYL DIZON | COMPLIANCE ENGINEER | c1dz@pge.com | 925-328-5721 |  |  |  |  | LAURENCE DENISTON | INTERIM MANAGER | 925-328-5756 | fsc2@pge.com | ON JUNE 22, 2013 AT APPROXIMATELY 0010 HOURS PACIFIC GAS AND ELECTRIC (PG&E) WAS NOTIFIED THAT A JUVENILE DRIVER WAS EVADING POLICE, LOST CONTROL OF A VEHICLE AND DAMAGED THE METER SET AT 397 BLUEFIELD DRIVE CAUSING A RELEASE OF GAS. THE GAS IGNITED AND CAUSED A STRUCTURE FIRE INVOLVING TWO HOMES AND RESULTING IN OVER $50,000 WORTH OF DAMAGES. PG&E'S GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SITE AT 0035 HOURS AND OBSERVED THAT TWO METER SETS WERE ENGULFED BY THE FIRE. FIELD CREWS ARRIVED AT 0050 HOURS AND STOPPED THE FLOW OF GAS AT 0133 HOURS BY DIGGING AND SQUEEZING THE 3/4-INCH STEEL BRANCH SERVICE IN ONE LOCATION. OUT OF AN ABUNDANCE OF CAUTION, THE FIRE DEPARTMENT EVACUATED SEVERAL HOMES IN THE NEIGHBORHOOD AND BLOCKED OFF THE AREA. MEDIA WAS NOT OBSERVED ON SCENE AND THERE WERE NO REPORTS TO PG&E OF INJURIES THAT REQUIRED IN-PATIENT HOSPITALIZATION. ADDITIONALLY, THERE WERE NO FATALITIES AS A RESULT OF THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC BECAUSE DAMAGES DUE TO THE RELEASE OF GAS ARE IN EXCESS OF $50,000.
2025-03-31 10:13 | NO | YES | NO | 20130087 | 15701 | 2013-07-29 15:15 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2013-06-29 15:30 |  |  | 2013 | 901 NW 7TH | GRAND PRAIRIE | DALLAS | TX | 75050 | 32.4506 | -97.0045 | [9 empty] | 2013-06-29 17:18 | 1052202 |  | NATURAL GAS |  | 2.19 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-06-29 16:06 |  |  |  | 2013-06-29 16:45 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1982 | [5 empty] | 0.5 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 0.5 |  |  | CLASS 3 LOCATION | 100000 | 124884.6116075813 | 2174 | 2714.991456348817462 | 0 | 0 | 0 | 0 |  |  | 12 | 10.5 |  | 0 | 102186 | 52857.6418194580263986557377049180327869 | 127610.103063930117462 | 0 | 0 | 0 |  |  |  |  | 22 | 22 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | OCCUPANT | BACKHOE/TRACKHOE | DRAINAGE | NO |  |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED | YES |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | KEN PARKS | OPERATIONS MANAGER | ken.parks@atmosenergy.com | 214-316-4911 | 817-375-7979 |  |  |  | MARC CHAPMAN | COMPLIANCE DIRECTOR | 214-206-2875 | marcus.chapman@atmosenergy.com | HOMEOWNER/EXCAVATOR WAS DIGGING IN YARD WITH A BACKHOE AND DAMAGED THE GAS SERVICE LINE. THE SINGLE SERVICE AT 901 NW 7TH IN GRAND PRAIRIE, TX WAS TERMINATED AT THE MAIN AND WILL NOT BE RESTORED, SO NO SUPPLEMENTAL REPORT WILL BE REQUIRED (PART A, ITEM 13.B).
2025-03-31 10:13 | NO | YES | YES | 20130089 | 15839 | 2013-08-08 17:13 | SUPPLEMENTAL FINAL | 31840 | UNISOURCE ENERGY SERVICES | 88 E BROADWAY | TUCSON, PIMA | AZ | 85701 | 2013-08-05 14:31 |  |  | 2013 | 1876 BOARDWALK AVE | PRESCOTT | YAVAPAI | AZ | 86301 | 34.5758 | -112.442 | [9 empty] | 2013-08-05 15:25 | 1056204 |  | NATURAL GAS |  | 5.06 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 1 | 2013-08-05 14:31 |  |  |  | 2013-08-05 14:38 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2000 | [5 empty] | 0.5 | ASTM D 2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 3408 | OTHER | [8 empty] | CONTRACTOR BURNED THROUGH PLASTIC SERVICE LINE WITH A TORCH | CLASS 3 LOCATION | 1200 | 1498.6153392909756 | 1322 | 1650.974565452224786 | 258 | 322.202297947559754 | 0 | 0 |  |  | 23 | 20.125 |  | 0 | 2803 | 1456.529009897563384590163934426229508197 | 3491.91720269076014 | 0 | 0 | 2 |  |  |  |  | 53 | 53 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | CONTRACTOR BURNED THROUGH PLASTIC SERVICE LINE WITH A TORCH. SEE PART H | [154 empty] | BILL PARRY | DISTRIC MANAGER | bparry@uesaz.com | 928-203-1222 | 928-717-1794 |  |  |  | NATHAN SHELLEY | SENIOR DIRECTOR | 928-226-2266 | nshelley@uesaz.com | AN INDEPENDENT PLUMBING CONTRACTOR EXCAVATED TO EXPOSE AN UNDERGROUND WATER LINE TO MAKE A REPAIR. THIS EXCAVATION WAS ON PRIVATE PROPERTY AND WAS DONE WITHOUT PROPER AUTHORIZATION THROUGH THE LOCAL 'ONE CALL' CENTER. THE CONTRACTOR WAS SWEATING AN UNDERGROUND COPPER WATER LINE WITH A PROPANE TORCH WHEN HE BURNED THROUGH A 1/2" PE NATURAL GAS SERVICE LINE. THIS RESULTED IN A FIRE THAT CAUSED INJURIES TO THE CONTRACTOR WHICH REQUIRED HOSPITALIZATION OF THE CONTRACTOR.
2025-03-31 10:13 | NO | YES | NO | 20130090 | 15887 | 2013-08-14 09:15 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2013-07-23 01:46 |  |  | 2013 | 1605 WINFIELD AVE | VILLAGE OF MAMARONECK | WESTCHESTER | NY | 10543 | 40.9677 | -73.7363 | [9 empty] | 2013-07-23 04:23 | 1054756 |  | NATURAL GAS |  | 57.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2013-07-23 01:46 |  |  |  | 2013-07-23 02:14 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 60 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1955 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | ELECTRIC ARCING | [5 empty] | CLASS 4 LOCATION | 55000 | 68686.536384169715 | 69000 | 86170.382009231097 | 11638 | 14534.071098890311694 | 500 | 624.4230580379065 | MATERIALS |  | 115 | 100.625 |  | 0 | 136253 | 70508.368902969120928950819672131147541 | 170116.037550329030194 | 0 | 0 | 9 |  |  |  |  | 11 | 11 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2340 | 718-904-4607 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | ON JULY 23,2013 AT 01:46 WESTCHESTER FIRE CONTROL REPORTED A BUILDING FIRE WITH A GAS ODOR AT THIS LOCATION TO THE GAS EMERGENCY RESPONSE CENTER (GERC). GAS DISTRIBUTION SERVICES (GDS) AND SUPERVISION WERE DISPATCHED. AT 02:02 WESTCHESTER FIRE CONTROL CALLED A SECOND TIME AND REPORTED A GAS IGNITION AT THE SAME LOCATION (STILL BELIEVED TO BE A BUILDING FIRE). GDS WAS UPDATED AND ARRIVED AT 02:14. THE GERC PROVIDED GDS MEASUREMENTS TO LOCATE A 4" 1956 MEDIUM PRESSURE (MP) MAIN VALVE-27428 WHICH WOULD HAVE ISOLATED THE INCIDENT AFFECTING 9 RESIDENTIAL SERVICES. GDS WAS UNABLE TO LOCATE THE MAIN VALVE AND 4 BACKUP MAIN VALVES WERE IDENTIFIED AND PROVIDED BY GERC. GAS EMERGENCY RESPONSE FORCE (ERF) EXCAVATED THE LOCATION OF MV-27428 AND WAS UNABLE TO LOCATE. THE (4) MAIN VALVES ON THE MP DISTRIBUTION SYSTEM WERE LOCATED BY GDS AND CLOSED BY 04:03. THE FLAME DECREASED IN SIZE BUT DID NOT EXTINGUISH. SYSTEM PRESSURES IN THE AREA AND WERE MONITORED IN RESPONSE TO CLOSURE OF A 8" MP MV-30551 AT GAS REGULATOR-583 AND WERE ADEQUATE. WESTCHESTER ERF AND BRONX ERF EXCAVATED TO LOCATE PRIMARY SHUTOFF VALVE MV-27428. TWO RESIDENTS FROM 1605 AND TWO RESIDENTS FROM 1611 WINFIELD AVE WERE EVACUATED BY MAMARONECK FD (MMFD) AS A PRECAUTION. AT 06:36 PRIMARY VALVE MV-27428 WAS EXPOSED AND CLOSED EXTINGUISHING THE FIRE AND SECURING THE LEAK. THIS VALVE WAS DISCOVERED UNDER A WATER DEPARTMENT VALVE BOX COVER AND "RITE HEIGHT" VALVE BOX EXTENSION DUE TO THE AREA RECENTLY BEING PAVED. THIS CONDITION CONCEALED THE GAS VALVE BOX COVER CORRECTLY INSTALLED OVER MV-27428. NINE CONFIRMED OUTAGES ON WINFIELD AVE. ONLY WAS THE EXTENT OF THE CUSTOMER IMPACT. THREE VISIBLE HOLES APPROXIMATELY THE SIZE OF A HALF DOLLAR EACH WERE DISCOVERED IN THE MP GAS MAIN LOCATED DIRECTLY UNDER THE PAVEMENT WHERE THE "A" PHASE BURNED THREE HOLES IN THE PAVEMENT. THE "A" PHASE OF 13 KV BOWMAN AUTO-LOOP IS SUSPECTED TO BE THE CAUSE OF THE FIRE. THE CUSTOMER IN 1605 WINFIELD AVE REPORTED LIGHTS WERE FLICKERING INSIDE HIS HOME, HE SAW SPARKS AND THEN SAW AN OVERHEAD WIRE FALL AND THEN HEARD A BOOMING SOUND. MMFD REPORTED 2-3 PRIVATE VEHICLES (>$50,000 DAMAGE) WERE ON FIRE THEN REALIZED NATURAL GAS WAS INVOLVED, PER NEWS 4 TV REPORTING. NO INJURIES REPORTED OR STRUCTURES IMPACTED. THE EVACUATION OF 1605 AND 1611 WINFIELD AVENUE WAS TERMINATED AT 07:05. NO GAS ODOR OR READINGS WERE DETECTED IN ANY SUB SURFACE STRUCTURES (SSS) OR BUILDINGS. CHANNEL 4 & CHANNEL 2 TV NEWS WERE ON LOCATION AND PHOTOGRAPHIC AND LAW DEPTS. RESPONDED. THE US DOT, NYS PSC, EMERGENCY MANAGEMENT, MEDIA RELATIONS AND PUBLIC AFFAIRS WERE NOTIFIED. MMFD CHIEF PECCHIA WAS ON LOCATION. THE PSC CALLED,WAS UPDATED AND RESPONDED TO LOCATION. GAS CONSTRUCTION WORKED AROUND THE CLOCK AND INSERTED THE 4" MP STEEL MAIN WITH 3" MP POLYETHYLENE. AT 10:51 THE SERIOUS LEVEL INCIDENT STATUS WAS TERMINATED. ON JULY 24, 2013 AT 12:51 GDS COMPLETED RESTORATION TO THE LAST CUSTOMER IMPACTED.
2025-03-31 10:13 | NO | NO | NO | 20130091 | 15724 | 2013-08-20 16:20 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2013-08-09 10:16 |  |  | 2013 | 2800 BOYNE MOUNTAIN ROAD | BOYNE FALLS | CHARLEVOIX | MI | 49713-8214 | 45.164 | -84.933 | [9 empty] | 2013-08-12 10:38 | 1056830 |  | NATURAL GAS |  | 149 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-08-09 10:16 |  |  |  | 2013-08-09 10:25 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1994 | [5 empty] | 4 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 1 | 3.7 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 77623 | 96939.182068152832499 | 1125 | 1404.951880585289625 | 0 | 0 |  |  | 705 | 616.875 |  | 0 | 79453 | 41301.8363000130475645245901639344262295 | 98961.008948738122124 | 7 | 0 | 193 |  |  |  |  | 58 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE BUSINESS | YES | [9 empty] | OCCUPANT | BACKHOE/TRACKHOE | WATER | NO |  |  |  | UNKNOWN/OTHER | NO | YES | 11 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JOHN D LUEDERS | COMPLIANCE ENGINEER | luedersj@dteenergy.com | 616.632.2646 | 616.632.2687 |  |  |  | ROBERT H FRECKELTON | COMPLIANCE MANAGER | 313.389.7755 | freckeltonr@dteenergy.com | MAINTENANCE CREW WORKING FOR SKI RESORT STRUCK AND COMPLETELY SEVERED A 4-INCH PLASTIC MAIN WHILE EXCAVATING FOR WATER SYSTEM USING A BACKHOE. DTE GAS EMERGENCY RESPONSE CREW PINCHED THE PLASTIC PIPE TO CONTROL GAS LEAKING AT 45 PSIG WITHIN 2 HRS 4 MIN OF NOTIFICATION, INTERRUPTING SERVICE TO 200 RESIDENTIAL AND COMMERCIAL CUSTOMERS TO THE WEST OF THE DAMAGE. REPAIR WAS MADE BY INSTALLING A 4-FOOT SEGMENT OF PRE-TESTED 4-INCH PLASTIC PIPE, JOINTS MADE USING TWO ELECTROFUSION COUPLINGS. REPAIR COMPLETED AT 15:45. ALL AFFECTED CUSTOMERS WERE SHUT OFF AT EACH SERVICE VALVE BY 17:00. A PURGE PLAN WAS EXECUTED STARTING AT 20:48 TO RE-ACTIVATE THE DISTRIBUTION SYSTEM. THE NORTHWEST SECTION OF THE SYSTEM WAS RESTORED TO NORMAL OPERATING PRESSURE AT 22:00, AND RELIGHTING OF THOSE CUSTOMERS WAS INITIATED. THE SYSTEM WAS COMPLETELY RESTORED AT 22:55. RELIGHTING OF CUSTOMERS CONTINUED UNTIL 01:00 ON 8/10/2013 WITH 107 CUSTOMERS RESTORED BY THEN. RESTORATION CONTINUED AT 09:30 ON 8/10/2013 AND COMPLETED AT 15:30 WITH AN ADDITIONAL 59 CUSTOMERS RESTORED, LEAVING 34 CUSTOMERS SHUT OFF SINCE NOBODY WAS AT HOME.
2025-03-31 10:13 | NO | YES | NO | 20130092 | 15708 | 2013-08-21 17:41 | ORIGINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2013-07-22 11:29 |  |  | 2013 | 32 GRACE DRIVE | OLD BRIDGE TOWNSHIP | MIDDLESEX | NJ | 08857 | 40.3946 | -74.3131 | [9 empty] | 2013-07-23 10:54 | 1054779 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 3 | 2013-07-22 11:29 |  |  |  | 2013-07-22 11:36 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1959 | [5 empty] | 0.75 | API 5L | UNKNOWN | STEEL |  |  |  | 0.113 | [6 empty] | OTHER | [8 empty] | GAS PIPE WAS CUT WITH A SAWZALL BY A THIRD PARTY | CLASS 3 LOCATION | 300000 | 374653.8348227439 | 4050 | 5057.82677010704265 | 1550 | 1935.71147991751015 | 0 | 0 |  |  | 0 | 0 |  | 0 | 305600 | 158066.8958067367472 | 381647.3730727684528 | 0 | 0 | 1 |  |  |  |  | 28 | 35 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE DAMAGE WAS CAUSED BY HUMAN ERROR AND FAILURE TO IDENTIFY THE PIPE BEFORE CUTTING THE PIPE WITH A SAWZALL. | [154 empty] | FRANKY CORIANO | PRINCIPAL REGULATORY SPECIALIST | franky.coriano@pseg.com | 609-421-8025 |  |  |  |  | TAMARA L. LINDE | VP REGULATORY | 973-430-8058 | tamara.linde@pseg.com | ON MONDAY, JULY 22ND, 2013, AN ASSOCIATE OF A.J. PERRI INC. OF 1138 PINE BROOK ROAD, TINTON FALLS, NJ 07724; WHILE WORKING TO UNCLOG A SEWER LINE JACK HAMMERED A CONCRETE SLAB INSIDE 32 GRACE DRIVE, OLD-BRIDGE, AND EXCAVATED ALONGSIDE THE SEWER DRAIN PIPE AND LOCATED A 11/4 INCH STEEL COATED LINE, AND PROCEEDED TO CUT THE PIPE WITH A SAWZALL. WHEN GAS STARTED TO LEAK THEY EVACUATED THE HOUSE WITH THE HOMEOWNER AND CALLED THE FIRE DEPARTMENT; SUBSEQUENTLY THE GAS IGNITED. UPON RECEIPT OF THE CALL FROM THE FIRE DEPARTMENT, PUBLIC SERVICE ELECTRIC AND GAS COMPANY DISPATCHED A FIRST RESPONDER AND A CREW TO THE LOCATION OF THE INCIDENT TO SHUT OFF THE GAS SERVICE. THE HOUSE WAS DEMOLISHED THAT EVENING.
2025-03-31 10:13 | NO | NO | NO | 20130093 | 15952 | 2013-08-23 15:16 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2013-07-26 10:28 |  |  | 2013 | 4367 GRESHAM DRIVE | EL DORADO HILLS | EL DORADO | CA | 95762 | 38.688 | -121.0617 | [9 empty] | 2013-07-26 12:40 | 1055196 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2013-07-26 10:28 |  |  |  | 2013-07-26 10:42 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 31 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2001 | [5 empty] | 0.5 | TR-418 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  |  | 2406 | MECHANICAL PUNCTURE | [9 empty] | CLASS 3 LOCATION | 50000 | 62442.30580379065 | 2000 | 2497.692232151626 | 2000 | 2497.692232151626 | 0 | 0 |  |  | 2000 | 1750 |  | 0 | 56000 | 29549.5212206779914426229508196721311475 | 69187.690268093902 | 0 | 0 | 5 |  |  |  |  | 56 | 56 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS APPARENT THAT CONROLLER/CONTROL ROOM ISSUES WERE NOT A CONTRIBUTING FACTOR TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | TRENCHER | DRAINAGE | NO |  |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED | YES | 10 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LAURENCE DENISTON | ACTING MANAGER REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT APPROXIMATELY 1028 HOURS ON JULY 26, 2013, PG&E WAS NOTIFIED BY CAL FIRE THAT A THIRD PARTY EXCAVATOR, DIGGING WITH A MECHANICAL TRENCHER AT 4367 GRESHAM DR IN EL DORADO HILLS, HAD STRUCK A 1/2-INCH PLASTIC SERVICE, RESULTING IN AN UNINTENTIONAL RELEASE OF GAS. THE TRENCHER SUBSEQUENTLY CAUGHT ON FIRE. THE CONTRACTOR, BREAULT ASPHALT, CALLED IN A USA DIG TICKET (TICKET # 0235482), WHICH HAD EXPIRED ON JULY 19, 2013. THEIR SUB CONTRACTOR, CENTRAL VALLEY ENGINEERING AND ASPHALT, DID NOT NOTIFY USA. A PG&E GAS SERVICE REPRESENTATIVE WAS ONSITE AT 1042 HOURS. PG&E CREWS WERE ONSITE AT 1126 HOURS AND FLOW OF GAS WAS STOPPED AT 1201 HOURS BY DIGGING AND SQUEEZING THE PLASTIC SERVICE. FIVE CUSTOMERS LOST SERVICE. THERE ARE NO INJURIES, NO FATALITIES. FIRE AND POLICE PERSONNEL WERE ONSITE. THE AREA WAS EVACUATED AND BLOCKED OFF, AND TRAFFIC WAS REROUTED. MAJOR SACRAMENTO NEWS MEDIA (CHANNEL 40 NEWS) WAS OBSERVED ON SITE AT 1245 HOURS. THIS INCIDENT BECAME REPORTABLE TO THE CPUC AND DOT WHEN ESTIMATED DAMAGES WERE EXPECTED TO EXCEED $50,000. (NOTE: THE ADDRESS HAS BEEN CORRECTED FROM 4372 GRESHAM DRIVE TO 4367GRESHAM DRIVE IN THIS PHMSA 7100 SUPPLEMENTAL REPORT.)
2025-03-31 10:13 | YES | NO | NO | 20130094 | 16008 | 2013-08-23 17:10 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2013-07-26 14:26 |  |  | 2013 | 20189 4TH STREET | HILMAR | MERCED | CA | 95324 | 37.4103 | -120.8535 | [9 empty] | 2013-07-26 | 1055225 |  | NATURAL GAS |  | 30 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-07-26 14:26 |  |  |  | 2013-07-26 14:46 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | CAL FIRE INDICATED THAT THE FIRE APPEARED TO HAVE ORIGINATED UNDER THE CARPORT, NEAR THE GAS METER SET. CAL FIRE STATED THAT THE FIRE IS SUSPICIOUS IN NATURE AND THE CAUSE IS UNKNOWN. | CLASS 2 LOCATION | 50000 | 62442.30580379065 | 4000 | 4995.384464303252 | 0 | 0 | 0 | 0 |  |  | 165 | 144.375 |  | 0 | 54165 | 28064.2240895304504590163934426229508197 | 67582.065268093902 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | ON JULY 26, 2013, AT APPROXIMATELY 1426 HOURS, PG&E WAS NOTIFIED BY CAL FIRE DEPARTMENT OF A STRUCTURE FIRE AT 20189 FOURTH STREET IN HILMAR. DUE TO THE HEAT OF THE FIRE, THE METER AND REGULATOR MELTED. A PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SITE AT 1446 HOURS. AT 1533 HOURS, CAL FIRE DEPARTMENT SHUT OFF GAS AT THE SERVICE VALVE. AFTER THE FIRE WAS EXTINGUISHED, PG&E'S GSR REMOVED THE METER SET AND PLUGGED THE GAS SERVICE. THE HOUSE WAS UNOCCUPIED AT THE TIME OF THE INCIDENT. CAL FIRE DEPARTMENT'S INCIDENT REPORT STATES THAT THE FIRE ORIGINATED IN A 4-FT. BY 4-FT. AREA AROUND THE GAS METER UNDER THE CARPORT. THREE MELTED GARBAGE CANS AND TWO CRACKED WINDOWS WERE OBSERVED IN THE AREA OF FIRE ORIGIN, BUT THE IGNITION SOURCE IS UNDETERMINED. CAL FIRE'S INCIDENT REPORT FURTHER STATES THAT THE FIRE WAS SUSPICIOUS IN NATURE. WITNESSES INDICATED TWO NEIGHBORHOOD YOUTHS WERE SEEN IN THE INCIDENT AREA BEFORE THE FIRE OCCURRED. BOTH WITNESSES NOTED THERE HAD BEEN MULTIPLE ISSUES (INCLUDING THEFT AND VANDALISM) INVOLVING THESE YOUTHS. TO CONFIRM THAT PIPELINE NATURAL GAS WAS NOT THE INITIAL IGNITION SOURCE, PG&E'S GSR PERFORMED BAR-HOLE PROBING WITH A COMBUSTIBLE GAS INSTRUMENT (CGI) ALONG THE SERVICE LINE TO THE MAIN, AND DID NOT DETECT ANY GAS LEAKS IN THE AREA. THERE WERE NO INJURIES AND NO FATALITIES ASSOCIATED WITH THIS INCIDENT. NO MAJOR NEWS MEDIA WAS OBSERVED ONSITE. THIS INCIDENT WAS REPORTED TO THE CPUC AND DOT AFTER IT WAS DETERMINED THAT ESTIMATED DAMAGES WOULD EXCEED $50,000. AS OF JAN. 13, 2015, THE STRUCTURE IS STILL UNINHABITABLE. SERVICE WILL BE RESTORED ONCE STRUCTURE REPAIRS ARE COMPLETE AND NEW SERVICE IS REQUESTED.
2025-03-31 10:13 | NO | YES | YES | 20130095 | 15830 | 2013-08-26 09:06 | SUPPLEMENTAL FINAL | 18104 | CPS ENERGY | 500 MCCULLOUGH | SAN ANTONIO | TX | 78215 | 2013-07-26 16:30 |  |  | 2013 | 12302 CONSTITUTION | SAN ANTONIO |  | TX | 78233 | 29.5519 | -98.3718 | [9 empty] | 2013-07-29 12:12 | 1055409 |  |  |  | 55 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | NO | 2 | 2013-07-26 17:45 |  |  |  | 2013-07-26 18:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | 1973 | [8 empty] | STEEL |  | OTHER | SMLS | 0.179 | [6 empty] | OTHER | [8 empty] | NATURAL GAS RELEASE RESULTED FROM A VEHICLE CRASHING THROUGH THE RESIDENTIAL GAS METER AND REGULATOR SETTING. THE GAS SERVICE RISER WAS SHEARED OFF CAUSING A RELEASE OF GAS. | CLASS 3 LOCATION | 40000 | 49953.84464303252 | 5000 | 6244.230580379065 | 104 | 129.879996071884552 | 0 | 0 |  |  | 209 | 182.875 |  | 0 | 45313 | 23498.5197824484115627540983606557377049 | 56510.830219483469552 | 0 | 0 | 2 |  |  |  |  | 9 | 9 | 33 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELEASE OF NATURAL GAS IN THE DISTRIBUTION SYSTEM WAS NOT LARGE ENOUGH FOR THE SCADA SYSTEM TO DETECT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | TORRY HURT | MANAGER GAS STANDARDS AND SPECIFICATIONS | tlhurt@cpsenergy.com | 210-353-6132 | 210-353-2072 |  |  |  | THOMAS NARENDORF | DIRECTOR GAS ENGINEERING DESIGN AND SPECIFICATION | 210-353-3766 | tlnarendorf@cpsenergy.com | THE PRIMARY CAUSE OF THE INCIDENT WAS DUE TO OTHER OUTSIDE FORCE DAMAGE. PER SAN ANTONIO FIRE DEPARTMENT REPORT, A MALE OCCUPANT WAS MOVING A CAR IN HIS GARAGE AND ACCIDENTALLY DROVE THE CAR FORWARD THROUGH THE GARAGE'S REAR WALL. THIS ACTION STRUCK THE GAS SERVICE METER AND REGULATOR INSTALLATION AND SHEARED THE SERVICE RISER CAUSING THE RELEASE OF GAS. BOTH THE CAR AND GARAGE CAUGHT FIRE. THE FIRE EXTENDED INTO THE MAIN HOUSE AND THE EXTERIOR WALL OF THE NEIGHBORING HOUSE AT 12306 CONSTITUTION. THE NIEGHBORING HOUSE IGNITED FROM RADIANT HEAT WHICH ALSO IGNITED THE GAS. FIRE PERSONNEL NOTIFIED CPS ENERGY AND OUR CREW RESPONDED BY SHUTTING OFF THE FLOW OF GAS TO BOTH SERVICES AT THE MAIN. THE TWO INGURIES WERE MINOR BURNS FROM THE RESULTING FIRE CAUSE BY THE VEHILCE ACCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20130096 | 15908 | 2013-08-28 15:56 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2013-07-30 13:45 |  |  | 2013 | 3116 E. VIENNA ROAD | CLIO | GENESEE | MI | 48420-9133 | 43.1777 | -83.6548 | [9 empty] | 2013-07-30 15:54 | 1055574 |  | NATURAL GAS |  | 17 |  | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 0 | 2013-07-30 13:45 |  |  |  | 2013-07-30 13:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1995 | [5 empty] | 1.125 | ASTM D2513 | PHILLIPS DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.103 |  | 3408 | OTHER | [8 empty] | BACKHOE HOOKED PLASTIC SERVICE APPROXIMATELY 8 FEET FROM RISER. BUCKET MADE SMALL PUNCTURE AT CONTACT POINT, AND SEPARATED THE SERVICE AT A REDUCER FUSED BETWEEN THE RISER AND THE SERVICE. | CLASS 2 LOCATION | 360000 | 449584.60178729268 | 1200 | 1498.6153392909756 | 235 | 293.478837277816055 | 0 | 0 |  |  | 155 | 135.625 |  | 0 | 361590 | 187072.1511372619125868032786885245901639 | 451512.320963861471655 | 0 | 0 | 1 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | OCCUPANT | BACKHOE/TRACKHOE | BUILDING CONSTRUCTION | YES | 31910839 |  |  | CONTRACT LOCATOR | YES | UNKNOWN/OTHER |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 |  |  |  |  | TRACY A. GOBLE | MANAGER OF REGULATORY AND COMPLIANCE | 517-768-3187 | tracy.goble@cmsenergy.com | AN EXCAVATOR WAS DIGGING WITH A BACKHOE AT THE NORTHEAST CORNER OF THE HOUSE AT 3116 VIENNA ROAD IN CLIO, MICHIGAN ON JULY 30, 2013 WHEN THE MACHINE'S BUCKET PULLED AND DAMAGED THE 1-1/8" PLASTIC MEDIUM PRESSURE SERVICE TO THE HOME. THE SERVICE HAD BEEN STAKED PROPERLY PRIOR TO THE EXCAVATION, BUT THE DAMAGING PARTY FAILED TO HAND EXPOSE THE FACILITY DURING EXCAVATION. THE CUSTOMER AT THE HOME NOTIFIED CONSUMERS ENERGY OF THE DAMAGE AT APPROXIMATELY 13:08 HOURS OF THE DAMAGE, INDICATING THAT ODOR WAS IN THE AIR AND THAT HISSING COULD BE HEARD. CONSUMERS ENERGY'S FIRST RESPONDER ARRIVED AT THE SCENE AT 13:41, BRIEFLY ASSESSED THE EXCAVATION AREA AND THE DAMAGED SERVICE, THEN RETURNED TO HIS VEHICLE TO NOTIFY DISPATCH AND CALL FOR A GAS DISTRIBUTION CREW. AFTER CALLING DISPATCH, THE FIRST RESPONDER EXITED HIS TRUCK, AND AT THAT TIME THE HOUSE EXPLODED (APPROXIMATELY 13:45). THE EXPLOSION RESULTED IN THE DEATH OF TWO CUSTOMERS AND THE HOSPITALIZATION OF A THIRD, ALL OF WHOM WERE IN THE HOME AT THE TIME OF THE EXPLOSION. FOLLOW-UP INVESTIGATION REVEALED THAT THE BACKHOE BUCKET PUNCTURED THE SERVICE, THE DAMAGE OCCURRING APPROXIMATELY 8 FEET FROM THE RISER. ADDITIONALLY, INVESTIGATORS BELIEVE THE HOOKING AND LIFTING MOTION SEPARATED THE SERVICE FROM THE RISER AT A FUSE ON A REDUCER CONNECTING THE 1-1/8" SERVICE TO THE 5/8" RISER. ADDITIONALLY, FOLLOW-UP INVESTIGATION HAS IDENTIFIED TWO POSSIBLE PATHS OF MIGRATION FROM THE DAMAGED FACILITY TO THE HOME: 1.) A CRAWL SPACE VENT, DIRECTLY BENEATH THE GAS METER LOCATION; AND/OR 2.) THE FOUNDATION OF THE HOME, CONSISTING OF LARGE RAILROAD STONES (4' WIDE BY 3' DEEP) AND POTENTIALLY MORE POROUS THAN OTHER FOUNDATION MATERIALS. THE CRAWL SPACE BENEATH THE HOME HAD A DIRT FLOOR. THE SOURCE OF INGITION IS UNKNOWN.
2025-03-31 10:13 | NO | YES | YES | 20130097 | 15964 | 2013-08-31 07:10 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2013-08-02 14:00 |  |  | 2013 | 12340 CONWAY RD | BELTSVILLE | PRINCE GEORGES' | MD | 20705-1305 | 39.0594 | -76.8873 | [9 empty] | 2013-08-02 16:37 | 1055933 | [5 empty] | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO |  |  |  |  | NO | 45 | 2013-08-02 14:06 |  |  |  | 2013-08-02 14:35 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | STORM SEWER INLET |  |  | NO | [11 empty] | OTHER | UNDETERMINED SOURCE | OTHER | UNDETERMINED SOURCE | UNKNOWN | [8 empty] | OTHER | UNDETERMINED MATERIAL | [9 empty] | OTHER | [8 empty] | UNDETERMINED SOURCE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 0 |  |  |  |  | 50 | 50 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | PAUL MOSES | SUPERVISOR - DOT PIPELINE SAFETY COMPLIANCE | gmoses@washgas.com | 703-750-4496 |  |  |  |  | DAVID SPANGLER | MANAGER - DOT PIPELINE SAFETY COMPLIANCE | 703-750-4341 | dspangler@washgas.com | WASHINGTON GAS WAS NOTIFIED AT 2:06 PM ON 8/2/2013 OF THE IGNITION OF AN UNDETERMINED VAPOR AT A STORM SEWER INLET IN FRONT OF 12340 CONWAY RD., BELTSVILLE, MD. THE WASHINGTON GAS FIRST RESPONDER ARRIVED ON SITE AT 2:35 PM. THE PRINCE GEORGES' COUNTY FIRE DEPARTMENT WAS ON SITE AND IN CONTROL OF THE INCIDENT SITE. THE AREA OF THE INCIDENT IS A COMMERCIAL/ INDUSTRIAL SITE. APPROXIMATELY 45 PEOPLE HAD BEEN EVACUATED FROM BUILDINGS IN THE IMMEDIATE AREA. TWO INDIVIDUALS WERE INJURED BY THE FLASH FIRE. ONE INDIVIDUAL WAS TREATED AND RELEASED. THE SECOND INDIVIDUAL WAS HOSPITALIZED FOR TREATMENT OF SECOND DEGREE BURNS. WASHINGTON GAS PERSONNEL PERFORMED LEAK SURVEYS IN THE AREA OF THE IGNITION AND IN A WIDENING AREA ATTEMPTING TO VERIFY THE INVOLVEMENT OF NATURAL GAS FROM A FACILITY. BAR AND TEST HOLES WERE PUT DOWN OVER WASHINGTON GAS FACILITIES IN THE AREA AND ADDITIONAL LEAK CHECKS WERE PERFORMED IN AND AROUND BUILDINGS IN THE AREA. WASHINGTON GAS PERSONNEL VALVED OFF A FOUR INCH GAS MAIN AT THE INTERSECTION OF FAIGLE RD AND OLD BALTIMORE PIKE. THE MAIN WAS EXPOSED AND A PRESSURE TEST CONDUCTED 560 FEET FROM THE MAIN DEADEND. THE PRESSURE TEST DID NOT HOLD PRESSURE. A FIBER OPTIC CAMERA INVESTIGATION WAS CONDUCTED ON THE GAS MAIN. AN INTRUSION WAS NOTED 76 FEET FROM THE DEADEND. FURTHER EXCAVATION REVEALED A ROCK IMPINGEMENT CAUSING A RELEASE AT THIS LOCATION. THE GAS MAIN WAS REPLACED. CAMERA INSPECTIONS WERE ALSO CONDUCTED ON SANITARY AND STORM SEWER FACILITIES IN THE AREA. THE INVESTIGATION CONTINUES AND A SUPPLEMENTAL REPORT WILL BE FILED. ADDITIONAL INVESTIGATION BY WASHINGTON GAS AND THE CONSULTING FORENSIC ENGINEERING FIRM ENGAGED FOR THIS INVESTIGATION HAVE NOT FOUND A MIGRATION PATH FROM THE DAMAGED WASHINGTON GAS FACILITY DESRCIBED ABOVE TO THE SITE OF THE FLASH FIRE. THE SOURCE AND IDENTIFICATION OF THE VAPOR INVOLVED IN THE FLASH FIRE ON 8/2/2014 HAVE NOT BEEN DETERMINED. FURTHER INVESTIGATION HAS PROVIDED NO ADDITIONAL INFORMATION. THE PREVIOUSLY SUBMITTED SUPPLEMENTAL REPORT IS THE FINAL REPORT FOR THIS INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20130098 | 15720 | 2013-09-05 18:55 | ORIGINAL FINAL | 15462 | PECO ENERGY CO | 2301 MARKET STREET, S9-1 | PHILADELPHIA | PA | 19103 | 2013-08-07 15:58 |  |  | 2013 | ROSEMONT COLLEGE, 1400 MONTGOMERY AVE | ROSEMONT |  | PA | 19010 | 40.0321 | -75.3288 | [9 empty] | 2013-08-07 18:00 | 1056407 |  | NATURAL GAS |  | 180 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-08-07 15:58 |  |  |  | 2013-08-07 16:24 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 168 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1983 | [5 empty] | 4 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | OTHER | [8 empty] | AUGER THROUGH MAIN. DUE TO DEPTH (14 FT), AREA WAS NOT EXCAVATED. | CLASS 3 LOCATION | 60000 | 74930.76696454878 | 69554 | 86862.242757537097402 | 1900 | 2372.8076205440447 | 0 | 0 |  |  | 648 | 567 |  | 0 | 132102 | 68517.0661855261948734098360655737704918 | 164732.817342629922102 | 2 | 0 | 0 |  |  |  |  | 25 | 25 | 33 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | AUGER | POLE | NO |  |  |  | UNKNOWN/OTHER | YES | YES | 1284 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MICHAEL J. LYONS P.E. | PRINCIPAL ENGINEER | michael.lyons@peco-energy.com | 610-832-6505 | 610-832-6559 |  |  |  | BRIAN CAMFIELD | MANAGER GAS ENGINEERING AND ASSET PERFORMANCE | 215-841-4197 | brian.camfield@peco-energy.com | ON 08/07/13, A DRILL RIG OPERATOR WAS AUGURING TO INSTALL A LIGHTING TOWER FOUNDATION FOR A NEWLY CONSTRUCTED SPORTS FIELD AT ROSEMONT COLLEGE WHEN THE CONTRACTOR STRUCK THE GAS MAIN. THE SPORTS FIELD CONSTRUCTION HAD ADDED FILL OVER THE EXISTING GAS MAIN, SO THAT A NEW COVER OVER THE MAIN WAS APPROXIMATELY 14 FEET. DURING CONSTRUCTION, PIPELINE MARKERS WERE RAISED TO MARK THE MAIN. THE AUGER STRUCK THE 4-INCH PE PLASTIC MAIN AND THE ESCAPING GAS IGNITED AT THE DRILL RIG TRUCK. THE CONTRACTOR DID NOT MAKE THE REQUIRED ONE-CALL NOTIFICATIONS PRIOR TO STARTING THE WORK. HOWEVER, PREVIOUS ONE-CALLS WERE MADE BY OTHER CONTRACTORS WORKING IN THE AREA RESULTED IN A MARK OUT OF THE GAS MAIN AND THE INSTALLATION OF PIPELINE MARKERS. THE MARKERS WERE VISIBLE AND THEY ACCURATELY MARKED THE LOCATION OF THE GAS MAIN. THE MARKERS' ACCURACY WAS VERIFIED THROUGH SUBSEQUENT EXCAVATIONS. DUE TO THE DEPTH OF THE FACILITIES AT THE HIT LOCATION, THIS SECTION WAS NOT EXCAVATED. THE PIPE WAS EXCAVATED AT THE STREET WHERE THIS SECTION IS TEED OFF AND WAS CUT AND CAPPED. A NEW MAIN WAS RUN TO RECONNECT THE COLLEGE FACILITIES AND WAS GASSED UP ON 8/22/13.
2025-03-31 10:13 | NO | YES | NO | 20130099 | 15722 | 2013-09-08 21:15 | ORIGINAL FINAL | 1640 | BOSTON GAS CO | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2012-02-23 07:58 |  |  | 2012 | 627 PLEASANT ST | WINTHROP | SUFFOLK | MA | 02152 | 42.3833 | -70.9915 | [9 empty] | 2012-02-24 12:40 | 1003862 |  | NATURAL GAS |  | 60 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 3 | 2012-02-23 07:58 |  |  |  | 2012-02-23 08:23 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | CUSTOMER OWNED PIPING | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | LEAK ON CUSTOMER OWNED PIPING | [5 empty] | CLASS 3 LOCATION | 500000 | 635850 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 500 | 451.374207188160676532769556025369978858 |  | 0 | 500500 | 263767.5475687103594080338266384778012685 | 636301.3742071881606765327695560253699789 | 0 | 0 | 1 |  |  |  |  | 0.35 | 0.34 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS ON CUSTOMER OWNED PIPING AND THE SCADA SYSTEM DID NOT PROVIDE ANY INFORMATION TO THE CONTROLLERS THAT AN INCIDENT OCCURRED, THUS THEY COULD NOT TAKE ANY ACTION AS A RESULT OF THE INCIDENT. EMERGENCY RESPONDERS ALERTED THE COMPANY. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | LEAK ON CUSTOMER PIPING IS UNKNOWN. | [47 empty] | KATHLEEN MCNAMARA | MANAGER NE DISPATCH AND SCHEDULING | kathleen.mcnamara@nationalgrid.com | 508-421-7450 |  |  |  |  | GARY BENNETT | DIRECTOR US DISPATCH AND SCHEDUING | 617-839-7208 | gary.bennett@nationalgrid.com | LEAK ON CUSTOMER OWNED PIPING.
2025-03-31 10:13 | NO | NO | NO | 20130100 | 15723 | 2013-09-08 21:29 | ORIGINAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2013-08-13 11:09 |  |  | 2013 | ROCKY HILL ROAD & RTE 116 | SMITHFIELD | PROVIDENCE | RI | 02917 | 41.8962 | -71.5209 | [9 empty] | 2013-08-15 12:55 | 1057207 |  | NATURAL GAS |  | 945.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-08-13 11:19 |  |  |  | 2013-08-13 11:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1969 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 25000 | 31221.152901895325 | 800 | 999.0768928606504 | RESTORATION & PAVING COSTS. |  | 3384 | 2961 |  | 0 | 29184 | 16083.7512134496123049180327868852459016 | 35181.2297947559754 | 0 | 1 | 0 |  |  |  |  | 30.9 | 32 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A THIRD PARTY DAMAGING THE COMPANY'S GAS MAIN AND THE CONTROLLERS WERE COMMUNICATING WITH THE COMPANY'S GAS DISPATCH GROUP ABOUT WHAT INFORMATION THE SCADA SYSTEM WAS PROVIDING TO THEM ABOUT THE INCIDENT AS THE INCIDENT WAS UNFOLDING. THE COMMUNICATIONS BETWEEN THE TWO GROUPS, EACH OF WHICH HAD INDIVIDUAL PIECES OF INFORMATION PRESENTED TO THEM BY TWO DIFFERENT SOURCES, PROVIDED THE COMPLETE PICTURE OF THE INCIDENT AND IT'S AFFECT ON THE GAS SYSTEM IN THAT AREA. THER | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | TRENCHER | TRAFFIC SIGNAL | NO |  |  |  | UNKNOWN/OTHER | YES |  |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | KATHLEEN MCNAMARA | MANAGER | kathleen.mcnamara@nationalgrid.com | 508-421-7450 | 508-357-4735 |  |  |  | GARY BENNETT | DIRECTOR | 617-839-7208 | gary.bennett@nationalgrid.com | DAMAGE WAS CAUSED BY THIRD PARTRY CONTRACTOR INSTALLING SIGNAL LINES FOR THE TOWN OF SMITHFIELD, RI. SITE TECH, THE THIRD PARTY CONTRACTOR, WAS USING A VERMEER TO EXCAVATE AND PUNCTURED OUR 6" MAIN. THE ROOT CASUE OF THIS DAMAGE WAS DUE TO THE CONTRACTOR'S NEGLIGENCE, IN NOT COMPLYING WITH PROPER DIG SAFE PROCEDURES.
2025-03-31 10:13 | NO | NO | NO | 20130101 | 15764 | 2013-09-11 16:51 | SUPPLEMENTAL FINAL | 2812 | CORPUS CHRISTI, CITY OF - GAS DIV | 4225 SOUTH PORT AVENUE | CORPUS CHRISTI | TX | 78415 | 2013-08-12 13:02 |  |  | 2013 | 15113 S PADRE ISLAND DR | CORPUS CHRISTI | NUECES | TX | 78418 | 27.6057 | -97.2229 | [9 empty] | 2013-08-12 14:36 | 1056948 |  | NATURAL GAS |  | 50 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2013-08-12 13:30 |  |  |  | 2013-08-12 13:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2013 | [5 empty] | 2 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 3 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 410 | 512.02690759108333 | 100 | 124.8846116075813 | 0 | 0 |  |  | 250 | 218.75 |  | 0 | 760 | 466.146206792742050327868852459016393443 | 855.66151919866463 | 0 | 0 | 0 |  |  |  |  | 12 | 12 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | [7 empty] | YES | [6 empty] | CONTRACTOR | AUGER | FENCING | NO |  |  |  | UTILITY OWNER | UNKNOWN/OTHER |  |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JESSE M CANTU JR | PETROLEUM SUPERINTENDENT | jessecantu@cctexas.com | (361)885-6941 | (361)853-3200 |  |  |  | JESSE CANTU | PETROLEUM SUPERINTENDENT | (361)885-6941 | jessecantu@cctexas.com | CONTRACTOR WAS DRILLING POST HOLES FOR THE INSTALLATION OF A FENCE WHEN THEY STRUCK A 2 INCH PE MAIN CREATING A 3 INCH GASH ON THE SIDE OF THE PIPE. THE LINE WAS A ONE WAY FEED DEAD END. THE LINE WAS SQUEEZED AND THE DAMAGE SECTION WAS REPLACED. THE CAUSE FOR THIS INCIDENT WAS THE EXCAVATOR'S FAILURE TO CALL FOR LINE LOCATES BEFORE HE STARTED HIS EXCAVATION.
2025-03-31 10:13 | NO | YES | NO | 20130102 | 15726 | 2013-09-13 14:06 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2013-08-16 00:43 |  |  | 2013 | 387 LA CADENA DR | RIVERSIDE | CA | CA | 92501 | 34.014 | -117.3437 | [9 empty] | 2013-08-16 05:19 | 1057274 |  | NATURAL GAS |  | 2987 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-08-16 00:43 |  |  |  | 2013-08-16 01:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 40 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1960 | [5 empty] | 6 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.212 | [6 empty] | MECHANICAL PUNCTURE | 6 | 6 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 580695 | 725198.695374644230035 | 1000 | 1248.846116075813 | 0 | 0 |  |  | 17922 | 15681.75 |  | 0 | 599617 | 315379.3214281115173543442622950819672131 | 742129.291490720043035 | 38 | 0 | 4000 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 30360997 | USA SOUTH |  | UTILITY OWNER | NO | YES | 35 | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | tbauer@semprautilities.com | 909-376-7208 | 909-885-6270 |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | AT APPROXIMATELY 12:43 AM ON AUGUST 16TH, 2013 AMES CONSTRUCTION WAS PERFORMING WORK FOR CAL TRANS ON A FREEWAY WIDENING PROJECT NEAR THE ADDRESS OF 387 LA CADENA DR IN RIVERSIDE ADJACENT TO INTERSTATE 215 SOUTH. AMES EMPLOYEES WERE EXCAVATING WITH A TRACKHOE WHEN THE END OF A 6' MEDIUM PRESSURE STEEL MAIN WAS SNAGGED IN A SCOOP OF THE TRACKHOE'S BUCKET. AS THE OPERATOR RAISED THE BUCKET AND TWISTED THE TRACKHOE 180 DEGREES, THE 6' MAIN WAS LIFTED, WITH THE SOIL IN THE BUCKET, UP AND AWAY IN AN EASTERLY DIRECTION. A LATERAL 6' MAIN TIED TO THIS MAIN CONTAINED A COMPRESSION INSULATING COUPLING APPROXIMATELY 3' WEST OF THE SNAGGED MAIN. AS THE PIPE WAS PULLED UP AND AWAY THE LATERAL WAS PULLED FROM THE COMPRESSION COUPLING RESULTING IN A 6' FULLY OPEN ORIFICE BLOWING GAS AND DEBRIS ONTO THE SOUTHBOUND I 215 FREEWAY, WHICH WAS SUBSEQUENTLY SHUT DOWN BY THE CALIFORNIA HIGHWAY PATROL. DUE TO THE LOCATION OF THE INCIDENT WITHIN THE PRESSURE DISTRICT, THE CLOSURE OF THE FREEWAY AND SIGNIFICANT LOSS IN PRESSURE WITHIN THE PRESSURE DISTRICT, GAS WAS CONTROLLED BY SHUTTING IN THE REGULATOR STATION TO THE DISTRICT. THIS SHUT IN RESULTED IN LOSS OF SERVICE TO OVER 4,000 CUSTOMERS. INVESTIGATION OF THE INCIDENT SITE REVEALED THAT THERE WAS A VALID USA TICKET FOR THE PROJECT AND THAT THE FACILITIES WERE PROPERLY MARKED. ASPHALT HAD BEEN REMOVED BY AMES AND EXISTENCE OF MARKS WERE THEREBY OBLITERATED.
2025-03-31 10:13 | NO | YES | NO | 20130103 | 30401 | 2013-09-13 17:27 | SUPPLEMENTAL FINAL | 1640 | BOSTON GAS CO | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2013-08-14 15:40 |  |  | 2013 | PLANK STREET & MIDDLESEX TURNPIKE | BEDFORD | MIDDLESEX | MA | 01730 | 42.5151 | -71.2416 | [9 empty] | 2013-08-14 17:31 | 1057121 |  | NATURAL GAS |  | 221 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-08-14 15:40 |  |  |  | 2013-08-14 15:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2013 | [5 empty] | 8 | ASTM D2513 | CHEVRON PHILIPS CHEMICAL CO. | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | OTHER | [8 empty] | NATURAL GAS WAS INTRODUCED INTO 8 INCH PLASTIC MAIN PRIOR TO COMPLETION OF TIE-IN | CLASS 4 LOCATION | 25000 | 31221.152901895325 | 68000 | 84921.535893155284 | 15700 | 19606.8840223902641 | 0 | 0 |  |  | 751 | 657.125 |  | 0 | 109451 | 56831.2808463720576377049180327868852459 | 136406.6978174408731 | 0 | 0 | 0 |  |  |  |  | 55.2 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | YES | 3 | 0 | YES | 4 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | CREW LEADER RELEASED THE PRESSURE ON THE HYDRAULIC SQUEEZE OFF TOOL AT ONE END OF THE TIE-IN PRIOR TO MAKING CONNECTION AT OTHER END. THIS RESULTED IN AN UNCONTROLLED RELEASE OF GAS. |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | KATHLEEN MCNAMARA | MANAGER DISPATCH | kathleen.amberymcnamara@us.ngrid.com | 508-421-7450 |  |  |  |  | CORINNE D BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAMS | 6317703549 | corinne.byrnes@nationalgrid.com | THE EVENT OCCURRED DURING A REINFORCEMENT PROJECT REQUIRING THE REPLACEMENT OF APPROX. 2800FT OF EXISTING 3'/4' COATED STEEL AND PLASTIC MAIN WITH AN 8'PLASTIC PIPE AT HIGH PRESSURE (60PSI) AND ASSOCIATED TIE-INS ALONG MIDDLESEX TURNPIKE, BEDFORD, MA. THE NEW 8' MAIN WAS INSTALLED BY NEW ENGLAND UTILITY CONSTRUCTORS INC. (NEUCO) WITH GASSING IN AND ASSOCIATED TIE-INS PERFORMED BY A NATIONAL GRID CREW. ON AUGUST 14, 2013, DURING THE OPERATION BY A NATIONAL GRID'S CREW TO TIE-IN THE EXISTING 8' MAIN ON PLANK STREET TO THE NEW 8' MAIN ON MIDDLESEX TURNPIKE, THE CREW LEADER RELEASED THE PRESSURE ON THE HYDRAULIC SQUEEZE OFF AT ONE END OF THE TIE-IN PRIOR MAKING THE CONNECTION AT THE OTHER END. THIS RESULTED IN AN UNCONTROLLED RELEASE OF GAS THROUGH THE OPEN ENDED PIPE WHICH IGNITED AND BURNED FOR APPROX. 70 MINUTES BEFORE BEING BROUGHT UNDER CONTROL AND EXTINGUISHED THERE WAS NO LOSS OF LIFE OR SIGNIFICANT INJURY BUT THERE WAS DAMAGE TO THIRD PARTY APPARATUS IN THE VICINITY INCLUDING OVERHEAD WIRES AND STREET LIGHTING AND COMPANY EQUIPMENT INCLUDING A BACK HOE. THERE WAS SIGNIFICANT MEDIA ATTENTION
2025-03-31 10:13 | NO | YES | NO | 20130104 | 15823 | 2013-09-18 18:08 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2013-08-23 19:23 |  |  | 2013 | 174 EVANS AVE | BLAIRSVILLE | INDIANA | PA | 15717-1061 | 40.4362 | -79.2532 | [9 empty] | 2013-08-24 | 1058071 |  | NATURAL GAS |  | 23 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-08-23 19:37 |  |  |  | 2013-08-23 20:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1982 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.099 |  | 2406 | OTHER | [8 empty] | SEPARATED DUE TO VEHICLE ACCIDENT. | CLASS 3 LOCATION | 109881 | 137224.460080526408253 | 137 | 171.091917902386381 | 813 | 1015.311892369635969 | 0 | 0 |  |  | 103 | 90.125 |  | 0 | 110934 | 57408.9995965229844092950819672131147541 | 138500.988890798430603 | 0 | 0 | 1 |  |  |  |  | 25 | 25 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MICHAEL L. SMITH | COMPLIANCE PROCESS MANAGER | michael.l.smith@peoples-gas.com | 1-412-244-2605 |  |  |  |  | KENNETH M. JOHNSTON | SR. VICE PRESIDENT CHIEF OPERATING OFFICER | 1-412-208-7930 | kenneth.m.johnston@peoples-gas.com | ON THE EVENING OF AUGUST 23, 2013, AT 7:23 PM, AN ELDERLY DRIVER WAS BACKING OUT OF HER DRIVEWAY AND LOST CONTROL OF HER VEHICLE, CROSSING RESIDENTIAL STREET, AND STRUCK HOUSE AT 174 EVANS AVE. THE VEHICLE STRUCK THE RESIDENTIAL GAS METER THAT WAS LOCATED AT THE RIGHT CORNER OF FOUNDATION, SHEARING THE PLASTIC SERVICE LINE RISER, CAUSING IGNITION. AT THE TIME, THE HOUSE WAS UNOCCUPIED AS THE HOME OWNER WAS OUT WALKING HER DOG. NATURAL GAS WAS SHUT OFF AT CURB STOP AT 8:00 PM, AND NO INJURIES WERE REPORTED. BOTH VEHICLE AND HOUSE WERE DECLARED A TOTAL LOSS. THE CONSUMER SERVICE WAS CAPPED AT THE CURB ON THE NIGHT OF THE FIRE, PENDING RESOLUTION. AFTER INSURANCE SETTLEMENTS, THE STRUCTURE HAS BEEN REBUILT WITH NEW CONSUMER GAS SERVICE INSTALLED BY QUALIFIED PLUMBER, ON 3/6/2014.
2025-03-31 10:13 | NO | NO | NO | 20130105 | 15732 | 2013-09-21 12:51 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2013-08-21 12:24 |  |  | 2013 | 8122 HANSOM DRIVE | OAKLAND | ALAMEDA | CA | 94605 | 37.7715 | -122.1356 | [10 empty] | 1057826 |  | NATURAL GAS |  | 97.25 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2013-08-21 12:24 |  |  |  | 2013-08-21 12:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL | [10 empty] | LEAK |  |  | OTHER | VEHICLE STRUCK METER SET/RISER | [5 empty] | CLASS 3 LOCATION | 70000 | 87419.22812530691 | 2500 | 3122.1152901895325 | 2500 | 3122.1152901895325 | 0 | 0 |  |  | 100 | 87.5 |  | 0 | 75100 | 38873.5381252585946721311475409836065574 | 93750.958705685975 | 0 | 0 | 2 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA ON THIS PART OF THE SYSTEM | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | CHERYL DIZON | COMPLIANCE ENGINEER | c1dz@pge.com | 925-979-8205 | 925-329-5591 |  |  |  | FRANCES YEE | DIRECTOR REGULATORY COMPLIANCE AND SUPPORT | 925-328-5733 | fsc2@pge.com | THE CORRECT ADDRESS OF THE INCIDENT LOCATION IS 8130 HANSOM DRIVE AND NOT 8122 HANSOME DRIVE, AS WAS STATED IN THE INITIAL REPORT. ON AUGUST 21, 2013 AT APPROXIMATELY 1224 HOURS PACIFIC GAS AND ELECTRIC (PG&E) WAS NOTIFIED THAT A DRIVER LOST CONTROL OF THEIR VEHICLE; THE VEHICLE TRAVELED THROUGH THE GARAGE OF THE HOUSE, STRIKING AND DAMAGING THE GAS METER SET AND RISER, CAUSING AN UNINTENTIONAL RELEASE OF GAS WHICH SUBSEQUENTLY IGNITED AND STARTED A STRUCTURE FIRE. PG&E WAS ONSITE AT 1245 HOURS AND THE GAS WAS SHUT OFF AT 1545 HOURS BY DIGGING AND SQUEEZING THE 1/2-INCH PLASTIC SERVICE LINE. OUT OF AN ABUNDANCE OF CAUTION, THE FIRE DEPARTMENT EVACUATED THREE NEIGHBORING HOUSES, BLOCKED OFF THE ROAD AND REROUTED TRAFFIC. TWO CUSTOMERS EXPERIENCED SERVICE INTERRUPTION AND ONE CUSTOMER WAS RESTORED AT 1800 HOURS. GAS SERVICE TO THE OTHER CUSTOMER WILL BE RESTORED FOLLOWING REPAIRS TO THE STRUCTURE AND AT THE CUSTOMER'S REQUEST. THERE WERE NO INJURIES OR FATALITIES. MAJOR BAY AREA NEWS MEDIA WAS ON SCENE AT 1300 HOURS TRIGGERING A REPORT TO THE CPUC. THIS INCIDENT WAS ALSO REPORTED TO THE DOT WHEN IT WAS DETERMINED THAT PROPERTY DAMAGES DUE TO THE RELEASE OF GAS WERE ESTIMATED TO EXCEED $50,000.
2025-03-31 10:13 | NO | YES | YES | 20130106 | 15735 | 2013-09-27 12:11 | ORIGINAL FINAL | 14210 | OKLAHOMA NATURAL GAS CO | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2013-08-29 11:42 |  |  | 2013 | 7734 S. VICTOR | TULSA | TULSA | OK | 74136 | 36.0525 | -95.9652 | [10 empty] | 1058620 |  | NATURAL GAS |  | 9.54 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 9 | 2013-08-29 11:42 |  |  |  | 2013-08-29 12:16 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 42 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1978 | [5 empty] | 2 | D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 191 | 238.529608170480283 | 3924 | 4900.472159481490212 | 843 | 1052.777275851910359 | EQUIPMENT |  | 42 | 36.75 |  | 0 | 5000 | 2598.445081645236908295081967213114754098 | 6228.529043503880854 | 0 | 0 | 6 |  |  |  |  | 38 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | OTHER | [12 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | WATER | NO |  |  |  | CONTRACT LOCATOR | NO | YES | 9 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | NICK NORMAN | ENGINEER III | nnorman@ong.com | 918-831-8303 | 918-831-8208 |  |  |  | BRYAN BREWSTER | DIRECTOR OKLAHOMA CITY METRO OPERATIONS | 405-556-5994 | bbrewster@ong.com | OKLAHOMA NATURAL GAS WAS NOTIFIED BY THE TULSA FIRE DEPARTMENT OF A GAS RELEASE WITH IGNITION ON PIPELINE FACILITIES. IT WAS REPORTED THAT THE DAMAGE OCCURED DURING EXCAVATION ACTIVITY BY THE CITY OF TULSA WATER AND SEWER DEPARTMENT. THE SOURCE OF IGNITION WAS REPORTED TO BE A CUTTING TORCH BEING USED BY A MUNICIPAL EMPLOYEE. A CITY OF TULSA REPRESENTATIVE INDICATED THAT THEY HAD REQUESTED A LOCATE FOR A NEARBY AREA (RECORDS INDICATE THIS TO BE 7902 S. UTICA), BUT DID NOT REQUEST A LOCATE FOR THE AREA OF EXCAVATION. ONE MUNICIPAL EMPLOYEE WAS TRANSPORTED TO THE HOSPITAL AND REMAINED OVERNIGHT FOR TREATMENT OF BURNS.
2025-03-31 10:13 | NO | YES | NO | 20130107 | 16142 | 2013-09-30 19:15 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2013-09-01 09:29 |  |  | 2013 | 529 E. 1ST STREET | GLADWIN | GLADWIN | MI | 48624-2208 | 43.9874 | -84.4811 | [9 empty] | 2013-09-01 13:04 | 1058900 |  | NATURAL GAS |  | 705.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 400 | 2013-09-01 09:29 |  |  |  | 2013-09-01 10:16 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 168 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2013 | [5 empty] | 6 | ASTM D2513 | PERFORMANCE PIPE DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.602 |  | 2708 | LEAK |  |  | CONNECTION FAILURE | UNKNOWN FAILURE MODE. | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 21783 | 27203.614946479434579 | 626 | 781.777668663458938 | 69458 | 86742.353530393819354 | LAB SERVICES INVESTIGATION & CAMERA WORK BY DEPENDABLE SEWER |  | 6414 | 5612.25 |  | 0 | 98281 | 52708.4514495390186494918032786885245902 | 120339.996145536712871 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 2013 | LACK OF PROPER FUSE BEAD ON ONE SIDE, LIKELY DUE TO INCOMPLETE FACING | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [7 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 |  |  |  |  | TRACY A. GOBLE | MANAGER OF REGULATORY AND COMPLIANCE | 517-768-3187 | tracy.goble@cmsenergyc.om | A FAILURE OCCURRED ON 6" PLASTIC DISTRIBUTION GAS MAIN IN THE CITY OF GLADWIN, MICHIGAN, RESULTING IN A LEAK THAT REQUIRED EVACUATION OF SEVERAL SURROUNDING STRUCTURES. AS PART OF THE INCIDENT RESPONSE, A GAS SERVICE WORKER CHECKED THE HOME ACROSS THE STREET FROM THE FAILURE POINT, AND PERFORMED ADDITIONAL BAR TESTS WITHIN THE SOIL NEAR THE FAILURE. NONE OF THESE TESTS FOUND ANY GAS MIGRATION. ALL THE GAS WAS VENTING TO ATMOSPHERE DIRECTLY ABOVE THE POINT OF FAILURE. THE POINT OF FAILURE ON THE MAIN WAS UNDER A COUNTY DRAIN DITCH, APPROXIMATELY 20' BELOW THE ROAD GRADE AND UNDER 14' OF SOIL. THE MAIN WAS CAPPED ON EACH SIDE OF THE FAILURE UPON SHUTOFF. THE FAILURE POINT WAS LATER EXTRACTED AND ANALYZED, REVEALING A FAILED BUTT FUSE JOINT. INADEQUATE FUSE BEAD ROLLOVER WAS OBSERVED ON ONE SIDE OF THE FUSE, INDICATING POSSIBLE INCOMPLETE FACING PRIOR TO UTILIZING THE HYDRAULIC BUTT FUSE MACHINE. THE NON-FUSED ZONE WAS CHARACTERIZED BY A GENERALLY SMOOTH FLAT SURFACE APPEARANCE, AS WELL AS PARALLEL CUT MARKS WHICH LIKELY INDICATE THAT THE SURFACE HAD NOT BEEN HEATED TO THE MELTING POINT DURING THE JOINT FUSION OPERATION. INITIAL ESTIMATES INDICATED THAT MORE THAN 3 MMCF OF GAS MAY HAVE BEEN RELEASED DURING THE LEAK, BUT REVISED FINDINGS (BASED ON OBSERVATIONS OF THE FAILED FUSE; SEE ATTACHED), INDICATE A GAS RELEASE OF LESS THAN 1 MMCF. A SUPPLEMENTAL PHMSA INCIDENT REPORT IS BEING SUBMITTED HEREWITH TO REFLECT THIS, AND ALSO REFLECT THE COSTS INCURRED DURING REPLACEMENT AND INVESTIGATION OF THE FAILED MAIN.
2025-03-31 10:13 | NO | NO | NO | 20130108 | 15737 | 2013-10-18 12:55 | ORIGINAL | 12903 | TWO HARBORS CITY MUNICIPAL GAS DEPT | 522 1 ST AVE | TWO HARBORS | MN | 55616 | 2013-09-23 09:15 |  |  | 2013 | 20TH AVENUE & CSAH 2 | TWO HARBORS | LAKE | MN | 55616 | 47.0394 | -91.6678 | [12 empty] | NATURAL GAS |  | 9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-09-23 09:20 |  |  |  | 2013-09-23 09:25 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1960 | [5 empty] | 10 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.375 | [6 empty] | MECHANICAL PUNCTURE | 1 | 3 | [7 empty] | CLASS 3 LOCATION | 4000 | 4995.384464303252 | 1500 | 1873.2691741137195 | 6800 | 8492.1535893155284 | 700 | 874.1922812530691 | EXCAVATION AND BACKFILLING |  | 58 | 50.75 |  | 0 | 13058 | 6770.996608378156409836065573770491803279 | 16285.749508985569 | 12 | 0 | 184 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY | 2013-09-17 | YES | 1997 | 60 | YES | YES | [8 empty] | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | NO | 132484043 |  |  | UTILITY OWNER | YES | YES | 8 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | SCOTT JOHNSON | GAS WATER SEWER SUPT. | cthgas@frontiernet.net | 218-834-8812 | 218-834-8840 |  |  |  | SCOTT JOHNSON | GAS WATER SEWER SUPT. | 218-834-8812 | cthgas@frontiernet.net | GAS DEPARTMENT EMPLOYEE SMELLED GAS AND ASKED DRILL RIG OPERATOR IF THEY HAD HIT THE GAS LINE. HE THOUGHT THEY HAD. 911 WAS CALLED, FIRE DEPARTMENT RESPONDED AND SHUT DOWN PROCEDURES WERE STARTED. PRESSURE IN MAIN WAS RELEASED. SHUT OFF ALL BUILDINGS IN EFFECTED AREA AND EXCAVATION FOR REPAIRS STARTED. PRIVATE CONTRACTOR MADE REPAIRS TO PIPE. PURGED PIPE AND STARTED RE-LIGHT PROCEDURES.
2025-03-31 10:13 | NO | YES | NO | 20130109 | 16344 | 2013-10-21 13:23 | SUPPLEMENTAL FINAL | 6720 | ATMOS ENERGY CORPORATION - COLORADO/KANSAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2013-09-20 19:51 |  |  | 2013 | SW CORNER OF 151ST & SWITZER | OVERLAND PARK | JOHNSON | KS | 66221 | 38.8545 | -94.7053 | [9 empty] | 2013-09-20 21:18 | 1060814 |  | NATURAL GAS |  | 1425 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2013-09-20 19:51 |  |  |  | 2013-09-20 19:51 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1980 | [5 empty] | 4 | ASTM2513 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 3 LOCATION | 160000 | 199815.37857213008 | 60000 | 74930.76696454878 | 2160 | 2697.50761072375608 | 0 | 0 |  |  | 6028 | 5274.5 |  | 0 | 228188 | 119788.0615353780137560655737704918032787 | 282718.15314740261608 | 0 | 0 | 6 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | YES | [7 empty] | YES | [6 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 13397523 |  |  | UTILITY OWNER | YES | YES | 12 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | STEVE MITCHELL | CORROSION COORDINATOR | steve.mitchell@atmosenergy.com | 970-304-2066 | 970-304-2085 |  |  |  | DOUGLAS L. SHATAS | MANAGER OF COMPLIANCE | 816-863-0951 | doug.shatas@atmosenergy.com | ATMOS ENERGY EMPLOYEES WERE ATTEMPTING TO DIG A REMOTE BELL HOLE TO ISOLATE A GRADE ONE LEAK UNDER PAVEMENT AT 151ST AND SWITZER IN OVERLAND PARK, KANSAS. THE BACKHOE OPERATOR WAS DIGGING ON TOP OF THE 4' POLY LINE FROM EAST TO WEST. THE LINE AT THIS LOCATION CHANGED ELEVATION FROM HIGHER IN THE WEST TO LOWER IN THE EAST. THE BACKHOE OPERATOR WAS ATTEMPTING TO LIFT A ROCK OUT OF THE BELL HOLE THAT HAD BEEN LEFT OVER OUR LINE FROM PREVIOUS CONSTRUCTION ACTIVITIES OF UNKNOWN ORIGIN. THE ROCK POTENTIALLY STRUCK AT AN ELECTRO-FUSE COUPLING OR PUNCTURED THE PIPE ITSELF AND THE IGNITION OCCURRED FROM UNKNOWN SOURCE. ALSO STREET LIGHTS IN THE AREA AND 2,500 ELECTRIC WERE WITHOUT POWER.
2025-03-31 10:13 | NO | YES | NO | 20130110 | 15795 | 2013-10-23 19:52 | SUPPLEMENTAL FINAL | 6243 | HAWAI`IGAS | 515 KAMAKEE STREET (P.O. BOX 3000) | HONOLULU | HI | 96802-3000 | 2013-09-23 11:30 |  |  | 2013 | KAMEHAMEHA HIGHWY NEAR ARIZONA ST. | HONOLULU |  | HI | 96818 | 21.36 | -157.94 | [9 empty] | 2013-10-07 11:00 | 1062328 |  | NATURAL GAS |  | 850 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 100 | 2013-09-23 11:30 |  |  |  | 2013-09-23 12:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 120 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1957 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1.3 | 1.3 | [7 empty] | CLASS 4 LOCATION | 54000 | 67437.690268093902 | 36000 | 44958.460178729268 | 32000 | 39963.075714426016 | 0 | 0 |  |  | 50747 | 44403.625 |  | 0 | 172747 | 104178.5748859397730163934426229508196721 | 196762.851161249186 | 0 | 0 | 0 |  |  |  |  | 6 | 12 | 17 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS SECTION OF GAS MAIN IS NOT CONTROLLED OR MONITORED BY A CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DRILLING | PUBLIC TRANSIT AUTHORITY | NO | 13007030 |  |  | UTILITY OWNER | YES |  |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | 10 FT DEPTH MADE LOCATING DIFFICULT AND INACCURATE MARKING | [169 empty] | EDWIN SAWA | IMP ENGINEER | esawa@hawaiigas.com | 808-594-5661 | 808-594-5630 |  |  |  | CHARLES CALVET | DIRECTOR OAHU OPERATIONS | 808-594-5570 | ccalvet@hawaiigas.com | ON 9/23/13, A CONTRACTOR WAS DRILLING ALONG KAMEHAMEHA HIGHWAY WHEN IT STRUCK HAWAI`IGAS' (HG) 4-INCH GAS MAIN. PRIOR TO COMMENCING THE DRILLING WORK, THE CONTRACTOR CALLED THE HAWAII ONE CALL CENTER TO REQUEST THAT TONING BE DONE BY HG TO MARK THE APPROXIMATE LOCATION OF THE GAS LINE. PER THE CONTRACTOR'S ONE CALL REQUEST, HG RESPONDED AND MARKED THE LOCATION OF ITS FACILITY. USING THE TONING MARKS BY HG AND ITS OWN EQUIPMENT, CONTRACTOR ATTEMPTED TO CONFIRM THE LOCATION OF THE GAS MAIN BEFORE DRILLING. HG WAS ADVISED THAT THE CONTRACTOR ATTEMPTED TO AVOID DAMAGING OUR LINE BY DRILLING MORE THAN 30 INCHES HORIZONTALLY FROM THE PIPE LOCATION TONING MARK AND TEST BORING USING A NON-POWERED AUGER BEFORE USE OF THE POWERED DRILL RIG. THE GAS MAIN WAS APPROXIMATELY 10 FEET DEEP WHEN THE CONTRACTOR'S POWERED DRILLING RIG HIT IT. HG DISPATCHED A CREW TO BEGIN EXCAVATING TO INSTALL LINE STOP FITTINGS. DUE TO THE PIPE'S DEPTH, HG HAD DIFFICULTY LOCATING AND EXPOSING THE DAMAGED SECTION OF THE LINE WHERE THE REPAIR WORK WOULD NEED TO BE DONE AND HALTED WORK AFTER SEVERAL HOURS OF EXCAVATING. TWO PERSONNEL REMAINED ON SITE OVERNIGHT TO MONITOR THE LEAK. ON 9/24/13, A NEW LOCATION WITH IMPROVED ACCESS TO THE GAS MAIN WAS SELECTED. AT 10:00 AM, THE FEDERAL FIRE DEPARTMENT EVACUATED SEVERAL BUILDINGS IN THE NEARBY NAVAL HOUSING AREA AS A PRECAUTION DUE TO THE DETECTION OF GAS. HG LEAK INSPECTORS PERFORMED BELOW GRADE STRUCTURE CHECKS AND DETECTED 100% GAS READINGS IN SEVERAL MANHOLES. AS A RESULT, HG SET UP BLOWERS TO VENTILATE THE MANHOLES TO ENSURE THE SAFETY OF ITS CREW AND THE GENERAL PUBLIC. BASED ON OUR INVESTIGATION, HG BELIEVES THE ROOT CAUSE OF THE INCIDENT WAS THE CONTRACTOR'S INABILITY TO ACCURATELY LOCATE THE PIPE PRIOR TO COMMENCING DRILLING.
2025-03-31 10:13 | NO | YES | NO | 20130111 | 16715 | 2013-10-25 14:11 | SUPPLEMENTAL FINAL | 15042 | PALATKA GAS AUTH | 518 MAIN ST | PALATKA | FL | 32177-3617 | 2013-10-22 23:54 |  |  | 2013 | 1705 WASHINGTON ST. - UNITS 176 & 177 | PALATKA | PUTNAM | FL | 32177-2056 | 29.6565 | -81.6448 | [9 empty] | 2013-10-23 13:00 | 1063803 |  | NATURAL GAS |  | 18 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 5 | 2013-10-22 23:54 |  |  |  | 2013-10-23 00:11 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2013 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | 3/4" NIPPLE BROKE DOWN STREAM OF THE SERVICE VALVE AND BEFORE THE HOUSE REGULATOR ON A 2-METER MANIFOLD | CLASS 3 LOCATION | 121440 | 151659.87233624673072 | 984 | 1228.864578218599992 | 300 | 374.6538348227439 | 5000 | 6244.230580379065 | VEHICLE DAMAGE |  | 106 | 92.75 |  | 0 | 127830 | 66149.0720861513122404590163934426229508 | 159600.371329667139612 | 0 | 0 | 2 |  |  |  |  | 50 | 50 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DONALD KITNER | GENERAL MANAGER | dkitner@palatkagas.org | 386-328-1591 | 386-325-9373 |  |  |  | DONALD KITNER | GENERAL MANAGER | 386-328-1591 | dkitner@palatkagas.org | AT 11:54 PM PGA'S ON-CALL EMPLOYEE WAS NOTIFIED BY PUTNAM COUNTY'S DISPATCHER, BY PHONE, OF A GAS RELATED INCIDENT AT 1705 WASHINGTON STREET. PGA FOUND A FORD EXPEDITION HAD RUN OVER A LARGE BUSH, THROUGH A 6" HIGH WROUGHT IRON FENCE AND STRUCK AN AIR CONDITIONER CONDENSER UNIT WHICH WAS FORCED INTO A 2-METER MANIFOLD SEVERING THE NIPPLE ON THE OUTLET SIDE OF THE SERVICE VALVE AND BEFORE THE HOUSE REGULATOR. THE GAS IGNITED AND BURNED A PORTION OF THE DUPLEX. NO INJURIES WERE REPORTED, THE RESIDENTS OF THE DUPLEX EXITED THE UNITS ON THEIR OWN. THE OCCUPANT(S) OF THE VEHICLE FLED THE SCENE AND THE POLICE ADVISED THE VEHICLE HAD BEEN REPORTED STOLEN EARLIER. THE GAS WAS SHUT OFF AT THE SERVICE VALVE WHICH WAS SUBSEQUENTLY LOCKED AND A PLUG INSTALLED ON THE OUTLET SIDE. THE AREA WAS SURVEYED FOR GAS LEAKAGE WITH A SENSIT GAS DETECTOR WITH NO LEAKAGE FOUND; A BAR HOLE SURVEY WAS NOT CONDUCTED THAT NIGHT DUE TO HIGH STANDING WATER. THE AREA WAS RESURVEYED AND BAR-HOLE SURVEY CONDUCTED THE NEXT MORNING AFTER THE STANDING WATER SUBSIDED AND AGAIN NO GAS WAS DETECTED.
2025-03-31 10:13 | NO | NO | NO | 20130113 | 16771 | 2013-10-30 12:40 | SUPPLEMENTAL FINAL | 32013 | AMERIGAS PROPANE LP | 500 N. GULPH RD. | KING OF PRUSSIA | PA | 19406 | 2013-10-18 06:00 |  |  | 2013 | 268 PONDEROSA DR. | KAYENTA | NAVAJO | AZ | 86033 | 36.7134 | -110.2463 | [9 empty] | 2013-10-19 04:00 | 1063473 |  | PROPANE GAS |  | 2.27 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-10-18 06:01 |  |  |  | 2013-10-18 09:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | OTHER | LPG LIQUEFIED PETROLEUM GAS (PROPANE) | SERVICE RISER |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.11 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 30 | 37.46538348227439 | 4000 | 4995.384464303252 | 0 | 0 |  |  | 210 | 183.75 |  | 0 | 4240 | 2254.434973187392421475409836065573770492 | 5216.59984778552639 | 0 | 0 | 118 |  |  |  |  | 17 | 17 | 20 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [156 empty] | DAVID HEDRICK | AMERIGAS PIPELINE SAFETY MANAGER | david.hedrick@amerigas.com | 2159704159 |  |  |  |  | DAVID HEDRICK | AMERIGAS PIPELINE SAFETY MANAGER | 2159704159 | david.hedrick@amerigas.com | FRIDAY OCTOBER 18TH AT APPROXIMATELY 6:00 P.M. WE WERE NOTIFIED OF A GAS LINE BREAK AT KAYENTA MOBILE HOME PARK. THE NAVAJO POLICE RESPONDED TO AN EMERGENCY CALL ABOUT VANDALS IN ONE OF THE PARKS ALLEY WAYS KICKING AT METERS, UPON ARRIVAL THEY FOUND THE BROKE METER RISER AT THE MOBILE HOME PARK AND EXPEDIENTLY USED THE EMERGENCY SHUTDOWN SYSTEM TO REMEDY THE SITUATION. THIS IMMEDIATELY CUT SERVICE TO 118 CUSTOMERS IN THE PARK. MYSELF (PHIL STAHL), KENNY WEICKUM AND DAN GOUGE RESPONDED TO THE CALL. WE ARRIVED ON SITE AT APPROXIMATELY 9:30 P.M. WE LOCATED THE DAMAGE AND FIXED THE SYSTEM AT APPROXIMATELY 1:30 A.M. I CALLED THE AMERIGAS EMERGENCY CALL CENTER AND INFORMED THEM THAT WE WOULD BE RESTARTING THE SYSTEM THE FOLLOWING MORNING AND TO TELL OUR CUSTOMERS THEY WOULD NEED TO BE HOME IN ORDER TO RESTORE SERVICE. WE THEN STARTED THE PROCEDURE OF SHUTTING EVERY VALVE OFF TO ALL CUSTOMERS BEFORE RESTARTING THE SYSTEM. WE STARTED THE SYSTEM BACK UP AT 9:30A.M. 10/19/2013. ONCE THE SYSTEM WAS UP TO FULL PRESSURE AND ALL SYSTEMS WERE NORMAL, WE BEGAN PUTTING CUSTOMERS BACK INTO SERVICE. THE COMPLETION OF RE-ESTABLISHING SERVICE TO ALL CUSTOMERS ON THE SYSTEM WAS COMPLETED ON 10/23/2013
2025-03-31 10:13 | NO | YES | NO | 20130114 | 15744 | 2013-10-31 08:25 | ORIGINAL FINAL | 13062 | NATIONAL FUEL GAS DISTRIBUTION CORP - NEW YORK | 6363 MAIN ST. | WILLIAMSVILLE | NY | 14221 | 2013-10-07 10:30 |  |  | 2013 | 24 LAKEVIEW AVENUE | RIPLEY | CHAUTAUQUA | NY | 14775-9701 | 42.2601 | -79.7103 | [9 empty] | 2013-10-07 13:30 | 1062302 |  | NATURAL GAS |  | 19.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2013-10-07 12:14 |  |  |  | 2013-10-07 12:19 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 0.75 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 9.8 |  |  | UNKNOWN | LEAK |  |  | OTHER | PLEASE SEE PART H (NARRATIVE) | [5 empty] | CLASS 3 LOCATION | 225000 | 280990.376117057925 | 500 | 624.4230580379065 | 2500 | 3122.1152901895325 | 0 | 0 |  |  | 175 | 153.125 |  | 0 | 228175 | 118071.1399171795704262295081967213114754 | 284890.039465285364 | 0 | 0 | 1 |  |  |  |  | 42 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | REGULATOR STATIONS FEEDING DISTRIBUTION SYSTEM ARE MANUALLY SET. SYSTEM PRESSURE IS MONITORED BY SCADA BUT LEAK WOULD NOT HAVE BEEN SIGNIFICANT ENOUGH TO BE NOTICED. CONTROLLERS' ACTIONS WOULD NOT HAVE AFFECTED OUTCOME. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | OCCUPANT | UNKNOWN/OTHER | DRAINAGE | NO |  |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED | YES |  | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | ANDREW D. EMHOF | ENGINEER I | emhofa@natfuel.com | 716-857-7630 | 716-857-7469 |  |  |  | MICHAEL D. COLPOYS | ASSISTANT VICE PRESIDENT | 814-871-8239 | colpoysm@natfuel.com | AT APPROXIMATELY 10:30 AM ON MONDAY, OCTOBER 7, 2013, THE RESIDENCE AT 24 LAKEVIEW AVENUE, RIPLEY, NY SUFFERED AN EXPLOSION. INVESTIGATION INTO THE INCIDENT INDICATES THE SERVICE LINE TO THE PROPERTY WAS PREVIOUSLY DAMAGED BY THE HOMEOWNER WHO MADE AN UNAUTHORIZED REPAIR WITHOUT THE KNOWLEDGE OF THE OPERATOR. THE REPAIR FAILED RESULTING IN NATURAL GAS MIGRATING INTO THE RESIDENCE WHERE IT IGNITED. SUBSEQUENT TO THE EVENT, THE SERVICE LINE INVOLVED IN THIS INCIDENT WAS CUT OFF AT THE MAIN AND ABANDONED.
2025-03-31 10:13 | NO | YES | NO | 20130115 | 15745 | 2013-10-31 18:16 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2013-10-01 17:55 |  |  | 2013 | 366 MAY STREET | ELGIN | KANE | IL | 60120 | 42.0248 | -88.2717 | [9 empty] | 2013-10-01 19:52 | 1061831 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 5 | 2013-10-01 17:55 |  |  |  | 2013-10-01 18:24 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET | [10 empty] | OTHER | ALUMINUM AND STEEL | [9 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 200000 | 249769.2232151626 | 500 | 624.4230580379065 | 1000 | 1248.846116075813 | 0 | 0 |  |  | 100 | 87.5 |  | 0 | 201600 | 104303.7158724843751721311475409836065574 | 251729.9923892763195 | 0 | 0 | 1 |  |  |  |  | 58 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LETICIA QUEZADA | MANAGER COMPLIANCE ASSURANCE | lquezad@aglresources.com | 630-388-2316 |  |  |  |  | LETICIA QUEZADA | MANAGER COMPLIANCE ASSURANCE | 630-388-2316 | lquezad@aglresources.com | A VAN SLIPPED OUT OF GEAR WHILE PARKED IN A DRIVEWAY, HITTING THE HOUSE THEN THE METER SET. GAS IGNITED CAUSING DAMAGE TO THE VAN AND THE HOUSE.
2025-03-31 10:13 | NO | NO | NO | 20130116 | 15752 | 2013-11-05 18:17 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2013-10-04 05:30 |  |  | 2013 | SOUTHWEST PART OF TOWN | WAYNE |  | NE | 68787 | 42.2426 | -96.9837 | [9 empty] | 2013-10-04 07:30 | 1062118 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2013-10-04 05:30 |  |  |  | 2013-10-04 05:50 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1981 | [5 empty] | 0.5 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | OTHER | TORNADO PULLED OUT OF GROUND | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 30000 | 37465.38348227439 | 7500 | 9366.3458705685975 | 0 | 0 |  |  | 0 | 0 |  | 0 | 37500 | 19396.2977511538875 | 46831.7293528429875 | 24 | 1 | 20 |  |  |  |  | 25 | 25 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | EMPLOYEES WERE AWARE OF TORNADO WIPING OUT PART OF TOWN AND RESPONDED |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY TORNADO HITTING TOWN OF WAYNE. SCADA/CONTROL ROOM WAS NOT INVOLVED IN INCIDENT IN ANY WAY. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [56 empty] | HIGH WINDS | [5 empty] | YES |  |  | YES | [215 empty] | NATHAN STEWART | STATE COMPLIANCE SPECIALIST | nathan.stewart@blackhillscorp.com | (402) 437-1734 | (402) 437-6734 |  |  |  | NATHAN STEWART | STATE COMPLIANCE SPECIALIST | (402) 437-1734 | nathan.stewart@blackhillscorp.com | PLEASE SEE UPLOADED FILE FOR NARRATIVE OF EVENT
2025-03-31 10:13 | NO | YES | NO | 20130117 | 15860 | 2013-11-05 21:03 | SUPPLEMENTAL FINAL | 7348 | DOMINION HOPE | 781 CHESTNUT RIDGE RD | MORGANTOWN | WV | 26505 | 2013-10-08 06:00 |  |  | 2013 | 400 ABBEY ROAD | BELINGTON | RANDOLPH COUNTY | WV | 26250-0000 | 38.9417 | -79.9495 | [9 empty] | 2013-10-14 17:07 | 1062990 |  | NATURAL GAS |  | 62.83 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2013-10-08 07:02 |  |  |  | 2013-10-08 08:03 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2004 | [5 empty] | 4 | ASTM 2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | RUPTURE |  |  |  |  | LONGITUDINAL |  | 4 | 4 |  | CLASS 3 LOCATION | 5000 | 6244.230580379065 | 71459 | 89241.294608661521167 | 100 | 124.8846116075813 | 21000 | 26225.768437592073 | CONSULTING FEES. |  | 210 | 183.75 |  | 0 | 97769 | 50630.8705029919775944754098360655737705 | 122019.928238240240467 | 1 | 1 | 0 |  |  |  |  | 513 | 70 | 100 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM OPERATORS ARE ONLY ABLE TO MONITOR (CANNOT MANIPULATE) THE GAS PRESSURE. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | JANETTE L. JONES | TECHNICAL SPECIALIST III | janette.l.jones@dom.com | 304-464-5949 |  |  |  |  | KENNETH L. SMITH | MANAGER GAS OPERATIONS | 304-464-5936 | kenneth.l.smith@dom.com | AT 06:09 ON 10/08/2013, AN OVERPRESSURE EVENT OCCURRED ON DOMINION HOPE GAS' MAIN PIPELINE (HM-3095). THE ROOT CAUSE WAS THE FAILURE OF HOPE GAS REGULATORS DUE TO ICING CONDITIONS. THESE REGULATORS ARE LOCATED IN STATION HX-363 AND REDUCE PRESSURE FROM OVER 500 PSIG TO 70 PSIG. AT 06:47, A SERVICE PIPELINE THAT IS CONNECTED TO M-3095 RUPTURED, CAUSING A BLOWING LEAK. THE SYSTEM WAS ISOLATED AND COMPLETELY SHUT DOWN AT 8:10. NO INJURIES OR PROPERTY DAMAGE OCCURRED. A CONSULTANT (JANA LABORATORIES, INC.) WAS EMPLOYED TO ANALYZE THE INCIDENT AND RECOMMEND CHANGES. AS ADVISED BY JANA LABS' PRELIMINARY REPORT, DOMINION HOPE GAS IS IN THE PROCESS OF INSPECTING AND/OR REPLACING VARIOUS COMPONENTS OF THE AFFECTED PIPELINE SYSTEM. TESTING OF THE PIPELINES AND THE REGULATING/METERING STATIONS WILL BE PERFORMED IN ACCORDANCE WITH 46 CFR PART 192. THE SYSTEM WILL BE PLACED INTO SERVICE ONLY WHEN ALL COMPONENTS ARE DEEMED SAFE AND OPERATIONAL. AS REQUESTED BY DOMINION, JANA LABORATORIES IS COMPILING AN ADDITIONAL REPORT TO RECOMMEND LONG-RANGE PLANS AND CONCERNS. COMPLETION INFORMATION: A CONSULTANT (JANA LABORATORIES) COMPLETED AN EVALUATION OF THE AFFECTED PIPELINE SYSTEM: 5.0 RECOMMENDATIONS BASED ON THE ANALYSIS TO DATE AND THE TESTING OF THE SAMPLES RECEIVED, THE FOLLOWING RECOMMENDATIONS ARE MADE: &#61623; THE OVERPRESSURIZATION RESULTED IN THE EXPOSURE OF THREE REGULATOR STATIONS, THE HDPE MAINLINE, AND THE MDPE BRANCH TO INCREASING PRESSURE UP TO >500 PSIG (MAXIMUM 528 PSIA, OR 513 PSIG), RAMPING UP OVER A PERIOD OF APPROXIMATELY ONE HOUR. THE ROOT CAUSE WAS REPORTEDLY THE FAILURE OF REGULATOR STATION HX-363 TO REGULATE PRESSURE FROM THE TRANSMISSION LINE DUE TO FROZEN WATER IN THE REGULATOR RUN. &#61623; THE INTEGRITY OF THE PIPES AND FITTINGS HAS BEEN ASSESSED AS FOLLOWS: O 6" HDPE PIPE AND ASSOCIATED HEAT FUSION, ELECTROFUSION, AND TRANSITION FITTINGS: NO EXPECTED IMPACT OF OVERPRESSURIZATION ON LONG-TERM PERFORMANCE O 6" HDPE BALL VALVES: NO EXPECTED IMPACT OF OVERPRESSURIZATION ON LONG-TERM PERFORMANCE O 4" MDPE PIPE AND ASSOCIATED HEAT FUSION, ELECTROFUSION, AND TRANSITION FITTINGS AFFECTED (PIPE BURST); NON-BURST REGIONS EXPOSED TO PRESSURE CLOSE TO TENSILE LIMIT O 4" MDPE BALL VALVE: POSSIBLY AFFECTED; EXPOSED TO PRESSURE CLOSE TO TENSILE LIMIT &#61623; THE INTEGRITY OF THE REGULATOR STATIONS HAS BEEN ASSESSED AS FOLLOWS: O HX-363: NOT EXPECTED TO BE AFFECTED; ROOT CAUSE ANALYSIS OF ENTRAINED WATER FREEZING ADVISED BEFORE REPRESSURIZATION O TYGART VALLEY REGIONAL JAIL: POSSIBLY AFFECTED; METER, VALVES, AND REGULATORS EXPOSED TO PRESSURE > MAOP O IS-267: POSSIBLY AFFECTED; METER, VALVES AND REGULATORS EXPOSED TO PRESSURE > MAOP &#61623; ALL POTENTIALLY AFFECTED COMPONENTS SHOULD BE CLOSELY EXAMINED FOR DAMAGE (IN SIMILAR FASHION TO HX-363 AFTER THE INCIDENT) AND REPLACED IF DAMAGE IS FOUND. IT HAS BEEN INDICATED THAT THE JAIL REGULATOR STATION AND THE ENTIRE MDPE LINE ARE SCHEDULED TO BE REPLACED.. 1 . REGULATORS WERE COMPLETED DISASSEMBLED AND INSPECTED AT ALL THREE STATIONS BY A CONSULTANT (MASTER CONTROLS). REGULATORS WERE FOUND TO BE UNAFFECTED BY THE OVERPRESSURE SITUATION. 2 TWIN 3X4 MERCER RELIEF VALVES WERE INSTALLED AS ADDITIONAL OVER-PRESSURE PROTECTION AT THE HIGH PRESSURE CUT REGULATION STATION. 3. BRUEST PILOT HEATERS WERE INSTALLED ON THE HIGH PRESSURE CUT REGULATION STATION. 4. NEW STEEL ENAMEL BUILDING INSTALLED OVER THE HIGH PRESSURE CUT REGULATION STATION TO PROTECT HEATERS FROM THE WIND. 5. MDPE PIPE WAS REMOVED AND REPLACE WITH HDPE. 6. ENTIRE SYSTEM WAS RETESTED WITH AIR TO 155 LBS. 7. COMPLETE STATION INSPECTIONS WERE PERFORMED WHEN GAS WAS REINTRODUCED. GAS WAS REINTRODUCED ON 11/25/13.
2025-03-31 10:13 | NO | YES | YES | 20130118 | 15753 | 2013-11-06 18:45 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2013-10-06 03:45 |  |  | 2013 | 1032 S. 13TH | NORFOLK |  | NE | 68701 | 42.0198 | -97.4272 | [9 empty] | 2013-10-06 05:42 | 1062195 |  | NATURAL GAS |  | 2 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2013-10-06 03:45 |  |  |  | 2013-10-06 04:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1987 | [8 empty] | STEEL |  |  |  | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 0.3 | 0.3 | [7 empty] | CLASS 3 LOCATION | 70000 | 87419.22812530691 | 1800 | 2247.9230089364634 | 1700 | 2123.0383973288821 | 0 | 0 | 0 |  | 12 | 10.5 |  | 0 | 73512 | 38026.4567070157178606557377049180327869 | 91800.6895315722555 | 1 | 0 | 0 |  |  |  |  | 68 | 68 | 70 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS LOSS WAS NOT SIGNIFICANT ENOUGH TO TRIGGER SCADA ALARM | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | NATHAN STEWART | STATE COMPLIANCE SPECIALIST | nathan.stewart@blackhillscorp.com | (402) 437-1734 | (402) 437-6734 |  |  |  | NATHAN STEWART | STATE COMPLIANCE SPECIALIST | (402) 437-1734 | nathan.stewart@blackhillscorp.com | CAR RAN INTO METER SET AT USA STEAK BUFFET IN NORFOLK, NE. DRIVER WAS UNDER THE INFLUENCE OF CHEMICALS AT THE TIME OF THE INCIDENT. LOG OF EMERGENCY RESPONSE ACTIVITIES AND TIMELINE IS ATTACHED TO THIS REPORT. METER SET WAS SUBSEQUENTLY REBUILT AND PLACED BACK INTO SERVICE.
2025-03-31 10:13 | NO | NO | NO | 20130119 | 15754 | 2013-11-07 14:28 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2013-10-09 10:07 |  |  | 2013 | 1900 SAM HOUSTON PARKWAY @ ALMEDA RD | HOUSTON | HARRIS | TX | 77007 | 29.6005 | -95.4647 | [9 empty] | 2013-10-09 12:00 | 1062505 |  | NATURAL GAS |  | 357 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-10-09 10:37 |  |  |  | 2013-10-09 10:37 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1993 | [5 empty] | 6.58 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 1424 | 1778.356869291957712 | 0 | 0 |  |  | 2354 | 2059.75 |  | 0 | 3778 | 2641.931424199445369967213114754098360656 | 3838.106869291957712 | 0 | 0 | 0 |  |  |  |  | 34.8 | 34.8 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF SYSTEM | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LESLIE J. DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steve.yarbrough@centerpointenergy.com | CONTRACTOR WAS SPREADING DIRT WITH DOZER AND GOUGED A 6" STEEL LINE. THE DIRT IN THE AREA WHERE WORK WAS BEING DONE WAS WET, MUDDY, AND SOFT AND THE DOZER SUNK INTO A 6" STEEL LINE.
2025-03-31 10:13 | YES | NO | NO | 20130120 | 15970 | 2013-11-08 12:07 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 1 METROTECH CENTER | BROOKLYN | NY | 11201 | 2013-10-12 01:17 |  |  | 2013 | 8740 124TH STREET | RICHMOND HILL | QUEENS | NY | 11418 | 40.6996 | -73.8263 | [9 empty] | 2013-10-12 02:49 | 1062786 |  |  |  | 0 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | YES |  | 2013-10-12 01:17 |  |  |  | 2013-10-12 01:41 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | GAS SYSTEM NOT INVOLVED | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | NO RELEASE INVOLVED. | CLASS 4 LOCATION | 200000 | 249769.2232151626 | 5000 | 6244.230580379065 | 2000 | 2497.692232151626 | 0 | 0 |  |  | 0 | 0 |  | 0 | 207000 | 107067.563586369459 | 258511.146027693291 | 0 | 0 | 4 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | RECEIVED NOTIFICATION FROM CON EDSION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INVESTIGATION WAS NOT NEEDED AS PRESSURE IN AREA REMAINED STABLE AT ALL TIMES WITH NO INTERACTION BETWEEN CONTROLLER, SCADA AND CONTROLS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | DAVID ANGELONE | MANAGER | david.angelone@nationalgrid.com | 718 403 3347 |  |  |  |  | R. DE MARINIS | VP MAINTENANCE AND CONSTRUCTION NY GAS | 516 545-4337 | robert.demarinis@nationalgrid.com | FDNY CLASSIFIES THE INCIDENT AS INCENDIARY IN NATURE AND AN ARREST WAS MADE. FIRES WERE EXTINGUISHED AT FOUR DIFFERENT LOCATIONS WITHIN THE SUBJECT RESIDENCE. INVESTIGATION REVEALS NO INDICATION THAT NATIONAL GRID FACILITIES WERE INVOLVED IN THE INCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20130122 | 15806 | 2013-11-13 10:37 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2013-10-16 21:28 |  |  | 2013 | 7616 W VARNEY ROAD | PEORIA | MARICOPA | AZ | 85345 | 33.5886 | -112.2294 | [9 empty] | 2013-10-16 23:12 | 1063231 |  | NATURAL GAS |  | 2 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | YES | 5 | 2013-10-16 21:28 |  |  |  | 2013-10-16 21:59 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 27 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1985 | [5 empty] | 0.5 | ASTM D2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 0.5 | 0.1 |  | CLASS 3 LOCATION | 0 | 0 | 5488 | 6853.667485024061744 | 243 | 303.469606206422559 | 0 | 0 |  |  | 8 | 7 |  | 0 | 5739 | 2970.74694081907702077049180327868852459 | 7164.137091230484303 | 0 | 0 | 5 |  |  |  |  | 40 | 40 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | OCCUPANT | HAND TOOLS | UNKNOWN/OTHER | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 4 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | SHAWN BRINK | ADMINISTRATOR COMPLIANCE | shawn.brink@swgas.com | 602-484-5489 | 602-484-5322 |  |  |  | RON BASSLER | GENERAL MANAGER CENTRAL SUPPORT | 602-395-4254 | ron.bassler@swgas.com | PL 2013-1321 SOUTHWEST GAS CORPORATION (SWG) RESPONDED TO A REPORTED EXPLOSION WITH FIRE AT 7916 WEST VARNEY ROAD IN PEORIA. TWO PEOPLE WERE TRANSPORTED TO THE HOSPITAL WITH BURNS. SWG CREWS RESPONDED AND CONTROLLED THE FLOW OF GAS BY SQUEEZING A 3/4-INCH BRANCH SERVICE. NOTIFICATION WAS MADE TO PHMSA VIA THE NATIONAL RESPONSE CENTER (NRC) REPORT NUMBER 1063231 AT 23:12 OF THE IN-PATIENT HOSPITALIZATION. THERE WERE NO FATALITIES AS A RESULT OF THE INCIDENT. UPON FURTHER INVESTIGATION, A 1/2-INCH PE SERVICE LINE AND TRACER WIRE WAS FOUND CUT COMPLETELY IN TWO. THE HOUSE WAS BEING REMODELED, AND THERE WAS RECENT EXCAVATION IN THE AREA OF DAMAGE. NO LINE LOCATE REQUEST WAS REQUESTED FOR THE EXCAVATION. NOTE: FOR PART #A, #10, THE ESTIMATED VOLUME OF GAS RELEASED THAT IS IDENTIFIED REPRESENTS AN ESTIMATE THAT PRESUMES A CUT PIPE THAT IS DISCHARGING INTO THE ATMOSPHERE AT 40 PSI, BEGINNING AT THE TIME OF THE INITIAL REPORT OF THE INCIDENT AND ENDING AT THE TIME THE PIPELINE WAS SHUT DOWN. HOWEVER, THE ACTUAL AMOUNT OF GAS LOSS IS UNKNOWN BECAUSE THE TIME THE GAS PIPELINE WAS CUT IS UNKNOWN. ALSO, THE IMPACT ON THE RESTRICTION OF THE GAS CAUSED BY ITS DISCHARGING INTO SOIL (AS OPPOSED TO BEING DISCHARGED TO ATMOSPHERE) IS NOT ACCOUNTED FOR IN THE ESTIMATE. SUPPLEMENTAL REPORT: THE SERVICE LINE WAS SEVERED BY THE OCCUPANT WHILE WORKING WITH HAND TOOLS. SECTION G3 #6 AND #7 HAVE BEEN REVISED TO REFLECT THIS FACT.
2025-03-31 10:13 | NO | NO | NO | 20130124 | 15759 | 2013-11-18 13:15 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2013-10-21 05:04 |  |  | 2013 | 43240 CORTE ALMONTE | TEMECULA | RIVERSIDE | CA | 92592 | 33.4954 | -117.1107 | [9 empty] | 2013-10-21 07:50 | 1063550 |  | NATURAL GAS |  | 13 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 8 | 2013-10-21 05:04 |  |  |  | 2013-10-21 06:22 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1992 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.75 | [6 empty] | MECHANICAL PUNCTURE | 0.8 | 0.8 | [7 empty] | CLASS 3 LOCATION | 50000 | 62442.30580379065 | 600 | 749.3076696454878 | 200 | 249.7692232151626 | 0 | 0 |  |  | 79 | 69.125 |  | 0 | 50879 | 26339.4626923609471409836065573770491803 | 63510.5076966513004 | 0 | 0 | 2 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | tbauer@semprautilities.com | 909-376-7208 | 909-335-7527 |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | ON OCT 21, 2013 AT 5:04 AM, THE GAS COMPANY WAS INFORMED OF A GAS LEAK AT THE ADDRESS OF 43240 CORTE ALMONTE IN TEMECULA. THE LEAK WAS FROM A GAS RISER AT THE GAS METER SET ASSEMBLY. THE CAUSE OF THE LEAK WAS A VEHICLE THAT HAD STRUCK THE METER SET ASSEMBLY SEVERING THE RISER. GAS COMPANY PERSONNEL RESPONDED AND PINCHED GAS SERVICE STOPPING THE FLOW OF GAS AT 7:26 AM. AFTER THE VEHICLE AND OTHER DEBRIS WERE CLEARED AND WHEN DECLARED BY THE EMERGENCY RESPONDERS THAT IT WAS SAFE TO DO SO, SERVICE WAS REPAIRED AND RESTORED AT APPROXIMATELY 1 PM. INVESTIGATION REVEALED THAT THE OPERATOR OF THE VEHICLE WAS GERARDO FIERRO WAS SUSPECTED OF DRIVING UNDER THE INFLUENCE. MORE INFORMATION ON THE INCIDENT MAY BE AVAILABLE IN THE TEMECULA POLICE DEPARTMENT REPORT #TE132940019 AND TEMECULA FIRE DEPARTMENT CASE # 106447. THE ESTIMATED DAMAGE TO THE PRIVATE PROPERTY OF THE HOUSE AT 43240 CORTE ALMONTE IS IN EXCESS OF $50,000.
2025-03-31 10:13 | YES | NO | NO | 20130125 | 15760 | 2013-11-19 12:31 | ORIGINAL FINAL | 2736 | CONSUMERS GAS UTILITY CO | 900 MEMORIAL BLVD | HUNTINGTON | WV | 25701 | 2013-10-21 22:30 |  |  | 2013 | 201 EAST MYLES AVENUE | PENNSBORO | RITCHIE | WV | 26415 | 39.2827 | -80.9658 | [9 empty] | 2013-10-22 04:45 | 1063635 |  | NATURAL GAS |  | 5 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-10-21 22:48 |  |  |  | 2013-10-21 23:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | EXPLOSION BROKE OFF OUTLET SPUD OF METER. | CLASS 2 LOCATION | 60000 | 74930.76696454878 | 400 | 499.5384464303252 | 750 | 936.63458705685975 | 0 | 0 |  |  | 41 | 35.875 |  | 0 | 61191 | 31662.0826749581086155737704918032786885 | 76402.81499803596495 | 0 | 0 | 1 |  |  |  |  | 0.5 | 0.5 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | GARY G. HALL | DIVISION MANAGER - SAFETY SUPERVISOR | mjconsumersgas@frontier.com | 304-659-2971 | 304-659-2972 |  |  |  | GARY G. HALL | DIVISION MANAGER-SAFETY SUPERVISOR | 304-659-2971 | mjconsumersgas@frontier.com
2025-03-31 10:13 | NO | NO | NO | 20130126 | 15762 | 2013-11-21 14:03 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2013-10-23 10:25 |  |  | 2013 | 13646 LIVE OAK LANE | IRWINDALE | LOS ANGELES | CA | 91760 | 34.1129 | -117.9744 | [9 empty] | 2013-10-23 16:12 | 1063854 |  | NATURAL GAS |  | 844 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 50 | 2013-10-23 10:25 |  |  |  | 2013-10-23 10:45 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 32 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1967 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.8 | 0.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 5000 | 6244.230580379065 | 1000 | 1248.846116075813 | 75000 | 93663.458705685975 | ESTIMATED COSTS OF LOSS PRODUCTION BY ALL AMERICAN ASPHALT |  | 5065 | 4431.875 |  | 0 | 86065 | 45995.7469949514133934426229508196721311 | 105588.410402140853 | 0 | 3 | 0 |  |  |  |  | 226 | 226 | 260 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 2 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 32760612 | ONE-CALL CENTER |  | CONTRACT LOCATOR | YES | YES | 12 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | tbauer@semprautilities.com | 909-376-7208 | 909-335-7527 |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | ON OCTOBER 23, 2013, WHILE EXCAVATING TO INSTALL A 3" NATURAL GAS SERVICE, A CONTRACTOR WORKING FOR SOUTHERN CALIFORNIA GAS COMPANY STRUCK AN EXISTING 3/4" HIGH PRESSURE GAS SERVICE. THIS DAMAGE RESULTED IN AN ASPHALT PLANT HAVING TO SHUT DOWN PRODUCTION. THE PLANT'S ESTIMATE OF LOSS PRODUCT WAS $75,000, PROMPTING INCIDENT TO BE REPORTED TO PHMSA. ALL REPAIRS HAVE BEEN COMPLETED, AND SERVICE TO THREE IMPACTED CUSTOMERS RESTORED. INVESTIGATION REVEALED THAT DAMAGED 3/4" BRANCH SERVICE WAS NOT ACTIVE, AND SERVICE RISER WAS BURIED AND NOT VISIBLE. FURTHER, SERVICE DID NOT APPEAR ON SOUTHERN CALIFORNIA GAS COMPANY MAPS PROVIDED TO THE CONTRACTOR. AS A RESULT, CONTRACTOR WAS NOT AWARE OF BRANCH SERVICE, AND IT WAS NOT MARKED. CONTRACTOR HAD A CURRENT VALID USA TICKET. THE BRANCH SERVICE WAS REMOVED FROM THE SYSTEM.
2025-03-31 10:13 | NO | YES | NO | 20130127 | 15765 | 2013-11-22 19:00 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2013-10-25 04:28 |  |  | 2013 | 450 N. PATRIOT DRIVE | HAINESVILLE | LAKE | IL | 60030 | 42.3523 | -88.0664 | [9 empty] | 2013-10-25 06:14 | 1063981 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2013-10-25 04:28 |  |  |  | 2013-10-25 04:50 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET | [10 empty] | OTHER | ALUMINUM AND STEEL PARTS | [9 empty] | OTHER | [8 empty] | SERVICE RISER WAS BENT AND SHEARED OFF. | CLASS 3 LOCATION | 295000 | 368409.604242364835 | 500 | 624.4230580379065 | 1500 | 1873.2691741137195 | 0 | 0 |  |  | 100 | 87.5 |  | 0 | 297100 | 153699.6208120896086721311475409836065574 | 370994.796474516461 | 0 | 0 | 2 |  |  |  |  | 23 | 23 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LETICIA QUEZADA | MANAGER COMPLIANCE ASSURANCE |  | 630-388-2316 |  |  |  |  | LETICIA QUEZADA | MANAGER COMPLIANCE ASSURANCE | 630-388-2316 | lquezad@aglresources.com | AN SUV TRAVELLING SOUTHBOUND VEERED ONTO NORTHBOUND TRAFFIC THEN JUMPED THE CURB AND RAN OFF THE ROAD. THE VEHICLE TRAVELLED OVER 200 YARDS BEFORE HITTING THE HOME AND DAMAGING THE METER SET, WHICH RESULTED IN IGNITION OF NATURAL GAS.
2025-03-31 10:13 | NO | YES | NO | 20130129 | 15963 | 2013-12-17 13:18 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 1 METROTECH CENTER | BROOKLYN | NY | 11201 | 2013-11-20 16:30 |  |  | 2013 | 7009 RIDGE BLVD. | BAY RIDGE | KINGS | NY | 11209 | 40.635 | -74.029 | [9 empty] | 2013-11-20 | 1066407 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-11-20 16:30 |  |  |  | 2013-11-20 16:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | SYSTEM NOT INVOLVED | UNKNOWN | [8 empty] | OTHER | SYSTEM NOT INVOLVED | [9 empty] | OTHER | [8 empty] | NO RELEASE | CLASS 4 LOCATION | 125000 | 156105.764509476625 | 0 | 0 | 4000 | 4995.384464303252 | 0 | 0 |  |  | 0 | 0 |  | 0 | 129000 | 66723.264263969373 | 161101.148973779877 | 0 | 0 | 16 |  |  |  |  | 10 | 10 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | OPERATORS PERSONEL THAT WERE ALREADY ONSITE AT TIME OF INCIDENT. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS ISOLATED TO A RANGE WITHIN THE APARTMENT BUILDING. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | PLASTIC HOUSEWARES LEFT IN OVEN CAUGHT ON FIRE. | [47 empty] | R. VERDERAME | LEAD SUPERVISOR | richard.verderame@nationalgrid.com | 718 403-3105 | 718 596-7452 |  |  |  | R. DE MARINIS | VP MAINTENANCE AND CONSTRUCTION NY GAS | 516 545-4337 | robert.demarinis@nationalgrid.com | AT THE TIME OF THE INCIDENT THERE WAS A NATIONAL GRID CREW ON LOCATION COMPLETING A LOW PRESSURE TO HIGH PRESSURE SERVICE UPGRADE. WHEN THE HEADER ALTERATION WORK WAS COMPLETED THE SERVICE CREW BEGAN RELIGHTS FOR ALL THE APPLIANCES IN THE BUILDING. APPROXIMATELY 20 MINUTES AFTER RELIGHTING APARTMENT B4 THE TENANT REPORTED A FIRE IN THE KITCHEN. THE SERVICE PERSON WHO COMPLETED THE RELIGHT WAS INTERVIEWED AND CONFIRMED THAT BEFORE LIGHTING THE OVEN , HE OPENED THE DOOR AND CHECKED FOR ANY UNSAFE CONDITIONS IN COMPLIANCE WITH NATIONAL GRID'S GAS WORK METHOD-RELIGHTING GAS APPLIANCES-DOCUMENT#CMS04001. THE FDNY REPORT IS AS FOLLOWS: "EXAMINATION SHOWED THAT THE FIRE ORIGINATED AT THE SUBJECT PREMISES, ON THE SECOND FLOOR, IN APARTMENT B4, IN THE KITCHEN AREA, WITHIN THE NATURAL GAS OVEN, IN COMBUSTIBLE MATERIAL (PLASTIC HOUSE WARE) FROM THE HEAT OF AN OPEN FLAME (NATURAL GAS BURNER). FIRE EXTENDED TO THE CONTENTS OF OVEN. FIRE FURTHER EXTENDED TO INTERIOR WEST KITCHEN WALL CABINETS AND CEILING AREA ABOVE VIA DIRECT FLAME IMPINGEMENT. FIRE WAS THEREFORE CONFINED AND EXTINGUISHED.
2025-03-31 10:13 | NO | NO | NO | 20130131 | 15773 | 2013-12-20 15:59 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2013-12-04 12:18 |  |  | 2013 | 6701 ALMEDA GENOA | HOUSTON | HARRIS | TX | 77007 | 29.621 | -95.3039 | [9 empty] | 2013-12-04 13:42 | 1067553 |  | NATURAL GAS |  | 72.69 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-12-04 12:18 |  |  |  | 2013-12-04 12:18 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 |  | YES |  |  | YES | CASED | [7 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2.375 | API5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 2 | 2 |  | CLASS 3 LOCATION | 0 | 0 | 344 | 429.603063930079672 | 1052 | 1313.786114111755276 | 2766 | 3454.308357065698758 | N/A |  | 479 | 419.125 |  | 0 | 4641 | 2540.445597009159023508196721311475409836 | 5616.822535107533706 | 0 | 0 | 0 |  |  |  |  | 44.8 | 44.8 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED THRESHOLDS OF SYSTEM | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 532167652 | LONE STAR 811 |  | CONTRACT LOCATOR | NO |  |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | LESLIE J. DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steven.yarbrough@centerpointenergy.com | SPAWGLASS CONSTRUCTION DAMAGED A 2" STEEL MAIN WITH TRACKHOE ALONG THE SOUTH SIDE OF ALMEDA GENOA JUST EAST OF MYKAWA AND THE RR TRACKS WHICH RESULTED IN THE CLOSURE OF THE RR TRACKS RUNNING NORTH AND SOUTH FOR APPROXIMATELY 3 AND 1/2 HOURS. TEMPORARY REPAIRS WERE MADE THAT EVENING AND PERMANANT REPAIRS WERE COMPLETED ON DECEMBER 11, 2013.
2025-03-31 10:13 | NO | YES | NO | 20130132 | 16404 | 2013-12-26 13:13 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2013-11-27 08:03 |  |  | 2013 | 2601 WESTCHESTER AVENUE | NEW YORK | BRONX | NY | 10461 | 40.8412 | -73.8414 | [9 empty] | 2013-11-27 08:15 | 1066967 |  |  |  | 0.15 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2013-11-27 08:03 |  |  |  | 2013-11-27 08:16 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1952 | [5 empty] | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 350000 | 437096.14062653455 | 17451 | 21793.613571639012663 | 3964 | 4950.426004124522732 | 0 | 0 |  |  | 2 | 1.75 |  | 0 | 371417 | 192110.3102989875797484426229508196721311 | 463841.930202298085395 | 2 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [9 empty] | YES |  |  |  | OTHER | CIRCUMFRENTIAL CRACK ON 6" CAST IRON MAIN | NO | [86 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | NICKOLAS HELLEN | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | hellenn@coned.com | ON WEDNESDAY NOVEMBER 27, 2013 AT 08:03 THE FIRE DEPARTMENT OF NEW YORK (FDNY) REPORTED TO THE GAS EMERGENCY RESPONSE CENTER (GERC) AN EXPLOSION AND BUILDING COLLAPSE WITH INJURIES AND GAS ODOR AT 2601 WESTCHESTER AVENUE. A CODE MURRE (MULTIPLE RESOURCE RESPONSE EVENT) WAS INITIATED AND GAS DISTRIBUTION SERVICES (GDS), NUMEROUS SUPERVISORS, CONSTRUCTION, PHOTOGRAPHER, CHEM LAB, EMERGENCY MANAGEMENT AND ELECTRIC #9 WERE DISPATCHED. AT 08:16 A CONSTRUCTION SUPERVISOR ARRIVED ON LOCATION, AND CONFIRMED THE COLLAPSE WITH SIGNIFICANT FDNY, NYPD, & EMS RESPONSE. THE FDNY WAS IN THE COLLAPSED BUILDING ATTEMPTING TO SECURE AN OPEN-ENDED GAS PIPE. GERC SUPPLIED THE CURB VALVE LOCATION FOR 1300 BLONDELL AVE, AS 2601 WESTCHESTER AVE HAD NO DIRECT GAS SERVICE. THE GAS SUPPLY PIPE TO A CEILING MOUNTED SPACE HEATER HAD BEEN DAMAGED BY FALLING DEBRIS RESULTING IN GAS FREELY BLOWING INTO THE ATMOSPHERE. AT 08:22 THE FDNY TEMPORARILY SECURED THE OPEN-ENDED HOUSE PIPE WITH TAPE. AT 08:24 THE CURB VALVE WAS CLOSED SECURING THE LEAK. AT 08:27 GDS VERIFIED A 100% SHUTDOWN FROM THE 1.25" LOW PRESSURE POLYETHYLENE CURB VALVE. AT 08:46 THE ELECTRIC SERVICE WAS DE-ENERGIZED TO THE BUILDING. CHANNEL 12 NEWS REPORTED THAT A ONE STORY AUTO BODY SHOP COLLAPSED DUE TO AN AIR COMPRESSOR EXPLOSION INSIDE THE BUILDING; ADDITIONAL REPORTS ON-SITE AND IN THE MEDIA STATED A GARAGE COMPRESSOR EXPLODED CAUSING THE BUILDING TO COLLAPSE. NO FIRE CONDITION WAS DETECTED PER FDNY CHIEF SAKOVICH. TWO OCCUPANTS, A FATHER AND SON (BENEDETTO MONDELLO - DOB-7/16/1950, BENJAMIN MONDELLO - DOB- 3/8/1978) WERE TAKEN BY EMS TO JACOBI HOSPITAL DUE TO INJURIES SUSTAINED IN THE EXPLOSION. FDNY CHIEF SEELIG INITIALLY REPORTED THE CAUSE OF THE EXPLOSION WAS UNDER INVESTIGATION. INITIAL LEAK INVESTIGATIONS DETECTED NO GAS ODOR OR READINGS IN THE BUILDINGS ACCESSED AS WELL AS IN SUBSURFACE STRUCTURES. A POGO SURVEY OF THE IMMEDIATE AREA BY GDS DETECTED NO OUTSIDE READINGS. LEAK SURVEY RESPONDED AND PERFORMED SEVERAL LEAK SURVEYS OF THE AREA SURROUNDING THE INCIDENT. THE INITIAL SURVEY AT 09:10 DETECTED NO READINGS BUT A SECOND SURVEY AT 09:50 DETECTED 4.4% AT THE OUTSIDE FOUNDATION WALL OF 1314 COOPER AVE. THE FDNY PROVIDED ACCESS AND 2% WAS DETECTED IN THE ELECTRIC POINT OF ENTRY AT THE INSIDE FOUNDATION WALL. 1320 COOPER AVE WAS CHECKED AND FOUND CLEAR, AND SB 24280 SUPPLYING #1314 WAS CHECKED AND 60% READING WAS RECEIVED. THE COVER WAS PULLED TO VENT THE STRUCTURE. SB 22786 WAS CHECKED AND 58% WAS DETECTED AND THE COVER PULLED TO VENT THE STRUCTURE; ADJACENT MANHOLES M10930 AND M23142 WERE FOUND CLEAR. A BAR HOLE SURVEY DETECTED 40%-90% GAS READINGS OVER THE 6" LPCI 1952 MAIN ON COOPER AVE. THE 6" MAIN WAS EXCAVATED AND CUT ON THE 6" SIDE OF THE 12" X 12" X 6" 3-WAY TEE ON WESTCHESTER AND COOPER AVES. AN INTEGRITY TEST OF THE HOUSE PIPING FROM THE 1/2" OPEN-ENDED PIPE BACK TO THE HOS VALVE WAS PERFORMED AT 6" W.C AND PASSED AFTER A 10 MINUTE TEST WHICH WAS WITNESSED BY THE PSC. LEAK SURVEILLANCE OF THE AREA DETECTED NO GAS READINGS AFTER THE MAIN WAS CUT AND CAPPED. ON MONDAY, DEC. 2 A CAMERA INSPECTION WITNESSED BY THE PSC OF THE ISOLATED SECTION OF MAIN IDENTIFIED A CIRCUMFERENTIAL CRACK WHICH WAS EXCAVATED, CONFIRMED AND REMOVED FOR ANALYSIS. CHEMICAL SAMPLING OF THE SOIL WITHIN THE IMMEDIATE VICINITY OF THE BUILDING COLLAPSE IDENTIFIED CHEMICALS INCLUDING ACETONE AND FUELS AT LEVELS THAT MET OR EXCEEDED NYC DEP AND/OR NYS DEC REPORTING THRESHOLDS AND NOTIFICATIONS WERE MADE TO THOSE AGENCIES. CHANNEL 2, 4 AND 12 NEWS MEDIA WERE ON LOCATION. CIG, PSC, DOT AND DEP WERE NOTIFIED. THERE WAS GREATER THAN $50,000 IN DAMAGE AND THE TWO INJURED OCCUPANTS REPORTEDLY SUSTAINED NON-LIFE THREATENING INJURIES. THE PSC AND OSHA RESPONDED TO THE LOCATION. THE FDNY FIRE MARSHALS ISSUED A REPORT CONCLUDING THAT THE INCIDENT WAS ATTRIBUTED TO NATURAL GAS.
2025-03-31 10:13 | NO | YES | NO | 20130133 | 16009 | 2013-12-27 15:32 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2013-11-30 16:52 |  |  | 2013 | 291 W CR 600 N | RUSHVILLE | RUSH | IN | 62681 | 39.6976 | -85.4463 | [9 empty] | 2013-11-30 20:07 | 1067185 |  | NATURAL GAS |  | 5160 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2013-11-30 16:52 |  |  |  | 2013-11-30 17:02 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 33 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1973 | [5 empty] | 10 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 7.5 | 1.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 7200 | 8991.6920357458536 | 61011 | 76193.350387901426943 | 0 | 0 |  |  | 23798 | 20823.25 |  | 0 | 92009 | 54543.8151672749407807704918032786885246 | 106008.292423647280543 | 0 | 0 | 6 |  |  |  |  | 148 | 148 | 150 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE EASEMENT | YES |  |  | YES | [6 empty] | CONTRACTOR | TRENCHER | DRAINAGE | YES | 1311191852 |  |  | CONTRACT LOCATOR | YES | YES | 44 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | MONTE MCMANIGELL | QUALITY ASSURANCE SPECIALIST | mmcmanigell@vectren.com | 812-348-6703 | 317-736-2943 |  |  |  | JOHN A. SPINKS | QUALITY ASSURANCE MANAGER | 937-440-1844 | jaspinks@vectren.com | AN EXCAVATOR INSTALLING FIELD DRAINAGE TILE DAMAGED A VECTREN 10 INCH, HIGH-PRESSURE DISTRIBUTION FACILITY LOCATED SOUTH OF W CR 600 N AND WEST OF STATE ROAD 3, NORTH OF RUSHVILLE INDIANA. VECTREN RESPONDED TO THE DAMAGED MAIN BY EXCAVATING AN EXISTING STOPPER FITTING ALONG THE WEST SIDE OF STATE ROAD 3, APPROXIMATE 1/2 MILE SOUTH OF CR 450 N AND INSTALLED A NEW STOPPER FITTING ON THE SOUTH SIDE OF W CR 600 N. STOPPERS WERE INSERTED INTO BOTH STOPPER FITTINGS TO DISCONTINUE THE FLOW OF NATURAL GAS AT THE INCIDENT SITE. THE SITE WAS INSPECTED AND CONFIRMED THAT THE FACILITY HAD BEEN ACCURATELY LOCATED. REMEDIAL ACTIONS INCLUDED INSTALLING 30 INCHES OF 10 INCH STEEL PIPE, REPLACING THE DAMAGED SECTION OF MAIN. AS A SUPPLEMENTARY MEASURE, FIVE ADDITIONAL FIELD TILE EXCAVATION CROSSINGS JUST SOUTH OF THE DAMAGE SITE WERE EXCAVATED AND INSPECTED FOR DAMAGE; NO DAMAGE HAD OCCURRED. ALL REPAIRS WERE COMPLETED ON 12/1/2013 AND SYSTEM ENERGIZED AT APPROXIMATE 4:30 P.M.
2025-03-31 10:13 | NO | NO | NO | 20140001 | 16011 | 2014-01-03 10:53 | SUPPLEMENTAL | 31292 | NORTHWEST GAS | 1608 NW 4TH STREET | GRAND RAPIDS | MN | 55744 | 2013-12-07 09:28 |  |  | 2013 | COUNTY RD 143 | Not Within a Municipality | CASS | MN | 56633 | 47.3316 | -94.6084 | [10 empty] | NRC NOTIFICATION NOT REQUIRED |  | NATURAL GAS |  | 280 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-12-07 11:07 |  |  |  | 2013-12-07 11:15 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1998 | [8 empty] | OTHER | REGULATOR FAILURE | [9 empty] | OTHER | [8 empty] | GAS WAS RELEASED THROUGH RELIEF VALVE | CLASS 1 LOCATION | 0 | 0 | 4000 | 4995.384464303252 | 1843 | 2301.623391927723359 | 0 | 0 |  |  | 1130 | 988.75 |  | 0 | 6973 | 3936.853446277386686081967213114754098361 | 8285.757856230975359 | 2 | 0 | 1 |  |  |  |  | 110 | 60 | 60 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | KIM WAGNER | OFFICE MANAGER | kim@nwgas.com | 2183263495 | 2189995495 |  |  |  | KIM WAGNER | OFFICE MANAGER | 2183263495 | kim@nwgas.com | INVESTIGATION OF THE INCIDENT OF DECEMBER 7, 2013 AT NORTHWEST GAS' CASS LAKE DISTRIBUTION SYSTEM TBS. AT AROUND 8:30 AM, A CASS LAKE SCHOOL SYSTEM EMPLOYEE NOTED GAS LEAKING FROM THE SERVICE RELIEF VALVE AT THE CASS LAKE HIGH SCHOOL. HE REPORTED THIS TO HIS SUPERVISOR, PETE RAIRDON (AT HOME AT THE TIME). MR. TOLD HIS EMPLOYEE THAT HE ( MR. RAIRDON) WAS ON HIS WAY TO HELP AND ALSO INSTRUCTED HIS EMPLOYEE TO CALL THE CASS LAKE FIRE DEPARTMENT IN CASE THE PROBLEM WAS MORE THAN THE TWO OF THEM COULD HANDLE. AT 9:12 AM JACK PALKKI (NW GAS ON-CALL TECHNICIAN) RECEIVED A CALL FROM THE CASS COUNTY SHERIFF'S DEPARTMENT DISPATCHER THAT THE CASS LAKE FIRE DEPARTMENT WAS ON-SITE AT THE CASS LAKE HIGH SCHOOL AND THAT THERE WAS AN OUTDOOR GAS LEAK REPORTED. JACK ASKED FOR AN ON-SITE CONTACT NUMBER WHICH HE WAS GIVEN AND WHEN HE MADE CONTACT WITH THE ON-SITE PERSONNEL LEARNED THAT THE GAS WAS NOW OFF AND THE SITUATION AT THE SCHOOL WAS SAFE. JACK THEN CALLED JOE ROY (NW GAS AREA SUPERVISOR) TO CONFER ABOUT WHAT WOULD LIKELY BE NEEDED TO RETURN THE SCHOOL SERVICE TO OPERATION. AT THIS POINT THE SUSPICION WAS A FAILED SERVICE REGULATOR AND THE DISCUSSION REFLECTED THAT. A SECOND CALL FROM THE SHERIFF'S DISPATCHER REPORTING GAS LEAKING FROM THE SERVICE RELIEF VALVE AT THE CASINO PROMPTED JACK AND JOE TO SUSPECT A LARGER PROBLEM AND TO GET JACK GOING IMMEDIATELY TO CASS LAKE. THE GAS WAS REPORTED SHUT OFF AT THE CASINO WHICH TERMINATED THE LEAK THERE AS WELL. AT THIS POINT, JOE RECEIVED A CALL FROM GARY LINDSTROM, THE CASS LAKE AREA GREAT LAKES GAS TRANSMISSION COMPANY FIELD TECHNICIAN, THAT A NEIGHBOR TO THE TBS LOCATION HAD REPORTED A HISSING SOUND AND THAT MR. LINDSTROM WAS ENROUTE (1/2 HOUR TRAVEL). JOE GAVE MR. LINDSTROM JACK'S CELL NUMBER SO THAT THE TWO FIELD TECHS COULD COMMUNICATE. JACK RECEIVED A CALL AT 11:07 FROM MR. LINDSTROM, WHO HAD JUST ARRIVED AT THE CASS LAKE TBS SITE, REPORTING THAT THERE WAS INDEED GAS ESCAPING FROM OUR SYSTEM'S TATTLE-TALE RELIEF VALVE AND THAT THE ESCAPING GAS HAD IGNITED. JACK INSTRUCTED MR. LINDSTROM TO CALL THE CASS LAKE FIRE DEPARTMENT, WHICH MR. LINDSTROM DID. AT THIS POINT, JACK WAS VERY CLOSE TO THE SITE AND ARRIVED BEFORE THE FIRE DEPARTMENT DID. THE FIRE DEPARTMENT ALSO REPORTED THAT THEY HAD TURNED OFF A THIRD SERVICE (AT MAUREEN MOOSE'S RESIDENCE) DUE TO GAS LEAKAGE FROM THE REGULATOR RELIEF OPENING. ALTHOUGH THERE WERE NO ACCESSIBLE PRESSURE GAUGES PRESENT WHICH COULD BE USED TO VERIFY THE DISTRIBUTION PIPELINE PRESSURE, JACK DETERMINED THAT IT WOULD BE BEST TO REDUCE THE PRESSURE IN OUR PIPELINE, SO HE TURNED OFF A GREAT LAKES VALVE TO ACCOMPLISH THIS. AT THIS POINT JOE ROY CALLED MIKE GORHAM, OWNER OF THE SYSTEM TO ADVISE HIM OF THE EVENTS GOING ON AND THAT JOE WAS ENROUTE TO CASS LAKE. JOE ALSO CALLED STEVE MCNIFF (ANOTHER NW GAS FIELD TECH) TO GET HIM MOVING TO CASS LAKE. MIKE PROCEEDED TO ACT AS THE INCIDENT RESPONSE LEADER COORDINATING THE RESPONSE FROM THAT POINT. WITH THE GAS TURNED OFF AT THE GREAT LAKES END AND THE PRESSURE IN THE PIPELINE FALLING, MIKE ASKED JACK TO ARRANGE FOR A FIREMAN IN TURNOUT GEAR TO APPROACH THE STILL-DISCHARGING RELIEF VALVE AND TURN IT OFF IF THAT OPERATION COULD BE SAFELY ACCOMPLISHED IN TURNOUT GEAR. THE FIREMAN AGREED AND THE GAS WAS SHUT OFF, WHICH EXTINGUISHED ALMOST ALL OF THE FIRE, THE ONLY REMNANT BEING GAS ESCAPING FROM THE SECOND-STAGE REGULATOR PILOT ON THE WEST REGULATOR RUN, WHICH WAS THEN ISOLATED USING THE INSTALLED ISOLATION VALVES. THIS ELIMINATION OF THE FIRE HAZARD ALLOWED FOR THE INSERTION OF A PRESSURE GAUGE IN THE DISTRIBUTION PIPELINE. THE INITIAL READING OF THIS GAUGE WAS JUST UNDER 110 PSIG. AT THIS POINT, MIKE DIRECTED JOE TO STOP FIRST AT THE REPORTED GAS-OFF SITES TO RESTORE SERVICE. SERVICE WAS SUCCESSFULLY RESTORED. THE FIRE DEPARTMENT WAS RELEASED FROM ALL OF THE RESPONSE SITES. THE NW GAS RESPONSE NOW TURNED TO PRESE
2025-03-31 10:13 | NO | NO | NO | 20140002 | 15880 | 2014-01-10 11:05 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2013-12-10 08:00 |  |  | 2013 | 4268 WELLINGTON HILLS LN | SNELLVILLE | GWINNETT | GA | 30039 | 33.8325 | -84.0739 | [9 empty] | 2013-12-10 09:40 | 1068048 |  | NATURAL GAS |  | 204 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2013-12-10 08:08 |  |  |  | 2013-12-10 08:23 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1976 | [5 empty] | 0.625 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 2406 | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 90000 | 112396.15044682317 | 500 | 624.4230580379065 | 1000 | 1248.846116075813 | 0 | 0 |  |  | 1050 | 918.75 |  | 0 | 92550 | 48176.8640537990920573770491803278688525 | 115188.1696209368895 | 0 | 0 | 1 |  |  |  |  | 58 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@aglresources.com | (404) 584-3733 | (404) 584-4807 |  |  |  | RICHARD R. LONN | DIRECTOR COMPLIANCE ASSURANCE | (404) 584-3552 | rlonn@aglresources.com | INITIAL FINDINGS AS INDICATED BY THE HOMEOWNER WERE THAT A LIGHTNING STRIKE OCCURRED IN THE VICINITY OF THE RESIDENCE SOMETIME BEFORE THE INCIDENT OCCURRED. UPON EXCAVATING AND TESTING THE SERVICE, A SMALL HOLE WAS FOUND IN THE PLASTIC SERVICE PIPE WHERE A LAB ANALYSIS DETERMINED THE HOLE TO BE CONSISTENT WITH THAT CAUSED BY A LIGHTNING STRIKE.
2025-03-31 10:13 | NO | YES | YES | 20140003 | 15788 | 2014-01-16 07:58 | ORIGINAL | 180 | ALABAMA GAS CORPORATION | 605 RICHARD ARRINGTON JR BLVD N | BIRMINGHAM | AL | 35203 | 2013-12-17 02:29 |  |  | 2013 | 7546 64TH COURTWAY SOUTH | BIRMINGHAM | JEFFERSON | AL | 35212 | 33.5415 | -86.7238 | [9 empty] | 2013-12-17 06:34 | 1068726 |  | NATURAL GAS |  | 147.2 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES |  | 2013-12-17 02:40 |  |  |  | 2013-12-17 03:23 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1951 | [5 empty] | 2.25 | UNKNOWN |  | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 500000 | 624423.0580379065 | 4800 | 5994.4613571639024 | 550 | 686.86536384169715 | 0 | 0 |  |  | 1760 | 1540 |  | 0 | 507110 | 262809.0986584842141795081967213114754098 | 632644.38475891209955 | 0 | 0 | 2 |  |  |  |  | 19 | 19 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF GAS INVOLVED WAS NOT SIGNIFICANT ENOUGH TO DETECT BY SCADA. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | RANDY WILSON | MANAGER - REGULATORY COMPLIANCE | randy.wilson@energen.com | 205-326-2987 | 205-326-8483 |  |  |  | ROBERT N. GARDNER | DIRECTOR - QUALITY ASSURANCE AND COMPLIANCE | 205-326-2584 | bob.gardner@energen.com | THE TWO-UNIT APARTMENT BUILDING EXPERIENCED EXTENSIVE DAMAGE DUE TO AN EXPLOSION AT THE NOTED ADDRESS. THE CAUSE IS UNDER INVESTIGATION. THE EVENT WAS DETERMINED TO MEET THE REQUIREMENTS OF A REPORTABLE INCIDENT AT APPROXIMATELY 06:30 AM.
2025-03-31 10:13 | NO | YES | YES | 20140004 | 16203 | 2014-01-20 17:55 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2013-12-21 17:01 |  |  | 2013 | 7916 HARWOOD RD | NORTH RICHLAND HILLS | TARRANT | TX | 76180 | 32.8423 | -97.21 | [9 empty] | 2013-12-21 18:22 | 1069197 |  | NATURAL GAS |  | 33 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO |  |  |  |  | NO | 10 | 2013-12-21 17:01 |  |  |  | 2013-12-21 17:15 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 44 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1972 | [5 empty] | 6 | 2306 | NIPAK | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | LEAK |  |  | OTHER | FUSION DEFECT | [5 empty] | CLASS 3 LOCATION | 103000 | 128631.149955808739 | 25000 | 31221.152901895325 | 15000 | 18732.691741137195 | 0 | 0 |  |  | 194 | 169.75 |  | 0 | 143194 | 74121.5774462580811639344262295081967213 | 178754.744598841259 | 1 | 0 | 3 |  |  |  |  | 38 | 38 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM WAS OPERATING PROPERLY | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 1972 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [7 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | YES | 2013 | 125 | [84 empty] | JESUS OQUENDO | OPERATIONS SUPERVISOR | jesus.oquendo@atmosenergy.com | 817-359-1303 | 817-359-1301 |  |  |  | MARC CHAPMAN | COMPLIANCE DIRECTOR | 214-206-2875 | marcus.chapman@atmosenergy.com | A LEAK OCCURRED ON THE GAS MAIN, WITH THE INCIDENT CAUSED BY GAS MIGRATING THROUGH SEWER LINES AND INTO A RESIDENCE BY WAY OF AN IMPROPERLY INSTALLED COMMODE.
2025-03-31 10:13 | NO | YES | NO | 20140005 | 30883 | 2014-01-24 14:30 | SUPPLEMENTAL FINAL | 2652 | NSTAR GAS COMPANY | 157 CORDAVILLE ROAD | SOUTHBOROUGH | MA | 01772 | 2013-12-27 13:00 |  |  | 2013 | 15 COLONIAL DR | SHREWSBURY | WORCESTER | MA | 01545 | 42.3256 | -71.7167 | [9 empty] | 2013-12-27 15:36 | 1069557 |  | NATURAL GAS |  | 550 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2013-12-27 13:00 |  |  |  | 2013-12-27 13:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1982 | [5 empty] | 4 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | 2000 | 2497.692232151626 | 90000 | 112396.15044682317 | 25000 | 31221.152901895325 | 0 | 0 |  |  | 6490 | 5678.75 |  | 0 | 123490 | 65769.6252131083257213114754098360655738 | 151793.745580870121 | 0 | 0 | 135 |  |  |  |  | 53 | 53 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS DUE TO FIELD PERSONNEL ACTIONS. CONTROL ROOM HAD NOTHING TO DO WITH WHAT OCCURRED. | [12 empty] | YES | 5 | 0 | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  |  | YES | SQUEEZE-OFF TOOL NOT INSTALLED CORRECTLY/COMPLETELY, SQUEEZE NOT VERIFIED | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ROBERT BUFFONE | MANAGER GAS ENGINEERING | robert.buffone@eversource.com | 5083057036 | 5083056918 |  |  |  | ROBERT BUFFONE | MANAGER GAS ENGINEERING | 5083057036 | robert.buffone@eversource.com | ON FRIDAY, DECEMBER 27, 2013 AT 1:00 PM NSTAR GAS HAD AN IGNITION AND FIRE IN AN EXCAVATION AT 15 COLONIAL DR. IN SHREWSBURY WHILE PERFORMING A MAIN CUT OUT. THE CREW WAS CUTTING OUT A SECTION OF 4 INCH IP PLASTIC MAIN THAT WAS LEAKING. THE CREW HAD INSTALLED A 2 INCH PLASTIC BYPASS AROUND THE LEAK AND HAD SQUEEZED OFF THE 4 INCH MAIN TO STOP OFF THE GAS. WHILE PREPARING FOR THE MAIN CUT OUT OF 4 INCH PLASTIC, A SUDDEN RUSH OF GAS OCCURRED AND THEN THE GAS IGNITED CAUSING A FIRE TO OCCUR IN THE EXCAVATION. THERE WERE 2 EMPLOYEES IN THE EXCAVATION WHO WERE ABLE TO GET THEMSELVES OUT OF THE HOLE JUST BEFORE THE IGNITION OCCURRED. ONE OF THESE EMPLOYEES DID RECEIVE SOME BURNS AND WAS TREATED AND RELEASED FROM A HOSPITAL. THE RESULTING FIRE ALSO SPREAD TO AN NSTAR BACKHOE PARKED AT THE EXCAVATION. THE SHREWSBURY FIRE DEPARTMENT WAS CALLED TO CONTROL THE GAS FIRE. AT 1:50 PM A MAIN VALVE ON COLONIAL DR. WAS SHUT TO STOP THE LEAKING GAS AND PUT OUT THE FIRE. THIS RESULTED IN AN OUTAGE TO 135 CUSTOMERS. NSTAR HAD TO REPLACE ABOUT 20 FEET OF 4 INCH PLASTIC MAIN DUE TO FIRE DAMAGE. AFTER THE SHUTDOWN PROCEDURE WAS COMPLETED FOR ALL CUSTOMERS, THE GAS MAINS WERE PURGED AND THE GAS WAS TURNED BACK ON AT 8:15 PM. THE FIRST CUSTOMER WAS RE-LIT AT 8:30 PM AND A FIRST PASS TO RE-LITE ALL 135 CUSTOMERS WAS COMPLETED AT 11:45 PM. NSTAR IS IN THE PROCESS OF DETERMINING WAS CAUSED THE SUDDEN LEAKAGE OF GAS AND ALSO WHAT CAUSED THE IGNITION TO OCCUR. SUPPLEMENTAL RESPONSE - UPON INVESTIGATION, IT WAS FOUND THAT A COMPLETE SQUEEZE WAS NOT ACHIEVED WITH A MUSTANG SQUEEZE TOOL USED ON THE DOWNSTREAM SIDE OF THE REPAIR. THIS RESULTED IN LIVE GAS IN WHAT WAS THOUGHT TO BE AN ISOLATED SECTION OF MAIN. THIS WAS NOT RECOGNIZED BY THE CREW, WHO THEN BEGAN TO REMOVE A STEEL FULL ENCIRCLEMENT CLAMP THAT HAD BEEN INSTALLED 3 DAYS PRIOR AS A TEMPORARY REPAIR, WHICH LED TO A RELEASE OF GAS. IT WAS DETERMINED THAT STATIC ELECTRICITY IGNITED THIS GAS. OM PROCEDURES WERE FOLLOWED FOR THE REPAIR AND HAVE SINCE BEEN REVISED TO INCLUDE ADDED SAFETY MEASURES.
2025-03-31 10:13 | NO | NO | NO | 20140006 | 15821 | 2014-01-29 16:47 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2013-12-30 15:30 |  |  | 2013 | 4565 KIPLING STREET | WHEATRIDGE | JEFFERSON | CO | 80033 | 39.7797 | -105.11 | [9 empty] | 2014-01-02 16:52 | 1069977 |  | NATURAL GAS |  | 3700 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 10 | 2013-12-30 15:30 |  |  |  | 2013-12-30 15:51 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1961 | [5 empty] | 10 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 5 | 5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 17058 | 21302.817048021218154 | 0 | 0 | 0 | 0 |  |  | 15984 | 13986 |  | 0 | 33042 | 21760.8567735038967394426229508196721311 | 35288.817048021218154 | 0 | 0 | 0 |  |  |  |  | 5 | 4 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | NO | 334500275 |  |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | CHANCE HUTSON | INVESTIGATOR | ryan.c.hutson@xcelenergy.com | 303-294-2076 | 303-294-2311 |  |  |  | JOHN KARTUS | MANAGER CLAIMS SERVICES SOUTH | 303-294-2665 | john.j.kartus@xcelenergy.com | ON DECEMBER 30, 2013 A THIRD PARTY CONTRACTOR BORED INTO 10" DISTRIBUTION MAIN. THERE WERE NO INJURIES OR FATALITIES, AND OUR ORIGINAL ESTIMATES OF PROPERTY DAMAGE AND LOSS GAS VOLUME DID NOT MEET THE REPORTABLE THRESHOLD. HOWEVER, ON JANUARY 2, 2014 LOSS OF GAS CALCULATIONS WERE REVISED TO INCLUDE A LARGER HOLE AND LONGER DURATION. THE NEW CALCULATIONS REVEALED THAT THE REPORTABLE CRITERIA FOR LOSS OF GAS HAD BEEN MET. SUPPLEMENTAL/FINAL HAS THE SAME INFORMATION AS THE ORIGINAL.
2025-03-31 10:13 | NO | NO | NO | 20140007 | 16226 | 2014-01-31 15:50 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2014-01-03 04:12 |  |  | 2014 | 12334 GEDDES ROAD | HEMLOCK | SAGINAW | MI | 48626-9409 | 43.4349 | -84.1637 | [9 empty] | 2014-01-06 10:30 | 1070175 |  | NATURAL GAS |  | 3375 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 30 | 2014-01-03 04:12 |  |  |  | 2014-01-03 05:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1999 | [8 empty] | OTHER | MIXED MATERIAL PILOT REGULATOR. | [9 empty] | OTHER | [8 empty] | METER STAND RELIEF VALVE BLEW DUE TO FROZEN PILOT REGULATOR. | CLASS 2 LOCATION | 0 | 0 | 0 | 0 | 509 | 623.59855491329468 | 200 | 245.028901734104 | HEATER INSTALLED ON PRIMARY REGULATOR & PILOT; CONTROL LINES WRAPPED/INSULATED |  | 16065 | 12013.5814360770577933450087565674255692 |  | 0 | 16774 | 11473.0256408828780509772329246935201401 | 12882.2088927244564733450087565674255692 | 0 | 0 | 0 |  |  |  |  | 86 | 60 | 125 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 571-788-0509 |  |  |  |  | AMANDA L. WARD | GAS REGULATORY SERVICES LEAD | 517-545-8746 | amanda.ward@cmsenergy | ON JANUARY 3, 2014, THE PILOT REGULATOR ON THE PRIMARY RUN OF THE WEST METER INSTALLATION AT HEMLOCK SEMICONDUCTOR ICED UP, CAUSING THE FIRST CUT REGULATOR TO OPERATE WIDE OPEN. AS A RESULT, THE FIRST CUT RELIEF VALVE (NOMINAL SIZE = 6") ACTUATED AND VENTED GAS TO THE ATMOSPHERE THROUGH THE RELIEF STACK. THE RELIEF VALVE BLEW FOR APPROXIMATELY THREE HOURS, VENTING 3.375 MMCF (MILLION CUBIC FEET) IN THE PROCESS. FIRE DEPARTMENT PERSONNEL BLOCKED OFF A ONE-MILE SECTION OF GEDDES ROAD ADJACENT TO THE FACILITY, AND SEVERAL EMPLOYEES WERE MOVED TO ANOTHER BUILDING ON THE SITE AS A RESULT OF THE INCIDENT. MEDIA WAS ON SITE REPORTING THE INCIDENT. UPON RESPONDING, THE PILOT REGULATOR WAS THAWED AND THE FIRST CUT PRIMARY REGULATION AT THE METER INSTALLATION WAS RETURNED TO NORMAL OPERATING CONDITIONS. AS A REMEDIAL MEASURE, A HEATER WAS INSTALLED ON THE PRIMARY RUN REGULATOR & PILOT, AND CONTROL LINES WERE HEAT-WRAPPED AND INSULATED TO HELP PREVENT RE-OCCURRENCE. INCIDENT NOTIFICATION TO THE NRC WAS DELAYED BECAUSE THE RELEASE VOLUME WAS INITIALLY ESTIMATED TO BE LESS THAN 1MMCF AND THEREFORE WOULD NOT MEET THE CRITERIA FOR A FEDERALLY REPORTABLE INCIDENT. SUBSEQUENT INCIDENT INVESTIGATION AND GAS LOSS CALCULATIONS PERFORMED CONFIRMED A GAS LOSS VOLUME OF APPROXIMATELY 3.375 MMCF THEREBY MAKING THE INCIDENT REPORTABLE AND NOTIFICATION TO BOTH THE NRC AND PEAS WERE REQUIRED.
2025-03-31 10:13 | NO | NO | NO | 20140009 | 15802 | 2014-02-13 13:01 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2014-01-14 15:22 |  |  | 2014 | 307 S. RAMONA ST | HEMET | RIVERSIDE | CA | 92543 | 33.744 | -116.975 | [9 empty] | 2014-01-14 17:14 | 1071164 |  | NATURAL GAS |  | 14 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 6 | 2014-01-14 15:22 |  |  |  | 2014-01-14 15:38 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 19 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1947 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 50000 | 61257.225433526 | 2000 | 2450.28901734104 | 200 | 245.028901734104 | 0 | 0 |  |  | 84 | 62.81611208406304728546409807355516637478 |  | 0 | 52284 | 26545.3340149620954577933450087565674256 | 64015.3594646852070472854640980735551664 | 0 | 0 | 2 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | tbauer@semprautilities.com | 909-376-7208 |  |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | ON JANUARY 14TH, 2014, SOCALGAS RESPONDED TO A GAS FIRE AT A RESIDENCE REPORTED BY HEMET FIRE DEPARTMENT. UPON ARRIVAL THE FD WAS MONITORING AND CONTROLLING THE FIRE BURNING IN THE YARD NEAR THE SIDE WALK WHERE THE SERVICE WAS LOCATED AND HAD EXTINGUISHED THE FIRE TO THE HOUSE. SOCALGAS EXCAVATED AND PINCHED THE SERVICE TO STOP THE GAS FLOW. A SO CAL EDISON CREW WORKING NEAR THE RESIDENCE REPORTED THAT HIGH WINDS HAD CAUSED TWO POWER LINES TO COME IN CONTACT WITH ONE ANOTHER. THE EDISON CREW SAID THIS CAUSED THE NEARBY TRANSFORMER TO BLOW CAUSING 12,000 VOLTS TO GO TO GROUND. THE CUSTOMER OF THE INVOLVED RESIDENCE REPORTED THERE WAS A LOUD NOISE (PRESUMABLY THE TRANSFORMER) AND THE LIGHTS INSIDE THE HOME FLASHED OFF AND ON BEFORE FINALLY REMAINING OFF. A NEXT DOOR NEIGHBOR KNOCKED ON THEIR DOOR AND ADVISED THAT THEIR HOUSE WAS ON FIRE AND TO GET OUT. THERE WERE NO INJURIES OR FATALITIES. AFTER EXCAVATING THE RESIDENCE'S SERVICE LINE, A 1/2" DIAMETER HOLE WAS FOUND IN THE BOTTOM OF THE 3/4" STEEL SERVICE LINE NEAR THE AREA WHERE THE FIRE HAD BEEN LOCATED. THE SERVICE LINE WAS 1/4" ABOVE A CAST IRON SEWER LINE AND THE ELECTRICITY LIKELY ARCED BETWEEN THESE TWO LINES CAUSING THE DAMAGE. A CROSS-SECTION OF THE SERVICE LINE SHOWED THE STEEL WAS IN EXCELLENT CONDITION. SERVICE HAS NOT BEEN RESTORED TO THIS ADDRESS AS THE HOME OWNER IS MAKING REPAIRS FROM THE FIRE DAMAGE. SERVICE WILL BE RESTORED ONCE REQUESTED. IN ADDITION TO THIS LOCATION, THE SURROUNDING AREA WAS LEAK SURVEYED ON JAN 14TH, TO ENSURE NO ADDITIONAL DAMAGE HAD OCCURRED AS A RESULT OF THIS ELECTRICAL INCIDENT. A MINOR LEAK WAS DETECTED ON A 3/4" STEEL SERVICE IN THE PARKWAY OF 407 ACACIA AVE IMMEDIATELY ACROSS THE STREET FROM THE DAMAGED TRANSFORMER. HOWEVER, IT IS NOT RELATED TO THIS ELECTRICAL INCIDENT AND WAS REPAIRED BY MEANS OF A CLAMP JAN 15TH. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO THE ESTIMATED DAMAGE COST ESTIMATED AT OVER $50,000.
2025-03-31 10:13 | NO | NO | NO | 20140010 | 16088 | 2014-02-17 14:38 | SUPPLEMENTAL FINAL | 32363 | MID-CONTINENT MARKET CENTER | 100 WEST FIFTH STREET | TULSA | OK | 74103-4298 | 2014-01-24 00:30 |  |  | 2014 | 6401 SOUTH OLIVER | WICHITA | SEDGWICK | KS | 67217 | 37.5768 | -97.2813 | [9 empty] | 2014-01-24 12:30 | 1072004 |  | NATURAL GAS |  | 115 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 5 | 2014-01-24 01:03 |  |  |  | 2014-01-24 01:58 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | FARM TAP METER/REGULATOR SET |  | 1961 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | DAMAGED VALVE | [5 empty] | CLASS 3 LOCATION | 16350 | 20031.112716763002 | 2625 | 3216.004335260115 | 1025 | 1255.773121387283 | 0 | 0 |  |  | 500 | 373.905429071803852889667250437828371278 |  | 0 | 20500 | 10494.246648377422486865148861646234676 | 24876.7956024822038528896672504378283713 | 0 | 0 | 4 |  |  |  |  | 575 | 580 | 721 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | LDC EMERGENCY CALL CENTER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A SMALL VOLUME RELEASE DID NOT TRIGGER A LOW PRESSURE ALARM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | KAREN PEREZ | REGULATORY COMPLIANCE COORDINATOR | karen.perez@oneok.com | 918-595-1703 | 918-588-7777 |  |  |  | KEVIN BROWN | MANAGER OPERATIONS | 620-672-9425 | kevin.brown@oneok.com | ON 1/24/14 AT 01:03 MCMC RECEIVED NOTIFICATION FROM KANSAS GAS SERVICE (KGS) OF A VEHICLE ACCIDENT INVOLVING A KGS REGULATOR STATION; AN MCMC TECHNICIAN WAS DISPATCHED TO THE SCENE. KGS REGULATOR & MCMC FARM TAP WERE DESTROYED BY A VEHICLE AND SAID VEHICLE WAS ON FIRE. A SECOND MCMC TECHNICIAN WAS DISPATCHED TO THE SCENE. TECHNICIAN(S) REPORTED THAT THE FIRE HAD BEEN EXTINGUISHED, THE VEHICLE HAD BEEN MOVED AWAY FROM THE REGULATOR STATION AND GAS WAS LEAKING. TWO MORE MCMC PERSONNEL WERE DISPATCHED TO THE SCENE. ONE ADDITIONAL MCMC EMPLOYEE WAS DISPATCHED TO THE SCENE ALONG WITH THIRD PARTY CONTRACTOR. MCMC PERSONNEL PARTIALLY CLOSED FIRST ABOVE-GROUND BLOCK VALVE, NOTIFICATION WAS MADE TO LARGE END USE CUSTOMER OF POSSIBLE SHUT DOWN OF PIPELINE. AFTER SECOND ATTEMPT THE FLOW OF GAS WAS STOPPED. DAMAGE WAS ASSESSED, REPAIRS WERE COMPLETED AND LINE WAS PUT BACK IN SERVICE AT 07:30.UPDATE 04/30/2015 PART A 12. CHANGE TO NO; UNABLE TO DETERMINE IF DRIVER'S INJURIES RESULTED IN HOSPITALIZATION AND THE GAS RELEASE DID NOT CAUSE HIS INJURIES.
2025-03-31 10:13 | NO | NO | NO | 20140011 | 15805 | 2014-02-19 07:54 | ORIGINAL FINAL | 11856 | COLONIAL GAS CO - LOWELL DIV | 40 SYLVAN RD | WALTHAM | MA | 02451 | 2014-01-15 11:15 |  |  | 2014 | 271 LITTLETON ROAD | WESTFORD | MIDDLESEX | MA | 01886 | 42.4843 | -71.2768 | [9 empty] | 2014-01-17 16:15 | 107459 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-01-15 13:08 |  |  |  | 2014-01-15 13:34 |  | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | LNG STORAGE SATELLITE FACILITY |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | LNG SATELLITE VAPORIZER | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | NO RELEASE OF GAS INVOLVED IN THIS EVENT. | CLASS 2 LOCATION | 0 | 0 | 0 | 0 | 10000 | 12251.4450867052 | 0 | 0 |  |  | 0 | 0 |  | 0 | 10000 | 5074.18111753372 | 12251.4450867052 | 0 | 0 | 0 |  |  |  |  | 56.52 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DEVICES TO MONITOR GAS QUALITY HAVE NEVER BEEN INSTALLED AT THE WESTFORD LNG SATELLITE FACILITY. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | HIGH BTU GAS SENT INTO THE LOCAL DISTRIBUTION SYSTEM. | [47 empty] | KATHLEEN A MCNAMARA | MANAGER NE DISPATCH | kathleen.mcnamara@nationalgrid.com | 508-421-7450 | 508-357-4735 |  |  |  | GARY BENNETT | DIRECTOR DISPATCH | 617-839-7208 | gary.bennett@nationalgrid.com | THE WESTFORD LNG TANK IS IN THE PROCESS OF BEING DECOMMISSIONED. INVENTORY WAS REMOVED ON DECEMBER 12TH 2013 BUT A SMALL AMOUNT OF LNG REMAINED. ON JANUARY 15TH 2014, PLANT PERSONNEL STARTED THE PLANT VAPORIZATION SYSTEM FOR A BRIEF PERIOD WITH THE INTENT OF SENDING THE RESIDUAL AMOUNT INTO THE LOCAL DISTRIBUTION SYSTEM. THE HEATING VALUE OF THE VAPOR WAS HIGHER THAN ANTICIPATED AND CAUSED LARGER THAN NORMAL FLAMES FOR CUSTOMER APPLIANCES IN THE AREA NEAR THE PLANT AND GENERATED A NUMBER OF CALLS TO THE COMPANY CALL CENTER. THE MASSACHUSETTS DEPARTMENT OF PUBLIC UTILITIES WAS NOTIFIED.
2025-03-31 10:13 | NO | YES | NO | 20140012 | 15956 | 2014-02-26 13:00 | SUPPLEMENTAL | 22777 | WISCONSIN ELECTRIC POWER COMPANY DBA WE ENERGIES | 231 W. MICHIGAN STREET | MILWAUKEE | WI | 53203 | 2014-01-30 11:18 |  |  | 2014 | 2800 LAKESHORE WAY | TWIN LAKES | KENOSHA | WI | 53181-9728 | 42.4995 | -88.2744 | [9 empty] | 2014-01-30 16:00 | 1072543 |  | NATURAL GAS |  | 6.48 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2014-01-30 11:47 |  |  |  | 2014-01-30 12:34 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 |  | NO | [11 empty] | OTHER | INVESTOR OWNED UTILITY | MAIN |  | 1958 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 2 | 0.1 |  | CLASS 3 LOCATION | 125000 | 153143.063583815 | 6600 | 8085.953757225432 | 9400 | 11516.358381502888 | 0 | 0 |  |  | 50 | 37.39054290718038528896672504378283712785 |  | 0 | 141050 | 71580.5421985564502486865148861646234676 | 172782.7662654505003852889667250437828371 | 0 | 0 | 2 |  |  |  |  | 53 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2013-05-21 | NO | [12 empty] | NO | YES | CITY STREET | [12 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 361 | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | MARK KEEHAN | SENIOR ENGINEER | mark.keehan@we-energies.com | 414-221-5359 |  |  |  |  | TIM STROMMEN | MANAGER REGULATORY COMPLIANCE | 414-221-5173 | tim.strommen@we-energies.com | ON THURSDAY, JANUARY 30, 2014, AT ABOUT 11:11 A.M., THE VILLAGE OF TWIN LAKES (TWIN LAKES) POLICE DEPARTMENT CALLED THE WE ENERGIES (COMPANY) FIRE AND POLICE LINE TO PROVIDE NOTIFICATION OF A HOUSE FIRE AT 2800 LAKESHORE WAY IN TWIN LAKES. THE CALLER STATED THE FIRE WAS CONTAINED AND THAT THERE WAS ALSO GAS BURNING. WE ENERGIES IMMEDIATELY DISPATCHED A FIRST RESPONDER TO THE SITE. THE FIRST RESPONDER ARRIVED ON SITE AT 11:47 A.M. AND OBSERVED A STRUCTURE FIRE; BUT THERE WERE NO SIGNS OF AN EXPLOSION. THE EMPLOYEE NOTED THAT THE STRUCTURE FIRE WAS ESSENTIALLY UNDER CONTROL BUT NATURAL GAS WAS BURNING AT THE OUTSIDE METER AND AT A FEW LOCATIONS ON THE GROUND NEAR THE BUILDING. THE FIRST RESPONDER SAW THAT MORE RESOURCES WERE NEEDED TO REMOTELY SHUT OFF THE GAS AND MADE THE REQUEST TO THE DISPATCHER. THE FIRST RESPONDER AND ANOTHER EMPLOYEE WHO HAD ARRIVED PROCEEDED TO CHECK FOR GAS MIGRATION AND WORK WITH FIRE DEPARTMENT PERSONNEL TO KEEP A SAFE PERIMETER. INITIAL PROBING AND RECHECKS VERIFIED THAT GAS WAS ONLY IN THE AREA OF THE STRUCTURE FIRE. AT ABOUT 12:52 P.M., MORE PERSONNEL ARRIVED AND BEGAN DIGGING TO REMOTELY SQUEEZE OFF GAS ON THIS ONE-WAY FEED TO 2800 LAKESHORE WAY AND THE PROPERTY TO THE NORTH. A FROST DEPTH OF ABOUT 3 FT. MADE EXCAVATION HARD, AND THE 1958-INSTALLED 1 1/4 IN. STEEL GAS MAIN TO THE PROPERTIES WAS SQUEEZED OFF AT ABOUT 3:09 P.M. ALL FIRE AT THE PROPERTY WAS EXTINGUISHED SHORTLY THEREAFTER. TO CONFIRM THE UNOCCUPIED HOME TO THE NORTH WAS SAFE, ACCESS WAS GAINED WITH POLICE ASSISTANCE AT ABOUT 1:30 P.M. AND ALL THREE LEVELS CHECKED AT 0%. DUE TO THE EXTENT OF DAMAGE POTENTIALLY CAUSED BY GAS LEAKAGE FROM OPERATOR FACILITIES, A PHONE NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER AT ABOUT 4:00 P.M. TO REPORT THIS EVENT AS A POSSIBLE INCIDENT PER 49 CFR PART 191.3. THE WISCONSIN PUBLIC SERVICE COMMISSION (WPSC) WAS ALSO NOTIFIED. A LINE STOPPER WAS INSTALLED AND SERVICE WAS RESTORED TO THE NEIGHBORING PROPERTY BY ABOUT 6:30 P.M. ON 1/30/14. AFTER VERIFYING THAT THE SITE WAS SAFE, THE DECISION WAS MADE TO WAIT UNTIL THE FOLLOWING DAY TO CONDUCT FURTHER INVESTIGATIONS. ON 1/31/14, TWIN LAKES FIRE, WPSC AND COMPANY PERSONNEL MET ON SITE FOR INVESTIGATIONS. INITIAL PRESSURE TESTING OF THE ABANDONED MAIN AND SERVICE INDICATED AN UNDERGROUND LEAK, AND IT WAS BELIEVED NECESSARY TO EXCAVATE AT THE SERVICE TEE. SINCE THE PROPERTY OWNERS WERE NOT AVAILABLE TO ASSIST WITH MOVING NECESSARY PERSONAL PROPERTY, FURTHER EXCAVATION WAS DELAYED UNTIL FEBRUARY 4TH. ON 2/4/14, TWIN LAKES FIRE, WPSC AND COMPANY PERSONNEL MET ON SITE TO CONTINUE THE INVESTIGATION. UPON EXCAVATION AT THE SERVICE TEE LOCATION FOR 2800 LAKESHORE WAY, A BENT SECTION OF MAIN WAS IDENTIFIED. THE MAIN WAS BENT IN AN ARC, AND WAS DISPLACED VERTICALLY BY ABOUT 3 IN. OVER A 6 FT. LENGTH. THE BOTTOM OF THE PIPE WAS FLATTENED AND A CRACK WAS FOUND IN THE BENT SECTION OF THE PIPE. IT IS PRESUMED THAT THE DAMAGE OCCURRED DURING A PRIOR EXCAVATION AND THAT MOVEMENT CAUSED BY THE DEEP FROST LEVELS OBSERVED THIS WINTER CONTRIBUTED TO THE FAILURE OF THE PIPE. ONE-CALL CENTER RECORDS DO NOT INDICATE ANY RECENT LOCATE TICKET REQUESTS AND IT IS THOUGHT THAT THE EXCAVATION ACTIVITY THAT DAMAGED THE PIPE OCCURRED MANY YEARS AGO. A NEW PE MAIN WAS INSTALLED ON LAKESHORE WAY AND GAS SERVICE TO THE AFFECTED PROPERTY WAS RESTORED ON 2/14/14. A FORMAL INCIDENT REVIEW WAS CONDUCTED ON 2/21/14. PARTICIPANTS IN THE REVIEW INCLUDED GAS DISTRIBUTION WORKERS AT THE SCENE AFTER THE FIRE WAS REPORTED AND OTHER COMPANY PERSONNEL WHO ASSISTED AT THE SCENE. PIPELINE SAFETY ENGINEERS FROM THE WPSC, ONE OF WHOM HAD INSPECTED THE SITE THE DAY AFTER THE FIRE, ALSO ATTENDED. THE REVIEW RECOUNTED THE ACTIONS TAKEN BY EACH PARTICIPANT AND INCLUDED COMMUNICATIONS CONDUCTED AMONG INVOLVED PERSONNEL. WE ENERGIES IS PERFORMING MORE LEAK SURVEYS BEYOND THOSE REQUIRED IN CFR 49, PART 192 ON SIMILAR TYPE FACILITIES BECAUSE OF THE EXTREME WINTER CONDITIONS IN OUR SERVICE TERRITOR
2025-03-31 10:13 | NO | YES | YES | 20140013 | 15977 | 2014-02-26 16:07 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 1 METROTECH CENTER | BROOKLYN | NY | 11201 | 2014-01-29 18:44 |  |  | 2014 | 101 DELAWARE STREET | NYC | STATEN ISLAND | NY | 10304 | 40.5959 | -74.1026 | [9 empty] | 2014-01-29 20:31 | 1072448 |  | NATURAL GAS |  | 0.05 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 2 | 3 | YES |  |  |  |  | YES | 20 | 2014-01-29 18:44 |  |  |  | 2014-01-29 18:51 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1926 | [5 empty] | 4 | CAST IRON | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 125000 | 153143.063583815 | 0 | 0 | 20473 | 25082.38352601155596 | 0 | 0 |  |  | 1 | 0.7478108581436077057793345008756567425569 |  | 0 | 145474 | 73816.3267399249049209737302977232924694 | 178226.1949206846995677057793345008756567 | 0 | 0 | 1 |  |  |  |  | 0.33 | 0.33 | 0.65 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AN INVESTIGATION OF THE AREA GOVERNORS AND SCADA SYSTEM SHOWED THAT ALL OF THE SYSTEMS WERE FULLY FUNCTIONAL AND AREA PRESSURES WERE ACCEPTABLE FOR WINTER OPERATIONS. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | THE MIGRATION PATH OF THE GAS INVOLVING THE INCIDENT WAS POTENTIALLY RELATED TO AN INAPPROPRIATE CUSTOMER SEWER CONNECTION WHICH IS CURRENTLY UNDER INVESTIGATION BY FDNY. | [47 empty] | DAVID ANGELONE | MANAGER | david.angelone@nationalgrid.com | 718 403 3347 |  |  |  |  | R. DE MARINIS | VP MAINTENANCE AND CONSTRUCTION NY GAS | 516 545-4337 | robert.demarinis@nationalgrid.com | DISPATCH AND SCHEDULE WAS NOTIFIED BY THE FDNY OF A GAS RELATED DISTURBANCE AT #101 DELAWARE STREET ON 1/29/14. CUSTOMER METER SERVICES RESPONDED AND AS PER STANDARD OPERATING PROTOCOL CONDUCTED A LEAK INVESTIGATION WHICH YIELDED GAS READINGS INVOLVING MULTIPLE SEWER MANHOLES. FIELD OPERATION'S CREWS WERE SUBSEQUENTLY CALLED TO THE LOCATION, SECURED GAS TO 101 DELAWARE PER FDNY REQUEST, FOUND AND REPAIRED A CRACK IN THE 4" CI GAS MAIN LOCATED IN THE PROXIMITY OF #14 DELAWARE STREET. UPON REPAIR OF THIS CRACK THE SEWER MANHOLE READINGS BEGAN TO SUBSIDE. THE MIGRATION PATH OF THE GAS WAS POTENTIALLY RELATED TO AN INAPPROPRIATE CUSTOMER SEWER CONNECTION; THE CAUSE OF THIS INCIDENT IS STILL UNDER INVESTIGATION BY FDNY. NATIONAL GRID CONTINUES TO ACTIVELY WORK WITH THE PSC AND OTHER CITY AGENCIES TO INVESTIGATE THE CAUSE OF THIS INCIDENT. FURTHER REMEDIATION WILL BE ADDRESSED AS DEEMED NECESSARY BASED ON THE INVESTIGATION FINDINGS TO ENSURE THE SAFETY OF THE PUBLIC AND THE INTEGRITY OF OUR GAS INFRASTRUCTURE.
2025-03-31 10:13 | NO | YES | YES | 20140014 | 30457 | 2014-02-27 11:24 | SUPPLEMENTAL FINAL | 15469 | PHILADELPHIA GAS WORKS | 800 W. MONTGOMERY AVENUE | PHILADELPHIA | PA | 19122 | 2014-01-30 19:05 |  |  | 2014 | 1849 S.S BANCROFT STREET | PHILADELPHIA | PHILADELPHIA | PA | 19145-2206 | 39.9275 | -75.1728 | [9 empty] | 2014-01-30 20:45 | 1072563 |  | NATURAL GAS |  | 5229 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | YES | 0 | 2014-01-30 17:21 |  |  |  | 2014-01-30 17:29 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1939 | [5 empty] | 4 | ASA A21.2 | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 4 | 0.1 |  | CLASS 4 LOCATION | 65300 | 80001.936416184956 | 268914 | 329458.51040462421528 | 41302 | 50600.91849710981704 | 0 | 0 |  |  | 24 | 17.94746059544658493870402802101576182137 |  | 0 | 375540 | 190560.2221050181191113695271453590192644 | 460079.3127785144349049387040280210157618 | 0 | 0 | 2 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOW PRESSURE SYSTEM NOT UNDER THE CONTROL OF CONTROL ROOM | [12 empty] | YES | 5 | 0 | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | NO | [218 empty] | RAYMOND WELTE | DIRECTOR FIELD OPERATIONS | raymond.welte@pgworks.com | 215-684-6033 | 215-684-6388 |  |  |  | JOSEPH HAWKINSON | VICE PRESIDENT FIELD OPERATIONS | 215-684-6342 | joseph.hawkinson@pgworks.com | ON THURSDAY, JANUARY 30, 2014 AT 17:21, PGW RECEIVED AN INSIDE LEAK CALL FROM A CUSTOMER THROUGH PGW'S CALL CENTER WITH A HEADING OF 1845 S. BANCROFT STREET. AN FSD TECHNICIAN WAS DISPATCHED TO INVESTIGATE THIS LEAK. HE ARRIVED ON LOCATION AT 17:29 AND BEGAN HIS INVESTIGATION. A READING OF 70% LEL AT THE FRONT FOUNDATION WALL TO 1845 S. BANCROFT WAS REPORTED BY THE TECHNICIAN TO THE FSD DISPATCHER. BASED ON THIS REPORT, A DISTRIBUTION CREW WAS DISPATCHED AT 18:10. FSD AND DISTRIBUTION SUPERVISION WERE ALSO DISPATCHED TO THE LOCATION. THE CREW ARRIVED ON LOCATION AT 18:24 AND IMMEDIATELY BEGAN THEIR INVESTIGATION. DURING THE COURSE OF THE INVESTIGATION AND WHILE THE DISTRIBUTION FOREMAN AND THE FSD TECHNICIAN WERE INSIDE THE PROPERTY AT 1849 S. BANCROFT CHECKING FOR GAS READINGS, AN EXPLOSION TOOK PLACE AT APPROXIMATELY 19:05 INSIDE 1849 S. BANCROFT. THE EXPLOSION SEVERELY DAMAGED THE TWO RESIDENTIAL BUILDINGS AT 1849 AND 1847 S. BANCROFT. IT ALSO INJURED BOTH PGW EMPLOYEES WHO WERE INSIDE THE HOUSE, AS WELL AS ONE HOMEOWNER. THE INJURIES SUSTAINED BY ALL THREE INDIVIDUALS WERE NON-LIFE THREATENING. BOTH THE DISTRIBUTION FOREMAN AND HOMEOWNER WERE TAKEN TO A LOCAL HOSPITAL FOR TREATMENT AND RELEASED ON THE SAME DAY WHILE THE FSD TECHNICIAN WAS ADMITTED WITH BURNS TO HIS NECK AND LOWER TORSO. THE EXPLOSION AT THE SCENE WAS OBSERVED BY A FSD SUPERVISOR WHO HAD JUST ARRIVED ON THE SCENE AT 19:05. PHILADELPHIA FIRE DEPARTMENT, PHILADELPHIA POLICE DEPARTMENT AND PECO ENERGY WERE CALLED IN FOR ASSISTANCE, IN ADDITION TO VARIOUS PGW RESOURCES SUCH AS, DISTRIBUTION CREWS, FSD TECHNICIANS, MOBILE EQUIPMENT, GREASE TRUCK, SUPERVISORY PERSONNEL, CHEMICAL SERVICES, ETC. THE PAPUC WAS ALSO NOTIFIED OF THE INCIDENT. THE GAS MAIN IN THE EAST FOOTWAY IN FRONT OF 1849 S. BANCROFT (4" 1939 LOW PRESSURE CAST IRON MAIN) WAS GREASED OFF THROUGH A PLASTIC SERVICE TO 1843 S. BANCROFT AT 19:51 AND THE LEAK CONSEQUENTLY WAS MADE SAFE. AS A RESULT OF THE GREASING OFF, A TOTAL OF FOUR (4) PROPERTIES WERE TEMPORARILY OUT OF GAS. PECO ALSO SHUT OFF THE ELECTRIC POWER TO 1849 S. BANCROFT AT 21:00. AFTER MAKING THE JOB SAFE AND RECEIVING THE GO AHEAD FROM PFD, PGW PERSONNEL ON THE SCENE CONTINUED WITH THE INVESTIGATION. EVERY BUILDING ON THE 1800 BLOCK OF S. BANCROFT WAS CHECKED FOR GAS READINGS. ALSO, THE 4" CAST IRON MAIN ON THE BLOCK ALONG WITH ALL ACTIVE GAS SERVICES WERE BAR HOLED IN ORDER TO CHECK FOR ANY POSSIBLE LEAKS. DURING THIS BLOCK CHECK THE CREW PICKED UP LEL READINGS IN FRONT OF 1835 AND 1816/1818. A BROKEN MAIN WAS EVENTUALLY FOUND AND REPAIRED IN FRONT OF 1818 AND A TOTAL OF SIX (6) SERVICES ON THE BLOCK WERE RENEWED WITH PLASTIC. THE GREASED 4" MAIN WAS ALSO CUT AND CAPPED AT 03:45. THIS PORTION OF THE 4" MAIN THAT WAS CUT AND CAPPED (100') WAS AIR TESTED AT 6" WC AND THE TEST FAILED. THIS SECTION OF THE MAIN WAS THEN EXCAVATED COMPLETELY AND A BROKEN MAIN WAS FOUND IN FRONT OF 1849. AN 8' SECTION OF THE PIPE, CONTAINING THE BROKEN MAIN, WAS CUT AND REMOVED FROM THE EXCAVATION, TAGGED AS EVIDENCE AND TRANSPORTED TO THE PGW EVIDENCE ROOM ON 1/31/2014. IT IS BELIEVED FROST HEAVE WAS THE CAUSE OF THE BROKEN MAIN, FOURTEEN INCHES OF FROST WAS MEASURED AT THIS LOCATION. THE SERVICES TO 1845 AND 1847 (BOTH 1 1/4" UNPROTECTED STEEL SERVICES) WERE ALSO AIR TESTED AND FAILED. AFTER THE INVESTIGATION WAS COMPLETED, THE GAS SERVICE WAS RESTORED TO THE PROPERTIES THAT WERE SHUT OFF DURING THE GREASE OFF PROCESS. THE BUILDING AT 1849 WAS DEMOLISHED ON 2/1/2014. PGW SUBSEQUENTLY REPLACED THE 4" CAST IRON MAIN. ANALYSIS OF THE INCIDENT PIPE SHOWED THAT IT NEVER COMPLETELY FRACTURED CIRCUMFERENTIALLY AND THE CRACK WAS CONSIDERED TIGHT WITH NO LARGE GAP BETWEEN THE MATING SURFACES. THE CAST IRON MAIN EXHIBITED GRAPHITIZATION BUT THE INTEGRITY OF THE PIPE WOULD HAVE PERSISTED IF LEFT UNDISTURBED AND NOT UNDER LOADING CONDITIONS. THE LOADING CONDITIONS ARE BELIEVED TO BE CAUSED BY THE EFFECTS OF 14 INCHES OF FROST.
2025-03-31 10:13 | NO | YES | NO | 20140015 | 16261 | 2014-02-28 10:21 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2014-01-29 11:33 |  |  | 2014 | MILLETT & GUINEA ROADS; CREYTS & SAGINAW ROADS; CREYTS & LANSING ROADS | LANSING | EATON | MI | 48917-9998 | 42.6968 | -84.6725 | [9 empty] | 2014-01-30 18:02 | 1072548 |  | NATURAL GAS |  | 3190 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 600 | 2014-01-29 11:36 |  |  |  | 2014-01-29 12:12 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2004 | [8 empty] | OTHER | FAILED RUBBER REGULATOR BOOT (STEEL REG) | [9 empty] | OTHER | [8 empty] | TWO VENTING RELIEF VALVES | CLASS 3 LOCATION | 0 | 0 | 12342 | 15120.73352601155784 | 533982 | 654205.11502890161064 | 39764 | 48716.64624277455728 | OTHER COSTS ARE ASSOCIATED WITH INCIDENT COMMAND & OFFICE SUPPORT |  | 15184 | 11354.760070052539404553415061295971979 |  | 0 | 601272 | 307895.484144707836897120840630472854641 | 729397.254867740265164553415061295971979 | 0 | 0 | 0 |  |  |  |  | 139 | 55 | 60 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 |  |  |  |  | TRACY A. GOBLE | MANAGER OF REGULATORY AND COMPLIANCE | 517-768-3187 | tracy.goble@cmsenergy.com | DEBRIS DAMAGED RUBBER REGULATOR BOOTS OF WORKER AND MONITOR REGULATORS AT MILLETT & GUINEA REGULATOR STATION (STATION #428), WEST OF I-69 ON MILLETT HIGHWAY IN DELTA TOWNSHIP, MICHIGAN. THE RESULTING DOUBLE REGULATOR FAILURE RESULTED IN AN OVERPRESSURE OF THE 60 PSIG MAOP DOWNSTREAM SYSTEM. PRESSURE RECORDING CHARTS AT MILLETT & GUINEA REGULATOR STATION RECORDED A MAXIMUM DOWNSTREAM PRESSURE OF 139 PSIG, AN EXCEEDANCE OF 131% OF MAOP. RELIEF VALVES AT TWO SEPARATE REGULATOR STATIONS - SEVERAL MILES AWAY AND BACKFEEDING THE 60 PSIG MAOP SYSTEM - BEGAN BLOWING AS A RESULT OF THE OVERPRESSURE EVENT. ALL TOLD, APPROXIMATELY 3.19 MMCF NATURAL GAS VENTED FROM BOTH VENTS COMBINED. THESE REGULATOR STATIONS ARE: - CREYTS ROAD & M-43, LANSING (STATION #46) + RELIEF VALVE SET PRESSURE = 63 PSIG + MAX PRESSURE RECORDED = 63 PSIG + DURATION OF VENTING = 130 MINUTES - CREYTS ROAD & M-78, LANSING (STATION #47) + RELIEF VALVE SET PRESSURE = 60 PSIG + MAX PRESSURE RECORDED = 94 PSIG + DURATION OF VENTING = 117 MINUTES POLICE AND FIRE DEPARTMENT WAS ON SITE AT THE INTERSECTIONS OF CREYTS & SAGINAW (M-43) AND CREYTS & LANSING (M-78), AND INTERSECTIONS WERE BLOCKED TO TRAFFIC. MEDIA WAS ALSO ON SITE REPORTING. LANSING MALL (5330 W. SAGINAW HIGHWAY, LANSING) AND ST. GERARD CATHOLIC SCHOOL (4433 W. WILLOW, LANSING) WERE EVACUATED AS A RESULT OF THE VENTING INCIDENT. APPROXIMATELY 120 MILES OF GAS DISTRIBUTION MAIN (60 PSIG MAOP) AS WELL AS 7,010 GAS SERVICES (60 PSIG MAOP) IN DELTA TOWNSHIP WERE OVERPRESSURED. LEAK SURVEY AND SUPPLEMENTAL LEAK INVESTIGATION (INCLUDING BAR TESTING) WAS PERFORMED ON THESE FACILITIES BETWEEN JANUARY 29 AND FEBRUARY 7. APPROXIMATELY 42 LEAKS WERE FOUND AND REPAIRED DURING THIS LEAK SURVEY, AND AN ADDITIONAL 92 LEAKS WERE CLASSIFIED FOR FUTURE REPAIR.
2025-03-31 10:13 | NO | YES | NO | 20140016 | 33306 | 2014-02-28 11:43 | SUPPLEMENTAL FINAL | 2604 | COLUMBIA GAS OF VIRGINIA INC | 1809 COYOTE DRIVE | CHESTER | VA | 23836 | 2014-02-01 21:41 |  |  | 2014 | 15 HOPKINS BRANCH WAY | FREDERICKSBURG | STAFFORD | VA | 22406 | 38.3522 | -77.5538 | [9 empty] | 2014-02-01 23:56 | 1072743 |  | NATURAL GAS |  | 210.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 10 | 2014-02-01 21:41 |  |  |  | 2014-02-01 22:11 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2014 | [5 empty] | 1 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.099 |  | 2406 | MECHANICAL PUNCTURE | 0.2 | 0.2 | [7 empty] | CLASS 3 LOCATION | 240000 | 294034.6820809248 | 3000 | 3675.43352601156 | 5000 | 6125.7225433526 | 0 | 0 |  |  | 877 | 655.830122591943957968476357267950963222 |  | 0 | 248877 | 126446.3729757819652819614711033274956217 | 304491.6682728809039579684763572679509632 | 0 | 0 | 1 |  |  |  |  | 54 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT DID NOT INVOLVE A PIPELINE CONTROLLED BY A SCADA BASED SYSTEM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | A UNMARKED, UNLOCATABLE, UNPRESSURIZED, PRIVATE WATER SERVICE LINE WAS STRUCK WHILE DIRECTIONAL DRILLING TO INSTALL A NEW GAS SERVICE LINE CAUSING DAMAGE. APPROXIMATELY FOUR WEEKS LATER, WHEN THE WATER SERVICE LINE WAS PRESSURIZED, THE WATER PRESSURE FROM A HOLE IN THE WATER SERVICE LINE BORED A HOLE INTO THE GAS SERVICE LINE, CAUSING A LEAK AND SUBSEQUENT EXPLOSION. | [154 empty] | BRIAN ROBERTS | OPERATIONS COMPLIANCE MANAGER | brroberts@nisource.com | 804-768-6415 | 804-768-5913 |  |  |  | DAVID SCHMIDT | OPERATIONS COMPLIANCE MANAGER | 804-263-5873 | dschmidt@nisource.com | AT 21:41 ON FEBRUARY 1, 2014 CGV RECEIVED NOTIFICATION FROM STAFFORD COUNTY FIRE DEPARTMENT THAT THERE HAD BEEN AN EXPLOSION AT 15 HOPKINS BRANCH WAY IN FREDERICKSBURG, VIRGINIA. CGV PERSONNEL WENT TO THE SITE, EXPOSED THE PLASTIC GAS SERVICE SERVING 15 HOPKINS BRANCH, SQUEEZED OFF, AND CUT AND CAPPED THE SERVICE LINE. WHEN CGV PERFORMED PRESSURE TEST ON THE FACILITY, IT WOULD NOT HOLD. UPON FURTHER INVESTIGATION IT WAS DISCOVERED THAT THERE WAS AN 1/8 INCH HOLE IN THE PLASTIC GAS SERVICE LINE WHERE IT CROSSED THE PLASTIC WATER SERVICE LINE. PENDING THE OUTCOME OF LAB ANALYSIS, THE CONCLUSION OF CGV'S INVESTIGATION IS THAT DURING INSTALLATION OF THE GAS SERVICE ON JANUARY 2, 2014, THE UNLOCATED (UNLOCATABLE) PRIVATE WATER SERVICE LINE WAS STRUCK WHILE DIRECTIONAL DRILLING CAUSING DAMAGE. THE WATER METER WAS SET AT THE SITE ON JANUARY 23, 2014 AND SOMETIME AFTER, THE WATER WAS TURNED ON TO THE PROPERTY. WHEN THE WATER SERVICE WAS PRESSURIZED, THE WATER PRESSURE FROM THE HOLE IN THE WATER SERVICE LINE CAUSED A HOLE TO EVENTUALLY FORM IN THE PLASTIC GAS SERVICE LINE. THE GAS MIGRATED INTO THE UNOCCUPIED NEW CONSTRUCTION RESIDENCE AND FOUND AN IGNITION SOURCE.
2025-03-31 10:13 | NO | YES | YES | 20140017 | 15812 | 2014-02-28 16:08 | ORIGINAL | 18104 | CPS ENERGY | 500 MCCULLOUGH | SAN ANTONIO | TX | 78215 | 2014-01-29 05:34 |  |  | 2014 | 245 LYMAN | TERRELL HILLS | BEXAR | TX | 78209 | 29.4789 | -98.4353 | [9 empty] | 2014-01-29 08:33 | 1072378 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 6 | 2014-01-29 06:39 |  |  |  | 2014-01-29 07:09 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | EXPLOSION IN KITCHEN AND SUBSEQUENT FIRE |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1950 | [5 empty] | 1.135 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.179 | [6 empty] | OTHER | [8 empty] | INITIAL INVESTIGATION FOUND A CRACK AT THE THREADED END OF THE 1" STEEL SERVICE WHERE IT CONNECTED WITH A BELOW-GROUND ELBOW FITTING TO THE RISER. THE INTERIOR GAS PIPING AND GAS APPLIANCES ARE BEING INVESTIGATED AS LIKELY GAS SOURCES. | CLASS 4 LOCATION | 243501 | 298323.91300578029052 | 2000 | 2450.28901734104 | 2800 | 3430.404624277456 | 0 | 0 |  |  | 0 | 0 |  | 0 | 248301 | 125992.424566474020972 | 304204.60664739878652 | 0 | 0 | 1 |  |  |  |  | 9 | 9 | 33 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THAT PORTION OF THE 1" STEEL SERVICE WITH THE CRACK AT ITS THREADED END WAS BELOW GROUND AND AT LEAST TWO LAYERS OF CONCRETE WITH MORTAR AND SALTILLO TILE ABOVE THAT. THE TOP LAYERS WERE INSTALLED AROUND THE RISER WITHOUT A SLEEVE OR SPACE TO ALLOW OR ACCOMMODATE FOR MOVEMENT. SEE THE NARRATIVE AT PART H. | [154 empty] | MICHAEL FUENTES | MANAGER GAS STANDARDS AND COMPLIANCE | mrfuentes@cpsenergy.com | 210-219-1309 | 210-353-6594 |  |  |  | DONALD STANTON | SR DIRECTOR GAS DELIVERY | 210-353-3125 | drstanton@cpsenergy.com | AN INVESTIGATION IS ONGOING. THE TERRELL HILLS POLICE DEPARTMENT REPORTED THE FEMALE HOMEOWNER WOKE UP AND NOTICED HER EYES BURNING A LITTLE AND SHE COULD SMELL AN ODOR. SHE WENT IN THE KITCHEN AND TURNED ON THE GAS STOVE (TOP) ON WHICH SAT A TEA KETTLE FILLED WITH WATER. SHE NOTICED THE BURNER FLAME WAS HIGHER THAN USUAL. SHE TURNED THE FLAME DOWN AS MUCH AS POSSIBLE. SHE TURNED AWAY FROM THE STOVE AND SUDDENLY NOTICED THAT SHE WAS ON THE GROUND WITH DEBRIS FALLING FROM THE CEILING AND FIRE AROUND HER. SHE TRIED TO GO TO THE BACK OF THE HOUSE WHERE HER HUSBAND WAS SLEEPING BUT COULD NOT AND SO SHE WALKED THROUGH THE GARAGE TO GET OUTSIDE. THAT PORTION OF THE 1" STEEL SERVICE WITH THE CRACK AT ITS THREADED END WAS BELOW GROUND AND AT LEAST TWO LAYERS OF CONCRETE WITH MORTAR AND SALTILLO TILE ABOVE THAT. THE TOP LAYER OF CONCRETE, MORTAR AND TILE WERE ALL INSTALLED AROUND THE RISER WITHOUT A SLEEVE OR SPACE TO ALLOW OR ACCOMMODATE FOR MOVEMENT CAUSED BY SHIFTING, SETTLING, EXPANDING OR CONTRACTING SOIL. THE BOTTOM LAYER OF CONCRETE HAD A VOID AROUND THE RISER WHICH SERVED AS A SLEEVE OR SPACE THAT WOULD ACCOMMODATE FOR SUCH MOVEMENT. MOVING SOIL ACTING ON THE IMMOVABLE RISER ENCASED IN CONCRETE, MORTAR AND TILE MAY HAVE CAUSED THE CRACK AT THE THREADED END OF THE SERVICE LINE. INITIAL VISUAL METALLURGIC EXAMINATION OF THE CRACK AT THE THREADED END OF THE SERVICE DID NOT SHOW OBVIOUS SIGNS OF CORROSION. THE INTERIOR GAS PIPING OF THE HOUSE AND THE GAS APPLIANCES IN THE HOUSE HAVE NOT YET BEEN TESTED.
2025-03-31 10:13 | NO | YES | YES | 20140018 | 16095 | 2014-03-05 13:00 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2014-02-09 15:52 |  |  | 2014 | 1914 EAST PALOMINO DRIVE | GILBERT | MARICOPA | AZ | 85296 | 33.3388 | -111.7489 | [9 empty] | 2014-02-09 19:35 | 1073454 |  | NATURAL GAS |  | 23 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 50 | 2014-02-09 18:20 |  |  |  | 2014-02-09 18:47 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1995 | [5 empty] | 1 | ASTM D2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 12500 | 15314.3063583815 | 50831 | 62275.32052023120212 | 688 | 842.89942196531776 | 0 | 0 |  |  | 100 | 74.78108581436077057793345008756567425569 |  | 0 | 64119 | 32553.5769790011185653730297723292469352 | 78507.3073863923806505779334500875656743 | 0 | 0 | 0 |  |  |  |  | 56 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [9 empty] | YES |  |  |  | OTHER | THERMAL OXIDATION PRODUCING AN AXIAL SLIT | NO | [86 empty] | SHAWN BRINK | ADMINISTRATOR COMPLIANCE | shawn.brink@swgas.com | 602-484-5489 | 602-484-5322 |  |  |  | LYNN MALLOY | GENERAL MANAGER OPERATIONS | 480-730-3700 | michael.chase@swgas.com | PL 2014-0244 SOUTHWEST GAS CORPORATION (SWG) RESPONDED TO A REPORTED FIRE AT 1914 EAST PALOMINO DRIVE IN GILBERT CALLED IN BY THE GILBERT FIRE DEPARTMENT AT 18:20. UPON ARRIVAL SERVICE TECHNICIAN WAS ADVISED THAT AN EXPLOSION HAD OCCURRED AND ONE PERSON WAS TRANSPORTED TO THE HOSPITAL WITH BURNS. SWG CREWS RESPONDED AND CONTROLLED THE FLOW OF GAS BY SQUEEZING A 2-INCH PE MAIN. NOTIFICATION WAS MADE TO PHMSA VIA THE NATIONAL RESPONSE CENTER (NRC) REPORT NUMBER 1073454 AT 19:35 OF THE IN-PATIENT HOSPITALIZATION. THERE WERE NO FATALITIES AS A RESULT OF THE INCIDENT. FURTHER INVESTIGATION INTO THE INCIDENT FOUND THE LEAK TO HAVE OCCURRED ON A 1" PE SERVICE STUB. THE CAUSE OF THE LEAK ON THE 1" PE LINE REMAINS UNDER INVESTIGATION. A SUPPLEMENTAL REPORT WILL BE SUBMITTED UPON COMPLETION OF THE INVESTIGATION BY SWG. NOTE: FOR PART A, #10, THE ESTIMATED VOLUME OF GAS RELEASED THAT IS IDENTIFIED REPRESENTS AN ESTIMATE THAT PRESUMES A CRACK THAT IS LEAKING AT 57 PSI, BEGINNING AT THE TIME OF THE INTIAL REPORT OF THE INCIDENT AND ENDING AT THE TIME THE PIPELINE WAS SHUT DOWN. HOWEVER, THE ACTUAL AMOUNT OF GAS LOSS IS UNKNOWN BECAUSE THE TIME THE GAS PIPELINE BEGAN LEAKING IS UNKNOWN. SUPPLEMENTAL REPORT: LABORATORY ANALYSIS SHOWS THAT THE LEAKS WERE PRESENT DUE TO THERMAL OXIDATION OF THE PIPES AT 1914 AND 1924 E. PALOMINO. THE THERMAL OXIDATION OF THE PIPES RESULTED IN AXIAL SLIT-CRACKS ON THE PIPES AT BOTH LOCATIONS. SECTION G5 IS REVISED TO REFLECT THIS FACT.
2025-03-31 10:13 | NO | YES | NO | 20140019 | 15841 | 2014-03-06 14:48 | SUPPLEMENTAL FINAL | 31632 | NORTHWESTERN ENERGY LLC | 3010 W. 69TH ST. | SIOUX FALLS | SD | 57108 | 2014-02-06 18:55 |  |  | 2014 | 620 E. PEACH | BOZEMAN | GALLATIN | MT | 59715-3034 | 45.4108 | -111.0139 | [9 empty] | 2014-02-07 00:59 | 1073250 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2014-02-06 18:55 |  |  |  | 2014-02-06 19:01 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1938 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.14 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  |  |  |  | CLASS 2 LOCATION | 250000 | 306286.12716763 | 15000 | 18377.1676300578 | 4500 | 5513.15028901734 | 0 | 0 |  |  | 100 | 74.78108581436077057793345008756567425569 |  | 0 | 269600 | 136818.3580001957504973730297723292469352 | 330251.2261725195007705779334500875656743 | 0 | 0 | 1 |  |  |  |  | 33 | 33 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | VEGITATION ROOT PRESSURE | NO | [218 empty] | DEVIN MCCARTHY | DOT COORDINATOR | devin.mccarthy@northwestern.com | 406-497-3218 | 406-497-2048 |  |  |  | DEVIN MCCARTHY | DOT COORDINATOR | 406-497-3218 | devin.mccarthy@northwestern.com | THIS IS NWE FINAL SUBMISSION OF THIS REPORT. NO CHANGES HAVE BEEN MADE FROM THE ORIGINAL SUBMISSION. THE PUBLIC SERVICE COMMISSION HAS BEEN NOTIFIED OF THE FINALIZATION.
2025-03-31 10:13 | NO | YES | NO | 20140020 | 15852 | 2014-03-07 13:24 | SUPPLEMENTAL FINAL | 11032 | LACLEDE GAS CO | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2014-02-05 13:13 |  |  | 2014 | 2222 MENARD STREET | ST. LOUIS | N/A | MO | 63104 | 38.6061 | -90.2083 | [9 empty] | 2014-02-05 14:26 | 1073090 |  | NATURAL GAS |  | 17 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 45 | 2014-02-05 13:17 |  |  |  | 2014-02-05 13:28 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 33 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1980 | [5 empty] | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | 2406 | MECHANICAL PUNCTURE | 2 | 0.3 | [7 empty] | CLASS 3 LOCATION | 750000 | 918858.38150289 | 62412 | 76463.71907514449424 | 37633 | 46105.86329479767916 | 0 | 0 |  |  | 89 | 66.55516637478108581436077057793345008757 |  | 0 | 850134 | 431389.7962309642786226619964973730297723 | 1041494.51903920695448581436077057793345 | 1 | 0 | 44 |  |  |  |  | 12.4 | 12 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS NOT DETECTABLE BY THE SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 140301962 |  |  | CONTRACT LOCATOR | YES | YES | 4 | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | MARK LAUBER | MANAGER PIPELINE SAFETY COMPLIANCE | mark.lauber@thelacledegroup.com | 314-658-5413 | 314-535-9414 |  |  |  | CRAIG R. HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES | 314-658-5410 | craig.hoeferlin@thelacledegroup.com | FOUR WINDS CONSTRUCTION LLC DAMAGED THE 2-INCH PLASTIC NATURAL GAS SERVICE LINE WHILE DIRECTIONAL BORING IN A CONDUIT FOR FIBER OPTIC CABLE. FOUR WINDS DID NOT REQUEST A LOCATE FOR THIS PROJECT. MISSOURI STATE LAW REQUIRES THE EXCAVATOR TO REQUEST THE LOCATE FOR THE PLANNED EXCAVATION ACTIVITY. THE LOCATE WAS CALLED BY MASTEC CONSTRUCTION (#140301962) BUT THEY DID NOT NAME FOUR WINDS CONSTRUCTION LLC AS THE EXCAVATOR. FOUR WINDS CONSTRUCTION DID NOT ATTEMPT TO IDENTIFY THE PROPERLY PLACED LOCATE MARKS AFTER THEY HAD BEEN COVERED BY SNOW. FURTHERMORE, FOUR WINDS DID NOT POT-HOLE THE SERVICE LINE THAT WAS DAMAGED. THE TIME AND DATE STATED IN PART A, 17A. OF THIS FORM IS THE TIME THE FIRE DEPARTMENT REPORTED TO LACLEDE THAT AN EXPLOSION HAD OCCURRED. THE REPORT WAS VERIFIED AND AT 13:28 HOURS ON FEBRUARY 5, 2014, LACLEDE BECAME AWARE THAT THE INCIDENT MET THE REPORTING CRITERIA OF CFR PART 191.3. LACLEDE REPORTED THE INCIDENT TO THE NATIONAL RESPONSE CENTER AT 14:26 HOURS ON FEBRUARY 5, 2014.
2025-03-31 10:13 | NO | YES | NO | 20140021 | 16594 | 2014-03-07 14:29 | SUPPLEMENTAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2014-02-11 10:50 |  |  | 2014 | 700 S. PERRY STREET | ATTICA | FOUNTAIN | IN | 47918-1634 | 40.2885 | -87.2522 | [9 empty] | 2014-02-11 13:06 | 1073624 |  | NATURAL GAS |  | 211 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 20 | 2014-02-11 11:50 |  |  |  | 2014-02-11 11:53 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 39 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1941 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 152000 | 186221.96531791904 | 45000 | 55131.5028901734 | 5000 | 6125.7225433526 | 0 | 0 |  |  | 971 | 726.124343257443082311733800350262697023 |  | 0 | 202971 | 103170.1661048291299894921190893169877408 | 248205.315094702483082311733800350262697 | 0 | 0 | 4 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SCADA BASED SYSTEM THAT MONITORED THE MAIN ON WHICH THE LEAK OCCURED ONLY PROVIDES A HIGH/LOW PRESSURE ALARM AND THE PRESSURE REMAINED WITHIN ACCEPTABLE PARAMETERS. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | CRACK IN A MITER JOINT |  |  |  |  | YES | [9 empty] | YES |  |  |  | OTHER | CRACK IN A MITER JOINT | NO | [86 empty] | JOHN A. SPINKS | MANAGER QUALITY ASSURANCE | jaspinks@vectren.com | 937-440-1844 | 937-440-1818 |  |  |  | JAMES M. FRANCIS | DIRECTOR ENGINEERING AND ASSET MANAGEMENT | 812-491-4369 | jmfrancis@vectren.com | VECTREN DID NOT RECEIVE NOTIFICATION OF THE EXPLOSION FROM LOCAL EMERGENCY RESPONDERS. A VECTREN EMPLOYEE HEARD OF EXPLOSION ON A SCANNER AND IMMEDIATELY NOTIFIED THE LOCAL SUPERVISOR. VECTREN SENT AN EMPLOYEE TO THE SITE FINDING NATURAL GAS MIGRATING INTO A STORM DRAIN AND NEARBY RESIDENTIAL HOMES DUE TO THE DEPTH OF FROST IN THE AREA. INVESTIGATING THE SOURCE OF ESCAPING NATURAL GAS, EMPLOYEE FOUND A LEAK UNDER NEW STREET, WHICH RUNS EAST AND WEST NORTH OF THE EXPLOSION LOCATION. AFTER MONITORING THE AREA, COMPANY CREWS EXCAVATED THE SOURCE OF LEAK FINDING A CRACK IN A 4' STEEL MAIN THAT TRANSVERSE AN OXY-ACETYLENE WELDED MITER JOINT. TWO STOPPLE FITTINGS WERE INSTALLED ON THE ONE-WAY FED MAIN TO BYPASS THE CRACKED MAIN ENABLING THE SECTION TO BE ISOLATED. A 45° WELD ELL WAS INSTALLED TO REPAIR THE CRACKED MAIN AND TO REMOVE THE MITER JOINT. AFTER THIS INSTALLATION, THE STOPPLE FITTINGS WERE REMOVED AND THE ISOLATED SECTION WAS ENERGIZED. AN INITIAL REPORT FROM THE ATTICA VOLUNTEER FIRE DEPARTMENT INDICATES THE ITEM FIRST IGNITED WAS GAS VAPOR IN AIR AND THAT FACTORS CONTRIBUTING TO IGNITION WERE RUPTURED GAS LINE ALLOWED GAS TO MIGRATE ALONG WATER LINES INTO BASEMENT OF BUILDING. VECTREN IS CONTINUING ITS OWN INDEPENDENT INVESTIGATION INTO THE CAUSE AND ORIGIN OF THIS INCIDENT. UPDATE: VECTREN'S INDEPENDENT INVESTIGATION INTO THE CAUSE AND ORIGIN OF THIS INCIDENT INCLUDED A ROOT CAUSE ANALYSIS AND A METALLURGICAL DESTRUCTIVE TESTING OF THE 4" STEEL MAIN REFERENCED IN THE FIRST PARAGRAPH OF THIS NARRATIVE. THE ROOT CAUSE ANALYSIS, WHILE BENEFICIAL IN IDENTIFYING POTENTIAL FACTORS THAT MAY HAVE PLAYED A ROLE IN THE INCIDENT, WAS INCONCLUSIVE AS TO THE ORIGIN OR CAUSE OF THE INCIDENT. ADDITIONALLY, THE METALLURGICAL DESTRUCTIVE TESTING OF THE 4" STEEL MAIN AND ASSOCIATED CRACKED OXY-ACETYLENE WELDED MITER JOINT PROVIDED NO DEFINITIVE CONCLUSION AS TO WHETHER THE CRACKED WELD WAS A RESULT OF THE EXPLOSION, OR A CONDITION EXISTING AT THE TIME OF THE EXPLOSION.
2025-03-31 10:13 | NO | NO | NO | 20140022 | 15923 | 2014-03-10 16:06 | SUPPLEMENTAL FINAL | 2812 | CORPUS CHRISTI, CITY OF - GAS DIV | 4225 SOUTH PORT AVENUE | CORPUS CHRISTI | TX | 78415 | 2014-02-11 11:00 |  |  | 2014 | 6200 SARATOGA BLVD | CORPUS CHRISTI | NUECES | TX | 78414 | 27.6799 | -97.3722 | [9 empty] | 2014-02-11 12:17 | 1073628 |  | NATURAL GAS |  | 347 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2014-02-11 11:30 |  |  |  | 2014-02-11 11:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1984 | [5 empty] | 10 | API 5L | UNKNOWN | STEEL |  |  |  | 0.219 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 26846 | 32890.22947976877992 | 32055 | 39272.0072254335186 | 12123 | 14852.42687861271396 | 0 | 0 |  |  | 1500 | 1121.716287215411558669001751313485113835 |  | 0 | 72524 | 37076.517209101440388595446584938704028 | 88136.3798710304240386690017513134851138 | 2 | 0 | 65 |  |  |  |  | 15 | 15 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 4 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | MATERIAL FAILURE OF PIPE OR WELD | BUTT WELD | [146 empty] | BUTT WELD |  |  | FABRICATION | [29 empty] | YES | [7 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | JESSE CANTU | PETROLEUM SUPERINTENDENT | jessecantu@cctexas.com | (361)885-6941 | (361)853-3200 |  |  |  | JESSE CANTU | PETROLEUM SUPERINTENDENT | (361)885-6941 | No Email Address | THE 10 INCH STEEL COATED MAIN LOCATED ON THE NORTH SIDE OF SARATOGA BLVD BETWEEN CIMMARON AND STAPLES BEGAN TO LEAK UNDER A CONCRETE DRIVEWAY ENTRANCE. WHILE LEAK CREW WAS IN THE PROCESS OF REMOVING CONCRETE IN ORDER TO DIG OUT THE LEAK, THE NATURAL GAS IGNITED. THE CREW NOTIFIED 911 AND MADE THE AREA SAFE. THE GAS CREW THEN ISLOATED THE LEAK USING STOPPLE EQUIPMENT AND ISOLATION VALVES. THE LEAK WAS CAUSED BY A CRACK ON A WELD THAT DEVELOPED AT THE 6 O'CLOCK POSITION. THE WELD WAS CUTOUT BY REPLACING A 2 FOOT SECTION OF PIPE.
2025-03-31 10:13 | NO | YES | NO | 20140023 | 15822 | 2014-03-18 14:00 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2014-02-18 21:48 |  |  | 2014 | 9506 CENTRAL AVE | MONTCLAIR | SAN BERNARDINO | CA | 91736 | 34.0813 | -117.6896 | [9 empty] | 2014-02-19 06:20 | 1074442 |  | NATURAL GAS |  | 548 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-02-18 21:48 |  |  |  | 2014-02-18 22:10 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 45 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1959 | [5 empty] | 8.625 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1240000 | 1519179.1907514448 | 2000 | 2450.28901734104 | 0 | 0 |  |  | 3288 | 2458.802101576182136602451838879159369527 |  | 0 | 1245288 | 632487.8306996144688336252189141856392294 | 1524088.28187036202213660245183887915937 | 63 | 0 | 1688 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HIGH PRESSURE WATER BORED HOLE INTO 8" STEEL NATRUAL GAS MAIN. | [154 empty] | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | tbauer@semprautilities.com | 909-376-7208 | 909-885-6270 |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | ON FEBRUARY 18, 2014 SOCALGAS WAS NOTIFIED OF A GAS LEAK AT 9506 CENTRAL AVE IN MONTCLAIR. MONTE VISTA WATER DISTRICT INDICATED THEY WERE WORKING ON A WATER LEAK ON THEIR MAIN IN THE INTERSECTION OF CENTRAL AVE AND PALO VERDE AND DETECTED GAS WHILE EXCAVATING. GAS CREWS RESPONDED AND CONFIRMED LEAKAGE AND THAT THE WATER HAD ENTERED THE GAS MAIN. THE WATER CREWS ISOLATED THE WATER MAIN AT THE INCURSION POINT AND SOCALGAS EXCAVATED AND REPAIRED THE GAS LEAK WITH A CLAMP. WHILE THE GAS LEAK WAS BEING BROUGHT UNDER CONTROL, SOCALGAS BEGAN INVESTIGATING THE AREA TO DETERMINE THE EXTENT OF THE WATER INCURSION. NUMEROUS LOCATIONS WERE IDENTIFIED DUE TO LOW ELEVATION AND ENDS OF THE DISTRIBUTION SYSTEM AS WATER EXTRACTION POINTS. OVER THE COURSE OF THE NEXT FIVE DAYS, APPROXIMATELY 6,100 GALLONS OF WATER WAS EXTRACTED FROM THE GAS LINES AND 1,751 IMPACTED METERS WERE REPLACED. AS OF 22:00 ON 2-23-14, ALL IMPACTED CUSTOMERS HAD EITHER BEEN RESTORED OR, IF CONTACT COULD NOT BE MADE BECAUSE OF VACANT RESIDENCES, MEMOS WERE PLACED ON THE ACCOUNTS AND LITERATURE LEFT AT THE RESIDENCE ON HOW TO CONTACT SOCALGAS FOR RESTORATION OF GAS SERVICE. INVESTIGATION REVEALED THAT THE WATER MAIN, LOCATED PERPENDICULAR TO AND DIRECTLY ABOVE THE GAS MAIN HAD A CORROSION LEAK ON THE BOTTOM OF THE PIPE. THAT WATER LEAK, OVER TIME, BORED A HOLE INTO THE TOP OF THE GAS MAIN. THE WATER PRESSURE WAS APPROXIMATELY 100 PSIG AND THE GAS WAS OPERATING AT 45 PSIG WHICH ALLOWED THE WATER TO ENTER THE GAS MAIN. THE GAS MAIN WAS REPAIRED WITH A CLAMP, THE WATER MAIN WAS REPLACED AT THE CROSSING. THIS INCIDENT WAS REPORTED TO PHMSA DUE TO THE ANTICIPATED COSTS OF THE INCIDENT WOULD EXCEED $50,000. THIS INCIDENT WAS ALSO REPORTED TO THE CPUC.
2025-03-31 10:13 | NO | YES | YES | 20140024 | 16324 | 2014-03-19 14:25 | SUPPLEMENTAL FINAL | 1088 | BALTIMORE GAS & ELECTRIC CO | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2014-02-19 18:00 |  |  | 2014 | 447 N. LAKEWOOD AV | BALTIMORE | Not Within a County or Parish | MD | 21224 | 39.2967 | -76.5791 | [9 empty] | 2014-02-19 18:00 | 1074520 |  |  |  | 1 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 2 | 2 | NO |  |  |  |  | NO | 0 | 2014-02-19 15:15 |  |  |  | 2014-02-19 15:39 |  | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | UNDETERMINED |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | UNDETERMINED | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNDETERMINED | CLASS 3 LOCATION | 70000 | 85760.1156069364 | 0 | 0 | 0 | 0 | 0 | 0 | PER BCFD THE ESTIMATED COST TO THE PROPERTY WAS $70,000. |  | 0 | 0 |  | 0 | 70000 | 35519.26782273604 | 85760.1156069364 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.3 | 0.36 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ABSENCE OF ANY EFFECT ( INDICATIONS OF ) ON SYSTEM PRESSURES / OPERATIONS. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | MICHAEL BOWLING | SUPERVISOR GAS | michael.bowling@bge.com | 4104707104 |  |  |  |  | MICHAEL BOWLING | SUPERVISOR GAS | 4104707104 | michael.bowling@bge.com | THIS REPORT AND THE RESPONSES SET FORTH IN PART A, #'S 4, 8, 13, 14, 15, AND 17A AND PART B, #3 ARE SUBMITTED BASED ON UNDETERMINED BASIS FOR GAS INVOLVEMENT. THE VALVE ON THE GAS SERVICE TO THE BUILDING WAS TURNED OFF ON 2/19/2014 AT 15:53. PART A #17A REFERS TO WHEN THE OPERATOR RECEIVED FIRST NOTICE OF A BUILDING FIRE AND ASKED TO RESPOND. IN PART A #16 NOTE THAT THE OPERATOR DID NOT EVACUATE ANY RESIDENCES, HOWEVER, THE BALTIMORE CITY FIRE DEPARTMENT EVACUATED ADJACENT BUILDINGS. FOLLOWING THE FINAL BALTIMORE CITY FIRE DEPARTMENT REPORT, GAS WAS REPORTED TO BE INVOLVED BUT THE SOURCE WAS INDETERMINABLE. THIS WILL SERVE AS THE FINAL REPORT.
2025-03-31 10:13 | NO | NO | NO | 20140025 | 30573 | 2014-03-21 13:11 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2014-02-19 06:46 |  |  | 2014 | 4226 KELLER ROAD | HOLT | INGHAM | MI | 48842-8798 | 42.6476 | -84.513 | [9 empty] | 2014-02-19 15:30 | 1074495 |  | NATURAL GAS |  | 18.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2014-02-19 06:46 |  |  |  | 2014-02-19 07:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1994 | [8 empty] | OTHER | GAS METER | [9 empty] | OTHER | [8 empty] | METER DAMAGE DUE TO FALLING ICE. | CLASS 3 LOCATION | 50000 | 61257.225433526 | 936 | 1146.73526011560672 | 1354 | 1658.84566473988408 | 0 | 0 |  |  | 158 | 118.154115586690017513134851138353765324 |  | 0 | 52448 | 26642.1925381897763458493870402802101576 | 64180.9604739681808175131348511383537653 | 0 | 1 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | ICE FELL FROM THE ROOF OF THE BUILDING ONTO THE GAS METER STAND, SEPARATING THE METER STAND FROM THE BUILDING WALL CAUSING A RELEASE OF GAS. | [154 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING TECHNICAL ANALYST LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | A GAS FIRE OCCURRED AT THE BUILDING WALL OF A STEEL POLE BARN AT MOORE TROSPER CONSTRUCTION COMPANY (4226 KELLER ROAD IN HOLT, MI) ON FEBRUARY 19. RELEASE OF GAS WAS APPARENTLY CAUSED BY FALLING ICE, WHICH DAMAGED THE BUILDING'S GAS METER STAND AND SEPARATED IT FROM THE BUILDING WALL. THE SOURCE OF IGNITION IS BELIEVED TO BE A GAS FURNACE ON THE INTERIOR SIDE OF THE WALL WHERE THE FIRE OCCURRED. ADJACENT TO THE GAS SERVICE/METER WAS A LARGE AIR INTAKE TO SUPPLY OUTSIDE AIR TO THE FURNACE. THIS INTAKE DUCT WAS THE APPARENT PATH OF GAS MIGRATION INTO THE FURNACE, WHERE IT WAS IGNITED. GAS WAS SHUTOFF AT THE BRANCH SERVICE CONNECTION (TO 4228 KELLER) BY THE RESPONDING GAS DISTRIBUTION CREW. THE FIRE WAS CONTAINED TO THE SOUTH BUILDING WALL OF THE POLE BARN AT 4226 KELLER, BUT FIRE DAMAGE OCCURRED BOTH INSIDE AND OUTSIDE THE BUILDING. INSIDE WATER DAMAGE FROM FIRE SUPPRESSION ACTIVITIES CAUSED FURTHER PROPERTY DAMAGE TO THE BUILDING. KELLER ROAD WAS BLOCKED OFF BY THE RESPONDING FIRE DEPARTMENT. THIS INCIDENT RECEIVED SIGNIFICANT ATTENTION FROM LOCAL TV AND PRINT MEDIA.
2025-03-31 10:13 | NO | NO | NO | 20140026 | 15828 | 2014-03-24 18:48 | SUPPLEMENTAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2014-02-22 17:26 |  |  | 2014 | S. CAMAS BEHIND WAPATO IRRIGATION | WAPATO | YAKIMA | WA | 98951 | 46.4335 | -120.414 | [9 empty] | 2014-02-28 18:21 | 1075436 |  | NATURAL GAS |  | 4823.75 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-02-22 17:26 |  |  |  | 2014-02-22 17:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1966 | [8 empty] | STEEL |  |  |  | 0.237 | [6 empty] | LEAK |  |  | OTHER | DEBRIS IN REGULATOR | [5 empty] | CLASS 2 LOCATION | 0 | 0 | 0 | 0 | 290 | 355.2919075144508 | 0 | 0 |  |  | 30388 | 22724.4763572679509632224168126094570928 |  | 0 | 30678 | 21168.622355735973501716287215411558669 | 23079.7682647824017632224168126094570928 | 0 | 0 | 0 |  |  |  |  | 64 | 56 | 60 |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | KEVIN MCCALLUM | PIPELINE SAFETY SPECIALIST | kevin.mccallum@cngc.com | 5097365542 | 5094578112 |  |  |  | TINA BEACH | MANAGER STANDARDS AND COMPLIANCE | 5097344576 | tina.beach@cngc.com | DEBRIS, METAL SHAVINGS FLOWING DOWNSTREAM FROM THE PIPELINE BUILT UP IN THE REGULATOR BOOT CAUSING IT TO MALFUNCTION.
2025-03-31 10:13 | NO | YES | NO | 20140027 | 16208 | 2014-03-27 12:48 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2014-02-28 22:00 |  |  | 2014 | 2754 WILDER LANE | WATERFORD | OAKLAND | MI | 48329-9998 | 42.6785 | -83.3899 | [9 empty] | 2014-03-07 15:18 | 1076019 |  | NATURAL GAS |  | 83 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-02-28 22:02 |  |  |  | 2014-02-28 22:49 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 53 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1955 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 110000 | 134765.8959537572 | 2188 | 2680.61618497109776 | 392 | 480.25664739884384 | 0 | 0 |  |  | 395 | 295.38528896672504378283712784588441331 |  | 0 | 112975 | 57398.379707709505924623467600700525394 | 138222.1540750938666437828371278458844133 | 0 | 0 | 1 |  |  |  |  | 58 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2013-11-18 | NO | [12 empty] | YES | YES | CITY STREET | [12 empty] | UTILITY | UNKNOWN/OTHER | WATER | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER |  |  | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 571-788-0509 |  |  |  |  | AMANDA L. WARD | GAS REGULATORY SERVICES LEAD | 517-545-8746 | amanda.ward@cmsenergy | CONSUMERS ENERGY'S FIRST RESPONDER ARRIVED ON SITE AT 2754 WILDER LANE IN WATERFORD, MI AT 10:49 PM, FEBRUARY 28, 2014, TO RESPOND TO A HOUSEFIRE INCIDENT. PIN BAR TESTING WAS PERFORMED AT THE NORTH SIDE OF THE HOUSE NEAR THE METER, WHERE 15% GAS READS WERE FOUND. ADDITIONAL BAR TESTING REVEALED SUSTAINED 95% GAS READS AT THE SOUTHWEST CORNER OF THE HOUSE AND 100% GAS READS APPROXIMATELY 45 FEET WEST OF THE HOUSE NEAR THE ROAD. A STRONG GAS ODOR WAS EVIDENT IN THIS LOCATION. FIRST RESPONDERS THEN TOOK GAS READINGS INSIDE THE BASEMENT AFTER BEING ESCORTED IN BY THE FIRE MARSHALL. BAR TESTING AT ADJACENT HOUSES (SOUTH AND WEST OF 2754 WILDER) PRODUCED NO GAS READS. AT 1:42 AM ON MARCH 1, A GAS DISTRIBUTION CREW ARRIVED AND EXPOSED THE 2 INCH STEEL MAIN IN FRONT OF (WEST OF) 2754 WILDER. THE MAIN WAS BENT, CRACKED AND LEAKING. THE CREW OPENED UP THE HOLE TO VENT THE BLOWING GAS. A FROST BALL ON THE LEAK WAS KNOCKED OFF AT 5:45 AM, AT WHICH POINT THE GAS BEGAN BLOWING. AT 9:20 AM, A 2" PLIDCO REPAIR SLEEVE, WHICH STOPPED THE LEAK AND REPAIRED THE MAIN. INVESTIGATION CONCLUDED THE APPARENT CAUSE OF THE MAIN LEAK WAS DAMAGE DURING INSTALLATION OF A WATER MAIN; THE EXACT TIME PERIOD OF THE WATER MAIN INSTALLATION IS UNKNOWN. THIS CONCLUSION IS BASED ON THE OBSERVED DAMAGE AND PROXIMITY OF THE WATER MAIN. THE LOCATION OF THE MAIN LEAK WAS APPROXIMATELY 45 FEET FROM THE SOUTHWEST CORNER OF THE HOUSE. A SEARCH OF MISS DIG STAKING REQUESTS FOR THIS LOCATION DID NOT YIELD ANY RECENT STAKING TICKETS WITHIN THE LAST 15 MONTHS. THE ORIGIN OF THE HOUSEFIRE WAS APPARENTLY THE BASEMENT OF THE HOME. ALTHOUGH AN ON-SCENE INVESTIGATOR REPRESENTING THE HOMEOWNER'S INSURANCE COMPANY (STATE FARM) INDICATED THAT THE GAS LEAK MAY HAVE CAUSED THE FIRE, FOLLOW-UP INVESTIGATION BY CONSUMERS ENERGY INDICATES THAT THIS SCENARIO IS UNLIKELY. THERE WAS NO EVIDENCE OF AN EXPLOSION OR INDEED IGNITION OF GAS IN THE HOME, AND WHILE THERE WERE EXTREMELY LOW LEVELS OF GAS DETECTED IN THE BASEMENT BY FIRST RESPONDERS (0.16% GAS READS, OR 4% LEL), THIS SEEMS TO HAVE OCCURRED AS A RESULT OF ALL DOORS AND WINDOWS (INCLUDING THOSE IN THE BASEMENT) BEING OPENED BY THE FIRE DEPARTMENT, ALLOWING GAS TO ENTER THE HOME FROM OUTSIDE. THERE WERE NO APPARENT CRACKS OR HOLES IN THE BASEMENT WALL WHICH WOULD OTHERWISE PROVIDE A PATH OF MIGRATION INTO THE HOME, AND NO LEAKS WERE FOUND ON THE METER OR THE STEEL GAS SERVICE TO THE HOME. FURTHERMORE, THE MAJORITY OF FIRE DAMAGE WAS SOME DISTANCE FROM THE NORTHWEST SIDE OF THE BASEMENT (THE SIDE CLOSEST TO THE GAS FACILITIES) THE FIRE DEPARTMENT CHIEF ON SITE WAS ULTIMATELY UNABLE TO COME TO A DETERMINATION ON THE CAUSE OF THE HOUSEFIRE. DUE TO THE LACK OF CERTAINTY ABOUT THE SOURCE OF FIRE, AS WELL AS PROPERTY DAMAGE WITHIN THE HOME (DAMAGES TO APPLIANCES AND SMOKE DAMAGE) LIKELY EXCEEDING $50,000, THIS INCIDENT WAS REPORTED TO THE NATIONAL RESPONSE CENTER. DAMAGE ESTIMATES FROM THE FIRE OBTAINED FROM VARIOUS INVESTIGATORS RANGE FROM APPROXIMATELY $50,000 TO $110,000; INSURANCE COMPANY REPRESENTATIVES STATED THAT THE HOME WAS INSURED TO A VALUE OF $160,000. INVESTIGATION INTO THE CAUSE OF THE FIRE WERE INCONCLUSIVE AND REPORTED AS SUCH ON THE 30-DAY PHMSA REPORT ORIGINALLY SUBMITTED ON MARCH 27, 2014. SUBSEQUENT SPECULATION BY AN INSURANCE COMPANY INVESTIGATOR (WITHOUT PERFORMING ANY INVESTIGATION) WAS THAT THE CAUSE OF THE FIRE WAS NATURAL GAS MIGRATION FROM AN EXTERNAL NATURAL GAS LEAK (CAUSED BY THE INSTALLATION OF A WATER MAIN). THE SPECULATION OF THE INSURANCE COMPANY INVESTIGATOR WAS INCORPORATED INTO THE WATERFORD REGIONAL FIRE DEPARTMENT'S REPORT. DUE TO THE COMPLETE DESTRUCTION OF THE SCENE BY THE FIRE DEPARTMENT, NO ACTUAL INVESTIGATION WAS POSSIBLE AND NO LEGITIMATE CONCLUSIONS CAN BE REACHED.
2025-03-31 10:13 | NO | YES | NO | 20140028 | 15869 | 2014-04-02 21:07 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-03-03 11:15 |  |  | 2014 | GUADALUPE STREET AT 3RD AVE. | CARMEL | MONTEREY | CA | 93923 | 36.5592 | -121.9168 | [9 empty] | 2014-03-03 13:30 | 1075638 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | YES | 1 | 2014-03-03 11:25 |  |  |  | 2014-03-03 11:35 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 1.25 | ASTM D2513 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  |  | 2406 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 300000 | 367543.352601156 | 2000 | 2450.28901734104 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 302000 | 153240.269749518344 | 369993.64161849704 | 0 | 0 | 1 |  |  |  |  | 48 | 48 | 52 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 5 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | DURING STEEL TAPPING OPERATION, CREW UNKNOWINGLY TAPPED INTO INSERTED PLASTIC CAUSING RELEASE OF GAS. |  |  |  | YES | INADEQUATE VERIFICATION OF SYSTEM STATUS AND CONFIGURATION WHEN PERFORMING WORK ON A LIVE LINE. | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | LAWRENCE KANG | COMPLIANCE ANALYST | lxkw@pge.com | 925-328-5760 |  |  |  |  | CHRISTIANE MASON | MANAGER REGULATORY COMPLIANCE | 925-328-5795 | c6mw@pge.com | AT APPROXIMATELY 1115 HOURS ON MARCH 3, 2014, A NATURAL GAS EXPLOSION CAUSED MAJOR DAMAGE TO A HOUSE AT GUADALUPE STREET AND 3RD AVE. SW IN CARMEL. A PACIFIC GAS & ELECTRIC (PG&E) CONSTRUCTION CREW TAPPED INTO A 2-INCH DIAMETER STEEL MAIN AND INADVERTENTLY TAPPED THROUGH THE 11/4-INCH DIAMETER PLASTIC MAIN INSERTED IN THE 2-INCH STEEL MAIN. THE CREW WAS NOT AWARE THAT THE 11/4-INCH DIAMETER PLASTIC MAIN HAD PREVIOUSLY BEEN INSERTED INTO THE 2-INCH DIAMETER STEEL LINE. THE CAUSAL EVALUATION OF THE INCIDENT PERFORMED BY A THIRD PARTY INVESTIGATOR DETERMINED THE CAUSE OF THE EXPLOSION TO BE "INADEQUATE VERIFICATION OF SYSTEM STATUS AND CONFIGURATION WHEN PERFORMING WORK ON A LIVE LINE." PG&E HAS DETERMINED THAT GAS MOST LIKELY ESCAPED FROM THE 11/4-INCH DIAMETER PLASTIC MAIN AND MIGRATED INTO A SEPARATED SEWER LATERAL THAT PROVIDED A PATH INTO THE HOUSE. NO ONE WAS IN THE HOUSE AT THE TIME OF THE EXPLOSION. A PG&E GAS SERVICE REPRESENTATIVE WAS ON SITE AT 1135 HOURS. PG&E REPAIR CREWS WERE ON SITE AT 1138 HOURS. THE HOUSE WAS NOT OCCUPIED AT THE TIME OF THE EXPLOSION, AND THERE WERE NO INJURIES OR FATALITIES. THE FIRE DEPARTMENT EVACUATED THE HOMES IN A 1-BLOCK RADIUS. DEBRIS FROM THE EXPLOSION FELL ONTO THE ROOF OF A NEIGHBORING HOUSE, AND GAS SERVICE TO THAT HOUSE WAS SHUT OFF AS A PRECAUTION. THE FLOW OF GAS WAS STOPPED AT 1145 HOURS BY SQUEEZING THE MAIN AT TWO LOCATIONS. THE REPAIR CREW ALSO DUG UP AND SQUEEZED THE SERVICE LINE TO THE DAMAGED HOUSE. THE GAS MAIN WAS THEN CAPPED AT 1209 HOURS. THIS INCIDENT WAS REPORTED TO THE DOT AND THE CALIFORNIA PUBLIC UTILITIES COMMISSION DUE TO PROPERTY DAMAGES EXCEEDING $50,000. PG&E CONDUCTED A SPECIAL LEAK SURVEY AFTER THE INCIDENT, AND ONE LEAK ON A SERVICE VALVE IN THE VICINITY WAS FOUND AND REPAIRED. SERVICE TO THE NEIGHBORING HOUSE WAS RESTORED ON 3/11/2014 BY THE HOMEOWNER'S CONTRACTOR WITHOUT NOTIFICATION TO PG&E, HOWEVER, AFTER THE OCCUPANTS INFORMED PG&E ON 3/12/2014, PG&E PERFORMED A SERVICE SHUT DOWN AND RESTART ON 3/12/2014, INCLUDING A PRESSURE CHECK, A SOAP TEST, AND A SAFETY CHECK OF ALL THE GAS APPLIANCES IN THE HOME.
2025-03-31 10:13 | NO | YES | YES | 20140029 | 15842 | 2014-04-03 16:18 | ORIGINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2014-03-04 12:52 |  |  | 2014 | 28 CROCKETT LANE | EWING | MERCER | NJ | 08628 | 40.2753 | -74.833 | [9 empty] | 2014-03-04 13:04 | 1075764 |  | NATURAL GAS |  | 11 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 7 | 3 | 0 | 0 | 0 | 10 | YES |  |  |  |  | YES |  | 2014-03-04 11:39 |  |  |  | 2014-03-04 12:03 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1989 | [5 empty] | 2 | ASTM D2513 | DRISCO 8000 | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | OTHER | [8 empty] | DAMAGE TO FACILITY | CLASS 3 LOCATION | 15000000 | 18377167.6300578 | 15000 | 18377.1676300578 | 40000 | 49005.7803468208 | 30000 | 36754.3352601156 | ELECTRIC AND COMMUNICATION FACILITIES |  | 2500 | 1869.527145359019264448336252189141856392 |  | 0 | 15087500 | 7656131.63786616653243432574430823117338 | 18483174.44044015321926444833625218914186 | 0 | 0 | 41 |  |  |  |  | 11 | 12 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 13 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | DIRECTIONAL DRILLING | ELECTRIC | YES | 140630026 |  |  | UTILITY OWNER | YES | YES |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | CURRENTLY STILL UNDER INVESTIGATION | [169 empty] | FRANKY CORIANO | PRINCIPAL REGULATORY SPECIALIST | franky.coriano@pseg.com | 609-421-8025 |  |  |  |  | ALEXANDER STERN | ASSOCIATE GENERAL REG COUNSEL | 973-430-5754 | alexander.stern@pseg.com | ON TUESDAY, MARCH 4, 2014, AT 11:39 AM, THE COMPANY RECEIVED A REPORT BY HENKELS & MCCOY THAT THEY DAMAGED THE GAS FACILITIES AT 28 CROCKETT LANE, EWING, NJ. COMPANY PERSONNEL ADVISED HENKELS & MCCOY TO CONTACT THE EMERGENCY TELEPHONE NUMBERS, AND DISPATCHED PERSONNEL TO THE SCENE. UPON ARRIVAL AT THE SCENE, THE COMPANY GAS DISTRIBUTION REPAIR CREW BEGAN TO HAND DIG TO LOCATE THE DAMAGE IN FRONT OF THE AFOREMENTIONED ADDRESS WHEN AN EXPLOSION OCCURRED AT 12:52 PM FOLLOWED BY AN IGNITION AND FIRE. A NUMBER OF DWELLINGS ON CROCKETT LANE AND PIONEER COURT WERE DESTROYED OR HEAVILY DAMAGED. MS. LINDA CERRITELLI WAS IN HER RESIDENCE (28 CROCKETT LANE) AT THE TIME OF THE EXPLOSION AND WAS KILLED IN THE INCIDENT. THERE WERE SEVEN PUBLIC SERVICE ELECTRIC & GAS EMPLOYEES AND THREE HENKELS & MCCOY EMPLOYEES THAT SUFFERED NON-LIFE THREATENING INJURIES THAT REQUIRED MEDICAL ATTENTION AND/OR HOSPITALIZATION.
2025-03-31 10:13 | NO | YES | NO | 20140030 | 15844 | 2014-04-09 10:50 | SUPPLEMENTAL FINAL | 2288 | CHATTANOOGA GAS CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2014-03-12 10:08 |  |  | 2014 | 100 PATTEN CHAPEL ROAD | CHATTANOOGA | HAMILTON | TN | 37419 | 35.0292 | -85.3627 | [9 empty] | 2014-03-12 11:40 | 1076471 |  | NATURAL GAS |  | 323.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 15 | 2014-03-12 10:08 |  |  |  | 2014-03-12 10:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1989 | [5 empty] | 2.375 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 250000 | 306286.12716763 | 4000 | 4900.57803468208 | 200 | 245.028901734104 | 0 | 0 |  |  | 210 | 157.040280210157618213660245183887915937 |  | 0 | 254410 | 129130.9554612973550444833625218914185639 | 311588.7743842563416182136602451838879159 | 1 | 0 | 0 |  |  |  |  | 50 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | WATER | YES | 140586227 |  |  | CONTRACT LOCATOR | YES | YES | 6 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@aglresources.com | (404) 584-3733 | (404) 584-4708 |  |  |  | RICHARD LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@aglresources.com | A 2-INCH PLASTIC NATURAL GAS MAIN WAS SEVERED BY A BACKHOE DURING EXCAVATION TO REPLACE A FIRE HYDRANT. THE ESCAPING GAS IGNITED BURNING THE BACKHOE, A DUMP TRUCK, THE ROOF ON THE BUILDING AT 306 BROWN FERRY ROAD AND POWER LINES ABOVE THE INCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20140031 | 16185 | 2014-04-11 14:33 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2014-03-12 09:31 |  |  | 2014 | 1644/1646 PARK AVENUE | NEW YORK | NEW YORK | NY | 10035-4645 | 40.7997 | -73.9434 | [9 empty] | 2014-03-12 10:48 | 1076464 |  | NATURAL GAS |  | 30 |  | YES | 0 | 0 | 0 | 0 | 8 | 8 | YES | 0 | 0 | 0 | 0 | 48 | 48 | YES |  |  |  |  | YES | 100 | 2014-03-12 09:39 |  |  |  | 2014-03-12 09:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2011 | [5 empty] | 2 | ASTM D2513 | PERFORMANCE PIPE, A DIVISION OF CHEVRON | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 1000000 | 1225144.50867052 | 250000 | 306286.12716763 | 200000 | 245028.901734104 | 1510000 | 1849968.2080924852 | INVESTIGATION, DOCUMENTATION, SUPPORT STAFF, OTHER DEPARTMENTS INVOLVED. |  | 200 | 149.562171628721541155866900175131348511 |  | 0 | 2960200 | 1502095.96455530511299474605954465849387 | 3626577.30783636792154115586690017513135 | 4 | 0 | 98 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SECTION OF THE DISTRIBUTION SYSTEM INVOLVED IN THIS INCIDENT IS NOT MONITORED BY THE CONTROLLER. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [56 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | OTHER |  |  |  | EARTH MOVEMENT CAUSED BY A SEWER BREACH WHICH AFFECTED SUBSURFACE FACILITIES, INCLUDING A CAST IRON WATER MAIN AND HDPE GAS FACILITIES. | NO | [218 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-597-5463 |  |  |  | VICTOR DADARIO | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | dadariov@coned.com | DESCRIPTION OF INCIDENT: ON MARCH 12, 2014 AT APPROXIMATELY 09:31 TWO MULTI-USE, FIVE-STORY BUILDINGS AT 1644 AND 1646 PARK AVENUE (WEST SIDE OF PARK AVENUE BETWEEN E. 116TH AND E. 117TH STREETS), NEW YORK, NY, WERE DESTROYED BY AN EXPLOSION AND FIRE. EIGHT FATALITIES AND APPROXIMATELY 48 REPORTED INJURIES RESULTED FROM THE EXPLOSION AND COLLAPSE. CON EDISON'S RESPONSE AND ACTION: AT 09:13 ON MARCH 12, 2014, CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A TELEPHONE REPORT FROM CON EDISON'S CALL CENTER OF AN INSIDE AND OUTSIDE GAS ODOR AT 1652 PARK AVENUE. AT 09:15, GERC DISPATCHED A GAS DISTRIBUTION SERVICES (GDS) MECHANIC TO INVESTIGATE THE ODOR REPORT. AT 09:34, GERC CONFIRMED WITH NEW YORK CITY FIRE DEPARTMENT (FDNY) A SCANNER REPORT OF AN EXPLOSION AND BUILDING COLLAPSE AT E. 114TH ST. AND PARK AVENUE (THE E. 114TH ST. LOCATION WAS INCORRECT). AT 09:38, THE GDS MECHANIC ENROUTE TO 1652 PARK AVENUE REPORTED OBSERVING SMOKE, FLAMES, AND HEAVY ACTIVITY ON PARK AVENUE SOUTH OF E. 119TH STREET. GERC DISPATCHED ADDITIONAL CON EDISON PERSONNEL TO THE LOCATION AT APPROXIMATELY 09:38. CON EDISON PERSONNEL FIRST ARRIVED AT THE LOCATION AT 09:40 AND CONFIRMED THE EXPLOSION AND COLLAPSE OF TWO BUILDINGS ON PARK AVENUE BETWEEN E. 116TH ST. AND E. 117TH ST. NUMEROUS CON EDISON PERSONNEL, INCLUDING GDS MECHANICS, CONSTRUCTION CREWS, SUPERVISORS, PLANNERS, AND MANAGERS RESPONDED TO THE SCENE OF THE BUILDING COLLAPSE. CON EDISON PERSONNEL CONDUCTED AN INVESTIGATION FOR GAS MIGRATION THAT INCLUDED ADJACENT BUILDINGS AND ACCESSIBLE SUBSURFACE STRUCTURES IN THE AREA. CON EDISON PERSONNEL IDENTIFIED THREE (3) FIRE BANK LOCATIONS FOR EXCAVATION TO STOP THE FLOW OF GAS ON THE WEST SIDE OF PARK AVENUE BETWEEN E 116TH ST AND E 117TH ST. AT APPROXIMATELY 13:44, A STREET COLLAPSE AND AN APPARENT WATER MAIN BREAK WERE OBSERVED IN THE ROADWAY IN FRONT OF 1644 AND 1646 PARK AVENUE. AT THE TIME OF THE STREET COLLAPSE, THERE WAS A STRONG ODOR OF GAS IN THE AREA. FIRE BANK EXCAVATIONS WERE COMPLETED AND STOPPERS WERE INSTALLED TO ISOLATE THE GAS SUPPLY TO THE AFFECTED AREA AT APPROXIMATELY 13:44, AND THE ODOR OF GAS DISSIPATED. THE 8" LOW PRESSURE POLYETHYLENE / 8" LOW PRESSURE CAST IRON MAIN SUPPLYING (7) SERVICES ON THE WEST SIDE OF PARK AVENUE AND ON THE NORTH SIDE OF E. 116TH ST., BETWEEN PARK AVENUE AND MADISON AVENUE, WERE ISOLATED. INVESTIGATION: FOLLOWING THE ACCIDENT, THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB) TOOK CONTROL OF THE INCIDENT SITE AND BEGAN ITS INVESTIGATION. THE CITY OF NEW YORK, THE NEW YORK STATE PUBLIC SERVICE COMMISSION, THE PIPELINE AND HAZARDOUS MATERIALS SAFETY ADMINISTRATION, CONSOLIDATED EDISON COMPANY OF NEW YORK, AND GEORG FISCHER CENTRAL PLASTIC WERE PARTIES TO THE INVESTIGATION. DURING THE COURSE OF THE NTSB INVESTIGATION, CON EDISON PROVIDED A PARTY SUBMISSION DESCRIBING THE PROBABLE CAUSE OF THE ACCIDENT AS A BREACH IN THE SEWER SYSTEM WHICH CAUSED SOIL EROSION AFFECTING SUBSURFACE UTILITIES, INCLUDING A CAST IRON WATER MAIN AND HDPE GAS FACILITIES, AND LIKELY RESULTED IN AN IMPACT BY FALLING ROADWAY PAVEMENT WHICH CRACKED THE SERVICE TEE TO 1642 PARK AVENUE. IN ITS ACCIDENT REPORT ADOPTED ON JUNE 9, 2015, THE NTSB DETERMINED THAT THE PROBABLE CAUSE OF THE ACCIDENT WAS (1) THE FAILURE OF THE DEFECTIVE FUSION JOINT AT THE SERVICE TEE, INSTALLED BY CONSOLIDATED EDISON COMPANY OF NEW YORK, INC., IN 2011, THAT ALLOWED NATURAL GAS TO LEAK FROM THE GAS MAIN AND MIGRATE INTO THE BUILDING WHERE IT IGNITED AND (2) A BREACH IN THE SEWER LINE THAT WENT UNREPAIRED BY THE NEW YORK CITY DEPARTMENT OF ENVIRONMENTAL PROTECTION SINCE AT LEAST 2006 THAT ALLOWED GROUNDWATER AND SOIL TO FLOW INTO THE SEWER, RESULTING IN A LOSS OF SUPPORT FOR THE GAS MAIN, WHICH CAUSED THE LINE TO SAG AND OVERSTRESSED THE DEFECTIVE FUSION JOINT.
2025-03-31 10:13 | NO | NO | NO | 20140035 | 16118 | 2014-04-21 12:42 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2014-03-05 23:21 |  |  | 2014 | BONNEVILLE AVENUE AND GRAND CENTRAL PARKWAY | LAS VEGAS | CLARK COUNTY | NV | 89106 | 36.1666 | -115.1556 | [9 empty] | 2014-03-21 14:41 | 1077348 |  | NATURAL GAS |  | 1435 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 12 | 2014-03-06 00:02 |  |  |  | 2014-03-06 00:02 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 126 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2007 | [5 empty] | 16 | API 5L | NMDA | STEEL |  | OTHER | ERW | 0.375 | [6 empty] | MECHANICAL PUNCTURE | 1.1 | 3.5 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 21470 | 26303.8526011560644 | 42944 | 52612.60578034681088 | 0 | 0 |  |  | 8235 | 6158.222416812609457092819614711033274956 |  | 0 | 72649 | 38381.5465376971155666690017513134851138 | 85074.680798315484737092819614711033275 | 2 | 0 | 0 |  |  |  |  | 228 | 270 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 12025 |  |  | CONTRACT LOCATOR | YES | YES | 11 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | YVONNE BRODEUR | ENGINEERING TECHNICIAN | yvonne.brodeur@swgas.com | 702-365-2149 | 702-221-4116 |  |  |  | THOMAS CARDIN | DIRECTOR OF GAS OPERATIONS | 702-365-2028 | thomas.cardin@swgas.com | ON MARCH 6, 2014, A TEAM FISHEL EMPLOYEE BORED INTO A SIXTEEN-INCH STEEL HIGH-PRESSURE DISTRIBUTION GAS MAIN WHILE INSTALLING A FIBEROPTIC LINE IN THE INTERSECTION OF BONNEVILLE AVENUE AND GRAND CENTRAL PARKWAY IN LAS VEGAS, NEVADA. TEAM FISHEL HAD A VALID DIG TICKET AND SOUTHWEST GAS CORPORATION'S CONTRACT LINE LOCATOR HAD LOCATED THE LINE. AS PART OF THE LINE LOCATE PROCESS, TEAM FISHEL WAS INFORMED THAT A HIGH-PRESSURE STANDBY WOULD BE REQUIRED DURING THE BORING OPERATION. TEAM FISHEL FAILED TO MEET WITH THE SOUTHWEST GAS CORPORATION REPRESENTATIVE AS IT HAD REQUESTED (NRS 455.110(B)(1), SEE ALSO NAC 455.145(1)(B)(3)); FAILED TO EXPOSE THE FACILITY BEFORE COMMENCING BORING OPERATIONS (NRS 455.137(1) & NAC 455.150(2)); AND FAILED TO NOTIFY SOUTHWEST GAS CORPORATION TO REQUEST ADDITIONAL INFORMATION WHEN THEY REALIZED THAT THEY COULD NOT EXPOSE THE FACILITY (NRS 455.137(3); NAC 455.150(3)). NO DEATH OR INJURY RESULTED FROM THE INCIDENT. ALTHOUGH THE INCIDENT INITIALLY DID NOT MEET PHMSA/DOT NOTIFICATION CRITERIA, ON MARCH 21, 2014, SOUTHWEST GAS CORPORATION ESTIMATED THE COSTS ASSOCIATED WITH THE INCIDENT WOULD LIKELY MEET THE CRITERIA, AND IMMEDIATELY NOTIFIED THE NATIONAL RESPONSE CENTER. SUPPLEMENTAL: SUBSEQUENT INVESTIGATION DETERMINED THAT THE 16-INCH PIPELINE WAS NOT MARKED CORRECTLY.
2025-03-31 10:13 | NO | YES | NO | 20140036 | 16156 | 2014-04-25 14:15 | SUPPLEMENTAL FINAL | 11032 | LACLEDE GAS CO | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2014-03-22 11:25 |  |  | 2014 | 321 GREYCLIFF BLUFF DR | ST. LOUIS | ST. LOUIS COUNTY | MO | 63129 | 38.4406 | -90.3005 | [9 empty] | 2014-03-22 13:19 | 1077416 |  | NATURAL GAS |  | 41 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2014-03-22 11:25 |  |  |  | 2014-03-22 11:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2003 | [8 empty] | STEEL |  | OTHER | ERW | 0.113 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 3 LOCATION | 600000 | 735086.705202312 | 2000 | 2450.28901734104 | 2060 | 2523.7976878612712 | 0 | 0 |  |  | 215 | 160.77933450087565674255691768826619965 |  | 0 | 604275 | 306659.7148834651827893520140105078809107 | 740221.5712420151868567425569176882661997 | 0 | 0 | 1 |  |  |  |  | 19 | 19 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO OPERATIONAL PARAMETERS WERE EXCEEDED | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MARK LAUBER | MANAGER PIPELINE SAFETY COMPLIANCE | mark.lauber@thelacledegroup.com | 314-658-5413 | 314-535-9414 |  |  |  | CRAIG R. HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES | 314-658-5410 | craig.hoeferlin@thelacledegroup.com | PROPERTY OWNER DROVE HIS CAR PAST THE END OF HIS DRIVEWAY AND HIT HIS GAS GENERATOR THAT WAS HARD PIPED ABOVE GROUND. THE RESULTING FORCE FROM THE COLLISION PULLING ON THE METER SET BROKE THE METER SET PIPING. THE ESCAPING GAS FROM THE BROKEN METER SET PIPING IGNITED, CATCHING THE PROPERTY OWNER'S HOUSE ON FIRE.
2025-03-31 10:13 | NO | NO | NO | 20140037 | 15856 | 2014-05-05 15:43 | ORIGINAL | 38997 | CORNING INCORPORATED | ONE RIVERFRONT PLAZA | CORNING | NY | 14831 | 2014-05-02 11:30 |  |  | 2014 | 1 MUSEUM WAY | CORNING | STEUBEN | NY | 14830 | 42.1504 | -77.0551 | [12 empty] | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 95 | 2014-05-02 11:58 |  |  |  | 2014-05-02 12:20 |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1992 | [5 empty] | 3 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | RUPTURE |  |  |  |  | LONGITUDINAL |  | 8 | 2 |  | CLASS 1 LOCATION | 0 | 0 | 1000 | 1225.14450867052 | 0 | 0 | 0 | 0 |  |  | 5 | 3.73905429071803852889667250437828371278 |  | 0 | 1005 | 510.87695588647182486865148861646234676 | 1228.883562961238038528896672504378283713 | 1 | 0 | 0 |  |  |  |  | 28 | 28 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IMMEDIATE NOTIFICATION OF THE INCIDENT AND ALMOST IMMEDIATE ISOLATION OF GAS FLOW AT A NEARBY VALVE. IT IS UNLIKELY THE SCADA SYSTEM WOULD HAVE DETECTED THE INCIDENT | [12 empty] | NO |  |  | YES | 2 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES |  |  | YES | [6 empty] | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SITE DEVELOPMENT | NO |  |  |  | UTILITY OWNER | YES | YES | 4 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | JOHN D SHIRLEY | FACILITIES SUPERVISOR | shirleyjd@corning.com | 607-974-3599 |  |  |  |  | JOHN D. SHIRLEY | FACILITIES SUPERVISOR | 607-974-3599 | shirleyjd@corning.com | ON MAY 2, 2014 AT APPROXIMATELY 11:30 AM, WHILE PERFORMING SITE WORK FOR THE CORNING MUSEUM OF GLASS EXPANSION PROJECT, THE CONTRACTOR WAS ATTEMPTING TO REMOVE A DRAINAGE CATCH BASIN IN THE VICINITY OF THE 3" HPDE SERVICE PIPELINE. THE UTILITY LOCATIONS HAD BEEN MAPPED BY A THIRD PARTY EARLY IN THE PROJECT. THE LINE WAS MAPPED AND MARKED IN A STRAIGHT LINE BUT IN ACTUALITY THE LINE TAKES AN OFFSET SO IT ENDED UP BEING IN THE PATH OF EXCAVATION. THE LINE WAS PUNCTURED BY A TOOTH OF THE EXCAVATOR BUCKET. THE RUPTURE WAS APPROXIMATELY 2"X8". THE SITE WHERE WORK WAS TAKING PLACE WAS APPROXIMATELY 100 FT FROM A SHUT OFF VALVE AND A VALVE WRENCH WAS ON SITE FOR PRECAUTIONARY MEASURES. THE JOB SITE WAS EVACUATED (APPROX. 95 CONSTRUCTION WORKERS) WHILE THE GAS SERVICE WAS SHUT OFF. CORNING NATURAL GAS (CORNING INC'S O&M CONTRACTOR) WAS CALLED TO ASSESS THE DAMAGE AND MAKE THE REPAIRS. THE CORNING MUSEUM OF GLASS' HOT GLASS SHOW AND CAFÉ WERE SHUT DOWN AS A RESULT OF THE GAS OUTAGE. THE MUSEUM REMAINED OPEN FOR BUSINESS THROUGHOUT THE OUTAGE. REPAIRS WERE MADE AND GAS SERVICE WAS RESTORED AT 15:45. BOTH THE EQUIPMENT OPERATOR AND SITE SUPERINTENDENT WERE IMMEDIATELY DRUG AND ALCOHOL TESTED FOLLOWING THE INCIDENT; BOTH TESTS CAME BACK NEGATIVE. INSUFFICIENT LINE LOCATING WAS DETERMINED TO BE THE ROOT CAUSE. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT
2025-03-31 10:13 | NO | YES | YES | 20140038 | 16078 | 2014-05-12 21:22 | SUPPLEMENTAL FINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2014-04-22 03:43 |  |  | 2014 | 7775 SMITHS CREEK ROAD | WALES TOWNSHIP | ST. CLAIR | MI | 48027 | 42.9166 | -82.6313 | [9 empty] | 2014-04-22 12:30 | 1080468 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 2 | 0 | 0 | 2 | YES |  |  |  |  | NO | 1 | 2014-04-22 03:43 |  |  |  | 2014-04-22 04:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2000 | [8 empty] | OTHER | OUTSIDE METER/REGULATOR SET | [9 empty] | LEAK |  |  | OTHER | ELECTRICAL ARCING | [5 empty] | CLASS 2 LOCATION | 50000 | 61257.225433526 | 0 | 0 | 2827 | 3463.48352601156004 | 0 | 0 |  |  | 76 | 56.83362521891418563922942206654991243433 |  | 0 | 52903 | 26857.9510204184999820035026269702276708 | 64777.5425847564742256392294220665499124 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | STEPHEN MAKOWSKI | MANAGER CODES AND STANDARDS | steve.makowski@semcoenergy.com | 8108874228 | 8108874233 |  |  |  | STEPHEN MAKOWSKI | MANAGER CODES AND STANDARDS | 8108874228 | steve.makowski@semcoenergy.com | TWO FIREFIGHTERS WERE TAKEN TO THE PORT HURON HOSPITAL AFTER FALLING OFF A LADDER WHILE FIGHTING THE BLAZE. BOTH FIREFIGHTERS WERE RELEASED FROM THE HOSPITAL WITH INJURIES THAT WERE NOT DEEMED LIFE THREATENING. SEMCO WAS NOT PROVIDED A COPY OF THE FIRE INVESTIGATORS REPORT FROM THE INSURANCE COMPANY. THE INVESTIGATION RESULTS INDICATED THE CAUSE OF THE FIRE WAS AN ELECTRICAL SURGE. SEMCO DID NOT CREATE AN INTERNAL REPORT RELATED TO THE INCIDENT. SEMCO PARTICIPATED IN THE INVESTIGATION ALONG WITH MPSC SAFETY ENGINEER KYLE FRISKE WHO HAS MADE AN OFFICIAL REQUEST TO OBTAIN THE FIRE INVESTIGATORS REPORT AS PER AN E-MAIL DATED 04/30/15 FROM MICHAEL ROARTY WITH REHMANN FIRE INVESTIGATION.
2025-03-31 10:13 | NO | YES | YES | 20140039 | 16146 | 2014-05-15 13:36 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2014-03-27 20:07 |  |  | 2014 | 19717 FAIRPORT | DETROIT | WAYNE | MI | 48205-1723 | 42.4408 | -82.9917 | [9 empty] | 2014-03-27 21:51 | 1077997 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 6 | 6 | YES |  |  |  |  | YES | 0 | 2014-03-27 20:07 |  |  |  | 2014-03-27 20:26 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2011 | [8 empty] | OTHER | SERVICE VALVE AT OUTSIDE METER MANIFOLD | [9 empty] | OTHER | [8 empty] | LOCKED SERVICE VALVE AT OUTSIDE METER MANIFOLD WAS BROKEN AND VALVE TURNED ON BY AN UNKNOWN PARTY. | CLASS 3 LOCATION | 30000 | 36754.3352601156 | 1188 | 1455.47167630057776 | 2160 | 2646.3121387283232 | 0 | 0 |  |  | 0 | 0 |  | 0 | 33348 | 16921.379190751449456 | 40856.11907514450096 | 0 | 0 | 0 |  |  |  |  | 2 | 2 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [156 empty] | ROBERT FRECKELTON | MANAGER | freckeltonr@dteenergy.com | 313-389-7755 | 313-389-7757 |  |  |  | ROBERT FRECKELTON | MANAGER | 313-389-7755 | freckeltonr@dteenergy.com | AT 20:07, ON THURSDAY, MARCH 27, 2014, DTE GAS COMPANY (DTE GAS) RESPONDED TO A REPORT OF AN EXPLOSION INVOLVING A RESIDENCE AT 19717 FAIRPORT STREET IN DETROIT, WAYNE COUNTY, MI. AT 20:26, DTE SERVICE TECHNICIAN ARRIVED AT THE SITE AND CONFIRMED THE EXPLOSION AND REPORTED THE GAS METER WAS ON FIRE. AT 21:50, DTE GAS SERVICE LINE WAS TESTED FOR LEAKS BETWEEN THE MAIN NEAR THE STREET TO THE METER ASSEMBLY AT THE OUTSIDE BUILDING WALL USING AIR AT A PRESSURE OF 2 PSIG FOR DURATION OF 10 MINUTES. THE SERVICE LINE WAS FOUND TO BE AIR-TIGHT AS A RESULT OF THIS TEST, DEMONSTRATING THE SERVICE LINE WAS NOT LEAKING PRIOR TO THE EXPLOSION. DTE GAS PERFORMED UNDERGROUND LEAK CHECKS OVER THE SERVICE LINES AND THE DISTRIBUTION MAIN IN THE AREA AROUND 19717 FAIRPORT; THERE WERE TRACE INDICATIONS OVER THE MAIN OF 0.5% GAS IN AIR, WHICH IS WELL BELOW THE LOWER EXPLOSIVE LIMIT. THERE WERE NO READINGS ALONG THE SERVICE LINE BETWEEN THE MAIN AND THE RESIDENCE. AS A RESULT OF THE INVESTIGATION, IT WAS DETERMINED THAT THE LOCKED SERVICE VALVE AT THE OUTSIDE METER MANIFOLD WAS BROKEN AND TURNED ON BY AN UNAUTHORIZED PERSON(S). DTE GAS RECORDS INDICATED ON FEBRUARY 18, 2014, THE ELECTRIC AND GAS SERVICE WERE TURNED OFF AT THE REQUEST OF PROPERTY OWNER OF RECORD. ON MARCH 26, 2014, ONLY THE ELECTRIC SERVICE WAS RESTORED AS REQUESTED BY THE PROPERTY OWNER. THERE WERE NO FATALITIES; HOWEVER FOUR ADULTS AND TWO SMALL CHILDREN WERE SERIOUSLY INJURED IN THE EXPLOSION. THE PROPERTY OWNER STATED THERE WAS NO LANDLORD/TENANT AGREEMENT AT THIS LOCATION. THE CAUSE OF THE EXPLOSION IS UNDETERMINED AT THIS TIME AND THE TRACE INDICATIONS WOULD NOT HAVE CAUSED OR CONTRIBUTED TO THE EXPLOSION.
2025-03-31 10:13 | NO | NO | NO | 20140040 | 33432 | 2014-05-16 16:21 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2014-04-17 09:42 |  |  | 2014 | 7806 EAGLE CT. | ALEXANDRIA | FAIRFAX COUNTY | VA | 22306 | 38.7462 | -77.0921 | [9 empty] | 2014-04-17 10:40 | 1079998 |  | NATURAL GAS |  | 1.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 5 | 2014-04-17 09:42 |  |  |  | 2014-04-17 09:49 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1971 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | UNDER INVESTIGATION. | CLASS 3 LOCATION | 0 | 0 | 2000 | 2450.28901734104 | 4000 | 4900.57803468208 | 72000 | 88210.40462427744 | APPROXIMATE VALUE OF THE BUILDINGS DAMAGED BY THE EVENT. |  | 35 | 26.17338003502626970227670753064798598949 |  | 0 | 78035 | 39602.8246256947147740805604203152364273 | 95587.445056335586269702276707530647986 | 0 | 0 | 1 |  |  |  |  | 20 | 20 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 2 | 0 | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | RICHARD FITZPATRICK | DOT PIPELINE SAFETY SUPERVISOR | richardfitzpatrick@washgas.com | 7037505921 |  |  |  |  | STEPHEN PRICE | AVP SAFETY QUALITY SYSTEM PROTECTION | 7037504586 | sprice@washgas.com | WASHINGTON GAS WAS NOTIFIED OF A POSSIBLE EXPLOSION AND FIRE AT 7806 EAGLE CT., ALEXANDRIA, VIRGINIA AT 9:42 AM ON 4/17/2014. UPON ARRIVAL, THE FAIRFAX COUNTY FIRE DEPARTMENT WAS ON SITE AND CONTROLLING THE SCENE. NATURAL GAS APPEARED TO BE RELEASING IN THE GENERAL AREA OF THE GAS METER. THE GAS WAS CONTROLLED BY SQUEEZE-OFF OF THE PLASTIC SERVICE LINE AT 11:08 AM. WASHINGTON GAS PERSONNEL CONDUCTED BAR/TEST IN THE AREA OF THE INCIDENT AND OBSERVED NO EVIDENCE OF GAS MIGRATION. AN ODORANT SAMPLE WAS TAKEN AND THE LEVEL OF ODORANT WAS DETERMINED TO BE ACCEPTABLE. A PRESSURE TEST WAS CONDUCTED ON THE PLASTIC SERVICE LINE FROM THE SQUEEZE-OFF POINT TO THE UPPER END OF THE STEEL SERVICE RISER. THE PRESSURE TEST WAS CONDUCTED AT OPERATING PRESSURE FOR 15 MINUTES. THE SERVICE HELD THE PRESSURE TEST. A FRACTURE WAS OBSERVED AT THE THREADED END OF THE RISER IMMEDIATELY BELOW THE STOPCOCK. FOLLOW-UP ANALYSIS OF THE THREADED END OF THE RISER INDICATED THAT THE FRACTURE OF THE STEEL PIPE WAS CAUSED BY THE APPLICATION OF A SINGLE HIGH LOAD EXCEEDING THE FRACTURE STRENGTH OF THE STEEL. THERE WAS NO INDICATION THAT ENVIRONMENT OR FATIGUE LOADING CONTRIBUTED TO THIS FAILURE. UPON GAINING ACCESS TO THE MOBILE HOME ON 5/5/2014, WASHINGTON GAS CONDUCTED A PRESSURE TEST ON THE REMAINING HOUSE LINES UNDER THE OBSERVATION OF THE FAIRFAX COUNTY FIRE MARSHAL. THE HOUSE LINE TO THE STOVE WAS FRACTURED AND THE STOVE WAS FOUND ON THE GROUND BENEATH THE FLOOR LEVEL OF THE MOBILE HOME. THIS LINE WAS CAPPED TO PERFORM THE PRESSURE TEST. THE TEST WAS CONDUCTED AT 10 INCHES OF WATER COLUMN FOR 13 MINUTES. THE HOUSE LINES HELD THE PRESSURE TEST. THE FRACTURED LINE TO THE STOVE WAS REMOVED FOR ANALYSIS. FAIRFAX COUNTY FM REPORT, IGNITION SOURCE CAN NOT BE DETERMINED BUT IS SUSPECTED AS INVOLVING THE GAS FURNACE. BASED UPON ALL KNOWN INFORMATION, THE CAUSE OF THE INCIDENT IS UNDETERMINED.
2025-03-31 10:13 | NO | NO | NO | 20140041 | 16166 | 2014-05-21 15:44 | SUPPLEMENTAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2014-04-22 13:39 |  |  | 2014 | INTERSECTION: O STREET & NATIONAL AVENUE | BREMERTON | KITSAP | WA | 98312 | 47.5623 | -122.6691 | [9 empty] | 2014-05-07 10:00 | 1082020 |  | NATURAL GAS |  | 138 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-04-22 13:39 |  |  |  | 2014-04-22 14:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 300 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1968 | [5 empty] | 2 | API 5L XTRU COAT PIPE | UNKNOWN | STEEL |  | SEAMLESS | SEAMLESS | 0.154 | [6 empty] | OTHER | [8 empty] | LINE HIT BY CONTRACTOR, 3RD PARTY DAMAGE | CLASS 3 LOCATION | 0 | 0 | 68447 | 83857.46618497108244 | 1494 | 1830.36589595375688 | 0 | 0 |  |  | 1318 | 985.61471103327495621716287215411558669 |  | 0 | 71259 | 36401.081467627704887376532399299474606 | 86673.4467919581142762171628721541155867 | 1 | 0 | 27 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CNGC HAS PROTECTION GUARD THROUGH THE RELIEF SYSTEMS AND ALSO IT WAS CLEAR THE INCIDENT WAS CAUSED BY BORING INTO THE PIPE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | OTHER |  |  | YES | [9 empty] | CONTRACTOR | AUGER | ENGINEERING/SURVEYING | YES | 14093011 |  |  | UTILITY OWNER | NO | YES | 49 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | PATTI CHARTREY | PIPELINE SAFETY SPECIALIST | patti.chartrey@cngc.com | 360-405-4231 | 360-377-2091 |  |  |  | TINA R. BEACH | MANAGER OF STANDARDS AND COMPLIANCE | 206-445-4121 | tina.beach@cngc.com | CONTRACTOR AUGERED INTO 2' STEEL MAIN IN AN AREA WHICH HAD NOT BEEN LOCATED. THE CONTRACTOR DID REQUEST LOCATES, HOWEVER, THE AREA TO BE LOCATED WAS NOT MARKED IN WHITE. (STATE OF WASHINGTON REQUIRES CONTRACTORS TO MARK LOCATE AREA IN WHITE) CNGC LOCATOR MADE PHONE CALL TO THE CONTRACTOR TO DISCUSS THE ACTUAL AREA TO BE LOCATED AND FROM THE DISCUSSION BELIEVED THE CONTRACTOR WOULD NOT BE WORKING NEAR THE 2" STEEL MAIN IN THE EASEMENT.
2025-03-31 10:13 | NO | NO | NO | 20140042 | 15862 | 2014-05-22 14:19 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2014-04-22 09:37 |  |  | 2014 | 8336 N. SAGINAW | MT. MORRIS | GENESEE | MI | 48458-1644 | 43.1286 | -83.6941 | [9 empty] | 2014-04-22 12:16 | 1080467 |  | NATURAL GAS |  | 19.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2014-04-22 09:37 |  |  |  | 2014-04-22 09:51 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 2011 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | OTHER | [8 empty] | PLASTIC RISER SEVERED FROM METER MANIFOLD BY VEHICLE IMPACT. | CLASS 3 LOCATION | 50000 | 61257.225433526 | 2830 | 3467.1589595375716 | 406 | 497.40867052023112 | 0 | 0 |  |  | 93 | 69.54640980735551663747810858143607705779 |  | 0 | 53329 | 27077.2450981781685345569176882661996497 | 65291.3394733911582366374781085814360771 | 1 | 0 | 0 |  |  |  |  | 54 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 |  |  |  |  | TRACY A. GOBLE | MANAGER OF REGULATORY AND COMPLIANCE | 517-768-3187 | tracy.goble@cmsenergy.com | AT APPROXIMATELY 9:37 AM ON APRIL 22, 2014, AN AMBULANCE BACKED INTO A TWO-METER MANIFOLD IN THE SOUTH PARKING AREA AT THE OFFICES OF MOBILE MEDICAL RESPONSE (8336 N. SAGINAW, MT. MORRIS). THE VEHICLE DAMAGE SEVERED THE RISER FROM THE GAS METER MANIFOLD ABOVE THE LOCKWING VALVE, CAUSING GAS TO BLOW. THE STRUCTURE WAS EVACUATED AS A RESULT OF THE DAMAGE. AT APPROXIMATELY 9:48 AM, AN EXPLOSION OCCURRED AT THE REAR (EASTERLY) SECTION OF THE BUILDING, BLOWING OUT WALLS AND CAUSING INTERNAL AND STRUCTURAL DAMAGE TO THE REAR OF THE BUILDING. ALL PERSONNEL HAD BEEN EVACUATED AND NO INJURIES OCCURRED AS A RESULT OF THE EXPLOSION. NO SURROUNDING STRUCTURES WERE DAMAGED. GAS WAS SHUT OFF AT THE LOCKWING AT APPROXIMATELY 10:45 AM. BAR TESTING INDICATED NO UNDERGROUND MIGRATION OF GAS. THE UNDERGROUND SERVICE TO THE BUILDING, AS WELL AS THE RISER, HELD DURING A POST-INCIDENT PRESSURE TEST. NO LEAKS WERE DETECTED AT THE MAIN, AND NO GAS WAS DETECTED IN NEARBY BUILDINGS. THE SPECIFIC PATH OF MIGRATION FROM THE SEVERED RISER INTO THE BUILDING PRIOR TO EXPLOSION IS UNDETERMINED.
2025-03-31 10:13 | NO | YES | NO | 20140043 | 30512 | 2014-05-23 09:18 | SUPPLEMENTAL FINAL | 13660 | NORTH SHORE GAS CO | 3001 W. GRAND AVENUE | WAUKEGAN | IL | 60085 | 2014-04-25 22:43 |  |  | 2014 | 4771 TRENTON COURT | LONG GROVE | LAKE | IL | 60047 | 42.2085 | -88.0021 | [9 empty] | 2014-04-25 23:49 | 1080892 |  | NATURAL GAS |  | 106.69 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2014-04-25 22:43 |  |  |  | 2014-04-25 22:43 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNKNOWN | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | NORTH SHORE GAS HAS DETERMINED THAT JURISDICTIONAL GAS PLAYED NO ROLE IN THE CAUSE OF THIS INCIDENT. | CLASS 3 LOCATION | 15613769 | 19129123.34999999638988 | 5000 | 6125.7225433526 | 10000 | 12251.4450867052 | 0 | 0 |  |  | 1330 | 994.588441330998248686514886164623467601 |  | 0 | 15630099 | 7931240.50754904051248306129597197898424 | 19148495.10607138518812868651488616462347 | 0 | 0 | 8 |  |  |  |  | 44 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | NORTH SHORE GAS HAS DETERMINED THAT JURISDICTIONAL GAS HAD NO ROLE IN THE CAUSE OF THIS INCIDENT. THE EVENT WAS CAUSED BY CUSTOMER OWNED PIPING AND/OR EQUIPMENT. | [47 empty] | SHAWN BARTELS | PRINCIPAL ENGINEER | srbartels@peoplesgasdelivery.com | 312-240-5421 |  |  |  |  | THOMAS WEBB | COMPLIANCE MANAGER | 3122404650 | tjwebb@peoplesgasdelivery.com | ON 4/24/14 AT 2222 HOURS, A NORTH SHORE GAS EMPLOYEE ARRIVED IN THE VICINITY OF THE EVENT. THE EMPLOYEE HAD BEEN DISPATCHED TO 4777 WELLINGTON DRIVE TO COMPLETE A LEAK INVESTIGATION ORDER THAT WAS CREATED AT 2152 HOURS. DURING THE LEAK INVESTIGATION, THE EMPLOYEE SMELLED AN ODOR AT THE CORNER OF WELLINGTON DRIVE AND TRENTON COURT AND DETECTED 0.3% LEL WITH A COMBUSTIBLE GAS INDICATOR (CGI). THE EMPLOYEE NOTICED FERTILIZER AND MULCH IN THE AREA. IN ACCORDANCE WITH PROCEDURES AND TRAINING, THE EMPLOYEE ATTACHED A CHARCOAL FILTER TO THE CGI AND DETECTED 0.0% LEL WITH THE FILTER INSTALLED. THE EMPLOYEE WALKED TOWARDS 4773 TRENTON COURT WHEN THE RESIDENT OF THE AREA FLAGGED THE EMPLOYEE DOWN AND SHOUTED THAT THERE IS A FIRE IN THE RESIDENCE NEXT DOOR. THE EMPLOYEE STARTED TO DIAL 911 AND 4771 TRENTON COURT EXPLODED AT APPROXIMATELY 2243 HOURS. NORTH SHORE GAS STOPPED THE FLOW OF GAS BY CLOSING A SINGLE VALVE AT 0032 HOURS ON 4/26/14 AT THE DIRECTION OF THE LONG GROVE FIRE DEPARTMENT. TWO PEOPLE RECEIVED MEDICAL ATTENTION ONSITE AND WERE RELEASED. OTHER HOMES IN THE AREA WERE DAMAGED DUE TO THE EXPLOSION AND THE EXTENT IS STILL UNDER INVESTIGATION. THE GAS MAIN THAT FED 4771 TRENTON COURT IS A 2" BLACK PLASTIC DIRECT BURIED MAIN THAT WAS INSTALLED IN 1991. THE GAS SERVICE FOR 4771 TRENTON COURT IS A 1.125" BLACK PLASTIC SERVICE THAT WAS INSTALLED IN 1996. THE SERVICE DID NOT HAVE AN EXCESS FLOW VALVE AS IT WAS NOT REQUIRED BY CODE AT THE TIME OF INSTALLATION. FOLLOWING THE EVENT, THE GAS MAIN AND ALL ASSOCIATED GAS SERVICE PIPES WERE PRESSURE TESTED ON 5/12/14. THE MAINS AND SERVICES WERE PRESSURE TESTED AT 44 PSIG, THE PRESSURE IN THE LINES AT THE TIME OF THE EXPLOSION FOR 1 HOUR. ALL MAINS AND SERVICES HELD PRESSURE DEMONSTRATING NO LEAKAGE OUT OF THESE LINES. REPRESENTATIVES OF THE ILLINOIS COMMERCE COMMISSION (ICC) PIPELINE SAFETY BRANCH WITNESSED THIS TESTING. THE 4" BLACK PLASTIC DIRECT BURIED MAIN IN WELLINGTON DRIVE WAS RESTARTED AT APPROXIMATELY 1000 HOURS ON 4/27/14. THE RISER FOR 4771 TRENTON COURT WAS REMOVED FROM THE SITE ON 5/15/14 FOR AN X-RAY AND IS SCHEDULED TO BE PERFORMED ON 5/23/14. THE METER AND REGULATOR ARE NOT IN A CONDITION THAT CAN BE TESTED. 6/4/14: AN X-RAY TEST WAS PERFORMED ON THE RISER PIPE ON 5/23/14 TO TEST THE MECHANICAL ASSEMBLY. 12/31/14: THE BORESCOPE PERFORMED ON 10/10/14 WAS INCONCLUSIVE. ON 11/3/14 THE RISER ASSEMBLY WAS PRESSURE TESTED AND DID NOT HOLD PRESSURE DUE TO EXTENSIVE DAMAGE TO THE PLASTIC PIPE INSIDE THE RISER. THE HOME APPLIANCES ARE STILL IN THE PROCESS OF BEING TESTED. 9/14/15: A RE-ASSEMBLY OF THE GAS SYSTEM INSIDE OF THE HOUSE IS BEING GENERATED. PGL IS PLANNING AN ADDITIONAL TEST ON THE RISER. 12/15/15: THE RE-ASSEMBLY AND TESTING OF THE GAS SYSTEM INSIDE OF THE HOUSE WAS COMPLETED. 6/27/17: FURTHER EXAMINATION OF THE RISER DETERMINED A STIFFENER HAD NOT BEEN INSTALLED IN THE SERVICE, AS WAS THE PRACTICE AT THE TIME THE SERVICE WAS INSTALLED. HOWEVER, THERE IS NO INDICATION THAT THE RISER WAS LEAKING OR THAT THERE WAS A PATH FOR THE GAS TO TRAVEL FROM THE OUTSIDE OF THE HOUSE INTO THE HOUSE IF GAS HAD BEEN PRESENT. THEREFORE, NSG HAS DETERMINED THAT JURISDICTIONAL GAS PLAYED NO ROLE IN THE CAUSE OF THIS INCIDENT. THE EVENT WAS CAUSED BY CUSTOMER OWNED PIPING AND/OR EQUIPMENT INSIDE THE HOUSE. NSG CONSIDERS THIS INCIDENT CLOSED.
2025-03-31 10:13 | NO | NO | NO | 20140044 | 15864 | 2014-05-28 15:03 | ORIGINAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 1 METROTECH CENTER | BROOKLYN | NY | 11201 | 2014-04-30 23:07 |  |  | 2014 | 149 AVE. TO 156 AVE FROM 77 ST. TO 80 ST. | HOWARD BEACH | QUEENS | NY | 11414 | 40.6682 | -73.8554 | [9 empty] | 2014-05-01 02:49 | 1081328 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-04-30 23:07 |  |  |  | 2014-04-30 23:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | THERE WAS NO RELEASE. INCIDENT OCCURED DUE TO STORM SURGE AND RESULTING FLOODING. | CLASS 4 LOCATION | 0 | 0 | 91888 | 112576.07861271674176 | 2000 | 2450.28901734104 | 0 | 0 |  |  | 0 | 0 |  | 0 | 93888 | 47640.471676300590336 | 115026.36763005778176 | 0 | 0 | 0 |  |  |  |  | 12 | 12 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM FDNY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS A RESULT OF STORM SURGE FLOODING. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | FLOODING DUE TO HEAVY RAIN. GAS PRESSURE REGULATORS WERE COMPROMISED BY STORM SURGE. | YES |  | YES | [216 empty] | R. VERDERAME | LEAD SUPERVISOR | richard.verderame@nationalgrid.com | 718 403-3105 |  |  |  |  | R. DE MARINIS | VP MAINTENANCE AND CONSTRUCTION NY GAS | 516 545-4337 | robert.demarinis@nationalgrid.com | THIS AREA SUSTAINED FLOODING DUE TO HEAVY RAIN AND A STORM SURGE. AS A RESULT, SOME GAS METERS AND HOUSE SERVICE REGULATORS WERE SUBMERGED. NATIONAL GRID RESPONDED AND FOUND THERE WAS NO IMPACT TO THE GAS SYSTEM NOR WERE THERE INTERRUPTIONS TO ANY GAS SERVICES IN THE AFFECTED AREA. NATIONAL GRID REPLACED COMPROMISED HOUSE SERVICE REGULATORS AS A PRECAUTIONARY MEASURE. INSPECTIONS FOUND SOME CUSTOMER UTILIZATION EQUIPMENT COMPROMISED BY THE FLOODING. THESE WERE ISOLATED AND TAGGED FOR SAFETY.
2025-03-31 10:13 | YES | NO | NO | 20140045 | 16186 | 2014-06-10 06:54 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2014-05-14 08:41 |  |  | 2014 | 25 E TURNBERRY DRIVE | TOWN OF GREENBURGH | WESTCHESTER | NY | 10583-0000 | 41.034 | -73.8654 | [9 empty] | 2014-05-14 08:54 | 1082731 |  | NATURAL GAS |  | 5.2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2014-05-14 08:41 |  |  |  | 2014-05-14 08:58 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | 1986 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | RESIDENTIAL BUILDING FIRE RESULTED IN GAS IGNITION AND EXPLOSION. | CLASS 4 LOCATION | 250000 | 306286.12716763 | 2000 | 2450.28901734104 | 2500 | 3062.8612716763 | 0 | 0 |  |  | 24 | 17.94746059544658493870402802101576182137 |  | 0 | 254524 | 129154.5118930720531593695271453590192644 | 311817.2249172427865849387040280210157618 | 0 | 0 | 10 |  |  |  |  | 54 | 54 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | OSCAR LEON | GAS EMERGENCY RESPONSE CENTER OPERATING SUPERVISOR | leono@coned.com | 718-319-2340 | 718-597-5463 |  |  |  | VICTOR DADARIO | GAS EMERGENCY RESPONSE CENTER DEPARTMENT MANAGER | 718-319-2350 | dadariov@coned.com | ON MAY 14, 2014 AT 08:36, WESTCHESTER COUNTY DEPT. OF EMERGENCY SERVICES (60 CONTROL) REPORTED A BUILDING FIRE AT 25 EAST TURNBERRY DRIVE IN THE TOWN OF GREENBURGH TO THE GAS EMERGENCY RESPONSE CENTER (GERC). A GAS EMERGENCY RESPONSE GROUP (ERG) SUPERVISOR REPORTED THE SAME UPON HEARING THE REPORT ON THE FIRE DEPARTMENT SCANNER. GAS DISTRIBUTION SERVICES (GDS) AND SUPERVISION WERE DISPATCHED . AT 08:40 THE HASTINGS FIRE DEPARTMENT (HFD) REPORTED AN OPEN GAS PIPE AT THAT LOCATION AND AT 08:41 A GAS FED FIRE WAS REPORTED BY THE HFD. SUPERVISION, GAS CONSTRUCTION, ADDITIONAL GDS RESPONDERS, THE COMPANY LAW DEPARTMENT AND A PHOTOGRAPHER WERE DISPATCHED. AT 08:43 THE HFD REPORTED ONE INJURY TO THE GERC, WITH NO OTHER INFORMATION AVAILABLE AT THAT TIME AND AT 08:45, AN ELECTRIC OPERATIONS ERG REPORTED FROM THE LOCATION OF THE FIRE THAT THE SIDE OF THE RESIDENTIAL HOUSE BLEW OUT DUE TO AN EXPLOSION. THE GAS OPERATIONS ERG ARRIVED ON LOCATION AT 08:58 AND HE WAS DIRECTED TO LOCATE AND CLOSE HIGH PRESSURE MAIN VALVE-21521 WHICH CONFIRMED CLOSED AT 09:05 BUT THE FIRE DID NOT EXTINGUISH. ADDITIONAL CREWS AND SUPERVISORS ARRIVED ON LOCATION AND LOCATED THE CURB VALVE FOR THIS LOCATION AND CLOSED THE VALVE AT 09:14. THE FIRE VISUALLY SUBSIDED AFTER THE CURB VALVE WAS CLOSED. GAS OPERATIONS PERSONNEL WERE INFORMED OF TWO INJURIES, ONE WAS THE RESIDENT OF #25 EAST TURNBERRY RD. AND THE OTHER WAS A FIREFIGHTER. BOTH INJURED PERSONS WERE TRANSPORTED TO AN UNKNOWN AREA HOSPITAL VIA EMS DUE TO SUSPECTED SMOKE INHALATION. GDS CONFIRMED 10 HOUSES WERE INTERRUPTED DUE TO CLOSURE OF THE MAIN VALVE. AT 09:37, THE BRONX/WESTCHESTER ELECTRIC CONTROL CENTER REPORTED TO THE GERC THAT THERE WAS A REPORT OF AN ELECTRICAL OUTAGE IN THE AREA NEAR THIS LOCATION PRIOR TO THE REPORTED FIRE. THE HASTINGS FIRE DEPARTMENT REPORTED THE FIRE WAS INSIDE THE GARAGE IN THE AREA OF THE GAS METER. PUBLIC AFFAIRS REPORTED THERE WERE INQUIRIES FROM NUMEROUS MEDIA OUTLETS. AT 13:13 HASTINGS FIRE CHIEF RUSSAK REPORTED TO 60 CONTROL THAT THE FIRE WAS OFFICIALLY OUT AND THE CAUSE OF THE FIRE WAS INVESTIGATED. GAS OPERATIONS TURNED ON THE MAIN VALVE AND INTRODUCED GAS SUPPLY TO THE AFFECTED SERVICES. THE AREA WAS INVESTIGATED FOR GAS LEAKS IN THE PRESENCE OF THE NYS PSC AND NO LEAKS WERE DETECTED. THREE SERVICES WERE CUT AND CAPPED FOR SAFETY DUE TO NO ACCESS. ALL OTHER AFFECTED SERVICES WERE RESTORED. THE BUILDING INVOLVED WAS INVESTIGATED FOR LEAKS IN THE PRESENCE OF THE NYS PSC AND NO LEAKS WERE DETECTED UP TO THE SERVICE HEAD VALVE. THE GAS METER AND HIGH PRESSURE SERVICE REGULATOR WERE DAMAGED BY THE FIRE. WESTCHESTER FIRE INVESTIGATORS REPORTED THE INITIAL FIRE WAS ELECTRICAL IN NATURE AND A SUBSEQUENT HEAT/BACKDRAFT EXPLOSION OCCURRED. SECONDARY GAS IGNITION WAS REPORTED WHICH WAS CAUSED WHEN THE METER & REGULATOR SUPPLYING #25 WHERE DESTROYED BY THE INITIAL FIRE. THERE DAMAGE IN EXCESS OF $50, 000 AND MULTIPLE MEDIA OUTLETS RESPONDED AND REPORTED ON THE FIRE. THE NRC/DOT AND NYS PSC WERE NOTIFIED AND THE PSC RESPONDED TO THE LOCATION.
2025-03-31 10:13 | NO | YES | NO | 20140046 | 15871 | 2014-06-10 18:35 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2014-05-16 15:14 |  |  | 2014 | 23136 PARK CONTESSA | CALABASAS | LOS ANGELES | CA | 91302 | 34.1508 | -118.6357 | [9 empty] | 2014-05-16 19:52 | 1083045 |  | NATURAL GAS |  | 21 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2014-05-16 15:41 |  |  |  | 2014-05-16 16:12 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1997 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 200000 | 245028.901734104 | 1600 | 1960.231213872832 | 400 | 490.057803468208 | 0 | 0 |  |  | 126 | 94.22416812609457092819614711033274956217 |  | 0 | 202126 | 102585.6214463352595866900175131348511384 | 247573.4149195711345709281961471103327496 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | tbauer@semprautilities.com | 909-376-7208 |  |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | ON MAY 16TH, 2014 A METER SET ASSEMBLY WAS STRUCK BY VEHICLE AT 23136 PARK CONTESSA IN CLABASAS, CAUSING A LEAK. THE LEAK WAS IGNITED IN AN EXPLOSION THAT SET THE GARAGE AND HOME ON FIRE. NO INJURIES OR DEATHS RESULTED FROM THIS INCIDENT. THE SERVICE TO THE RESIDENCE WAS ABANDONED AND WILL BE REINSTATED AT OWNER'S REQUEST ONCE EXTENSIVE HOME REPAIRS ARE MADE. INVESTIGATION OF THE INCIDENT SHOWED THE VEHICLE LEFT THE ROADWAY AND TRAVELED INTO THE METER SET ASSEMBLY AND SIDE OF THE GARAGE. THE ESTIMATED COSTS OF THE DAMAGE TO THE HOME AND VEHICLE ARE EXPECTED TO EXCEED THE FIFTY THOUSAND DOLLAR THRESHOLD.
2025-03-31 10:13 | NO | YES | YES | 20140047 | 15872 | 2014-06-13 19:00 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-05-14 10:30 |  |  | 2014 | 405 RAMBLER RD | MERCED | MERCED | CA | 95348-3349 | 37.3157 | -120.4763 | [9 empty] | 2014-05-14 | 1082800 |  | NATURAL GAS |  | 92.34 |  | YES | 0 | 0 | 0 | 0 | 2 | 2 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2014-05-14 11:10 |  |  |  | 2014-05-14 11:32 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | UNKNOWN | [8 empty] | STEEL | [10 empty] | OTHER | [8 empty] | VEHICLE STRUCK METER AND SERVICE RISER | CLASS 3 LOCATION | 0 | 0 | 3000 | 3675.43352601156 | 0 | 0 | 0 | 0 |  |  | 496 | 370.914185639229422066549912434325744308 |  | 0 | 3496 | 1865.371673263618626970227670753064798599 | 4046.347711650789422066549912434325744308 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 415-450-1626 |  |  |  |  | CHRISTIANE MASON | SENIOR MANAGER REGULATORY AND FIELD COMPLIANCE | 925-328-5795 | c6mw@pge.com | TRAVELING AT A HIGH RATE OF SPEED, A VEHICLE LEFT THE ROADWAY AND STRUCK A RESIDENCE AT 405 RAMBLER RD., MERCED--CAUSING SIGNIFICANT STRUCTURAL DAMAGE. THE VEHICLE ALSO STRUCK PG&E GAS AND ELECTRIC FACILITIES AT 405 RAMBLER RD., MERCED. THE EVENT RESULTED IN A FIRE AND TWO FATALITIES, WHO WERE OCCUPANTS OF THE VEHICLE. PG&E RECEIVED THE CALL AT 1110 HOURS AND PG&E PERSONNEL ARRIVED ON SCENE AT 1132 HOURS. PG&E REPAIR CREW ARRIVED ONSITE AT 1148 HOURS AND STOPPED THE FLOW OF GAS AT 1327 HOURS BY SQUEEZING AND CAPPING THE STEEL SERVICE. POLICE, FIRE, AMBULANCE, AND NEWS MEDIA WERE ON SCENE. THIS WAS REPORTED TO THE CALIFORNIA PUBLIC UTILITIES COMMISSION (COMMISSION) AND DEPARTMENT OF TRANSPORTATION (DOT) DUE TO THE FATALITIES, IGNITION (FROM THE RELEASE OF GAS FROM PG&E FACILITIES), AND MEDIA PRESENCE.
2025-03-31 10:13 | NO | YES | NO | 20140050 | 16022 | 2014-06-25 12:45 | SUPPLEMENTAL FINAL | 31636 | NORTHERN STATES POWER CO OF MINNESOTA | 414 NICOLLET MALL | MINNEAPOLIS | MN | 55402 | 2014-05-29 21:47 |  |  | 2014 | 3475 WILLOW LAKE BLVD | VADNAIS HEIGHTS | RAMSEY | MN | 55127 | 45.0469 | -93.0554 | [9 empty] | 2014-05-29 23:46 | 1084342 |  | NATURAL GAS |  | 130 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2014-05-29 21:49 |  |  |  | 2014-05-29 21:59 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2003 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | STEEL METER SET PIPING SHEARED OFF BY VEHICLE | CLASS 3 LOCATION | 180000 | 220526.0115606936 | 3000 | 3675.43352601156 | 5000 | 6125.7225433526 | 0 | 0 |  |  | 645 | 482.338003502626970227670753064798598949 |  | 0 | 188645 | 95840.795902803813408056042031523642732 | 230809.5056335603869702276707530647985989 | 7 | 0 | 0 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LISA KALLBERG | PRINCIPAL PIPELINE COMPLIANCE CONSULTANT | elisabeth.m.kallberg@xcelenergy.com | 651-229-2282 |  |  |  |  | KATHERINE HELLFRITZ | SR DIRECTOR GAS GOVERNANCE | 303-571-3162 | katherine.hellfritz@xcelenergy.com | A POLICE VEHICLE TRAVELING AT A HIGH RATE OF SPEED LOST CONTROL, WENT OVER THE CURB AND SMALL HILL, THROUGH A PARKING LOT AND COLLIDED WITH THE ABOVE GRADE 3 METER HEADER. THE GAS FACILITIES WERE DESTROYED AND THE GAS RELEASED WAS IGNITED. THE RESULTING FIRE CAUSED DAMAGED TO THE POLICE VEHICLE AND BUILDING. ON DECEMBER 10, 2014 GAS SERVICE WAS RESTORED AT THIS LOCATION.
2025-03-31 10:13 | NO | NO | NO | 20140051 | 15879 | 2014-06-25 16:55 | ORIGINAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2013-05-03 15:57 |  |  | 2013 | 4205 CHERRY HILL DRIVE | POUGHKEEPSIE |  | NY | 12603 | 41.7041 | -73.8826 | [12 empty] | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 144 | 2013-05-03 15:57 |  |  |  | 2013-05-03 16:19 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1984 | [8 empty] | OTHER | ALUMINUM METER | [9 empty] | OTHER | [8 empty] | CAR JUMPED CURB, STRUCK BUILDING IN LOCATION OF OUTSIDE METER SET AREA. THE IMPACT OF THE CAR, SEVERED METER FROM GAS RISER. | CLASS 3 LOCATION | 55000 | 68686.536384169715 | 150 | 187.32691741137195 | 8150 | 10178.09584601787595 | 0 | 0 |  |  | 460 | 402.5 |  | 0 | 63760 | 33113.2866695215325918032786885245901639 | 79454.4591475989629 | 0 | 0 | 6 |  |  |  |  | 25 | 25 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | DUTCHESS COUNTY 911 OPERATOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS DISTRIBUTION SYSTEM IS NOT MONITORED BY THE COMPANY'S SCADA SYSTEM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LENORE J. CLARKE | SECTION LEADER GAS SAFETY AND COMPLIANCE | lclarke@cenhud.com | 845 486 5521 |  |  |  |  | LAWRENCE CAMBALIK | MANAGER OF GAS AND MECHANICAL ENGINEERING | 845 486 5741 | lcambalik@cenhud.com | A RESIDENT WITHIN THE APARTMENT COMMUNITY IMPROPERLY OPERATED THEIR VEHICLE. THE VEHICLE JUMPED THE CURB, CRASHED INTO THE BUILDING WHERE THE OUTSIDE METER SET WAS LOCATED. THE IMPACT OF THE CAR TO THE BUILDING/METER SET, SEVERED THE METER FROM THE RISER AND THE LEAKING GAS IGNITED. NO INJURIES OR FATALITIES OCCURRED. DURING AN INTERNAL AUDIT OF UNSCHEDULED INTERRUPTIONS OF SERVICE, IT WAS NOTED THAT THIS INCIDENT WAS REPORTED TO THE NEW YORK STATE DEPARTMENT OF PUBLIC SERVICE BUT NOT FILED WITH PHMSA.
2025-03-31 10:13 | NO | NO | NO | 20140052 | 15886 | 2014-06-30 17:04 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2014-06-02 10:04 |  |  | 2014 | 1042 NORTH 51ST AVENUE | PHOENIX | MARICOPA | AZ | 85043 | 33.4604 | -112.1692 | [9 empty] | 2014-06-02 11:23 | 1084624 |  | NATURAL GAS |  | 446 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-06-02 10:04 |  |  |  | 2014-06-02 10:20 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1998 | [8 empty] | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY | LONGITUDINAL ERW (UNKNOWN FREQUENCY) | 0.154 | [6 empty] | OTHER | [8 empty] | DISTRICT REGULATORY STATION STRUCK BY VEHICLE | CLASS 3 LOCATION | 0 | 0 | 70000 | 85760.1156069364 | 1688 | 2068.04393063583776 | 0 | 0 |  |  | 2200 | 1645.183887915936952714535901926444833625 |  | 0 | 73888 | 37897.6810139396548782066549912434325744 | 89473.3434254881747127145359019264448336 | 21 | 0 | 0 |  |  |  |  | 172 | 175 | 175 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | SHAWN BRINK | ADMINISTRATOR COMPLIANCE | shawn.brink@swgas.com | 602-484-5489 | 602-484-5322 |  |  |  | LYNN A MALLOY PE | GENERAL MANAGER OPERATIONS | 602-484-5477 | lynn.malloy@swgas.com | PL 2014-0679 SOUTHWEST GAS CORPORATION (SWG) RESPONDED TO A REPORTED VEHICULAR ACCIDENT RESULTING IN DAMAGES TO A DISTRICT REGULATOR STATION AT 1042 NORTH 51ST AVENUE IN PHOENIX CALLED IN BY THE PHOENIX SHERIFF DEPARTMENT AT 10:04. UPON ARRIVAL, A SWG SERVICE TECHNICIAN WAS ADVISED THAT A COLLISION BETWEEN TWO AUTOMOBILES CAUSED INJURIES TO TWO PEOPLE, ONE OF WHOM WAS TRANSPORTED WITH MINOR INJURIES TO AND LATER RELEASED FROM THE HOSPITAL LATER THAT DAY. SWG CREWS RESPONDED AND CONTROLLED THE FLOW OF GAS BY CLOSING A 4-INCH REGULATOR STATION INLET VALVE AND MADE REPAIRS BY REPLACING THE REGULATOR STATION. THERE WAS AN OUTAGE OF 21 COMMERCIAL CUSTOMERS AND A MEDIA INQUIRY WAS RECEIVED FROM CHANNEL 15. NOTIFICATION WAS MADE TO PHMSA VIA THE NATIONAL RESPONSE CENTER (NRC) REPORT NUMBER 1084624 AT 11:23 CONCERNING AN ESTIMATED PROPERTY DAMAGE EXCEEDING $50,000. THERE WERE NO FATALITIES AS A RESULT OF THE INCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20140053 | 16100 | 2014-07-01 16:14 | SUPPLEMENTAL FINAL | 31159 | KANSAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2014-06-02 15:47 |  |  | 2014 | 150'SOUTH OF THE INTERSECTION OF NW GRANT & NW TYLER | TOPEKA | SHAWNEE | KS | 66608 | 39.0734 | -95.673 | [9 empty] | 2014-06-02 17:10 | 1084647 |  | NATURAL GAS |  | 0.07 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2014-06-02 15:47 |  |  |  | 2014-06-02 15:47 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | IN OTHER ENCLOSED SPACE |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1953 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.312 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 7500 | 9188.5838150289 | 5000 | 6125.7225433526 | 20000 | 24502.8901734104 | PERMANENT REPAIR OF REGULATOR STATION |  | 1 | 0.7478108581436077057793345008756567425569 |  | 0 | 32501 | 16491.7804008112099649737302977232924694 | 39817.9443426500436077057793345008756567 | 0 | 0 | 0 |  |  |  |  | 0.75 | 0.75 | 0.75 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | INCORRECTLY PERFORMING A MAINTENANCE FUNCTION, NOT FOLLOWING PROCEDURES. |  |  | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | BILL HAISLIP | REGULATORY COMPLIANCE SPECIALIST | bhaislip@kgas.com | 785-431-4272 | 785-431-4224 |  |  |  | RANDY SPECTOR | DIRECTOR OF ENGINEERING | 785-431-4241 | rspector@kgas.com | ON MONDAY, JUNE 2, 2014, THREE EMPLOYEES WERE ASSIGNED TO WORK ON THE REGULATOR STATION IN THE VAULT AT NW TYLER & NW GRANT. THE WORK INVOLVED REPLACING A WEIGHTED LEVER REGULATOR WITH A WORKER/MONITOR REGULATOR SET STYLE OF STATION. THE EXISTING REGULATOR WAS REMOVED AND NEW REGULATORS WERE INSTALLED. ONCE INSTALLED, LEAKAGE WAS DISCOVERED ON THE NEW REGULATOR STATION PRE-ASSEMBLED PIPING. THE NEW STATION REGULATORS WERE REMOVED TO MAKE REPAIRS. WHILE REPAIRS WERE BEING MADE TO THE WORKER/MONITOR SET, IT WAS DISCOVERED THAT A FITTING USED FOR ONE OF THE CONTROL LINES WAS LEAKING. A WELDER WAS REQUESTED AND DISPATCHED TO THE WORK SITE TO REPAIR THE LEAKING FITTING. BLIND FLANGES WERE INSTALLED WHERE THE NEW WORKER/MONITOR SET HAD BEEN REMOVED AND TWO EMPLOYEES BEGAN MAKING A REPAIR TO THE LEAKING FITTING. A WELD CONE WAS INSTALLED INTO THE LEAKING THREADED FITTING TO STOP THE LEAK PRIOR TO FINALIZING THE REPAIR. DURING THE CONTAINMENT OF THE LEAKAGE, AS ADDITIONAL WORK WAS BEING CONDUCTED, A SMALL FLASH FIRE OCCURRED, CAUSING SUPERFICIAL BURNS TO ONE OF THE EMPLOYEES COMPLETING THE WORK IN THE VAULT. THE INJURED EMPLOYEE WAS HOSPITALIZED OVERNIGHT TO HAVE HIS INJURIES EXAMINED AND TO CONFIRM THAT THE BURNS WERE EXTERNAL AND MINOR IN NATURE. THE FOLLOWING SUPPLEMENTAL REPORT CHANGES WERE MADE TO THIS INCIDENT REPORT - GAS DISTRIBUTION SYSTEM. 6/22/2015 BH PAGE 1, PART A, LINE 10. THE TOTAL GAS LOST WAS 67 CU. FT. THIS EQUATES TO.067 MCF. ROUNDING TO 2 DECIMALS GIVES A LOST GAS QUANTITY OF .07 MCF. THIS VALUE WAS CORRECTED AS PART OF THIS SUPPLEMENTAL REPORT. PAGE 2, PART A, LINE 13B. THE LOCAL TIME THIS PIPELINE/FACILITY WAS RESTARTED WAS AUGUST 28, 2014 AT 13:00 HRS. THIS TIME WAS ADDED TO THE SUPPLEMENTAL REPORT. PAGE 2, PART C, LINE 4A. THIS INSTALLATION WAS DONE IN 08/1953. THE MATERIAL CHECKOUT DOCUMENTATION ONLY LISTS THE PIPE DIAMETER AND WALL THICKNESS. NO OTHER SPECIFICATIONS WERE LISTED SO THE SEAM TYPE IS UNKNOWN. THIS RESPONSE REMAINS UNKNOWN. PAGE 3, PART D LINE 2F. WE HAVE SHOWN THE GAS LOST AS .07 MCF. OUR COST OF GAS AT THE TIME OF THE INCIDENT WAS $6.5132. THIS EQUATES TO A COST OF $.45. SINCE WHOLE DOLLARS ARE REQUIRED, THE COST OF GAS LOST WAS $1.00. PAGE 3, PART E, LINES 1-3. THIS WAS A DISTRIBUTION LINE OPERATING AT 12 OUNCES. BECAUSE THE PRESSURE MUST BE SHOWN AS PSIG, THE PRESSURE WOULD EQUATE TO .75 PSIG. NO CHANGES WERE MADE TO THESE LINES. PAGE 4, PART G1. THIS SUPPLEMENTAL REPORT CORRECTS THE CAUSE OF THIS INCIDENT AS INCORRECT OPERATION, PART G7. WITH THIS CHANGE MADE, THE INFORMATION FORMERLY SHOWN IN PART G1 HAS BEEN REMOVED. SEE PART G7 FOR CORRECTED INFORMATION. PAGE 9, PART G7, LINE 1. OTHER INCORRECT OPERATION WAS SELECTED. THE INCORRECT OPERATION WAS NOT FOLLOWING PROCEDURES. PAGE 9, PART G7, LINE 2. THE SELECTION, FAILURE TO FOLLOW PROCEDURE WAS SELECTED. PAGE 9, PART G7, LINE 3. THE CATEGORY TYPE SELECTED WAS OTHER MAINTENANCE. A REGULATOR/FULL RELIEF VALVE SETTING WAS BEING REPLACED WITH A WORKER/MONITOR REGULATOR STATION AND BEING REMOVED FROM A VAULT.
2025-03-31 10:13 | NO | YES | NO | 20140054 | 16274 | 2014-07-03 16:24 | SUPPLEMENTAL FINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2014-06-08 21:20 |  |  | 2014 | INDIAN TRAIL ROAD, BETWEEN 26 AND 27 MILE ROAD | RAY TOWNSHIP | MACOMB | MI | 48096 | 42.7256 | -82.8845 | [9 empty] | 2014-06-09 05:52 | 1085263 |  | NATURAL GAS |  | 9800 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-06-08 21:20 |  |  |  | 2014-06-08 21:53 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 38 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1979 | [5 empty] | 8 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.277 | [6 empty] | MECHANICAL PUNCTURE | 4 | 2 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 150524 | 184413.65202312135248 | 0 | 0 | 0 | 0 |  |  | 53324 | 39876.2661996497373029772329246935201401 |  | 0 | 203848 | 113266.4847642475791871943957968476357268 | 224289.9182227710897829772329246935201401 | 0 | 0 | 113 |  |  |  |  | 277 | 277 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SCADA SYSTEM WAS ALARMING AT THE SAME TIME AS A CALL WAS RECIEVED FROM THE EMERGENCY 911 DISPATCH. COMPANY PERSONNEL WERE DISPATCHED TO THE SITE IMMEDIATELY FOLLOWING THE NOTIFICATION. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | [5 empty] | YES | [8 empty] | FARMER | BACKHOE/TRACKHOE | AGRICULTURE | NO |  |  |  | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 6 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | STEPHEN MAKOWSKI | MANAGER CODES AND STANDARDS | steve.makowski@semcoenergy.com | 8108874228 | 8108874233 |  |  |  | STEPHEN MAKOWSKI | MANAGER CODES AND STANDARDS | 8108874228 | steve.makowski@semcoenergy.com | REFERENCE: MICHIGAN PUBLIC SERVICE COMMISSION STAFF INVESTIGATION REPORT SEMCO ENERGY INDIAN TRAIL INCIDENT INDIAN TRAIL ROAD, RAY INCIDENT DATE: JUNE 8, 2014 CASE: 282829 REPORT DATE: JULY 30, 2015 EXECUTIVE SUMMARY ON JUNE 8, 2014, SEMCO ENERGY (SEMCO) NOTIFIED THE MICHIGAN PUBLIC SERVICE COMMISSION STAFF (STAFF) OF A THIRD-PARTY DAMAGE ON THEIR EIGHT-INCH HIGH PRESSURE MAIN WEST OF INDIAN TRAIL ROAD, BETWEEN 26 MILE AND 27 MILE ROADS IN RAY TOWNSHIP. STAFF DETERMINES THAT THE PROBABLE CAUSE OF THE INCIDENT WAS THAT THE LESSEE OF THE PROPERTY WAS REMOVING TREE STUMPS WITH A BACKHOE AND PUNCTURED THE PIPELINE WITH A TOOTH FROM THE LOADER BUCKET.
2025-03-31 10:13 | NO | NO | NO | 20140056 | 15892 | 2014-07-10 20:49 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-06-10 15:00 |  |  | 2014 | 439 CORBETT AVENUE | SAN FRANCISCO | SAN FRANCISCO | CA | 94114 | 37.758 | -122.4454 | [9 empty] | 2014-06-10 | 1085489 |  | NATURAL GAS |  | 57 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2014-06-10 15:21 |  |  |  | 2014-06-10 15:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2011 | [8 empty] | OTHER | REGULATOR IS METAL; METER IS ALUMINUM | [9 empty] | OTHER | [8 empty] | THE REGULATOR ON THE THREE-METER MANIFOLD HAD A 2-INCH HOLE IN IT. THE 2-INCH HOLE WAS A RESULT OF VANDALISM (I.E., FROM SOMEONE HITTING THE REGULATOR). | CLASS 3 LOCATION | 0 | 0 | 10000 | 12251.4450867052 | 0 | 0 | 0 | 0 |  |  | 330 | 246.777583187390542907180385288966725044 |  | 0 | 10330 | 5302.464830318308441330998248686514886165 | 12498.222669892590542907180385288966725 | 0 | 0 | 3 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [156 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 415-450-1626 |  |  |  |  | LARRY DENISTON | INTERIM MANAGER | 925-328-5756 | lcd1@pge.com | ON JUNE 10, 2014, AT 1521 HOURS, PG&E WAS NOTIFIED BY THE SAN FRANCISCO FIRE DEPARTMENT (SFFD) OF AN UNINTENTIONAL RELEASE OF GAS AND TWO ALARM STRUCTURE FIRE AT 439 CORBETT AVENUE, INVOLVING A THREE-METER MANIFOLD. A PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SCENE AT 1545 HOURS, AND FOUND THAT THE SFFD HAD ALREADY STOPPED THE FLOW OF GAS AT THE CURB VALVE. ACCORDING TO THE SFFD, WITNESS STATEMENTS INDICATED THAT THE RELEASE OF GAS WAS CAUSED BY VANDALISM. THE REGULATOR ON THE THREE-METER MANIFOLD WAS FOUND TO HAVE A 2-INCH HOLE IN IT. THE REGULATOR WAS REMOVED BY PG&E CREWS AT APPROXIMATELY 1808 HOURS AND RETAINED AS EVIDENCE. ALL THREE METERS COMPLETELY MELTED FROM THE HEAT OF THE FIRE. THE SOURCE OF IGNITION IS UNKNOWN. THERE WERE NO INJURIES OR FATALITIES FROM THE INCIDENT. BAY CITY NEWS WAS OBSERVED ON SITE. IT IS ESTIMATED THAT DAMAGES TO THE STRUCTURE AND GAS FACILITIES EXCEED $50,000, MAKING THIS INCIDENT REPORTABLE TO THE CPUC AND DOT. ON JUNE 10, A LEAK SURVEY WAS CONDUCTED AFTER THE INCIDENT AND NO LEAKS WERE FOUND. THE MAIN AND CONNECTED SERVICES WERE SURVEYED 50 FEET, IN BOTH DIRECTIONS.
2025-03-31 10:13 | NO | NO | NO | 20140058 | 15896 | 2014-07-17 20:23 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-06-20 15:30 |  |  | 2014 | SOMERSVILLE RD. & JAMES DONLON BLVD. | ANTIOCH | CONTRA COSTA | CA | 94509 | 37.9873 | -121.8529 | [9 empty] | 2014-07-17 11:19 | 1089374 |  | NATURAL GAS |  | 3.59 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-06-20 15:33 |  |  |  | 2014-06-20 15:54 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2005 | [5 empty] | 4 | UNKNOWN | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 70000 | 85760.1156069364 | 0 | 0 | 0 | 0 |  |  | 21 | 15.7040280210157618213660245183887915937 |  | 0 | 70021 | 35533.7949680950592644483362521891418564 | 85775.8196349574157618213660245183887916 | 0 | 0 | 280 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SITE DEVELOPMENT | YES | 171085 | USAN |  | UTILITY OWNER | YES | YES | 1680 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | CHRISTIANE MASON | SENIOR MANAGER REGULATORY AND FIELD COMPLIANCE | 925-328-5795 | c6mw@pge.com | AT APPROXIMATELY 1530 HOURS, A THIRD-PARTY DIG-IN OCCURRED NEAR SOMERSVILLE ROAD AND JAMES DONLON BLVD. IN ANTIOCH. AN EXCAVATOR STRUCK A 4-INCH PLASTIC DISTRIBUTION MAIN THAT CAUSED AN UNINTENTIONAL RELEASE OF GAS. A PG&E GAS SERVICE REPRESENTATIVE (GSR) AND REPAIR CREW ARRIVED ON SCENE AT APPROXIMATELY 1554 HOURS. THE USA TICKET (NO. 0171085) IS VALID AND FACILITIES WERE PROPERLY MARKED. THE THIRD-PARTY OPERATOR WAS AWARE OF THE PIPE LOCATION BUT DID NOT EXERCISE CAUTION AND PROCEEDED TO DIG. NO POLICE, NO FIRE DEPARTMENT, NOR MAJOR MEDIA WERE ON SCENE. THERE WERE NO INJURIES, NO FATALITIES, AND NO IGNITION DURING THE INCIDENT. THE AMOUNT OF GAS RELEASED WAS LESS THAN 3 MMCF. THE GAS WAS SHUT IN AT 1835 HOURS BY ISOLATING THE MAIN, WHICH RESULTED IN 280 CUSTOMERS LOSING GAS SERVICE. PG&E REACHED OUT TO ALL 280 CUSTOMERS BY 0100 HOURS ON JUNE 21, 2014. BY 1030 HOURS ON JUNE 21, 2014, SERVICE WAS RESTORED FOR 190 CUSTOMERS. AS OF 1450 HOURS ON JUNE 21, 2014, SERVICE HAS BEEN RESTORED FOR AN ADDITIONAL 60 CUSTOMERS. BY JUNE 24, 2014, THE 30 REMAINING CUSTOMERS (WHO WERE OUT OF TOWN DURING THE RELIGHTING EFFORTS) HAD GAS SERVICE RESTORED. THIS INCIDENT WAS REPORTED TO THE CPUC BECAUSE OF OPERATOR JUDGMENT AND ALSO CONSIDERED SIGNIFICANT DUE TO THE LARGE NUMBER OF CUSTOMERS THAT LOST GAS SERVICE. PG&E RECENTLY CONFIRMED THAT DAMAGES RELATING TO THIS INCIDENT EXCEED $50,000. PG&E NOTIFIED THE NATIONAL RESPONSE CENTER ON JULY 17, 2014.
2025-03-31 10:13 | NO | NO | NO | 20140059 | 16002 | 2014-07-25 15:28 | SUPPLEMENTAL FINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2014-06-25 05:47 |  |  | 2014 | UNKNOWN | BUSHLAND | POTTER | TX | 79124 | 35.2065 | -102.0724 | [9 empty] | 2014-06-25 11:01 | 1087039 |  | NATURAL GAS |  | 2699 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 200 | 2014-06-25 05:47 |  |  |  | 2014-06-25 06:20 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | INSTRUMENT AND CONTROLS | 2010 | [8 empty] | OTHER | VARIOUS | [9 empty] | OTHER | [8 empty] | VENTING RELIEF VALVE. | CLASS 2 LOCATION | 0 | 0 | 70000 | 85760.1156069364 | 500 | 612.57225433526 | 0 | 0 |  |  | 14000 | 10469.3520140105078809106830122591943958 |  | 0 | 84500 | 45457.7404512922356322241681260945709282 | 96842.0398752821678809106830122591943958 | 0 | 0 | 0 |  |  |  |  | 631 | 450 | 800 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | WILLIAM BROOKS | ENGINEERING AND COMPLIANCE MANAGER | bill.brooks@atmosenergy.com | 8067984433 | 8067984495 |  |  |  | RIC KISSINGER | VP TECH SERVICES | 8067984432 | ric.kissinger@atmosenergy.com | AT APPROXIMATELY 5:47 THE STATION THAT INTERCONNECTS OUR SYSTEM TO OUR SUPPLIERS WAS STRUCK BY LIGHTNING DAMAGING THE ELECTRONIC CONTROL AND MONITORING EQUIPMENT. OUR GAS CONTROL DISPATCHED AN ALARM AT 5:49. THE CONTROL VALVE FAILED OPEN. A RELIEF VALVE VENTED GAS TO PROTECT THE SYSTEM FOLLOWING THE STATION DAMAGE. THE EQUIPMENT RESPONDED AS DESIGNED TO PROTECT BOTH THE PUBLIC AND THE GAS SYSTEM. WE WERE ABLE TO VALVE OFF THE STATION AND THE AREA WAS DEEMED SAFE AROUND 7:00AM. THERE WAS NO LOSS CUSTOMER SERVICE. THE TESTING TO DETERMINE THE EXTENT OF DAMAGE TOOK SEVERAL HOURS TO COMPLETE. THE STATION IS CURRENTLY LOCKED OFF.
2025-03-31 10:13 | NO | NO | NO | 20140061 | 16198 | 2014-07-28 18:22 | SUPPLEMENTAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2014-06-26 15:00 |  |  | 2014 | EL PASO DISTRIBUTION SYSTEM | EL PASO | EL PASO | TX | 79949 | 31.7587 | -106.4869 | [9 empty] | 2014-06-27 11:18 | 1087308 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-06-26 20:00 |  |  |  | 2014-06-26 15:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | EL PASO DISTRIBUTION SYSTEM | UNKNOWN | [8 empty] | OTHER | SYSTEM WIDE | [9 empty] | OTHER | [8 empty] | UPON NOTIFICATION FROM OUR NATURAL GAS SUPPLIER THAT ODORANT LEVELS MAY NOT BE CONSISTENT, TGS BEGAN CONDUCTING ODORANT TESTS OF THE SYSTEM AND DISCOVERED LOW LEVELS OF ODORANT IN THE EL PASO PIPELINE SYSTEM. | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ODORIZATION IS NOT CONTROLLED BY SCADA BASED SYSTEMS. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | UPON NOTIFICATION FROM OUR NATURAL GAS SUPPLIER ON JUNE 26, 2014, THAT ODORANT LEVELS MAY NOT BE CONSISTENT, TGS BEGAN CONDUCTING ODORANT TESTS ON THE SYSTEM AND DISCOVERED LOW LEVELS OF ODORANT IN THE EL PASO PIPELINE SYSTEM. | [47 empty] | AMY MARK | REGULATORY COMPLIANCE SPECIALIST | amy.mark@onegas.com | 512-370-8378 | 512-370-8700 |  |  |  | MARK MONTGOMERY | DIRECTOR OF ENGINEERING AND COMPLIANCE | 512-370-8348 | mbmontgomery@onegas.com | ON JUNE 26, 2014 TEXAS GAS SERVICE WAS NOTIFIED BY OUR NATURAL GAS SUPPLIER, THAT ODORANT LEVELS MAY NOT BE CONSISTENT. TEXAS GAS SERVICE IMMEDIATELY BEGAN TESTING THE EL PASO PIPELINE SYSTEM FOR ODORANT LEVELS, AND DISCOVERED LATE IN THE EVENING OF JUNE 26, 2014, LOW LEVELS OF ODORANT IN THE EL PASO PIPELINE SYSTEM. UPON LEARNING OF THE LOW LEVEL OF ODORANT, TEXAS GAS SERVICE NOTIFIED THE MEDIA AND PUBLIC THROUGH A PRESS RELEASE. TEXAS GAS SERVICE IMMEDIATELY IMPLEMENTED A PLAN TO MONITOR THE ODORANT LEVELS AND TO INSTALL ADDITIONAL EQUIPMENT TO ADD ODORANT TO THE APPROPRIATE LEVELS. AS OF JUNE 29, 2014 ODORANT EQUIPMENT HAS BEEN INSTALLED AND ODORANT HAS BEEN ADDED, AND THE LEVELS ARE BEING MONITORED.
2025-03-31 10:13 | NO | YES | YES | 20140062 | 15903 | 2014-08-07 12:00 | ORIGINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2014-07-08 16:26 |  |  | 2014 | NW 28TH STREET & N. ROCKWELL AVENUE | BETHANY | OKLAHOMA | OK | 73008 | 35.4984 | -97.6366 | [9 empty] | 2014-07-18 16:00 | 1089515 |  | NATURAL GAS |  | 28.62 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2014-07-08 16:28 |  |  |  | 2014-07-08 16:50 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1960 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | DAMAGED BY VEHICLE. NIPPLE BROKE AT THREADS. | CLASS 3 LOCATION | 0 | 0 | 208 | 254.83005780346816 | 1342 | 1644.14393063583784 | 0 | 0 |  |  | 188 | 140.588441330998248686514886164623467601 |  | 0 | 1738 | 916.550612622280015061295971978984238179 | 2039.562429770304248686514886164623467601 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ONG DISPATCH WAS NOTIFIED BY FIRE DEPARTMENT (THIRD-PARTY). | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | RONALD WOODS | MANAGING ATTORNEY | ronald.woods@onegas.com | (918) 947-7051 |  |  |  |  | RICHARD LAMIRAND | MANAGER - REGULATORY COMPLIANCE | (918) 947-7037 | richard.lamirand@onegas.com | A MULTI-VEHICLE ACCIDENT INVOLVING A FATALITY OCCURRED WHEN A LARGE MOVING TRUCK CROSSED THE MARKED CENTER LANE LINE INTO ONCOMING TRAFFIC AND COLLIDED WITH SEVERAL VEHICLES, INCLUDING AN F-150 TRUCK. THE COLLISION ULTIMATELY FORCED THE F-150 TRUCK OFF THE ROAD, CAUSING IT TO STRIKE AND DAMAGE A RESIDENTIAL GAS METER. THE ONSITE INVESTIGATION REVEALED THAT THE F-150 TRUCK SUSTAINED SIGNIFICANT DAMAGE FROM THE COLLISION, INCLUDING SEVERING THE FUEL LINES, AND CAUGHT FIRE. UPON BEING NOTIFIED BY THE FIRE DEPARTMENT THAT THE GAS METER HAD BEEN DAMAGED AS A RESULT OF THE VEHICLE ACCIDENT, ONG RESPONDED TO THE SCENE. ONG PERSONNEL FOUND THE NATURAL GAS TO HAVE BEEN IGNITED AND BURNING IN THE OPEN AIR. THE FIRE DEPARTMENT ALLOWED ONG TO TURN OFF THE GAS SUPPLY BY CLOSING THE VALVE ON THE DAMAGED RISER. THE INVESTIGATION REVEALED THAT THE F-150 TRUCK WAS FORCED INTO THE NATURAL GAS SERVICE METER LOCATED IN THE UTILITY RIGHT-OF-WAY, CAUSING THE FITTING THREADS TO BREAK AND ALLOWING GAS TO BE RELEASED.
2025-03-31 10:13 | NO | YES | YES | 20140063 | 16215 | 2014-08-08 14:54 | SUPPLEMENTAL FINAL | 18112 | SAN DIEGO GAS & ELECTRIC CO | 8326 CENTURY PARK COURT | SAN DIEGO | CA | 92123 | 2014-07-19 04:18 |  |  | 2014 | 3802 HILLTOP DRIVE | SAN DIEGO | SAN DIEGO | CA | 92102 | 32.7153 | -117.1118 | [9 empty] | 2014-07-19 06:25 | 1089562 |  | NATURAL GAS |  | 20 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 4 | 2014-07-19 04:18 |  |  |  | 2014-07-19 04:54 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1972 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.8 | 0.8 | [7 empty] | CLASS 3 LOCATION | 20000 | 24502.8901734104 | 850 | 1041.372832369942 | 200 | 245.028901734104 | 0 | 0 |  |  | 119 | 88.98949211908931698774080560420315236427 |  | 0 | 21169 | 10763.4717427762564318739054290718038529 | 25878.2813996335353169877408056042031524 | 0 | 0 | 1 |  |  |  |  | 46 | 46 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | tbauer@semprautilities.com | 909-376-7208 | 909-885-9270 |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | ON JULY 19TH, 2014 SDG&E WAS NOTIFIED A VEHICLE INVOLVED ACCIDENT AT THE ABOVE LOCATION THAT IMPACTED THE METER CAUSING AN IGNITED LEAK. THE DRIVER OF THE VEHICLE FAILED TO EXECUTE A RIGHT TURN FROM BOUNDARY STREET ONTO HILLTOP DRIVE AND DROVE INTO THE DRIVEWAY OF 3082 HILLTOP DR. SHEARING OF THE GAS METER. THE ESCAPING GAS IGNITED BURNING THE CAR AND CAUSING MINOR DAMAGE TO THE HOUSE. AN OCCUPANT OF THE VEHICLE, CLAIMING NOT TO HAVE BEEN THE DRIVER, WAS TRANSPORTED TO UCSD HOSPITAL DUE TO BURNS TO HIS FACE AND ARMS. THE INJURED PERSON WAS HOSPITALIZED FOR THE INJURIES. ALL REPAIRS HAVE BEEN COMPLETED, AND CUSTOMER WITHOUT SERVICE HAS BEEN RESTORED.
2025-03-31 10:13 | NO | NO | NO | 20140064 | 15905 | 2014-08-08 17:58 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-05-29 11:05 |  |  | 2014 | RUBY AVE. & TULLY RD. | SAN JOSE | SANTA CLARA | CA | 95148 | 37.3386 | -121.7863 | [9 empty] | 2014-07-31 17:46 | 1090885 |  | NATURAL GAS |  | 67.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2014-05-29 11:05 |  |  |  | 2014-05-29 11:29 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 28 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1986 | [5 empty] | 4 | TR418 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 67203 | 82333.38641618495556 | 0 | 0 | 0 | 0 |  |  | 364 | 272.203152364273204903677758318739054291 |  | 0 | 67567 | 34351.8232170515257664378283712784588441 | 82605.5895685492287649036777583187390543 | 0 | 0 | 8 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | UNKNOWN/OTHER | YES | 189976 | USA NORTH 811 |  | UTILITY OWNER | YES | YES | 168 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | CHRISTIANE MASON | SENIOR MANAGER REGULATORY AND FIELD COMPLIANCE | 925-328-5795 | c6mw@pge.com | ON MAY 29, 2014 AT APPROXIMATELY 1105 HOURS, PACIFIC GAS AND ELECTRIC (PG&E) WAS NOTIFIED THAT A THIRD PARTY CONTRACTOR, AIKEN UNDERGROUND, STRUCK A 4-INCH PLASTIC GAS DISTRIBUTION MAIN WITH A BACKHOE WHILE DIGGING TO INSTALL A UTILITY LINE. THE CONTRACTOR HELD A VALID USA TICKET (#0189976) FOR THE AREA WHERE THE MAIN WAS STRUCK AND THE GAS FACILITIES WERE PROPERLY LOCATED AND MARKED, BUT THE CONTRACTOR FAILED TO HAND DIG, EXPOSE AND PROTECT THE GAS MAIN WHILE EXCAVATING. THE FLOW OF GAS WAS STOPPED AT 1429 HOURS BY DIGGING AND SQUEEZING IN TWO LOCATIONS: ONE WAS ON THE 4-INCH PLASTIC MAIN AND THE OTHER WAS ON A CONNECTED 6-INCH STEEL MAIN. EIGHT RESIDENTIAL CUSTOMERS EXPERIENCED GAS SERVICE INTERRUPTION. SERVICE WAS RESTORED AT APPROXIMATELY 1115 HOURS ON MAY 30, 2014. THERE WERE NO INJURIES, FATALITIES, OR IGNITION AS A RESULT OF THIS INCIDENT AND THE RELEASE OF GAS IS ESTIMATED TO BE LESS THAN 3 MMCF. THIS WAS REPORTED TO THE CPUC DUE TO THE PRESENCE OF MAJOR BAY AREA NEWS MEDIA ON SCENE AT 1230 HOURS. PG&E RECENTLY DETERMINED THAT DAMAGES RELATING TO THIS INCIDENT EXCEED $50,000. THE HIGHER THAN AVERAGE COSTS WERE DUE TO A NUMBER OF FACTORS INCLUDING THE LOCATION OF THE DAMAGE AND THE SIZE AND TYPE MAINS INVOLVED. PG&E NOTIFIED THE NATIONAL RESPONSE CENTER ON JULY 31, 2014.
2025-03-31 10:13 | NO | NO | NO | 20140065 | 15907 | 2014-08-08 18:11 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2014-07-08 07:24 |  |  | 2014 | 1ST & ELM | MILFORD | SEWARD | NE | 68405 | 40.772 | -97.0523 | [9 empty] | 2014-07-08 09:30 | 1088355 |  | NATURAL GAS |  | 25 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-07-08 07:24 |  |  |  | 2014-07-08 08:12 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2013 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | FITTING (PLUG VALVE) WAS CRACKED BY VEHICLE RUNNING INTO IT CAUSING LEAK | CLASS 2 LOCATION | 1000 | 1225.14450867052 | 3000 | 3675.43352601156 | 40000 | 49005.7803468208 | 0 | 0 | 0 |  | 142 | 106.189141856392294220665499124343257443 |  | 0 | 44142 | 22424.628090528403026269702276707530648 | 54012.5475233592722942206654991243432574 | 85 | 0 | 755 |  |  |  |  | 44 | 44 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | NATHAN STEWART | STATE COMPLIANCE SPECIALIST | nathan.stewart@blackhillscorp.com | 4026101108 | 4024376734 |  |  |  | NATHAN STEWART | STATE COMPLIANCE SPECIALIST | 4026101108 | nathan.stewart@blackhillscorp.com | AT APPROXIMATELY 7:45 A DRIVER OF A VEHICLE ROUNDING THE CORNER OF INTERSECTION FIRST STREET AND SOUTH ELM AVENUE, MILFORD NE WAS DISTRACTED, THE VEHICLE LEFT ROADWAY AND WAS LAUNCHED AIR BORNE FOR A SHORT DISTANCE BEFORE IMPACTING A DISTRICT REGULATING STATION (DRS). THE IMPACT FRACTURED A 2' BY-PASS VALVE. 911 CALLED, MILFORD VOLUNTEER FIRE DEPARTMENT, MILFORD POLICE DEPARTMENT RESPONDED. BLACK HILLS ENERGY WAS CONTACT BY 911 CALL CENTER AND BHE PERSONNEL DISPATCHED. MILFORD MUNICIPAL UTILITIES WERE ALSO DISPATCHED TO AREA. FIRST RESPONDING AGENTS INDICATED THAT THE VEHICLE HAD BACKED OFF AND AWAY FROM REGULATING STATION AND WAS SITTING IN THE STREET (ELM STREET). DRIVER NOT INJURED. FIRST RESPONDING BHE PERSONNEL ARRIVED AT 0810 HOURS, ASSESSED SITUATION AND ELECTED TO ALLOW GAS TO FEED, MONITOR AREA AND PREPARE FOR DISRUPTION OF SERVICE TO MOST OF THE SYSTEM. GAS FLOW WAS SHUT-OFF TO THE DRS AT 0902, DISRUPTING SERVICE TO SOME 800 CUSTOMERS. BHE IMPLEMENTED INCIDENT COMMAND SYSTEM, HEAD QUARTERED AT MILFORD CITY LIBRARY. AT APPROXIMATELY 0950 HOURS A MEETING WAS CONDUCTED BY BLACK HILLS ENERGY WITH PUBLIC OFFICIALS, FIRE DEPT. POLICE DEPART. CITY UTILITIES. BHE OPERATIONS AND MAINTENANCE PERSONNEL EXPOSED INLET PIPING, MADE REPAIRS TO BY-PASS VALVE, CONDUCTED LEAKAGE TESTS AND STATION REGULATING/RELIEF DEVICE INSPECTION. IT WAS AT THIS TIME THAT SERVICE WAS RESTORED TO ALL 840 AFFECTED CUSTOMERS.
2025-03-31 10:13 | NO | NO | NO | 20140066 | 15910 | 2014-08-15 12:33 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-07-18 08:45 |  |  | 2014 | 1840 E. 23RD ST. UNIT A | MERCED | MERCED | CA | 95340 | 37.2971 | -120.4527 | [9 empty] | 2014-07-18 | 1089493 |  | NATURAL GAS |  | 127 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2014-07-18 09:04 |  |  |  | 2014-07-18 09:17 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | REGULATOR: POT METAL; METER: ALUMINUM | [9 empty] | OTHER |  |  |  | ARCING ELECTRIC WIRE DAMAGES |  |  |  |  | THE ELECTRICAL WEATHER HEAD HAD FALLEN ONTO THE GAS METER SET AND WAS MAKING A POPPING NOISE. THE METER SET PIPING APPEARS TO HAVE BEEN DAMAGED FROM THE ARCING ELECTRIC WIRES. THE METERS, REGULATOR, AND PIPING SUSTAINED FIRE DAMAGE FROM THE SUBSEQUENT RELEASE AND IGNITION OF NATURAL GAS. | CLASS 3 LOCATION | 50000 | 61257.225433526 | 2000 | 2450.28901734104 | 0 | 0 | 0 | 0 |  |  | 508 | 379.887915936952714535901926444833625219 |  | 0 | 52508 | 26737.1603750982862066549912434325744308 | 64087.4023668039927145359019264448336252 | 0 | 0 | 2 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | CHRISTIANE MASON | SENIOR MANAGER REGULATORY AND FIELD COMPLIANCE | 925-328-5795 | c6mw@pge.com | AT APPROXIMATELY 0904 HOURS ON JULY 18, 2014, PG&E WAS NOTIFIED BY THE MARIPOSA FIRE DEPARTMENT OF A RESIDENTIAL FIRE AT 1840 E 23RD STREET UNIT A, IN MERCED. THE PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON-SITE AT 0917 HOURS AND CONFIRMED THAT NATURAL GAS HAD IGNITED AT THE METER SET. THE RESIDENT REPORTED TO THE FIRE DEPARTMENT THAT HE SMELLED SMOKE, WENT OUTSIDE, AND FOUND THAT THE ELECTRICAL WEATHER HEAD HAD FALLEN ONTO THE GAS METER SET AND WAS MAKING A POPPING NOISE. THE METER SET PIPING APPEARS TO HAVE BEEN DAMAGED FROM THE ARCING ELECTRIC WIRES. THE METERS, REGULATOR, AND PIPING SUSTAINED FIRE DAMAGE FROM THE SUBSEQUENT RELEASE AND IGNITION OF NATURAL GAS. PG&E REMOVED THE TWO-METER MANIFOLD. LOCAL MEDIA (ABC 30 ACTION NEWS) ARRIVED ON SITE AT 0928 HOURS TO REPORT THE INCIDENT. PG&E REPAIR CREW ARRIVED ON-SITE AT 0959 HOURS. THE FLOW OF GAS WAS SHUT OFF AT APPROXIMATELY 1349 HOURS BY INSTALLING AND PLUGGING TWO PRESSURE CONTROL FITTINGS ON THE 2-INCH STEEL GAS MAIN. TWO CUSTOMERS LOST GAS SERVICE DURING THE INCIDENT (UNITS A AND B AT E. 23RD STREET). THERE WERE NO REPORTED INJURIES OR FATALITIES DURING THE INCIDENT. A SPECIAL LEAK SURVEY WAS CONDUCTED IMMEDIATELY AFTER THE INCIDENT, AND NO LEAKS WERE DETECTED. ON AUGUST 1, 2014 (AT APPROXIMATELY 1040 HOURS) SERVICE WAS RESTORED FOR UNIT B AT 1840 E. 23RD STREET. UNIT A AT 1840 E. 23RD STREET IS UNINHABITABLE BECAUSE OF THE FIRE DAMAGE AND PROPERTY DAMAGE IS ESTIMATED AT BEING GREATER THAN $50,000. THIS INCIDENT WAS REPORTED TO THE DOT AND THE CPUC BECAUSE OF THE UNINTENTIONAL RELEASE OF GAS AND SUBSEQUENT IGNITION THAT CONTRIBUTED TO THE ESTIMATED PROPERTY DAMAGES OF OVER $50,000.
2025-03-31 10:13 | NO | YES | NO | 20140067 | 16256 | 2014-08-15 14:25 | SUPPLEMENTAL | 15462 | PECO ENERGY CO | 2301 MARKET STREET, S9-1 | PHILADELPHIA | PA | 19103 | 2014-07-17 11:28 |  |  | 2014 | 118 PENROSE LANE | COATESVILLE | CHESTER | PA | 19320 | 39.9811 | -75.8146 | [9 empty] | 2014-07-17 13:00 | 1089360 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2014-07-17 11:29 |  |  |  | 2014-07-17 11:29 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | CUSTOMER FUEL LINE | [9 empty] | OTHER | [8 empty] | CUSTOMER FUEL LINE FAILED. | CLASS 4 LOCATION | 125000 | 153143.063583815 | 10000 | 12251.4450867052 | 40000 | 49005.7803468208 | 0 | 0 | N/A |  | 9 | 6.73029772329246935201401050788091068301 |  | 0 | 175009 | 88804.3954762796796847635726795096322242 | 214407.0193150642924693520140105078809107 | 0 | 0 | 7 |  |  |  |  | 25 | 25 | 33 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 6 | 0 | YES | 6 | 0 | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [222 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED |  | YES |  |  |  |  | COMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | BRIAN CAMFIELD | MANAGER GAS ASSET MANAGEMENT AND PERFORMANCE | brian.camfield@peco-energy.com | (215) 841-4197 |  |  |  |  | BRIAN CAMFIELD | MANAGER GAS ASSET MANAGEMENT AND PERFORMANCE | (215) 841-4197 | brian.camfield@peco-energy.com | THE COMPANY WAS PERFORMING AN UPRATING PROCEDURE TO CHANGE A LOW PRESSURE DISTRIBUTION MAIN TO MEDIUM PRESSURE AT PRE-SET INCREMENTS. AFTER THE LINE PRESSURE WAS BROUGHT TO 25 PSIG, AN UNIDENTIFIED NON-STANDARD SERVICE OVER PRESSURIZED THE CUSTOMER FUEL LINE. A GAS LEAK OCCURRED INSIDE THE HOME, WHICH IGNITED AND EXPLODED. EMERGENCY FIRST RESPONDERS ARRIVED QUICKLY. THE COMPANY PERFORMED REPAIRS AND REMAINED ON SITE UNTIL ALL REPAIRS WERE COMPLETED. NO ONE WAS AT THE PROPERTY AT THE TIME OF THE EVENT AND NO INJURIES OCCURRED.
2025-03-31 10:13 | NO | NO | NO | 20140068 | 16179 | 2014-08-20 17:30 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2014-07-21 23:40 |  |  | 2014 | 1809 EDSON | HUDSONVILLE | OTTAWA | MI | 49426 | 42.8821 | -85.8291 | [9 empty] | 2014-07-23 17:00 | 1090032 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-07-21 23:40 |  |  |  | 2014-07-22 00:41 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1956 | [8 empty] | OTHER | FLOW COMPUTER FOR ODORANT | [9 empty] | OTHER | [8 empty] | OVER ODORIZATION AT GEORGETOWN GATE STATION | CLASS 3 LOCATION | 0 | 0 | 69970 | 85723.3612716762844 | 5760 | 7056.8323699421952 | 11520 | 14113.6647398843904 | FLARING TO DISPOSE OF GAS WITH EXCESSIVE LEVELS OF MERCAPTAN |  | 0 | 0 |  | 0 | 87250 | 44272.230250481707 | 106893.85838150287 | 0 | 0 | 0 |  |  |  |  | 140 | 140 | 145 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES |  | YES |  |  |  | YES | YES | INCORRECT SETTING OF FLOW RATE ALARM; | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT |  | YES | [8 empty] | YES | FLOW COMPUTER SENSED FALSE HIGH PRESSURE READING, SENDING AN INCORRECT SIGNAL TO THE ODORIZATION EQUIPMENT CAUSING THAT DEVICE TO ACTIVATE AT AN INCREASED RATE AND RESULTING IN AN ELEVATED RATE OF MERCAPTAN INJECTION. | [71 empty] | ROBERT FRECKELTON | MANAGER | freckeltonr@dteenergy.com | 313-389-7755 | 313-389-7757 |  |  |  | ROBERT FRECKELTON | MANAGER | 313-389-7755 | freckeltonr@dteenergy.com | DTE GAS CONTROL RECEIVED NOTIFICATION AT APPROXIMATELY 09:30, JULY 21, 2014 FROM GRAND RAPIDS FIELD TECHNICIANS THAT ROUTINE MAINTENANCE WORK WAS BEING PERFORMED AT THAT FACILITY DURING THAT DAY. NO ALARMS OR UNUSUAL ACTIVITY WERE NOTICED BY GAS CONTROL. AT APPROXIMATELY 16:55, AN ELECTRONIC FLOW COMPUTER AT GEORGETOWN REGULATING STATION BEGAN SENSING FALSE HIGH FLOW AND A FALSE HIGH INLET AND OUTLET PRESSURES. DURING NORMAL OPERATIONS, ODORANT IS AUTOMATICALLY INJECTED INTO THE GRAND RAPIDS DISTRIBUTION SYSTEM BASED UPON VOLUME DELIVERY SIGNALS FROM THE FLOW COMPUTER. THE FALSE HIGH FLOW SIGNALS FROM THE MALFUNCTIONING COMPUTER RESULTED IN OVER-INJECTION OF ODORANT (MERCAPTAN) INTO THE DISTRIBUTION SYSTEM CREATING AN OVER-ODORIZED CONDITION. DTE GAS CONTROL IMMEDIATELY BEGAN RECEIVING AN ALARM FOR HIGH INLET AND OUTLET PRESSURES. THE CONTROLLER PRESUMED THE ALARMS WERE ACTIVATED IN THE COURSE OF THE ROUTINE WORK BEING CONDUCTED BY GRAND RAPIDS FIELD TECHNICIANS. AT APPROXIMATELY 17:00, THE GRAND RAPIDS FIELD TECHNICIANS ONSITE COMPLETED THEIR WORK, WHICH WAS NOT RELATED TO ANY OF THE FLOW OR PRESSURE DEVICES AND LEFT THE SITE UNAWARE THAT AN ALARM HAD BEEN ACTIVATED AT GAS CONTROL. AT APPROXIMATELY 23:40, GAS CONTROL BECAME CONCERNED THEY HAD NOT RECEIVED ANY CONTACT FORM THE GRAND RAPIDS FIELD TECHNICIANS SINCE EARLY THAT MORNING AND CONTACTED AN OPERATIONS SUPERVISOR. A SECOND FIELD CREW WAS DEPLOYED TO GEORGETOWN STATION TO INVESTIGATE, ARRIVING AT 00:41 JULY 22, 2014. AT 00:49, THE FIELD CREW DETERMINED THE ODORANT INJECTION SYSTEM WAS OPERATING AT ABNORMALLY HIGH RATE AND PLACED THE SYSTEM INTO STANDBY MODE. THE FIELD CREW CONTACTED THE REGION CONTROLS TECHNICIAN WHO ALSO RESPONDED TO THE GEORGETOWN STATION. THE FLOW COMPUTER WAS RESET BY THE CONTROLS TECHNICIAN, THE ABNORMAL PRESSURE AND FLOW SIGNALS WERE CLEARED, AND THE COMPUTER RESUMED NORMAL OPERATION. AT 01:30, THE FIELD CREW REPORTED TO GAS CONTROL THAT THE ODOR INJECTION SYSTEM HAD BEEN OPERATING AT AN ABNORMALLY HIGH RATE OVER THE PAST SEVERAL HOURS. AT 05:45, GEORGETOWN GATE STATION WAS ISOLATED FROM THE SYSTEM IN AN EFFORT TO CONTAIN EXCESS ODORANT FROM GETTING INTO THE SYSTEM. BY 08:00, JULY 23 THE EVENT WAS OVER AND LEAK COMPLAINT VOLUME WAS BACK TO NORMAL. THE ABNORMAL HIGH ODORIZATION RATE RESULTED IN 610 LEAK COMPLAINTS THAT WERE RESPONDED TO AND INVESTIGATED BY GRAND RAPIDS FIELD PERSONNEL.
2025-03-31 10:13 | NO | YES | NO | 20140069 | 15914 | 2014-08-22 19:34 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2014-07-24 13:21 |  |  | 2014 | 2000 W. OCEANFRONT | NEWPORT BEACH | ORANGE | CA | 92663 | 33.6074 | -117.9278 | [9 empty] | 2014-07-24 18:10 | 1090181 |  | NATURAL GAS |  | 4021 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 20 | 2014-07-24 13:21 |  |  |  | 2014-07-24 13:21 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1966 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 11 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 500000 | 612572.25433526 | 1500 | 1837.71676300578 | 0 | 0 |  |  | 24124 | 18040.1891418563922942206654991243432574 |  | 0 | 525624 | 271158.414217696093026269702276707530648 | 632450.1602401221722942206654991243432574 | 29 | 0 | 3104 |  |  |  |  | 43 | 43 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | OTHER | [12 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | NO |  |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED | YES | 65 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | tbauer@semprautilities.com | 909-376-7208 | 909-885-6270 |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | ON JULY 24TH, 2014 A CONTRACTOR STRUCK AN 8 INCH STEEL DISTRIBUTION LINE WHILE GRADING, CAUSING A LEAK. NO INJURIES OR PUBLIC PROPERTY DAMAGE RESULTED FROM THIS INCIDENT. CREWS RESPONDED AND CONTROLLED THE GAS UTILIZING EXISTING PRESSURE CONTROL FITTINGS. ALL REPAIRS WERE COMPLETED AND THE DAMAGED SECTION OF PIPE WAS REPLACED. BY 20:00 HOURS ON JULY 27TH, THE 3,133 CUSTOMERS WHOSE SERVICE WAS INTERRUPTED WERE RESTORED OR LEFT NOTICES ON HOW TO CONTACT THE COMPANY TO RESTORE SERVICE. INVESTIGATION OF THE INCIDENT SHOWED THE CONTRACTOR HAD NOT CONTACTED USA AND WERE IN THE PROCESS OF SAND REMEDIATION ON THE BEACH WHEN THEY STRUCK THE LINE. THIS INCIDENT WAS REPORTED TO DOT AND THE CPUC DUE TO THE ESTIMATED COSTS WOULD EXCEED $50,000 AND THE GAS LOSS WOULD EXCEED THREE MILLION CUBIC FEET.
2025-03-31 10:13 | NO | NO | NO | 20140070 | 34476 | 2014-08-26 08:29 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2014-05-08 12:37 |  |  | 2014 | 272 RIVER RD | ANDOVER | ESSEX | MA | 01810 | 42.6754 | -71.224 | [9 empty] | 2014-08-26 06:30 | 1093449 |  | NATURAL GAS |  | 1528.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-05-08 12:41 |  |  |  | 2014-05-08 13:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 38 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1988 | [5 empty] | 6 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.602 |  | 3408 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 57066 | 69914.09653179189432 | 0 | 0 | 0 | 0 |  |  | 13525 | 10114.1418563922942206654991243432574431 |  | 0 | 70591 | 38312.495345352952821702276707530647986 | 80028.2383881841885406654991243432574431 | 0 | 0 | 260 |  |  |  |  | 89 | 89 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 20141713378 |  |  | UTILITY OWNER | YES | YES | 10 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | MEGGAN BIRMINGHAM | MANAGER COMPLIANCE GAS OPERATIONS | meggan.pena@eversource.com | 508.468.9956 |  |  |  |  | MEGGAN BIRMINGHAM | MANAGER COMPLIANCE GAS OPERATIONS | 508.468.9956 | meggan.pena@eversource.com | CONTRACTOR WAS INSTALLING A SEWER LINE AND EXCAVATION WAS NOT PERFORMED WITH PRECAUTION TO PREVENT DAMAGE TO GAS LINE FACILITY. THERE WAS A BREAKDOWN IN THE NOTIFICATION PROCESS WHICH RESULTED IN A DELAYED NRC CALL BEING MADE.
2025-03-31 10:13 | NO | NO | NO | 20140072 | 15920 | 2014-09-02 11:58 | ORIGINAL | 31588 | COSERV GAS, LTD | 7701 SOUTH STEMMONS | CORINTH | TX | 76210 | 2014-08-13 09:43 |  |  | 2014 | ELDERADO PARKWAY & PRESTON ON THE LAKES | LITTLE ELM | DENTON | TX | 75068 | 33.1687 | -96.908 | [9 empty] | 2014-08-21 07:48 | 1092954 |  | NATURAL GAS |  | 241 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2014-08-13 09:43 |  |  |  | 2014-08-13 10:09 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 120 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2012 | [5 empty] | 6 | ASTM D2513 | POLY PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.8 | 2.4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 14000 | 17152.02312138728 | 9000 | 11026.30057803468 | 0 | 0 |  |  | 1884 | 1408.875656742556917688266199649737302977 |  | 0 | 24884 | 12973.9090396795700105078809106830122592 | 29587.199356164516917688266199649737303 | 0 | 0 | 0 |  |  |  |  | 35 | 35 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | TEXAS 811 ONE CALL |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BORING | WATER | YES | 147189045 | TEXAS 811 |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | BRIAN STILES | COMPLIANCE AND TECHNOLOGY SUPERINTENDENT | bstiles@coserv.com | 940-321-7800 | 940-270-6830 |  |  |  | BRIAN STILES | COMPLIANCE AND TECHNOLOGY SUPERINTENDENT | 940-321-7800 | bstiles@coserv.com | EXCAVATOR POT HOLED UNKNOWN LINE AND ASSUMED IT WAS THE GAS LINE. THEY PROCEEDED AND STRUCK A 6" PLASTIC MAIN APPROX. 10 FOOT IN DEPTH. SECTION OF MAIN WAS DISCONNECTED AND ISOLATED UNTIL REPAIRS WERE MADE. DURING INVESTIGATION IT WAS DETERMINED THAT THE MARKINGS WERE APPROX. 2 FT INACCURATE.
2025-03-31 10:13 | NO | YES | YES | 20140074 | 15922 | 2014-09-03 15:10 | ORIGINAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2014-08-04 13:00 |  |  | 2014 | 15253 EVANSTON | DETROIT | WAYNE | MI | 48224 | 42.4079 | -82.957 | [9 empty] | 2014-08-05 11:25 | 1091337 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2014-08-04 13:00 |  |  |  | 2014-08-04 13:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1928 | [5 empty] | 1.5 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 410 | 502.3092485549132 | 360 | 441.0520231213872 | 0 | 0 |  |  | 5 | 3.73905429071803852889667250437828371278 |  | 0 | 775 | 394.17079018319626486865148861646234676 | 947.100325967018438528896672504378283713 | 0 | 0 | 0 |  |  |  |  | 2 | 2 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 42130254 | NO |  | UTILITY OWNER | NO |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ROBERT FRECKELTON | MANAGER | freckeltonr@dteenergy.com | 313.389.7755 | 313.389.7757 |  |  |  | ROBERT FRECKELTON | MANAGER | 313.389.7755 | freckeltonr@dteenergy.com | DURING THE PROCESS OF ABANDONING THE SERVICE LINE FOR 15253 EVANSTON, A DTE GAS BACKHOE OPERATOR STRUCK THE 11/2-INCH STEEL SERVICE LINE WITH THE BACKHOE BUCKET AND CRACKED THE THREADS AT A COUPLING NEAR THE MAIN CAUSING A NATURAL GAS LEAK. A DTE GAS MAINTENANCE FITTER ENTERED THE EXCAVATION TO STOP THE LEAK. THE MAINTENANCE FITTER ATTEMPTED TO REMOVE THE 1-1/2 INCH PLUG FROM THE TOP OF THE STREET TEE AT THE MAIN IN ORDER TO INSERT AN EXPANDABLE STOPPER TO SHUT OFF THE GAS BUT WAS UNABLE TO DO SO. THE MAINTENANCE FITTER DECIDED TO CUT THE SERVICE LINE WITH A FOUR-WHEEL PIPE CUTTER IN ORDER TO STOP THE FLOW OF GAS BY INSERTING A PLUG INTO THE END OF THE PIPE. WHEN THE MAINTENANCE FITTER ATTEMPTED TO MOUNT THE CUTTER ON THE 1-1/2 INCH PIPE THE ESCAPING GAS IGNITED, BURNING THE MAINTENANCE FITTER WHO WAS STILL IN THE EXCAVATION. THE MAINTENANCE FITTER WAS TRANSPORTED TO THE HOSPITAL BY AMBULANCE AND TREATED FOR FIRST AND SECOND DEGREE BURNS TO FACE AND ARMS. THE MAINTENANCE FITTER WAS HOSPITALIZED OVERNIGHT AND RELEASED THE NEXT DAY. A SECOND REPAIR CREW WAS SENT TO THE SITE AND COMPLETED THE REPAIR BY INSTALLING A SERVICE SADDLE REPAIR CLAMP.
2025-03-31 10:13 | NO | NO | NO | 20140075 | 15983 | 2014-09-08 11:49 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD N.E. SUITE 20 | ALBUQUERQUE | NM | 87109 | 2014-08-08 15:18 |  |  | 2014 | 6908 REDONDO PEAK RD, N.E. | RIO RANCHO | SANDOVAL | NM | 87124 | 35.2982 | -106.5907 | [9 empty] | 2014-08-08 16:34 | 1091745 |  | NATURAL GAS |  | 0.296 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2014-08-08 15:46 |  |  |  | 2014-08-08 15:46 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1992 | [8 empty] | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | METER SET MELTED AND GAS WAS RELEASED FROM THE RISER AND IGNITED. | CLASS 3 LOCATION | 55000 | 67382.9479768786 | 250 | 306.28612716763 | 230 | 281.7832369942196 | 0 | 0 |  |  | 2 | 1.49562171628721541155866900175131348511 |  | 0 | 55482 | 28152.9403777303184899474605954465849387 | 67972.5129627567368154115586690017513135 | 0 | 0 | 1 |  |  |  |  | 53 | 53 | 56 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | GARY G. ROYBAL | MANAGER DOT PIPELINE SAFETY COMPLIANCE | gary.roybal@nmgco.com | 505-697-3636 | 505-697-4481 |  |  |  | ED KACER | VP OPERATIONS AND ENGINEERING | 505-697-3303 | ed.kacer@nmgco.com | NMGC WAS NOTIFIED BY THE FIRE DEPARTMENT OF A FIRE NEAR OR AT THE METER LOCATED AT 6908 REDONDO PEAK DR. NE, RIO RANCHO, NM. THE FIRE MELTED THE METER AND CAUSED A RELEASE OF GAS WHICH FUELED THE FIRE. WHEN NMGC RESPONSE PERSONNEL ARRIVED, GAS HAD BEEN SHUT-OFF AT THE SERVICE STOP BY THE FD. THE METER SET WAS MELTED. A BARHOLE SURVEY OF THE SERVICE LINE SHOWED 0 GAS READINGS. CAUSE OF FIRE THAT MELTED THE METER IS UNKNOWN. FIRE DEPARTMENT REPORT DID NOT IDENTIFY HOW THE FIRE STARTED OR WHERE IT STARTED. BASED ON AVAILABLE INFORMATION, THE ROOT CAUSE OF THIS EVENT IS UNDETERMINED.
2025-03-31 10:13 | YES | NO | NO | 20140076 | 15931 | 2014-09-08 15:42 | SUPPLEMENTAL FINAL | 4483 | ENSTAR NATURAL GAS CO | 3000 SPENARD ROAD | ANCHORAGE | AK | 99503 | 2014-08-16 01:30 |  |  | 2014 | 18117 N PARKVIEW TERRACE LOOP | EAGLE RIVER | ANCHORAGE | AK | 99577 | 61.3067 | -149.5439 | [9 empty] | 2014-08-16 03:47 | 1092498 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2014-08-16 01:30 |  |  |  | 2014-08-16 02:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1983 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.062 |  | 3408 | OTHER | [8 empty] | HOT EMBERS FROM A BBQ GRILL STARTED THE STRUCUTRE ON FIRE AND THE SERVICE LINE, REGULATOR AND METER SUBSEQUENTLY CAUGHT FIRE ANND BURNED. THIS IS A FIRE FIRST INCIDENT. | CLASS 3 LOCATION | 300000 | 367543.352601156 | 500 | 612.57225433526 | 500 | 612.57225433526 | 0 | 0 |  |  | 100 | 74.78108581436077057793345008756567425569 |  | 0 | 301100 | 152802.0285204269684973730297723292469352 | 368843.2781956408807705779334500875656743 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | DAVID BREDIN | DIRECTOR OF OPERATIONS | dave.bredin@enstarnaturalgas.com | 907-264-3745 | 907-562-0053 |  |  |  | DAVID BREDIN | DIRECTOR OF OPERATIONS | 907-264-3745 | dave.bredin@enstarnaturalgas.com | THIS WAS A FIRE FIRST INCIDENT. HOT EMBERS FROM A BBQ STARTED THE FIRE AND THE SERVICE LINE, REGULATOR AND METER SUBSEQUENTLY CAUGHT FIRE.
2025-03-31 10:13 | NO | NO | NO | 20140077 | 16026 | 2014-09-10 07:45 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2014-08-11 08:27 |  |  | 2014 | 136 W. MAIN ST | NEWARK | LICKING | OH | 43055-5008 | 40.0564 | -82.4079 | [9 empty] | 2014-08-11 10:05 | 1091910 |  | NATURAL GAS |  | 3.35 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 25 | 2014-08-11 08:27 |  |  |  | 2014-08-11 08:55 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 58250 | 71364.66763005779 | 3000 | 3675.43352601156 | 1500 | 1837.71676300578 | 0 | 0 |  |  | 34 | 25.42556917688266199649737302977232924694 |  | 0 | 62784 | 31864.006652629171809106830122591943958 | 76903.2434882520126619964973730297723292 | 1 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ROB SMITH | OPERATION COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB SMITH | OPERATION COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | A CAR STUCK THE BUILDING AND ABOVE GROUND GAS LINE (RISER) AT 136 W. MAIN ST, NEWARK. THE CAR STRIKING THE GAS LINE CAUSED MOVEMENT OF BOTH JURISDICTIONAL AND NON-JURISDICTIONAL GAS PIPING INSIDE THE METER/MECHANICAL ROOM RESULTING IN A RELEASE OF GAS. THE GAS BUILT UP INSIDE THE METER/MECHANICAL ROOM AND WAS IGNITED BY AN UNKNOWN SOURCE RESULTING IN AN EXPLOSION AND FIRE. THE EXPLOSION AND FIRE OCCURRED PRIOR TO GAS COMPANY PERSONNEL ARRIVAL. UPON EXAMINATION OF THE DAMAGED GAS PIPING WITHIN THE METER/MECHANICAL ROOM COLUMBIA OBSERVED AN INLET METER SWIVEL SHEERED FROM THE SETTING AND SEVERAL CUSTOMER OWNED HOUSE LINES BROKEN. COLUMBIA IS UNABLE TO DETERMINE WHETHER THE DAMAGE TO THE JURISDICTIONAL PIPING WAS A RESULT OF THE IMPACT OF THE VEHICLE OR AS A RESULT OF THE EXPLOSION AND SUBSEQUENT STRUCTURAL DAMAGE.
2025-03-31 10:13 | NO | YES | NO | 20140078 | 16224 | 2014-09-10 15:20 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2014-08-10 15:00 |  |  | 2014 | 310 PAIGE ST. | SCHENECTADY | Not Within a County or Parish | NY | 12307 | 42.8079 | -73.9387 | [9 empty] | 2014-08-10 16:38 | 1091862 |  | NATURAL GAS |  | 5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | YES | 0 | 2014-08-10 15:00 |  |  |  | 2014-08-10 16:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1937 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | THE POST-INCIDENT INVESTIGATION INDICATES THAT THE CAUSE OF THE INCIDENT WAS GAS ESCAPING FROM A FRACTURED GAS LINE INSIDE THE PREMISES, BEYOND THE METER. THE LEAK WAS THE RESULT OF TRESPASSERS CUTTING AND REMOVING SEGMENTS OF CUSTOMER GAS PIPING INSIDE THE PREMISES PRIOR TO THE EXPLOSION. | CLASS 4 LOCATION | 120000 | 147017.3410404624 | 5000 | 6125.7225433526 | 15000 | 18377.1676300578 | 0 | 0 |  |  | 0 | 0 |  | 0 | 140000 | 71038.53564547208 | 171520.2312138728 | 0 | 0 | 0 |  |  |  |  | 8.3 | 8 | 12 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | GAS DISPATCH CALLED GSO |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VIEW ONLY OF SCADA NO CONTROL | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | THE POST-INCIDENT INVESTIGATION INDICATES THAT THE CAUSE OF THE INCIDENT WAS GAS ESCAPING FROM A FRACTURED GAS LINE INSIDE THE PREMISES, BEYOND THE METER OF THIS PROPERTY LATER DETERMINED TO BE VACANT. THE LEAK WAS THE RESULT OF TRESPASSERS CUTTING AND REMOVING SEGMENTS OF GAS PIPING INSIDE THE PREMISES PRIOR TO THE EXPLOSION. | [47 empty] | BRIAN J. DOWNING | LEAD SUPERVISOR UPSTATE DISPATCH AND SCHEDULING | brian.downing@nationalgrid.com | 315-460-2035 | 315-460-2762 |  |  |  | BRYAN PATTERSON | MANAGER UPSTATE DISPATCH AND SCHEDULING | 315-460-2635 | bryan.patterson@nationalgrid.com | AN EXPLOSION OCCURRED AT 310 PAIGE STREET PROMPTING THE SHUTDOWN OF THE GAS SERVICE LINE TO THIS DWELLING. THE ROOT CAUSE OF THE INCIDENT INDICATES THAT THE CAUSE OF THE INCIDENT WAS GAS ESCAPING FROM A FRACTURED GAS LINE INSIDE THE PREMISES, BEYOND THE METER OF THIS PROPERTY LATER FOUND TO BE VACANT. THE LEAK WAS THE RESULT OF TRESPASSERS CUTTING AND REMOVING SEGMENTS OF GAS PIPING INSIDE THE PREMISES PRIOR TO THE EXPLOSION.. THE SERVICE WAS PERMANENTLY RETIRED ON AUGUST 10, 2014.NATIONAL GRID BILLING RECORDS INDICATE THAT THE ELECTRIC AND GAS SERVICES TO BOTH UNITS WERE INACTIVE FROM MARCH 2013 THROUGH THE DATE OF THE INCIDENT. THE GAS SERVICE WAS DISCONTINUED BY THE COMPANY VIA 'SOFT CLOSURE,' WHERE NO MECHANICAL DEVICE OR FITTING WAS INSTALLED AT THE SERVICE VALVE TO PREVENT THE FLOW OF GAS. THE COMPANY USED 'SOFT CLOSURE' BECAUSE THE SERVICE VALVES AND METERS WERE INSIDE THE RESIDENCE, AND THE COMPANY CLAIMS IT COULD NOT GAIN ACCESS TO PHYSICALLY LOCK THEM. A CONTRIBUTING FACTOR TO THIS INCIDENT WAS NATIONAL GRID'S POLICY IN PLACE AT THE TIME AND DECISION NOT TO PHYSICALLY LOCK THE GAS SERVICE LINE VALVES AND/OR PHYSICALLY DISCONNECT THE CUSTOMER PIPING FROM THE GAS SUPPLY, WHEN THE SERVICE WAS DISCONTINUED.
2025-03-31 10:13 | NO | YES | YES | 20140079 | 15928 | 2014-09-16 15:10 | ORIGINAL | 3110 | DANVILLE, CITY OF | 1040 MONUMENT ST | DANVILLE | VA | 24541 | 2014-08-16 01:16 |  |  | 2014 | 677 ARNETT BLVD | DANVILLE |  | VA | 24541 | 36.6155 | -79.3987 | [9 empty] | 2014-08-16 14:00 | 1092529 |  | NATURAL GAS |  | 7100 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 6 | 6 | YES |  |  |  |  | YES | 16 | 2014-08-16 01:20 |  |  |  | 2014-08-16 01:42 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | 2004 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 0.09 |  |  | UNKNOWN | OTHER | [8 empty] | VEHICLE IMPACT, DISLOCATION OF METER PIPING | CLASS 3 LOCATION | 550000 | 673829.479768786 | 500 | 612.57225433526 | 750 | 918.85838150289 | 0 | 0 |  |  | 71 | 53.09457092819614711033274956217162872154 |  | 0 | 551321 | 279763.349690736332513134851138353765324 | 675414.0049755523461471103327495621716287 | 0 | 0 | 14 |  |  |  |  | 30 | 30 | 100 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | TIM W. LOVE | COMPLIANCE COORDINATOR DANVILLE WATER AND GAS | lovetw@danvilleva.gov | 434-799-5268 | 434-857-3329 |  |  |  | ALLEN WILES | DIRECTOR DANVILLE WATER AND GAS | 434-799-5284 | wilesal@danvilleva.gov | ON THE MORNING OF AUGUST 16, 2014 AT APPROXIMATELY 1:15 AM, A VEHICLE, DRIVEN BY AN UN-LICENSED, ALCOHOL IMPAIRED INDIVIDUAL, WHO WAS CHARGED WITH DUI, CROSSED OVER ARNETT BLVD FROM GUILFORD ST. JUMPED OVER THE CURB & GUTTER AND TRAVELED AN ADDITIONAL 119FT BEFORE IMPACTING THE SIDE OF THE APARTMENT COMPLEX LOCATED AT 677 ARNETT BLVD AND SUBSEQUENTLY IMPACTING A METER SET AND DISLODGING THE METER FROM THE RISER. THE IMPACT WAS SUCH THAT IT PUSHED THE RISER SECTION TOWARDS THE CRAWL SPACE OF THE APARTMENT COMPLEX AND RELEASED GAS INTO SAID SPACE. THE GAS THEN PROCEEDED TO MIGRATE INTO THE BULDING AND WAS IGNITED, IGNITION SOURCE UNKNOWN.
2025-03-31 10:13 | NO | NO | NO | 20140080 | 16054 | 2014-09-19 10:21 | SUPPLEMENTAL FINAL | 15329 | PEOPLES GAS LIGHT & COKE CO | 200 E RANDOLPH STREET | CHICAGO | IL | 60601 | 2014-08-20 15:55 |  |  | 2014 | EAST 80TH STREET AND CRANDON AVENUE | CHICAGO | COOK | IL | 60617 | 41.7499 | -87.5686 | [9 empty] | 2014-08-20 17:28 | 1092926 |  | NATURAL GAS |  | 1756 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-08-20 15:55 |  |  |  | 2014-08-20 15:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 60 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1962 | [5 empty] | 20 | UNKNOWN | UNKNOWN | DUCTILE IRON | [10 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 77825 | 95346.871387283219 | 0 | 0 |  |  | 12139 | 9077.676007005253940455341506129597197898 |  | 0 | 89964 | 47887.1963335459307161120840630472854641 | 104424.5473942884729404553415061295971979 | 0 | 0 | 0 |  |  |  |  | 22 | 22 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 8 | 0 | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | HARSH MEHTA | ENGINEER | hbmehta@peoplesgasdelivery.com | 3122403999 |  |  |  |  | TOM WEBB | COMPLIANCE MANAGER | 3122404650 | tjwebb@peoplesgasdelivery.com | ON AUGUST 20, 2014 AT 1555 HOURS, A PEOPLES GAS CREW WAS RE-PRESSURIZING A 20" DUCTILE IRON MEDIUM PRESSURE MAIN AT THE INTERSECTION OF EAST 80TH STREET AND CRANDON AVENUE IN CHICAGO, ILLINOIS. PRIOR TO RE-PRESSURIZING THE MAIN, THE CREW PLACED A CONCRETE THRUST BLOCK AGAINST THE CAP THAT WAS ATTACHED TO THE END OF THE MAIN IN THE EXCAVATION. TWO EMPLOYEES WERE WORKING ON THE OPPOSITE SIDE OF THE EXCAVATION ON A DEAD SECTION OF THE MAIN, PREPARING IT FOR INSERTION. AFTER THE LIVE SIDE HAD BEEN RE-PRESSURIZED TO LINE PRESSURE OF 22 PSIG, AN UNEXPOSED MECHANICAL JOINT FAILED, CAUSING THE SEGMENT OF THE LIVE MAIN TO DISLODGE. AS A RESULT OF THE PRESSURE FROM THE SEPARATION, THE MAIN SEGMENT HIT AND PUSHED THE THRUST BLOCK TO THE OTHER SIDE OF THE EXCAVATION, INJURING THE TWO EMPLOYEES. THE EMPLOYEES WERE TREATED AND RELEASED FROM A HOSPITAL THE SAME DAY, WITHOUT BEING FORMALLY ADMITTED. IT WAS DETERMINED THAT THE THRUST BLOCK WAS NOT ADEQUATELY SIZED ACCORDING TO THE PROCEDURE FOR THIS TYPE OF WORK AND THE APPARENT CAUSE IS LISTED AS INCORRECT OPERATION. ALTHOUGH THIS INCIDENT DOES NOT MEET THE REPORTING CRITERIA IN 49 CFR 191.3 (1) OR (2), AN INCIDENT REPORT IS BEING SUBMITTED TO FOLLOW UP ON THE INITIAL TELEPHONIC REPORT MADE TO THE NATIONAL RESPONSE CENTER.
2025-03-31 10:13 | NO | YES | YES | 20140081 | 15930 | 2014-09-22 15:13 | ORIGINAL FINAL | 603 | CENTERPOINT ENERGY RESOURCES CORP. | 401 W. CAPITOL, SUITE 600 | LITTLE ROCK | AR | 72201 | 2014-08-25 10:35 |  |  | 2014 | 37 KNIGHT DR | NORTH LITTLE ROCK | PULASKI | AR | 72117 | 34.7699 | -92.2635 | [9 empty] | 2014-08-25 11:58 | 1093370 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 1 | 2014-08-25 10:39 |  |  |  | 2014-08-25 10:42 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | OTHER | PUBLICALLY OWNED LDC | SERVICE |  | UNKNOWN | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 50000 | 61257.225433526 | 100 | 122.514450867052 | 500 | 612.57225433526 | 0 | 0 | NONE ANTICIPATED-SEE REMARKS IN NARRATIVE |  | 12 | 8.97373029772329246935201401050788091068 |  | 0 | 50612 | 25683.6576806400627796847635726795096322 | 62001.2858690260352924693520140105078809 | 0 | 0 | 0 |  |  |  |  | 10 | 10 | 20 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 4 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BORING | NATURAL GAS | YES | 1408120262 |  |  | CONTRACT LOCATOR | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | JAY REBER | DISTRICT OPERATIONS MANAGER | jay.reber@centerpointenergy.com | 501-377-4980 | 501-377-4721 |  |  |  | KEITH KITTINGER | REGIONAL OPERATIONS DIRECTOR | 501-377-4669 | keith.kittinger@centerpointenergy.com | J.F. CONSTRUCTION, A CONTRACTOR WORKING FOR CENTERPOINT ENERGY, WAS IN THE PROCESS OF REPLACING AN EXISTING 3/4" STEEL SERVICE LINE TO AN INACTIVE ACCOUNT AT 37 KNIGHT DRIVE, NORTH LITTLE ROCK, AR. A LOCATE WAS REQUESTED FROM THE ARKANSAS ONE CALL CENTER TO LOCATED ALL FACILITIES; HOWEVER THE CONTRACTOR WAS RESPONSIBLE FOR LOCATING THE CENTERPOINT ENERGY FACILITIES. EMPLOYEES OF J.F CONSTRUCTION USED A PIPE LOCATOR TO VERIFY THE LOCATION OF THE EXISTING SERVICE, FOUND IT TO NOT BE IN CONFLICT WITH THEIR PLANNED WORK, BUT DID NOT COMPLETELY MARK THE REMAINDER OF THE SERVICE LINE. DUE TO THE LARGE TREES ON THE PROPERTY, THE ORIGINAL SERVICE LINE INSTALLATION DID NOT TAKE A PERPENDICULAR PATH FROM THE MAIN. A PNEUMATIC BORING TOOL WAS PLACED IN A BELL HOLE FOR THE PURPOSE OF INSTALLING A NEW SERVICE. AFTER BORING FOR ABOUT 20 MINUTES, THE TOOL STRUCK WHAT WAS DETERMINED TO BE THE EXISTING SERVICE LINE. THE IMPACT FROM THE BORING TOOL BENT THE 3/4' STEEL SERVICE LINE AT THE IMPACT POINT, CAUSING A PARTIAL SEPARATION OF THE PIPE AT A THREADED COUPLING SIX FEET EAST OF THE MOBILE HOME AND ANOTHER LEAK OF UNDETERMINED NATURE UNDER THE MOBILE HOME. APPROXIMATELY 10 MINUTES AFTER THE LEAK BEGAN, A SMALL EXPLOSION TOOK PLACE AND THE RESULTING FLASH CAUSED SECOND-DEGREE BURNS TO THE RESIDENT INSIDE THE MOBILE HOME. HYDRAULIC SQUEEZE TOOLS WERE USED TO STOP THE FLOW OF GAS AND TO RETIRE/ABANDON THE SERVICE LINE. THE PIPELINE FACILITY (SERVICE LINE) REMAINS SHUT DOWN. HOWEVER, INSTALLATION OF A NEW SERVICE IS NOT ANTICIPATED. THEREFORE, WE ARE NOT PLANNING TO FILE A SUPPLEMENTAL REPORT. CENTERPOINT ENERGY DOES NOT ANTICIPATE ANY ADDITIONAL COSTS FROM THIS INCIDENT. WE ANTICIPATE ALL ASSOCIATED COSTS TO BE BORNE BY THE CONTRACTOR. ALSO, SINCE WE HAVE NO ACCESS TO PROPERTY DAMAGE OR MEDICAL CLAIM INFORMATION, WE ARE ESTIMATING THESE TO BE $50,000.
2025-03-31 10:13 | NO | YES | NO | 20140082 | 15936 | 2014-09-23 21:33 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-08-24 03:20 |  |  | 2014 | EARTHQUAKE EPICENTER | AMERICAN CANYON | NAPA | CA | 94559 | 38.1763 | -122.3026 | [9 empty] | 2014-08-24 | 1093289 | [5 empty] | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2014-08-24 04:50 |  |  |  | 2014-08-24 05:05 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | METER SET, SERVICES, MAIN |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | MAIN, SERVICES | UNKNOWN | [8 empty] | OTHER | PLASTIC, STEEL | [9 empty] | OTHER | [8 empty] | DAMAGES CAUSED BY EARTHQUAKE | CLASS 3 LOCATION | 0 | 0 | 15400000 | 18867225.433526008 | 0 | 0 | 0 | 0 | PLEASE NOTE THAT THE EARTHQUAKE-RELATED GAS WORK IS ONGOING |  | 0 | 0 |  | 0 | 15400000 | 7814238.9210019288 | 18867225.433526008 | 5 | 0 | 155 |  |  |  |  | 0 | 0 | 0 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS THE EARTHQUAKE | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [56 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | EARTHQUAKE |  |  |  |  | NO | [218 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LARRY DENISTON | ACTING MANAGER REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT APPROXIMATELY 0320 HOURS ON AUGUST 24, 2014, A MAGNITUDE 6.0 EARTHQUAKE STRUCK THE NAPA COUNTY AREA CAUSING DAMAGE TO DISTRIBUTION FACILITIES RESULTING IN AN UNINTENTIONAL RELEASE OF GAS FROM BOTH PG&E AND CUSTOMER FACILITIES. OVER 11,000 DISTRIBUTION SERVICES WERE SURVEYED AND OVER 675,000 FEET OF DISTRIBUTION MAIN WAS SURVEYED. PG&E HAS DETECTED AND REPAIRED OVER 1,300 LEAKS ON ITS GAS DISTRIBUTION SYSTEM THROUGHOUT THE COUNTIES OF NAPA, SOLANO AND SONOMA. EXTERNAL FORCES FROM THE EARTHQUAKE WERE RESPONSIBLE FOR AN ESTIMATED SERVICE DISRUPTION TO APPROXIMATELY 160 CUSTOMERS. THE MAJORITY OF THESE ARE DUE TO LEAKS ON CUSTOMER FACILITIES. IN ADDITION, PG&E RESPONDED TO OVER 5,800 CUSTOMER INITIATED REQUESTS RELATED TO GAS ODOR CALLS, LEAK CHECKS, PILOT RELIGHTS, GAS TURN-ONS, AND PERFORMED APPROXIMATELY 2,500 ADDITIONAL COURTESY SAFETY CHECKS. THERE ARE NO KNOWN INJURIES OR DEATHS RELATING TO PG&E'S GAS FACILITIES. PG&E REPORTED THIS INCIDENT TO THE DOT AND THE CPUC BASED ON OPERATOR JUDGMENT OF THE SIGNIFICANCE OF THIS EVENT. PLEASE NOTE THAT PG&E'S RESPONSES TO PARTICULAR SECTIONS OF THIS REPORT MAY NOT APPLY AS OUR REPORTING IS ON THE REPAIR AND RESPONSE WORK PERFORMED ON PG&E'S GAS DISTRIBUTION SYSTEM AND NOT A SPECIFIC LOCATION. (NOTE: THE EARTHQUAKE MAGNITUDE HAS BEEN CORRECTED FROM 6.1 TO 6.0 IN THIS PHMSA 7100 SUPPLEMENTAL REPORT.)
2025-03-31 10:13 | NO | NO | NO | 20140083 | 16030 | 2014-09-26 10:49 | SUPPLEMENTAL | 30961 | GOODHUE MUNICIPAL GAS, CITY OF | 405 N. BROADWAY | GOODHUE | MN | 55027 | 2014-09-16 06:00 |  |  | 2014 | 35189 CO 6 | GOODHUE | GOODHUE | MN | 55027 | 44.4355 | -92.6417 | [10 empty] | NRC NOTIFICATION NOT REQUIRED |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-09-16 06:00 |  |  |  | 2014-09-16 06:20 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OTHER | INLET VALVE | 2014 | [8 empty] | OTHER | INLET VALVE | [9 empty] | OTHER | [8 empty] | THERE WAS NO RELEASE. INLET VALVE WAS ACCIDENTLY CLOSED OVERNIGHT. | CLASS 1 LOCATION | 0 | 0 | 0 | 0 | 2000 | 2450.28901734104 | 0 | 0 |  |  | 0 | 0 |  | 0 | 2000 | 1014.836223506744 | 2450.28901734104 | 27 | 1 | 422 |  |  |  |  | 0 | 48 | 66 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | INCORRECT OPERATION | INCORRECT VALVE POSITION | [222 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | KYLE MCKEOWN | MANAGER | goodhuepuc@sleepyeyetel.net | 651-923-5306 | 651-923-5113 |  |  |  | KYLE MCKEOWN | MANAGER | 651-380-2026 | goodhuepuc@sleepyeyetel.net | CONTRACTOR CREW WAS PLACING NEW DISTRICT REGULATOR (DRS) FOR THE CITY OF GOODHUE. THIS WAS A ONE WAY FEED. THE CREW WAS TURNING ON THE NEW DRS BY TURNING THE VALVE ON PART WAY. THE GAUGE WAS BEING MONITORED AND THE PRESSURE DROPPED 5LBS AND HELD THERE. THEN THEY SQUEEZED OFF THE BYPASS, PRESSURE WAS HOLDING. CREW MEMBER WAS TOLD TO TURN THE INLET VALVE ALL THE WAY ON. IN DOING SO, THE CREW MEMBER TURNED THE VALVE THE WRONG WAY AND SHOT THE VALVE OFF INSTEAD OF OPENING IT ALL THE WAY. CREW LEFT A FEW HOURS LATER WITH THE LINE HOLDING THE PRESSURE. THE LINE PACK WAS USED OVERNIGHT AND ENDED UP THE TOWN OF GOODHUE, MN WAS WITHOUT GAS.
2025-03-31 10:13 | NO | NO | NO | 20140084 | 15935 | 2014-09-26 17:26 | ORIGINAL FINAL | 30769 | MISSOURI GAS ENERGY | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2014-08-28 08:40 |  |  | 2014 | 629 HWY D | LOCKWOOD | DADE | MO | 65682 | 37.4854 | -94.0238 | [9 empty] | 2014-08-28 12:10 | 1093736 |  | NATURAL GAS |  | 9193 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-08-28 08:40 |  |  |  | 2014-08-28 09:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 4 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1963 | [5 empty] | 8 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 3.9 | 3.2 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 7224 | 8850.44393063583648 | 500 | 612.57225433526 | 0 | 0 |  |  | 52972 | 39613.0367775831873905429071803852889667 |  | 0 | 60696 | 40563.6757788958299164413309982486865149 | 49076.0529625542838705429071803852889667 | 0 | 0 | 0 |  |  |  |  | 150 | 150 | 157 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | GRADER/SCRAPER | DRAINAGE | NO |  |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED |  |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MARK LAUBER | MANAGER PIPELINE SAFETY COMPLIANCE | mark.lauber@thelacledegroup.com | 314-658-5413 | 314-535-9414 |  |  |  | CRAIG R. HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES | 314-658-5410 | craig.hoeferlin@thelacledegroup.com | CONTRACTOR WAS OPERATING A TRACK LOADER CLEANING OUT A FARM POND AT 629 HWY D AND HIT THE TOP OF AN 8" GAS MAIN IN EASEMENT THAT HAD ONLY 4 INCHES OF COVER. THE LINE WAS INSTALLED IN 1963 AND AT THE TIME IT SKIRTED THE OUTER EDGES OF THE POND AND HAD APPROXIMATELY 30 TO 40 INCHES OF COVER. SOMETIME LATER THE POND WAS DUG OUT AND ENLARGED WITHOUT MISSOURI GAS ENERGY'S (PIPELINE OPERATOR) KNOWLEDGE, REDUCING THE COVER OVER THE LINE TO 4 INCHES. MISSOURI ONE CALL WAS NOT NOTIFIED OF THE WORK AND HENCE NO UTILITY LOCATES WERE MADE IN THE AREA.
2025-03-31 10:13 | NO | NO | NO | 20140085 | 15939 | 2014-10-03 09:27 | ORIGINAL FINAL | 30769 | MISSOURI GAS ENERGY | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2014-09-04 09:03 |  |  | 2014 | 25TH ST. AND HOLMES | KANSAS CITY | JACKSON COUNTY | MO | 64108 | 39.0815 | -94.576 | [9 empty] | 2014-09-04 14:46 | 1094380 |  | NATURAL GAS |  | 5230 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 15 | 2014-09-04 09:07 |  |  |  | 2014-09-04 09:23 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 62 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 8 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | OTHER | [8 empty] | DURING EXCAVATION FOR REPAIRING A WATER MAIN, A PIECE OF LOOSE FLOWABLE FILL FELL ON THE EXPOSED 8" GAS MAIN HITTING IT AND CRACKING IT WHICH CAUSED THE PIPE TO LEAK | CLASS 3 LOCATION | 0 | 0 | 12230 | 14983.5173410404596 | 500 | 612.57225433526 | 0 | 0 |  |  | 30136 | 22536.0280210157618213660245183887915937 |  | 0 | 42866 | 27306.5779216396900083362521891418563923 | 38132.1176163914814213660245183887915937 | 8 | 0 | 0 |  |  |  |  | 1.1 | 1.1 | 2.2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 142462816 | MOCS |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | MARK LAUBER | MANAGER PIPELINE SAFETY COMPLIANCE | mark.lauber@thelacledegroup.com | 314-658-5413 | 314-535-9414 |  |  |  | CRAIG R. HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES | 314-658-5410 | craig.hoeferlin@thelacledegroup.com | CONTRACTOR HIRED BY WATER COMPANY TO REPAIR A BROKEN WATER MAIN AT 25TH AND HOLMES WAS USING THE BUCKET OF THEIR BACKHOE TO TEST THE STABILITY OF THE UNDERMINED PAVEMENT; A PIECE OF BROKEN OUT FLOWABLE FILL FROM UNDER THE WASHED OUT STREET FELL DOWN IN THE HOLE HITTING AND CRACKING THE EXPOSED 8" CAST IRON GAS MAIN CAUSING IT TO LEAK. CONTRACTOR STARTED THIS WORK BEFORE THE MGE INSPECTOR HAD ARRIVED AT THE JOBSITE.
2025-03-31 10:13 | NO | YES | NO | 20140086 | 16120 | 2014-10-06 13:22 | SUPPLEMENTAL FINAL | 2585 | COLUMBIA GAS OF KENTUCKY INC | 2001 MERCER ROAD | LEXINGTON | KY | 40511 | 2014-09-07 18:14 |  |  | 2014 | 3050 LAKECREST CIRCLE | LEXINGTON | FAYETTE | KY | 40513-1706 | 38.0163 | -84.5533 | [9 empty] | 2014-09-07 19:19 | 1094643 |  |  |  | 10.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 70 | 2014-09-07 18:23 |  |  |  | 2014-09-07 18:42 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1994 | [8 empty] | STEEL |  |  |  | 0.191 | [6 empty] | OTHER | [8 empty] | POSSIBLE BREAK AT THREADED CONNECTION | CLASS 4 LOCATION | 5000000 | 6125722.5433526 | 3000 | 3675.43352601156 | 2400 | 2940.346820809248 | 0 | 0 |  |  | 70 | 52.34676007005253940455341506129597197898 |  | 0 | 5005470 | 2539879.04038819160634816112084063047285 | 6132390.67045949086053940455341506129597 | 1 | 0 | 0 |  |  |  |  | 48 | 48 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | TIMOTHY MCKUNE | OPERATION COMPLIANCE MANAGER | tmckune@nisource.com | 859-288-0241 | 859-288-0258 |  |  |  | TIMOTHY MCKUNE | OPERATION COMPLIANCE MANAGER | 859-288-0241 | tmckune@nisource.com | A CAR JUMPED THE CURB, CROSSED A GRASS STRIP, A SIDEWALK, AND ANOTHER GRASS STRIP STRIKING THE METER SETTING AND BUILDING AT 3050 LAKECREST CIRCLE IN LEXINGTON, KENTUCKY. THE CAR STRIKING THE METER SETTING CAUSED MOVEMENT OF BOTH JURISDICTIONAL AND NON-JURISDICTIONAL GAS PIPING LOCATED ON THE OUTSIDE AND INSIDE OF THE BUILDING BY PUSHING THE METER SETTING THROUGH THE OUTSIDE WALL INTO THE MECHANICAL ROOM. THE GAS BUILT UP INSIDE THE STRUCTURE AND WAS IGNITED BY AN UNKNOWN SOURCE RESULTING IN AN EXPLOSION AND FIRE. THE EXPLOSION AND FIRE OCCURRED PRIOR TO THE GAS COMPANY PERSONNEL ARRIVAL. UPON EXAMINATION OF THE DAMAGED PIPING, COLUMBIA OBSERVED A TEE ABOVE THE BYPASS AND BELOW THE REGULATION TO BE SHEARED OFF AND MUCH OF THE HOUSELINE PIPING TO BE SEVERELY DAMAGED.
2025-03-31 10:13 | NO | NO | NO | 20140087 | 15942 | 2014-10-08 17:25 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2014-09-04 12:56 |  |  | 2014 | 3575 WEST TROPICANA AVENUE | LAS VEGAS | CLARK COUNTY | NV | 89103 | 36.0603 | -115.1114 | [9 empty] | 2014-09-09 09:24 | 1094813 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-09-04 12:56 |  |  |  | 2014-09-04 12:56 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1984 | [5 empty] | 2 | D2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 698 | 855.15086705202296 | 79916 | 97908.64855491327632 | 0 | 0 |  |  | 0 | 0 |  | 0 | 80614 | 40905.003660886330408 | 98763.79942196529928 | 536 | 1 | 0 |  |  |  |  | 38 | 38 | 43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | DEBRIS AT FUSION INTERFACE AND A MITERED JOINT RESULTED IN AN INCOMPLETE FUSION. |  |  | YES |  |  | NORMAL OPERATING CONDITIONS | NO | [50 empty] | YVONNE BRODEUR | ENGINEERING TECHNICIAN | yvonne.brodeur@swgas.com | (702) 365-2149 | (702) 221-4116 |  |  |  | THOMAS CARDIN | DIRECTOR OF GAS OPERATIONS | (702) 365-2028 | thomas.cardin@swgas.com | DURING A LEAK PATROL, SOUTHWEST GAS DISCOVERED A GRADE 1 LEAK ON A TWO-INCH PE STUB AT 3575 WEST TROPICANA AVENUE IN LAS VEGAS, NEVADA. SOUTHWEST GAS IMPLEMENTED A SECTION OF THEIR VALVE ISOLATION PLAN TO QUICKLY MITIGATE THE SITUATION AND ELIMINATE THE LEAK. FOR THIS REASON, SERVICE TO 537 ACTIVE CUSTOMERS WAS DISCONTINUED UNTIL REPAIRS WERE COMPLETED. ALTHOUGH THE INCIDENT INITIALLY DID NOT MEET PHMSA/DOT NOTIFICATION CRITERIA, ON SEPTEMBER 9, 2014, SOUTHWEST GAS CORPORATION ESTIMATED THE COSTS ASSOCIATED WITH THE INCIDENT WOULD LIKELY MEET THE CRITERIA AND IMMEDIATELY NOTIFIED THE NATIONAL RESPONSE CENTER.
2025-03-31 10:13 | NO | YES | NO | 20140088 | 15943 | 2014-10-10 16:14 | ORIGINAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDENCE BLVD | VIRGINIA BEACH | VA | 23452 | 2014-07-18 14:50 |  |  | 2014 | LYNNHAVEN PKWY & BEAUFAN BLVD | VIRGINIA BEACH |  | VA | 23464-7500 | 36.7741 | -76.1807 | [9 empty] | 2014-09-12 15:38 | 1095173 |  | NATURAL GAS |  | 2674 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 15 | 2014-07-18 15:04 |  |  |  | 2014-07-18 15:31 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2013 | [5 empty] | 8 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 7.5 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 24776 | 30354.18034682080352 | 98609 | 120810.27485549130668 | 0 | 0 |  |  | 22312 | 16685.1558669001751313485113835376532399 |  | 0 | 145697 | 78042.5297782344627138704028021015761821 | 167849.6110692122853313485113835376532399 | 0 | 0 | 870 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELEASE OF GAS WAS TOO SMALL TO BE DETECTED BY THE SCADA SYSTEM ALARMS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 418102384 |  |  | CONTRACT LOCATOR | YES | YES | 12 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | BILL ROBINSON | DISTRIBUTION QUALITY ASSURANCE PROGRAM MANAGER | brobinso@aglresources.com | 757-616-7530 | 757-616-7517 |  |  |  | KERRY CAMPBELL | VICE PRESIDENT OF OPERATIONS AT VNG | 757-466-5559 | kcampbel@aglresources.com | A THIRD PARTY EXCAVATOR, AMERICAN INFRASTRUCTURE, DAMAGED THE VIRGINIA NATURAL GAS (VNG) 8" PLASTIC DISTRIBUTION GAS MAIN WHILE PERFORMING ROAD CONSTRUCTION WORK. TO MAKE THE LEAK SAFE, VNG CREWS ISOLATED THE PIPELINE WHICH CAUSED AN OUTAGE OF DOWN-STREAM CUSTOMERS. IT IS NOTED THAT IT TOOK A COUPLE OF MONTHS TO RECEIVE ALL INVOICING AND ASSEMBLE THE FINAL TOTAL EXPENSE IN THE REPAIR, RESTORATION AND RE-LIGHT OF CUSTOMERS, WHICH ULTIMATELY AND UNEXPECTEDLY EXCEEDED THE $50,000 NOTIFICATION THRESHOLD.
2025-03-31 10:13 | NO | YES | YES | 20140089 | 15944 | 2014-10-14 13:14 | ORIGINAL | 6240 | WASHINGTON PARISH, GAS UTIL DIST # 2 OF | 205 11TH AVENUE, SUITE 2 | FRANKLINTON | LA | 70438 | 2014-09-22 11:00 |  |  | 2014 | HIGHWAY 62 | FRANKLINTON |  | LA | 70438 | 30.8762 | -90.0052 | [12 empty] | NATURAL GAS |  | 36 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2014-09-22 11:00 |  |  |  | 2014-09-22 11:20 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1969 | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYVINYL CLORIDE (PVC) | [5 empty] | RUPTURE |  |  |  |  | LONGITUDINAL |  |  |  |  | CLASS 2 LOCATION | 0 | 0 | 2809 | 3441.43092485549068 | 3000 | 3675.43352601156 | 1000 | 1225.14450867052 | TOTAL COST FOR PREPARING THE JOB SITE TO PREVENT EROSION. |  | 198 | 148.066549912434325744308231173380035026 |  | 0 | 7007 | 3591.980150599463012798598949211908931699 | 8490.075509450005005744308231173380035026 | 0 | 0 | 2 |  |  |  |  | 38 | 38 | 66 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JOHN U ROCHESTER III | GAS SUPERINTENDENT | mhaleywpg@outlook.com | 9858395026 | 9858395025 |  |  |  | JOHN U ROCHESTER III | GAS SUPERINTENDENT | 9858395026 | mhaleywpg@outlook.com | SEMI TRACTOR TRAILER, LOADED WITH LOGS, WAS TRAVELING AT A HIGH RATE OF SPEED AROUND CURVE RATED FOR 45 MPH. IT THEN LOST CONTROL AND THE LOAD SHIFTED SPILLING LOGS INTO DITCH. TRUCK FLIPPED ON SIDE SLIDING DOWN HIGHWAY. THE LOAD OF LOGS IMPACTING DITCH BANK AND SLIDING DOWN THE DITCH FRACTURED MAIN. THIS CAUSING LEAK IN MAIN. SEMI TRACTOR TRAILER BURNING CAUSED GAS TO IGNITE.
2025-03-31 10:13 | NO | YES | NO | 20140090 | 15945 | 2014-10-15 16:32 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-09-15 14:15 |  |  | 2014 | 3218 QUANDT ROAD | LAFAYETTE | CONTRA COSTA | CA | 94549 | 37.9087 | -122.0972 | [9 empty] | 2014-10-13 14:25 | 1098172 |  | NATURAL GAS |  | 77.99 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2014-09-15 14:39 |  |  |  | 2014-09-15 14:51 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 35 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1954 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 115000 | 140891.6184971098 | 0 | 0 | 0 | 0 |  |  | 315 | 235.560420315236427320490367775831873905 |  | 0 | 115315 | 58570.9900320230689667250437828371278459 | 141127.1789174250364273204903677758318739 | 0 | 0 | 105 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | WATER | YES | 354045 | USAN |  | UTILITY OWNER | YES | YES | 2362 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LARRY DENISTON | ACTING MANAGER REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT APPROXIMATELY 1439 HOURS ON SEPTEMBER 15, 2014, THE CONTRA COSTA FIRE DEPARTMENT NOTIFIED PG&E OF A THIRD-PARTY DIG-IN AT 3218 QUANDT ROAD IN LAFAYETTE. THE THIRD PARTY, EAST BAY MUNICIPAL UTILITY DISTRICT (EBMUD), WAS CONDUCTING WATER MAIN WORK. EBMUD STRUCK PG&E'S 2-INCH STEEL DISTRIBUTION MAIN WITH A BACKHOE, CAUSING AN UNINTENTIONAL RELEASE OF GAS. THERE WAS A VALID USA TICKET (#354045) AND THE GAS FACILITIES WERE PROPERLY MARKED. THE THIRD-PARTY FAILED TO HAND-DIG AND EXPOSE FACILITIES PRIOR TO USING MECHANICAL EQUIPMENT. PG&E'S GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SCENE AT 1451 HOURS WITH A REPAIR CREW ARRIVING AT 1520 HOURS. GAS WAS SHUT-IN AT 1650 HOURS BY EXCAVATING AND SQUEEZING THE DISTRIBUTION MAIN, WHICH RESULTED IN LOSS OF GAS SERVICE FOR 105 CUSTOMERS. THE FIRE DEPARTMENT AND POLICE WERE ON SCENE. TRAFFIC WAS REROUTED. THERE WERE NO INJURIES OR FATALITIES. NO MEDIA WAS OBSERVED ON SCENE. REPAIRS TO THE 2-INCH STEEL MAIN WERE COMPLETED AT 0455 HOURS ON SEPTEMBER 16, 2014. AS OF 1515 HOURS ON SEPTEMBER 16, PG&E RESTORED GAS SERVICE TO 87 CUSTOMERS. THE REMAINING 18 CUSTOMERS WERE NOT AVAILABLE DURING THE INITIAL RELIGHT EFFORT. AS OF SEPTEMBER 23, 2014, GAS SERVICE WAS RESTORED FOR ALL REMAINING CUSTOMERS. THE AMOUNT OF GAS RELEASED IS LESS THAN 3 MMCF. THIS WAS INITIALLY REPORTED ONLY TO THE CPUC BASED ON OPERATOR JUDGMENT AS APPROXIMATELY 105 CUSTOMERS LOST GAS SERVICE AS A RESULT OF THE DIG IN. PG&E RECENTLY CONFIRMED THAT DAMAGES RELATING TO THIS INCIDENT EXCEED $50,000. PG&E NOTIFIED THE NATIONAL RESPONSE CENTER ON OCTOBER 13, 2014.
2025-03-31 10:13 | NO | YES | NO | 20140092 | 15947 | 2014-10-30 19:45 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-09-30 12:38 |  |  | 2014 | RIDDER PARK DR. & SCHALLENBERGER RD. | SAN JOSE | SANTA CLARA COUNTY | CA | 95131 | 37.3796 | -121.9 | [9 empty] | 2014-09-30 17:09 | 1097097 |  | NATURAL GAS |  | 3251 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2014-09-30 12:38 |  |  |  | 2014-09-30 12:56 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 66 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1966 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | PIPE WAS COMPLETELY SEVERED BY MECHANICAL EQUIPMENT | CLASS 3 LOCATION | 0 | 0 | 86000 | 105362.42774566472 | 0 | 0 | 0 | 0 |  |  | 13136 | 9823.243432574430823117338003502626970228 |  | 0 | 99136 | 52725.0329172698518949211908931698774081 | 115185.6711782391508231173380035026269702 | 34 | 0 | 216 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | OTHER | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | LANDSCAPING | YES | 388378 | USAN |  | UTILITY OWNER | NO | YES | 55 | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LARRY DENISTON | ACTING MANAGER REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT APPROXIMATELY 1238 HOURS ON SEPTEMBER 30, 2014, PG&E WAS NOTIFIED OF A THIRD-PARTY DIG-IN IN SAN JOSE (NEAR THE INTERSECTION OF RIDDER PARK DRIVE AND SCHALLENBERGER ROAD). THE PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SCENE AT APPROXIMATELY 1256 HOURS. THE THIRD-PARTY, J.J. ALBANESE, STRUCK A 4-INCH STEEL DISTRIBUTION MAIN WITH A BACKHOE, CAUSING AN UNINTENTIONAL RELEASE OF NATURAL GAS. THE EXCAVATOR HAD CALLED USA (TICKET NO. 388378), BUT FAILED TO DELINEATE THE AREA WHERE THE DIG-IN TOOK PLACE, THUS THE GAS FACILITIES IN THE AREA WHERE THE DIG-IN TOOK PLACE COULD NOT BE LOCATED AND MARKED. PG&E REPAIR CREW ARRIVED AT 1312 HOURS. GAS WAS SHUT-IN AT 1652 HOURS BY EXCAVATING AND SQUEEZING THE STEEL DISTRIBUTION MAIN (NORTH OF THE DIG-IN). REPAIRS WERE MADE BY APPROXIMATELY 2000 HOURS ON OCTOBER 1, 2014. AT APPROXIMATELY 0800 HOURS ON OCTOBER 2, 2014, PG&E BEGAN RESTORING GAS SERVICE FOR CUSTOMERS. AS OF APPROXIMATELY 1600 HOURS ON OCTOBER 2, 34 OF THE 35 SERVICES HAD GAS SERVICE RESTORED (ONE SERVICE FEEDS A MASTER METER FOR A MOBILE HOME PARK). A TOTAL OF 216 MOBILE HOME UNITS LOST GAS SERVICE FROM THE DIG-IN INCIDENT. RELIGHTING EFFORTS FOR THE MOBILE HOME PARK BEGAN OCT. 2, 2014 AT 1900 HOURS AND FINISHED AT APPROXIMATELY 0030 HOURS (OCT. 3, 2014). PG&E RELIT 189 MOBILE HOME UNITS. PG&E WAS UNABLE TO ACCESS 32 UNITS DURING THE RELIGHT EFFORT. AS OF OCT. 3, 2014 AFTERNOON, THE MOBILE HOME PARK CONFIRMED THEY FINISHED RELIGHT FOR THE REMAINING 27 UNITS AND CONFIRMED THAT 5 UNITS WERE VACANT. THERE WAS NO IGNITION, NO EXPLOSIONS, NO INJURIES, AND NO FATALITIES DURING THE INCIDENT. NO MEDIA WAS OBSERVED ON SCENE. THIS INCIDENT WAS REPORTED ONLY TO THE CPUC BASED ON OPERATOR JUDGMENT AS OVER 200 CUSTOMERS LOST GAS SERVICE AS A RESULT OF THE DIG-IN. THIS INCIDENT WAS REPORTED TO THE DOT ON OCTOBER 1, 2014 BECAUSE THE COST OF DAMAGES WAS EXPECTED TO EXCEED $50,000.
2025-03-31 10:13 | NO | YES | NO | 20140093 | 16031 | 2014-10-31 11:45 | SUPPLEMENTAL FINAL | 4060 | DOMINION EAST OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2014-10-01 21:26 |  |  | 2014 | 7373 SHERMAN CHURCH RD | EAST SPARTA | STARK | OH | 44626 | 40.703 | -81.435 | [9 empty] | 2014-10-02 06:15 | 1097118 |  | NATURAL GAS |  | 75 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 170 | 2014-10-01 21:26 |  |  |  | 2014-10-01 21:48 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 144 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1972 | [5 empty] | 30 | API 5L | U.S. STEEL | STEEL |  | OTHER | DOUBLE SUBMERGED ARC WELDED | 0.298 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 1500 | 1837.71676300578 | 84000 | 102912.13872832368 | 5000 | 6125.7225433526 | 700000 | 857601.156069364 | COST OF PIPELINE REPLACEMENT |  | 375 | 280.429071803852889667250437828371278459 |  | 0 | 790875 | 401373.430651023052865148861646234676007 | 968757.1631758499128896672504378283712785 | 0 | 0 | 0 |  |  |  |  | 155 | 155 | 174 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | CORROSION | INTERNAL | INTERNAL CORROSION | [32 empty] | LOCALIZED PITTING |  |  |  | YES |  |  |  |  | YES |  |  | YES |  |  |  |  | NO | YES | 2014-02-04 | NO | [227 empty] | AARON MCCOY | TECHNICAL SPECIALIST | aaron.m.mccoy@dom.com | 3304589186 | 3304783760 |  |  |  | AARON MCCOY | TECHNICAL SPECIALIST | 3304589186 | aaron.m.mccoy@dom.com | ON OCTOBER 1, 2014 A 30" DISTRIBUTION MAIN LEAKED RESULTING IN A REPORTABLE INCIDENT. AT APPROXIMATELY 9:26 P.M. ON 10/1/2014, DOMINION EAST OHIO RECEIVED AN ODOR COMPLAINT AT 7373 SHERMAN CHURCH RD. A TECHNICIAN WAS IMMEDIATELY DISPATCHED TO THE AREA. AT 9:48 P.M. THE TECHNICIAN ARRIVED ON SITE, CONDUCTED A LEAK SURVEY OF THE AREA AND CONCLUDED THAT GAS WAS NOT MIGRATING AND ACCORDING TO AVAILABLE DATA DID NOT BELIEVE THE LEAK TO BE ON A DOMINION FACILITY. THE TECHNICIAN NOTIFIED THE FIRE CHIEF OF HIS FINDINGS. AT APPROXIMATELY 11:55 P.M. DOMINION WAS NOTIFIED BY THE EPA THAT OIL WAS BUBBLING UP FROM THE GROUND AND THAT THEY WERE PICKING UP HIGH NATURAL GAS READINGS. ANOTHER TECHNICIAN WAS IMMEDIATELY DISPATCHED TO THE SCENE, ARRIVED AT 12:47 A.M. ON 10/2/2014, AND UPON INVESTIGATION DETERMINED THAT DEO'S 30" DISTRIBUTION LINE WAS LEAKING AND CALLED IN FOR A CONSTRUCTION CREW. THE TECHNICIAN CONTINUED TO LEAK SURVEY THROUGHOUT THE NIGHT. AS ADDITIONAL DOMINION PERSONNEL ARRIVED ON SITE, THE INVESTIGATION CONTINUED AND DETERMINED THAT THE LINE WAS DEEPER THAN A DOMINION CREW COULD HANDLE, THEREFORE A CONTRACTING CREW WAS MOBILIZED. AT APPROXIMATELY 5:00 A.M. DOMINION'S ENVIRONMENTAL CONTRACTORS ARRIVED ON SITE AND BEGAN ENVIRONMENTAL CLEANUP ACTIVITIES. THE AREA WAS EVACUATED AT APPROXIMATELY 6:00 A.M. AS MEASURE OF SAFETY, BEFORE EXCAVATING COULD OCCUR DOMINION DECIDED TO LOWER THE PRESSURE IN THE PIPELINE. AT APPROXIMATELY 10:00 AM THE PRESSURE WAS LOWERED FROM 155 PSIG TO 60 PSIG. ONCE THE PRESSURE WAS STABILIZED DOMINION BEGAN EXCAVATING. AT APPROXIMATELY 5:00 P.M. A CLAMP WAS INSTALLED AND PRESSURE RESTORED. THE SECTION OF PIPE THAT LEAKED WAS CUT OUT AND SENT TO KIEFNER & ASSOCIATES FOR A 3RD PARTY FAILURE ANALYSIS. THE RESULTS OF THE TEST CONCLUDED THAT THE CAUSE OF THE LEAK WAS A THROUGH-WALL INTERNAL CORROSION PIT AT THE 6 O'CLOCK POSITION. TEST RESULTS SUGGEST THAT MICROBIAL-INDUCED CORROSION (MIC) PLAYED A ROLE IN THE PITTING CORROSION. DOMINION REPLACED APPROXIMATELY 800 FEET OF THE 30" HIGH PRESSURE DISTRIBUTION LINE THAT LEAKED AND WILL REPLACE ADDITIONAL PORTIONS OF ADJACENT PIPELINES THROUGHOUT 2015.
2025-03-31 10:13 | NO | YES | NO | 20140094 | 15950 | 2014-10-31 14:41 | ORIGINAL FINAL | 13062 | NATIONAL FUEL GAS DISTRIBUTION CORP - NEW YORK | 6363 MAIN ST. | WILLIAMSVILLE | NY | 14221 | 2014-10-02 08:40 |  |  | 2014 | NW CORNER OF MAIN ST AND SUNNYSIDE ST | BEMUS POINT | CHAUTAUQUA | NY | 14712-9303 | 42.1589 | -79.3913 | [9 empty] | 2014-10-02 11:11 | 1097145 |  | NATURAL GAS |  | 129.2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2014-10-02 08:48 |  |  |  | 2014-10-02 09:05 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2014 | [5 empty] | 6 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 3 LOCATION | 245000 | 300160.4046242774 | 55000 | 67382.9479768786 | 2500 | 3062.8612716763 | 0 | 0 |  |  | 958 | 716.40280210157618213660245183887915937 |  | 0 | 303458 | 154156.6933412969564448336252189141856392 | 371322.6166749338761821366024518388791594 | 32 | 0 | 148 |  |  |  |  | 38 | 38 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | COMPANY REPRESENTATIVE CONTACTED BY THIRD PARTY (SHERIFF'S OFFICE) |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | REGULATOR STATIONS FEEDING THE DISTRIBUTION SYSTEM ARE MANUALY SET. SYSTEM IS NOT MONITORED BY SCADA. CONTROLLER'S ACTIONS WOULD NOT HAVE AFFECTED OUTCOME. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | AUGER | TRAFFIC SIGN | YES | 929454217600 | N/A |  | CONTRACT LOCATOR | YES | YES | 12 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | STEVEN M. MONNIE | ASSOCIATE ENGINEER | monnies@natfuel.com | 814-871-8204 | 814-871-8659 |  |  |  | MICHAEL D. COLPOYS | ASSISTANT VICE PRESIDENT | 814-871-8239 | colpoysm@natfuel.com | AT APPROXIMATELY 8:40 AM ON THURSDAY, OCTOBER 2, 2014, A CONTRACTOR USING A 4" AUGER TO INSTALL TRAFFIC SIGNS STRUCK A 6" PLASTIC NATURAL GAS MAIN LINE WHICH RESULTED IN A FIRE DAMAGING THE TRUCK AND AUGER. THE NY DEPARTMENT OF PUBLIC SERVICE WAS NOTIFIED AT 10:18 AM. THERE WERE NO INJURIES OR FATALITIES. THE ONE-CALL CENTER WAS NOTIFIED OF THE EXCAVATION ACTIVITY. INVESTIGATION INTO THE INCIDENT SHOWS LOCATING PRACTICES WERE NOT SUFFICIENT. PAINT MARKS WERE FOUND ON THE PAVEMENT MARKING AN ABANDONED 6" STEEL MAIN LINE. THERE WERE NO MARKINGS FOR THE 6" PLASTIC LINE, WHICH WAS OFFSET APPROXIMATELY 6 FEET FROM THE ABANDONED LINE.
2025-03-31 10:13 | NO | NO | NO | 20140095 | 16075 | 2014-11-04 08:10 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2014-10-31 14:02 |  |  | 2014 | 2404 VENUS ST. | PORTAGE | PORTER | IN | 46368 | 41.5824 | -87.1731 | [9 empty] | 2014-10-31 16:21 | 1099878 |  | NATURAL GAS |  | 12 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2014-10-31 14:33 |  |  |  | 2014-10-31 15:16 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1963 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 75000 | 91885.838150289 | 650 | 796.343930635838 | 2000 | 2450.28901734104 | 0 | 0 |  |  | 60 | 44.86865148861646234676007005253940455342 |  | 0 | 77710 | 39442.5225072465336984238178633975481611 | 95177.3397497544944623467600700525394046 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FACILITY INVOLVED AND LEAK WERE SMALL IN NATURE COMPARED TO THE SYSTEM, THEREFORE IT WOULD NOT EFFECT PRESSURE ON THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | HIGH WINDS KNOCKED OVER LARGE OAK TREE | NO | [218 empty] | LUKE E. SELKING | MANAGER PIPELINE SAFETY AND COMPLIANCE | leselking@nisource.com | 260-433-6115 | 260-422-9151 |  |  |  | LUKE E. SELKING | MANAGER PIPELINE SAFETY AND COMPLIANCE | 260-433-6115 | leselking@nisource.com | LARGE OAK TREE FELL DUE TO HIGH WINDS. TREE ROOTS PULLED SERVICE LINE BELOW GROUND CAUSING DAMAGE TO FACILITY. A CONCRETE PATIO WAS COVERED THE SERVICE LINE (APPROX 12'X12') ADJACENT TO THE BACK OF HOME NEAR THE UTILITY ROOM AND GARAGE. IT APPEARS THE LEAKING GAS MIGRATED INTO THE STRUCTURE FROM UNDER THE PATIO. THE HOMEOWNER WAS OUTSIDE REVIEWING THE TREE DAMAGE WHEN THE EXPLOSION OCCURED.
2025-03-31 10:13 | NO | YES | YES | 20140096 | 16059 | 2014-11-04 14:03 | SUPPLEMENTAL FINAL | 2676 | COMMUNITY NATURAL GAS INC | 116 N MAIN ST | OWENSVILLE | IN | 47665 | 2014-10-30 11:00 |  |  | 2014 | WEST SIDE OF IN161, EAST SIDE OF 2ND AVE, SOUTH MAIN STREET | HOLLAND | DUBOIS | IN | 47541 | 38.1445 | -87.2101 | [9 empty] | 2014-10-30 12:33 | 1099761 |  | NATURAL GAS |  | 105 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | YES | 75 | 2014-10-30 11:04 |  |  |  | 2014-10-30 11:12 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2013 | [5 empty] | 2 | POLY 2406 | DRISPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 2 LOCATION | 90000 | 110263.0057803468 | 900 | 1102.630057803468 | 7185 | 8802.6632947976862 | 0 | 0 |  |  | 578 | 432.234676007005253940455341506129597198 |  | 0 | 98663 | 50169.9478731158323748161120840630472855 | 120600.5338089549594539404553415061295972 | 25 | 1 | 225 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | 2010-07-21 | NO | [12 empty] | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 1410202080 |  |  | UTILITY OWNER | YES | YES | 27 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | DEAN J. KIEFFER | OPERATIONS MANAGER | dean@communitynaturalgas.com | 6189724060 | 6182633215 |  |  |  | DEAN J. KIEFFER | OPERATIONS MANAGER | 6182633328 | dean@communitynaturalgas.com | AROUND 11:00 AM CST 10/30/14 CONTRACTOR FOR THE OPERATOR WAS MAKING A TIE-IN FOR TWO 6" POLY NATURAL GAS LINES. 2" LINE COMES OFF EXISTING 6" LINE AND FEEDS 8 HOUSEHOLDS. NEW 6" LINE AND EXISTING 2" LINE ARE IN CLOSE PROXIMITY. LABORER WAS DIGGING WITH HAND TOOLS AROUND THOSE LINES AND THE BACKHOE OPERATOR WAS REMOVING DIRT ONCE IT WAS UNCOVERED. THIS AREA WAS UNCOVERED THE NIGHT BEFORE THE INCIDENT AND WAS APPROX. 20' LONG X 10' WIDE X 4' DEEP. CONTRACTOR WAS MAKING HOLE LONGER TO PERFORM A TIE IN. WHILE DIGGING OUT EXCESS DIRT, 2" LINE WENT UP AND AT NEAR 90 DEG ANGLE. THIS IS WHERE A TOOTH FROM BACKHOE HIT THE LINE. LABORER TURNED AROUND TO CUT OFF GAS AT 2" TAP. NATURAL GAS IGNITED BEFORE THIS COULD HAPPEN. LABORER CAUGHT ON FIRE AND SUSTAINED SECOND DEGREE BURNS TO ARMS AND FACE. NO INTERNAL DAMAGES TO LABORER. NO ONE ELSE WAS HURT. NO PERSONAL PROPERTY WAS DAMAGED. 11:21 AM CST NATURAL GAS WAS SHUT OFF AND FIRE DEPARTMENT PUT OUT FIRE. STARTED SHUTTING OFF METERS IN TOWN. MADE REPAIRS TO PIPELINE AND STARTED TURNING METERS BACK ON FROM 4:45 PM TO 9:40 PM. CHANGED ANSWERING MACHINE MESSAGE AT LOCAL OFFICE IN DALE. TO LET CUSTOMERS KNOW WE ARE AWARE OF OUTAGE AND LEFT A CELL PHONE NUMBER TO CALL TO GET GAS TURNED BACK ON. 11 PEOPLE WENT DOOR TO DOOR TO RE-LIGHT CUSTOMERS. ONLY 8 CUSTOMERS WERE NOT ABLE TO BE TURNED BACK ON SAME NIGHT. SOME HOUSES WERE FOR SALE AND NO ONE LIVED THERE. FURTHERMORE, SOME CUSTOMERS WERE ON VACATION. NOTES WERE LEFT ON THOSE HOUSES. ALL CUSTOMERS WERE ABLE TO BE TURNED BACK ON BY 1:50 PM CST ON 10/31/14.
2025-03-31 10:13 | NO | YES | NO | 20140097 | 16025 | 2014-11-04 15:38 | SUPPLEMENTAL FINAL | 5330 | FLORIDA PUBLIC UTILITIES CO | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2014-11-03 20:15 |  |  | 2014 | 417 PRIMAVERA AVE. | PALM BEACH | PALM BEACH | FL | 33480 | 26.7106 | -80.0421 | [9 empty] | 2014-11-04 07:35 | 1100120 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2014-11-03 20:34 |  |  |  | 2014-11-03 20:57 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 20 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1963 | [5 empty] | 3 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | CURRENT ARCED HOLE IN GAS MAIN | [5 empty] | CLASS 2 LOCATION | 3000000 | 3675433.52601156 | 20000 | 24502.8901734104 | 1000 | 1225.14450867052 | 0 | 0 |  |  | 50 | 37.39054290718038528896672504378283712785 |  | 0 | 3021050 | 1532944.70404826781024868651488616462347 | 3701198.95123654810038528896672504378284 | 0 | 0 | 25 |  |  |  |  | 20 | 20 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | MICHAEL MCCARTY | OPERATIONS COMPLIANCE MANAGER | mmccarty@fpuc.com | (863) 224-0417 | (863) 299-2554 |  |  |  | MICHAEL MCCARTY | OPERATIONS COMPLIANCE MANAGER | (863) 224-0417 | mmccarty@fpuc.com | AT APPROXIMATELY 20:34 ON 11/3/14, FLORIDA PUBLIC UTILITIES (FPU) RECEIVED A CALL FROM PALM BEACH COUNTY FIRE RESCUE THAT AN EXPLOSION AND FIRE HAD OCCURRED AT 417 PRIMAVERA AV IN PALM BEACH. FPU TECHNICIANS ARRIVED AT 20:57 AND DISCOVERED THE RESIDENCE AT THE ADDRESS ENGULFED IN FLAMES. THE FIRE DEPARTMENT HAD SHUT OFF THE NATURAL GAS SERVICE METER TO THE RESIDENCE BUT NATURAL GAS WAS STILL FEEDING THE FLAMES. CREWS FROM FPU STOPPED THE FLOW OF GAS IN THE 3" MAIN ON THE STREET AT THE INTERSECTION OF PRIMAVERA AV AND COCOANUT ROW. THIS STOPPED THE FLOW OF GAS TO THE HOUSE AT 417 PRIMAVERA AVE. APPROXIMATLEY 25 ADDITIONAL RESIDENCES WERE AFFECTED BY THE FLOW OF GAS BEING STOPPED. THE GAS MAIN IS A 3" BARE STEEL MAIN OPERATED AT 20 PSIG. THE SERVICE TO 417 PRIMAVERA IS A 3/4" PE SERVICE OPERATED AT 20 PSIG. THERE ARE CONFLICTING PRELIMINARY REPORTS OF INJURIES FROM THIS RESIDNECE. THE INCIDENT COMMANDER FROM TOWN OF PALM BEACH FIRE RESCUE STATED ONE PERSON, A POSSIBLE PROPERTY CARETAKER, AND ONE PALM BEACH COUNTY FIREMAN WERE TREATED FOR MINOR INJURIES AND RELEASED AT GOOD SAMARITAN HOSPITAL IN WEST PALM BEACH. INITIAL NEWS REPORTS STATED THAT THE 82 YEAR OLD HOMEOWNER AND HIS WIFE WERE TREATED AND RELEASED FROM GOOD SAMARITAN HOSPITAL IN WEST PALM BEACH. NEITHER OF THESE REPORTS CAN BE CONFIRMED AT THIS TIME (09:19 ON 11/4/14). SUPPLEMENTAL NARRATIVE UPDATE 11/18/14: THE HOMEOWNER DETECTED LEAKING NATURAL GAS IN THE GARAGE AND EXITED THE GARAGE TO THE OUTSIDE WHEN THE GAS IGNITED FROM UNKOWN SOURCES. IT HAS BEEN DETERMINED THAT THE GAS ESCAPED THE MAIN UNDER THE PAVING IN THE STREET WHERE IT WAS IN CONTACT WITH A STEEL CONDUIT FOR AN AT&T PHONE CALBE AND A STEEL CONDUIT FOR THE ELECTRIC SERVICE TO THE HOUSE. THE ESCAPING GAS TRAVELED THROUGH HOLES IN THE GAS MAIN AND THE PHONE CONDUIT CREATED BY ELECTRICAL ARC BURNS. THE GAS ENTERED 417 PRIMAVERA VIA THE PHONE CONDUIT INTO THE GARAGE. THREE PERSONS WERE TRANSPORTED TO A LOCAL HOSPITAL AND ALL WERE EXAMINED AND RELEASED. THE 82 YEAR OLD HOMEOWNER WAS TREATED FOR MINOR INJURIES AND RELEASED. HIS WIFE WAS ALSO CHECKED OUT AND RELEASED. ONE FIREFIGHTER WAS TREATED FOR A KNEE INJURY SUSTAINED WHEN SHE TRIPPED OVER HOSE LINE AND RELEASED. UPON A PRESSURE TEST OF THE MAIN AND SERVICES ON THE STREET, ADDITIONAL ARC BURNS WERE DETECTED IN A 3/4" PE SERIVCE IN THE STREET NEAR THE CONDUITS. THE 3" BS GAS MAIN WAS INSERTED WITH 2" PE AND THE SERVICES WERE REPAIRED AND ALL THE AFFECTED FACILITIES WERE PRESSURE TESTED AGAIN AND SERVICE WAS RESTORED TO THE REMAINING HOUSES ON THE STREET ON 11/6/2014. AT&T HAS ALSO REPLACED THE PHONE CABLE IN THE STREET AND ABANDONED THE STEEL CONDUIT BY 11/17/2014. FINAL - UPDATED NARRATIVE 2/25/15 A JOPINT INSPECTION OF THE PROPERTY WAS CONDUCTED ON 12/4/2014 BY INVESTIGATORS FOR THE INSURANCE COMPANIES, FLORIDA POWER AND LIGHT AND FLORIDA PUBLIC UTILITIES. IT WAS DETERMINED THAT NATURAL GAS ENTERED THE GARAGE VIA A PHONE CONDUIT. THE GAS IGNITED IN THE GARAGE AND FUELED THE FIRE. IT WAS NOT DETERMINED HOW THE GAS ENTERED THE PHONE CONDUIT. A METALURGICAL INSPECTION OF THE STEEL PHONE CONDUIT AND GAS PIPE THAT WAS REMOVED FROM THE STREET IN FRONT OF THE HOUSE WILL BE CONDUCTED AT THE FACILITIES OF SEA LIMITED, INC. IN JACKSONVILLE ON 3/17/2015. THE STATE FIRE MARSHAL'S REPORT, #14-3028 DATED 1/12/2015 LISTS THE CAUSE AS UNDETERMINED BUT DOCUMENTS FP&L EMPLOYEES VISIT TO THE HOME IN THE DAYS PRIOR TO THE INCIDENT AND OBSERVED CHARRING/SCORCH MARKS ON THE CONDUIT LEADING TO THE SMART METER ON THE ELECTRIC SERVICE AND THE NEED TO CONTACT AN ELECTRICIAN TO INVESTIGATE.
2025-03-31 10:13 | YES | NO | NO | 20140098 | 15957 | 2014-11-04 20:05 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-10-05 00:54 |  |  | 2014 | 935 BROADWAY STREET | KING CITY | MONTEREY COUNTY | CA | 93930 | 36.2065 | -121.135 | [9 empty] | 2014-10-05 | 1097417 |  | NATURAL GAS |  | 102.17 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO |  | 2014-10-05 00:54 |  |  |  | 2014-10-05 01:08 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET | [10 empty] | OTHER | POT METAL/ALUMINUM | [9 empty] | OTHER | [8 empty] | THE METER WAS DAMAGED FROM THE HEAT OF THE FIRE (OUR FACILITIES WERE SECONDARILY INVOLVED) | CLASS 3 LOCATION | 0 | 0 | 23000 | 28178.32369942196 | 0 | 0 | 0 | 0 |  |  | 410 | 306.602451838879159369527145359019264448 |  | 0 | 23410 | 11954.2417892417416392294220665499124343 | 28484.9261512608391593695271453590192644 | 1 | 0 | 30 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LARRY DENISTON | ACTING MANAGER REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT 0054 HOURS ON OCT. 5, 2014, PG&E WAS NOTIFIED BY THE KING CITY FIRE DEPARTMENT (KCFD) OF A STRUCTURE FIRE AT 935 BROADWAY ST. IN KING CITY. THE FIRE DAMAGED FOUR MOBILE HOMES AND THE NEIGHBORING AUTO DEALERSHIP. DEPUTIES EVACUATED 30 MOBILE HOMES DURING THE INCIDENT. KCFD STATED THAT THE IGNITION SOURCE ORIGINATED FROM ONE OF THE MOBILE HOMES AND RULED OUT NATURAL GAS AS THE IGNITION SOURCE. HEAT FROM THE FIRE DAMAGED TWO METER SETS, CAUSING AN UNINTENDED RELEASE OF NATURAL GAS AND SUBSEQUENT IGNITION. PG&E'S GAS SERVICE REPRESENTATIVE ARRIVED ON SITE AT 0108 HOURS. REPAIR CREW ARRIVED AT APPROXIMATELY 0330 HOURS. GAS WAS SHUT IN AT 0810 HOURS BY CUTTING AND CAPPING THE GAS SERVICE. THREE INJURIES WERE REPORTED DURING THE INCIDENT: (1) ONE DEPUTY WAS TREATED AND RELEASED, (2) ANOTHER MEMBER OF THE PUBLIC WAS TREATED AND RELEASED, AND (3) A RESIDENT (WHO WAS TRANSPORTED TO THE HOSPITAL WITH THIRD-DEGREE BURNS) HAS BEEN IN AN INDUCED COMA SINCE. THE INCIDENT WAS REPORTED TO THE DOT AND THE CPUC FOR THE IGNITION OF UNINTENTIONALLY RELEASED NATURAL GAS AND THE REPORTED INJURIES. A LEAK SURVEY WAS CONDUCTED BY APPROXIMATELY 1430 HOURS ON OCT. 5, 2014 AND NO LEAKS WERE DETECTED. TWO GAS SERVICES LOST SERVICE AS A RESULT OF THE INCIDENT (ONE OF THE METERS SERVES 30 MOBILE HOME UNITS WHILE THE OTHER SERVES THE AUTO DEALERSHIP.) DAMAGE TO THE MOBILE HOMES AND AUTO DEALERSHIP IS EXPECTED TO EXCEED $50,000. ON OCT. 13, 2014, REPAIR CREW TIED GAS SERVICE BACK IN AND INSTALLED A NEW RISER AND METER FEEDING THE MOBILE HOME PARK AT APPROXIMATELY 1500 HOURS. PG&E BEGAN RESTORING GAS SERVICE AT APPROXIMATELY 1500 HOURS ON OCT. 13, 2014. 26 OF THE 30 MOBILE HOME UNITS HAD GAS SERVICE RESTORED BY OCT. 13. THE REMAINING 4 MOBILE HOME UNITS AND THE NEIGHBORING AUTO DEALERSHIP STILL DO NOT HAVE GAS SERVICE AS THE STRUCTURES WERE SEVERELY DAMAGED FROM THE FIRE. NO MEDIA WAS REPORTED ON SITE DURING THE INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20140099 | 15958 | 2014-11-07 11:42 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2014-10-10 08:55 |  |  | 2014 | BELMONT STREET AND LAKE MEAD BOULEVARD | NORTH LAS VEGAS | CLARK COUNTY | NV | 89030 | 36.1958 | -115.1068 | [9 empty] | 2014-10-10 20:10 | 1097987 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 4 | 2014-10-10 08:55 |  |  |  | 2014-10-10 08:55 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 60 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | TRANSITION FITTING | 1960 | [8 empty] | PLASTIC |  |  |  |  | POLYVINYL CLORIDE (PVC) |  |  | 0.065 |  |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 15328 | 18779.01502890173056 | 41800 | 51211.040462427736 | 0 | 0 |  |  | 0 | 0 |  | 0 | 57128 | 28987.781888246635616 | 69990.05549132946656 | 1 | 0 | 2 |  |  |  |  | 40 | 40 | 43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | TWO-INCH PVC TO STEEL TRANSITION FITTING |  |  |  |  | YES | [6 empty] | YES | DEFLECTION |  | YES |  |  |  | OTHER | CIRCUMFERENTIAL CRACK | NO | [86 empty] | YVONNE BRODEUR | ENGINEERING TECHNICIAN | yvonne.brodeur@swgas.com | 702-365-2149 | 702-221-4116 |  |  |  | THOMAS CARDIN | DIRECTOR OF GAS OPERATIONS | 702-365-2028 | thomas.cardin@swgas.com | DURING A LEAK SURVEY, SOUTHWEST GAS DISCOVERED A HAZARDOUS LEAK ON A TWO-INCH PVC MAIN IN THE INTERSECTION OF BELMONT STREET AND LAKE MEAD BOULEVARD IN NORTH LAS VEGAS, NEVADA. THE FLOW OF GAS TO THE SECTION OF PIPE WAS DISCONTINUED IN ORDER TO COMPLETE THE REPAIR, RESULTING IN AN OUTAGE OF THREE ACTIVE CUSTOMERS. THE COSTS OF SOUTHWEST GAS' EMERGENCY RESPONSE, LEAK LOCATING, FACILITY REPAIR AND SERVICE RESTORATION RESULTED IN THE INCIDENT MEETING PHMSA/DOT NOTIFICATION CRITERIA.
2025-03-31 10:13 | NO | YES | YES | 20140100 | 15960 | 2014-11-10 16:13 | ORIGINAL FINAL | 31457 | FIVE VALLEY GAS CO | 2500 W. BROADWAY | MISSOULA | MT | 59808 | 2014-10-31 08:00 |  |  | 2014 | 3166 HWY 83N | SEELEY LAKE | MISSOULA | MT | 59868 | 47.1795 | -113.4852 | [9 empty] | 2014-10-31 08:30 | 1099854 |  | PROPANE GAS |  | 0.24 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 1 | 0 | 2 | YES |  |  |  |  | YES | 0 | 2014-10-31 08:30 |  |  |  | 2014-10-31 08:45 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | OTHER | PROPANE, PRIVATE OWNED | SERVICE |  | UNKNOWN | [5 empty] | 0.75 | ASTMD2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 6 | 1 | [7 empty] | CLASS 3 LOCATION | 300 | 367.543352601156 | 200 | 245.028901734104 | 10000 | 12251.4450867052 | 0 | 0 |  |  | 766 | 572.823117338003502626970227670753064799 |  | 0 | 11266 | 5857.785094601299169877408056042031523643 | 13436.8404583784635026269702276707530648 | 20 | 0 | 95 |  |  |  |  | 13 | 13 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | BUILDING CONSTRUCTION | YES | 14091065 | MT 811 |  | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 8 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | JERRY THORSTAD | GENERAL MANAGER | jthorstad@energypartnerspropane.com | 406-541-6800 | 406-541-6804 |  |  |  | JERRY THORSTAD | GENERAL MANAGER | 406-541-6800 | jthorstad@energypartnerspropane.com | ON 10-31-14 AT APPROXIMATELY 8:30A IN SEELEY LAKE , MT A 3RD PARTY CONTRACTOR DUG THRU A 3/4" POLY SERVICE LINE. THE CONTRACTOR WAS DIGGING FOR A REMODEL ON A COMMERCIAL BUILDING. OUR TECHNICIAN WAS ATTEMPTING TO PLUG/SQUEZZE OFF THE LINE WHEN GAS IGNITED CAUSING AN EXPLOSION AND FIRE. OUR TECH AND ONE CONTRACTOR EMPLOYEE WERE BURNED AND FLOWN TO HOSPITAL IN SEATTLE, WA. THE CONTRACTOR DID NOT CALL THE FIRE DEPT WHEN THE BREACH HAPPENED. THE FIRE DEPT ARRIVED WHEN THE GAS WAS BURNING. VERY LITTLE PROPERTY DAMAGE. THE REPAIR WAS COMPLETE BY 2PM THAT SAME DAY AND CUSTOMERSHAD SERVICE BY 6PM THAT SAME DAY.
2025-03-31 10:13 | NO | YES | NO | 20140102 | 15966 | 2014-11-19 14:00 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2014-10-20 15:24 |  |  | 2014 | 2101 N. PITCHER STREET | KALAMAZOO | KALAMAZOO | MI | 49007-1889 | 42.3121 | -85.5791 | [9 empty] | 2014-10-21 09:30 | 1098863 |  | NATURAL GAS |  | 6422.25 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-10-20 15:24 |  |  |  | 2014-10-20 15:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1950 | [5 empty] | 6 | API 5L GRADE B | UNKNOWN | STEEL |  | OTHER | ELECTRIC WELD | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 1.2 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 35051 | 42942.54017341039652 | 27173 | 33290.85173410403996 | 1680 | 2058.2427745664736 | INCIDENT RESPONSE MEAL COSTS |  | 31000 | 23182.1366024518388791593695271453590193 |  | 0 | 94904 | 53870.8806387063984736392294220665499124 | 101473.7712845327489591593695271453590193 | 3 | 0 | 0 |  |  |  |  | 190 | 190 | 200 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS IMMEDIATELY REPORTED TO OPERATOR WHEN IT OCCURRED. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  |  |  | YES | [9 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 42820561 |  |  | CONTRACT LOCATOR | NO | YES | 35 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | alan.chichester@cmsenergy.com | 989-791-5841 |  |  |  |  | TRACY A. GOBLE | REGULATORY AND COMPLIANCE MANAGER | 517-768-3187 | tracy.goble@cmsenergy.com | ON OCTOBER 20TH, 2014, UNDERGROUND UTILITY CONTRACTOR DIG IT, INC. WAS INSTALLING TELECOMMUNICATIONS FACILITIES WITH DIRECTIONAL BORE UNDER N. PITCHER STREET, KALAMAZOO. DURING THIS WORK, THE CONTRACTOR BORED INTO, AND PUNCTURED, A 6-INCH DIAMETER STEEL HIGH PRESSURE DISTRIBUTION GAS MAIN OPERATING AT APPROXIMATELY 190 PSIG. THIS PARTICULAR SEGMENT OF MAIN IS ONE OF THE TWO HIGH-PRESSURE FEEDS SERVING GRAPHICS PACKAGING, AS WELL AS SEVERAL OTHER COMMERCIAL AND INDUSTRIAL CUSTOMERS IN THE AREA. THERE WERE TWO SEPARATE DIG IT DIRECTIONAL BORE CREWS WORKING ON N. PITCHER STREET. ONE CREW WAS INSTALLING FACILITIES IN PARALLEL TO THE EXISTING HIGH PRESSURE MAIN (NORTH-SOUTH), AND A SECOND CREW WAS WORKING ON LATERALS CROSSING N. PITCHER STREET (WEST-EAST). THE DAMAGE OCCURRED DURING A WEST-TO-EAST BORE. THERE WERE FOUND TO BE MULTIPLE MISS DIG STAKING REQUESTS FOR THE AREA. MISS DIG TICKETS B42820566 AND B4280561 WERE IDENTIFIED FOR STAKING OF THE EAST SIDE OF N. PITCHER STREET, STARTING AT THE INTERSECTION WITH MOSEL AVENUE AND HEADING SOUTH FOR 2,500 FEET. THIS AREA INCLUDES THE DAMAGE LOCATION AND APPROXIMATELY 2,000 FEET TO THE NORTH OF DAMAGE. TWO ADDITIONAL MISS DIG TICKETS (B42820548 AND B42820550) WERE IDENTIFIED FOR STAKING BOTH SIDES OF THE ROAD FROM 1819 N. PITCHER STREET TO THE NORTH, FOR APPROXIMATELY 600 FEET. THIS AREA IS IMMEDIATELY TO THE SOUTH OF THE DAMAGE LOCATION. WHILE STAKING WAS EVIDENT BOTH NORTH AND SOUTH OF THE DAMAGE LOCATION, THE MARKINGS IN THE IMMEDIATE VICINITY OF THE DAMAGE (WITHIN 5 FEET) WERE APPARENTLY NOT SUFFICIENT TO ALERT THE CREW OF THE GAS MAIN'S PRESENCE. THE DAMAGE LOCATION IS IN A RELATIVELY UNCONGESTED COMMERCIAL AREA. THIS AREA WAS FOUND TO BE A LOCATION WHERE TRAFFIC COULD BE DIVERTED, AND THE DAMAGE LOCATION SECURED, SUCH THAT GAS COULD BE VENTED SAFELY WHILE A PLAN FOR ISOLATION OF THE SEGMENT WAS DEVELOPED. GAS VENTED FOR APPROXIMATELY 29 HOURS WHILE CREWS WORKED MULTIPLE OPTIONS FOR ISOLATING THE DAMAGED SEGMENT, MINIMIZING INTERRUPTION OF SERVICE TO CUSTOMERS IN THE AREA.
2025-03-31 10:13 | NO | NO | NO | 20140103 | 15968 | 2014-11-21 10:58 | ORIGINAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 1 METROTECH CENTER | BROOKLYN | NY | 11201 | 2014-10-29 12:07 |  |  | 2014 | 45 TRANTOR PLACE | NEW YORK | RICHMOND | NY | 10302 | 40.6324 | -74.1428 | [9 empty] | 2014-10-29 15:06 | 1099674 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-10-29 12:35 |  |  |  | 2014-10-29 12:36 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 14 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2000 | [5 empty] | 8 | MEDIUM DENSITY MD2406 YELLOW | PLEXCO/DRISCOPIPE 6500 | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | OTHER | [8 empty] | NO RELEASE INVOLVED | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 64000 | 78409.24855491328 | 0 | 0 |  |  | 0 | 0 |  | 0 | 64000 | 32474.759152215808 | 78409.24855491328 | 11 | 1 | 212 |  |  |  |  | 44 | 44 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | NUMEROUS CALLS FROM THE PUBLIC REPORTING "NO GAS" CONDITIONS IN THEIR HOMES. |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES | [9 empty] | YES | CONNECTIVITY TOOL IN THE NRG MAPPING SYSTEM MALFUNCTIONED BECAUSE IT INDICATED THAT THE 8' PL 60PSI MAIN ON TRANTOR PL WAS A VIABLE ISOLATION POINT. | YES | 2 | 0 | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | FLD OPS CONTACTED GAS CONTROL (GC) TO CONFIRM CONNECTIVITY OF THE MAIN. THE GC OPER USED THE 'CONNECTIVITY' TOOL (TOOL) IN THE MAP SYS TO CONFIRM CONNECTIVITY. THE GC OPER ALSO REVIEWED THE AREA IN THE MAP SYS TO ABOUT A 600 SCALE. THE TOOL & A REVIEW OF THE AREA CONFIRMED THAT THE MAIN WAS BACK FED, APPROVAL TO PERFORM THE SQZ OFF WAS GRANTED BY GC. THE TOOL DID NOT ACCOUNT FOR THE DEAD END OF THE MAIN WHICH IS ABOUT 1.6 MILES FROM THE JOB LOCATION & WOULD BE VIEWED AT ABOUT A 900 SCALE | [47 empty] | DAVID ANGELONE | MANAGER | david.angelone@nationalgrid.com | 718 403 3347 |  |  |  |  | ROBERT DEMARINIS | VP MAINT AND CONSTR NY GAS | 5165454337 | robert.demarinis@nationalgrid.com | ON OCTOBER 28TH OF 2014, A NATIONAL GRID STATEN ISLAND FIELD OPS CREW MOBILIZED TO INVESTIGATE A LEAK AT 45 TRANTOR PL. THEY FOUND A STEEL PROTECTION PLATE ON TOP OF THE SERVICE TEE CAP. AS A RESULT, THE SERVICE TEE WAS LEAKING AND REQUIRED REPAIR. THE CREW INSTALLED A NEW SERVICE TEE, TRANSFERRED THE SERVICE CONNECTION AND INSTALLED AN ADAM SLEEVE OVER THE LEAKING SECTION AS A 'MAKE SAFE' TEMPORARY REPAIR. THEY MONITORED THE LOCATION OVERNIGHT. THE FOLLOWING DAY (OCTOBER 29TH) THE CREW RETURNED TO THE LOCATION TO MAKE THE PERMANENT REPAIR. IN ORDER TO PERFORM THE REPAIR, THEY NEEDED TO ISOLATE THE SECTION OF MAIN BY APPLYING SQUEEZE OFF DEVICES. THEY REVIEWED THE NRG MAPS AND CONTACTED GAS CONTROL TO CONFIRM THAT THE MAIN WAS BACK FED. THE GAS CONTROL OPERATOR UTILIZED THE 'CONNECTIVITY' TOOL IN THE NRG MAPPING SYSTEM AND PANNED TO ABOUT 600 SCALE IN ORDER TO CONFIRM BACKFEED. SINCE THE 'CONNECTIVITY' TOOL AND A PAN OF THE AREA CONFIRMED THAT THERE WAS A BACKFEED, APPROVAL TO PERFORM THE SQUEEZE OFF WAS GRANTED BY GAS CONTROL. UNFORTUNATELY, THE 'CONNECTIVITY' TOOL DID NOT ACCOUNT FOR THE DEAD END OF THE MAIN WHICH IS ABOUT 1.6 MILES FROM THE JOB LOCATION. FIELD OPS NOR GAS CONTROL IDENTIFIED THE DEADEND IN THE NRG MAPPING SYSTEM WHEN THEY REVIEWED IT BECAUSE TO CAPTURE BOTH THE JOB LOCATION AND THE DEAD END, THE USER WOULD HAVE TO ZOOM OUT TO 900 SCALE. THE CREW INSTALLED AND MONITORED PRESSURE GAUGES PRIOR TO THE INSTALLATION OF THE ISOLATION DEVICES (SQUEEZE OFFS). KNOWLEDGE OF THE UNPLANNED SUPPLY INTERRUPTION OCCURRED WHEN THE NATIONAL GRID CALL CENTER STARTED TO RECEIVE NO GAS CALLS AROUND 12:00PM. THERE WERE 226 CUSTOMERS INVOLVED IN THE OUTAGE.
2025-03-31 10:13 | NO | NO | NO | 20140104 | 15969 | 2014-11-21 11:49 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2014-10-23 10:10 |  |  | 2014 | 457 RED WING LANE | DEKALB | DEKALB | IL | 60115 | 41.9673 | -88.7307 | [9 empty] | 2014-10-23 12:50 | 1099108 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2014-10-23 10:22 |  |  |  | 2014-10-23 10:22 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2013 | [5 empty] | 1.125 | ASTM D2513 | JM EAGLE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.099 |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 46000 | 56356.64739884392 | 500 | 612.57225433526 | 500 | 612.57225433526 | 0 | 0 |  |  | 150 | 112.171628721541155866900175131348511384 |  | 0 | 47150 | 23952.4165764014787460595446584938704028 | 57693.9635362359811558669001751313485114 | 1 | 0 | 5 |  |  |  |  | 58 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | AUGER | FENCING | YES | 2860734 | J.U.L.I.E. |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | LETICIA QUEZADA | DIR COMPLIANCE AND QA | lquezad@aglresources.com | [5 empty] | LETICIA QUEZADA | DIR COMPLIANCE AND QA | 6303882316 | lquezad@aglresources.com | FENDING COMPANY HIT 1" SERVICE LINE WHILE AUGERING FOR FENCE POST INSTALLATION.
2025-03-31 10:13 | NO | NO | NO | 20140106 | 30432 | 2014-11-25 13:37 | SUPPLEMENTAL FINAL | 15259 | UGI PENN NATURAL GAS | 1 UGI DRIVE | DENVER | PA | 17517 | 2014-11-24 07:31 |  |  | 2014 | 1600 MAIN | DICKSON CITY | LACKAWANNA | PA | 18519 | 41.4698 | -75.609 | [9 empty] | 2014-11-24 18:04 | 1101892 |  | NATURAL GAS |  | 3534 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 25 | 2014-11-24 07:31 |  |  |  | 2014-11-24 07:49 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2014 | [8 empty] | OTHER | PRESSURE RELIEF VALVE | [9 empty] | OTHER | [8 empty] | PRESSURE RELIEF VALVE / OVER-PRESSURE PROTECTION | CLASS 3 LOCATION | 0 | 0 | 21000 | 25728.03468208092 | 1500 | 1837.71676300578 | 0 | 0 |  |  | 18000 | 13460.595446584938704028021015761821366 |  | 0 | 40500 | 23868.7463936102395271453590192644483363 | 41026.346891671638704028021015761821366 | 0 | 0 | 0 |  |  |  |  | 297 | 270 | 282 |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  | YES | [73 empty] | FRANK BENNETT | DIRECTOR ENGINEERING AND TECHNICAL SERVICES | fbennett@ugi.com | 610-458-3567 |  |  |  |  | HANS BELL | CHIEF OPERATING OFFICER | 610-796-3450 | hbell@ugi.com | A PRESSURE RELIEF VALVE ON A REGULATOR STATION OPENED AND VENTED AN ESTIMATED 3.5MM CUBIC FEET OF NATURAL GAS. ROOT CAUSE INVESTIGATION REVEALED THAT THE REGULATORS FOR THE CONTROL GAS TO THE POSITIONER ON THE CONTROL VALVE FAILED, WHICH RESULTED IN EXCESSIVE PRESSURE BEYOND THE CONTROL VALVE AND THE OPENING OF THE RELIEF VALVE PROVIDING OVER-PRESSURE PROTECTION TO THE DOWNSTREAM SYSTEM. AFTER THE RELIEF VALVE OPENED, THE VALVE FAILED TO RE-SEAT DUE TO A PIECE OF WELD SLAG ON THE SEAT OF THE RELIEF. IN RESPONSE TO THE INCIDENT, CREWS SHUT THE INLET VALVE TO THE REGULATOR STATION, HOWEVER THE RELIEF CONTINUED TO VENT DUE TO THE SLAG ON SEAT OF THE RELIEF. THE ISSUE WAS RESOLVED AT APPROXIMATELY 8:59 AM WHEN THE OUTLET VALVE TO THE STATION WAS CLOSED. THE INCIDENT IS BEING REPORTED ON THE BASIS OF THE VOLUMETRIC REPORTING CRITERIA. SUBSEQUENT TO THE INCIDENT, AND BEFORE RETURNING THE STATION TO SERVICE, A DEDICATED FILTER WAS PLACED IN FRONT OF THE REGULATORS TO THE INSTRUMENT GAS TO MINIMIZE THE PROBABILITY OF RE-OCCURRENCE. ADDITIONALLY, A RELIEF VALVE WAS ADDED TO THE INSTRUMENT GAS LINES AS SUPPLEMENTAL OVER-PRESSURE PROTECTION AND SUPPLY GAS TUBING LINES WERE RELOCATED TO MINIMIZE VIBRATION. FINALLY, ADDITIONAL PERIODIC MAINTENANCE HAS BEEN IMPLEMENTED TO INSURE THE REMEDIATION MEASURES TAKEN REMAIN ADEQUATE. 6/1/2018 SUPPLEMENTAL REPORT SUBMITTED TO INDICATE REPORT AS "FINAL"
2025-03-31 10:13 | NO | YES | NO | 20140107 | 15973 | 2014-11-25 16:02 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2014-11-04 12:27 |  |  | 2014 | 19910 LIZZIE RIDGE LN | CYPRESS | HARRIS | TX | 77433 | 29.9308 | -95.7105 | [9 empty] | 2014-11-04 14:10 | 1100176 |  | NATURAL GAS |  | 126.74 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2014-11-04 12:42 |  |  |  | 2014-11-04 12:42 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2014 | [5 empty] | 2 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  |  | MECHANICAL PUNCTURE | 2.9 | 0.4 | [7 empty] | CLASS 3 LOCATION | 200000 | 245028.901734104 | 404 | 494.95838150289008 | 1266 | 1551.03294797687832 | 645 | 790.2182080924854 | ADMINISTARTION COST |  | 829 | 619.93520140105078809106830122591943958 |  | 0 | 203144 | 103231.7716366514071432224168126094570928 | 248485.0464730773045880910683012259194396 | 0 | 0 | 0 |  |  |  |  | 42.6 | 42.6 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHHOLDS OF SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  | YES | [6 empty] | YES | [7 empty] | YES | [6 empty] | CONTRACTOR | AUGER | FENCING | YES | 542250117 | LONE STAR 811 |  | CONTRACT LOCATOR | NO |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | LESLIE J. DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steve.yarbrough@centerpointenergy.com | THE EXCAVAOR (JOHNSON FENCE COMPANY) FAILED TO RECALL LOCATE TICKET #542250117 AFTER MARKS DESTROYED AT 19914 LIZZIE RIDGE LN. THE BUILDER (ASHTON WOODS) CONSTRUCTION SUPERINTENDENT (RANDY LEE - 832-256-0259) HAD (CONTRACTOR LANDSCAPING - 281-345-4777) SET FINAL GRADE ON LOT AND SPREAD SAND WHICH DESTROYED MARKS AFTER (ULS) LOCATOR MARKED TICKET. AT THE TIME OF THE DAMAGE, THE LOT WAS COVERED WITH LOOSE SAND AND ALL MARKS INCLUDING GAS, ELECTRIC AND TELEPHONE HAD BEEN REMOVED. PERMANENT MARKERS WERE PLACED IN THE STREET IN FRONT AND TO THE RIGHT OF 19914 LIZZIE RIDGE LN WHICH INDICATES A GAS LINE RUNNING BETWEEN 19914 AND 19910. JOHNSON FENCE CREW WAS DRILLING HOLES TO SET FENCE POSTS WITH MOTORIZED AUGER THAT DAMAGED A 2" PLASTIC MAIN, ESCAPING GAS IGNITED AND DAMAGED (3) UNOCCUPIED HOMES UNDER CONSTRUCTION. THE HOMES DAMAGED ARE 19906, 19910, & 19914 LIZZIE RIDGE LN.
2025-03-31 10:13 | NO | YES | NO | 20140108 | 16085 | 2014-11-28 13:43 | SUPPLEMENTAL FINAL | 13302 | NATIONAL GAS & OIL CORP | 1500 GRANVILLE ROAD | NEWARK | OH | 43055 | 2014-10-26 08:00 |  |  | 2014 | 1149 PEMBROKE | NEWARK | LICKING | OH | 43055 | 40.0656 | -82.465 | [9 empty] | 2014-10-26 10:07 | 1099337 |  | NATURAL GAS |  | 7.01 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2014-10-26 08:29 |  |  |  | 2014-10-26 08:50 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1981 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 405000 | 496183.5260115606 | 2000 | 2450.28901734104 | 2000 | 2450.28901734104 | 10000 | 12251.4450867052 | 10,000 IN COST TO INVESTIGATE INCIDENT, COPY RECORDS, WRITE REPORTS ETC. |  | 1000 | 747.810858143607705779334500875656742557 |  | 0 | 420000 | 213299.957651282832973730297723292469352 | 514083.3599910914877057793345008756567426 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL LEAK OF THIS KIND WAS NOT DETECTABLE ON SUCH A LARGE SYSTEM MONITORED BY SCADA | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | NUT FOLLOWER |  | RISER |  | ROBROY |  | OTHER | MATERIALS JOINED: 1ST PLASTIC, 2ND STEEL | [22 empty] | YES | AFTER THE LABORATORY INVESTIGATION, IT APPEARS THE RISER THAT WAS INSTALLED BY THE HOMEOWNERS CONTRACTOR (AT TIME OF CONSTRUCTION) PULLED FROM THE SEALING RING, CAUSING LEAKAGE. |  |  | YES |  |  |  |  | NO | [86 empty] | PATRICK SEAMUS MULLIGAN | ENGINEERING MANAGER | smulligan@theenergycoop.com | 740 348-1116 | 740 348-1131 |  |  |  | PATRICK S. MULLIGAN | ENGINEERING MANAGER | 740 348-1116 | smulligan@theenergycoop.com | ON SUNDAY, OCTOBER 26, 2014, A NEIGHBOR REPORTED AN EXPLOSION AND CALLED 911. NATIONAL GAS & OIL COOPERATIVE WAS NOTIFIED APPROXIMATELY 30 MINUTES LATER. WHEN COOPERATIVE EMPLOYEES ARRIVED, THE SERVICE LINE VALVE WAS SHUT AND THE FIRE DEPARTMENT EXTINGUISHED THE FLAMES. READINGS INDICATED THAT NATURAL GAS WAS PRESENT IN THE GROUND AROUND THE HOMEOWNER'S NATURAL GAS RISER. THE HOMEOWNER'S NATURAL GAS SERVICE LINE WAS TESTED AND LEAKAGE WAS FOUND AT THE RISER HEAD. THE HOMEOWNER'S RISER WAS REMOVED AND THE SERVICE LINE CAPPED AT THE BASE OF THE RISER AND RETESTED. THE SERVICE LINE HELD THE PRESSURE TEST WITHOUT THE RISER. THE HOMEOWNER'S RISER WAS LATER EXAMINED IN A LABORATORY. THE LABORATORY TESTS ON THE RISER SUGGESTED THAT THE PIPE INSERTED INSIDE THE RISER HEAD HAD PULLED PAST THE SEALING RING. THIS RISER WAS INSTALLED BY THE HOMEOWNER (OR PREDECESSOR HOMEOWNER) OR THE HOMEOWNER'S CONTRACTOR OR REPRESENTATIVE, NOT BY THE NATIONAL GAS & OIL COOPERATIVE.
2025-03-31 10:13 | NO | YES | YES | 20140109 | 15975 | 2014-12-04 16:11 | ORIGINAL FINAL | 11800 | ATMOS ENERGY CORPORATION - LOUISIANA | 101 AIRLINE DRIVE | METAIRIE | LA | 70001 | 2014-11-08 10:05 |  |  | 2014 | LOUISIANA HIGHWAY 21 @ N. AZALEA | COVINGTON | ST. TAMMANY | LA | 70471 | 30.4591 | -90.1236 | [9 empty] | 2014-11-08 11:05 | 1100522 |  | NATURAL GAS |  |  |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2014-11-08 10:30 |  |  |  | 2014-11-08 10:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | OTHER | BELL HOLE EXCAVATION | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1987 | [5 empty] | 2 | SDR 11 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | 3408 | OTHER | [8 empty] | PURGING TO DE-ACTIVATE PIPE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 78 | 80 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | NOT FOLLOWING OPERATOR'S PROCEDURE. |  |  | YES |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | STEPHANIE LEWIS | ENGINEER II | stephanie.lewis@atmosenergy.com | 5048494417 | 5048494345 |  |  |  | DANIEL WAGUESPACK | COMPLIANCE MANAGER | 5048494363 | daniel.waguespack@atmosenergy.com | NOTE: DETAILS OF THE INCIDENT DESCRIPTION AND THE FINDINGS IN THE INVESTIGATION ARE SUPPORTED BY INFORMATION SUPPLIED TO ATMOS ENERGY FROM MILLER PIPELINE. INCIDENT DESCRIPTION: ON SATURDAY, NOVEMBER 8, 2014, MILLER PIPELINE CORP., A CONTRACTOR PERFORMING WORK FOR ATMOS ENERGY LOUISIANA DIVISION, WAS SCHEDULED TO DEACTIVATE AND ABANDON A 4" PE GAS LINE ON HWY 21 @ N. AZALEA IN COVINGTON, LA. THIS WAS A COOL DAY WITH LOW HUMIDITY. MILLER PIPELINE EMPLOYEE ANTHONY DUNCAN (CREW FOREMAN) WAS IN CHARGE OF THIS WORK AND WAS QUALIFIED IN THE ASSOCIATED OQ TASKS. - ALL LINE STOPPERS UTILIZED TO BLOCK THE SOURCE OF GAS WERE INSTALLED PREVIOUSLY. - BEFORE BEGINNING THE PURGING PROCESS, MR. DUNCAN CHECKED TO MAKE SURE ALL SOURCES OF GAS WERE BLOCKED FROM THE GAS LINE TO BE DEACTIVATED. - AFTER CONFIRMATION THAT ALL SOURCES OF GAS WERE BLOCKED, MR. DUNCAN PROCEEDED TO OPEN THE VALVE (ON PURGE RISER) TO BEGIN DE-PRESSURING AND BLOWING DOWN THE GAS FROM THE LINE. HE WAITED 15 - 20 MINUTES FOR THE LINE TO BLOW DOWN. - ONCE HE THOUGHT THE LINE WAS COMPLETELY BLOWN DOWN, MR. DUNCAN GOT IN THE EXCAVATION TO REMOVE THE BLOW DOWN RISER. HE USED 2-INCH PLASTIC CUTTERS TO PERFORM THIS TASK. IT WAS DURING THIS PROCESS THAT THE RESIDUAL GAS IN THE PIPE IGNITED AND A FLASH FIRE OCCURRED INJURING MR. DUNCAN. - MR. DUNCAN WAS TRANSPORTED TO THE HOSPITAL WHERE HE WAS HELD OVERNIGHT FOR TREATMENT AND OBSERVATION. CAUSE OF THE INCIDENT: IT SEEMS THE PRIMARY CAUSE OF THE INCIDENT WAS THE GAS LINE TO BE ABANDONED WAS NOT PURGED OF GAS PROPERLY, ALLOWING RESIDUAL GAS TO REMAIN IN THE LINE. SECONDLY, PRECAUTIONS TO PREVENT ACCIDENTAL IGNITION WERE NOT FOLLOWED BY NOT PROPERLY GROUNDING THE PIPE OR TOOLS PRIOR TO CUTTING THE PURGE RISER. STATIC ELECTRICITY SEEMS TO HAVE BEEN THE SOURCE OF IGNITION OF THE RESIDUAL GAS. THIRDLY, MR. DUNCAN WAS NOT WEARING THE PROPER PPE (PERSONAL PROTECTIVE EQUIPMENT) FIRE RETARDANT CLOTHING/GLOVES. THIS ADDED PROTECTION COULD HAVE MINIMIZED THE EXTENT OF THE INJURIES. FOURTHLY, MR. DUNCAN SENT HIS HELPER (ON FIRE WATCH) AWAY TO PERFORM ANOTHER JOB DUTY. BY HAVING SOMEONE ON FIRE WATCH AT THE EXCAVATION WITH A FIRE EXTINGUISHER COULD ALSO HAVE MINIMIZED THE EXTENT OF THE INJURIES, BY EITHER EXTINGUISHING THE FIRE RIGHT AWAY OR PULLING MR. DUNCAN OUT OF THE EXCAVATION AND AWAY FROM THE FIRE. ROOT CAUSE: THERE SEEMS TO BE HUMAN ERROR IN JUDGMENT BY MR. DUNCAN IN SEVERAL INSTANCES INVOLVING FOLLOWING PROCEDURES AND SAFETY POLICIES; THE BELOW FACTORS IN COMBINATION RELATED TO THE CAUSE OF THE FLASH FIRE WHICH RESULTED IN THE INCIDENT: - DID NOT PURGE NATURAL GAS FROM DEACTIVATED LINE BY USING AIR OR NITROGEN GAS; - DID NOT CHECK FOR COMPLETE PURGING (0% GAS) OF NATURAL GAS WITH A CGI (COMBUSTIBLE GAS INDICATOR) FROM THE PURGE RISER; - DID NOT PRACTICE PREVENTING STATIC ELECTRICITY HAZARD BY USING SOAPY WATER OR ANTI-STATIC SPRAY AND BURLAP SACK ON PLASTIC PIPE AND ALSO GROUNDING TOOLS PRIOR TO CUTTING PURGE RISER FROM DEACTIVATED PIPE. THIS ALONG WITH RESIDUAL GAS IN THE DEACTIVATED PIPE RESULTED IN A FLASH FIRE WHICH CAUSED THE INJURY. - DID NOT WEAR PROPER PPE (PERSONAL PROTECTIVE EQUIPMENT); FIRE RETARDANT CLOTHING AND GLOVES. - DID NOT HAVE ANOTHER WORKER AT PURGE LOCATION ON FIRE WATCH WITH A FIRE EXTINGUISHER. THE ABOVE INSTANCES (WHICH WERE NOT FOLLOWED) ARE COVERED IN ATMOS ENERGY'S O&M PROCEDURES AND SAFETY MANUAL; THEY ARE ALSO COVERED UNDER OQ TASKS L2 - ACTIVATING AND PURGING PIPELINES AND M8 - PREVENTING ACCIDENTAL IGNITION.
2025-03-31 10:13 | NO | YES | NO | 20140111 | 15978 | 2014-12-08 13:40 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-11-07 11:14 |  |  | 2014 | 1 S. MARKET STREET | SAN JOSE | SANTA CLARA | CA | 95113 | 37.3349 | -121.8922 | [9 empty] | 2014-11-07 | 1100473 |  | NATURAL GAS |  | 1228 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO |  | 2014-11-07 11:14 |  |  |  | 2014-11-07 11:31 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 63 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1988 | [5 empty] | 2 | TR-418 PL | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | THE 2-INCH PLASTIC MAIN WAS SEPARATED AT THE COUPLING | CLASS 4 LOCATION | 0 | 0 | 105000 | 128640.1734104046 | 0 | 0 | 0 | 0 |  |  | 4640 | 3469.842381786339754816112084063047285464 |  | 0 | 109640 | 56488.7090896206974781085814360770577933 | 132110.0157921909397548161120840630472855 | 40 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD-PARTY DIG-IN | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 459722 | USAN |  | UTILITY OWNER | UNKNOWN/OTHER | YES | 16 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT 1114 HOURS PG&E WAS NOTIFIED OF A THIRD PARTY DIG-IN AT 1 SOUTH MARKET STREET IN SAN JOSE. A THIRD PARTY (GM ENGINEERING) STRUCK A 2-INCH PLASTIC DISTRIBUTION MAIN (NEAR A 3-WAY TEE, WHICH BRANCHES OFF A 4-INCH PLASTIC DISTRIBUTION MAIN) WITH A BACKHOE, CAUSING AN UNINTENTIONAL RELEASE OF NATURAL GAS. THE THIRD PARTY CALLED USA (NO. 459722) ON 11/3/2014. PG&E RECEIVED THE NORMAL NOTICE ON 11/03/2014 (11:25:55 AM). IN RESPONSE TO THE TICKET, PG&E ATTEMPTED TO MAKE CONTACT WITH THE EXCAVATOR BEFORE LOCATING AND MARKING ITS FACILITIES. PG&E LEFT A MESSAGE FOR THE EXCAVATOR ON 11/5/2014 BUT DID NOT RECEIVE A RESPONSE FROM THE EXCAVATOR TO COORDINATE THE LOCATE AND MARK PRIOR TO THE EXCAVATION. (AS IS CUSTOMARY FOR LARGE EXCAVATION PROJECTS, PG&E COMMUNICATES WITH THE EXCAVATORS TO PHASE THE MARKING OF PG&E FACILITIES TO ENSURE MARKINGS REMAIN VISIBLE IN THE EXCAVATION AREA.) A PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SCENE AT 1131 HOURS. PG&E REPAIR CREW ARRIVED AT APPROXIMATELY 1140 HOURS. GAS WAS COMPLETELY SHUT IN AT 1702 HOURS BY CLOSING 10 DISTRIBUTION MAIN VALVES AND ISOLATING APPROXIMATELY 4 BLOCKS OF THE GAS DISTRIBUTION SYSTEM AND 40 CUSTOMERS. PG&E INITIALLY PLANNED TO SAFELY SQUEEZE THE 2-INCH DIAMETER PLASTIC PIPE AT A LOCATION AWAY FROM THE PERIPHERY OF THE DIG-IN LOCATION. UPON FURTHER EVALUATION IT WAS DETERMINED THAT DIGGING AND SQUEEZING THE LINE WOULD TAKE A SUBSTANTIAL AMOUNT OF TIME DUE TO THE DEPTH EXCEEDING 5 FEET AND THE NEED TO INSTALL SHORING TO COMPLETE THIS WORK. ONCE PG&E ESTIMATED THE TOTAL TIME REQUIRED FOR THE SHUT-IN, PG&E DECIDED TO LOOK FOR AN ALTERNATIVE THAT INCLUDED CLOSING VALVES IN THE SURROUNDING AREA THAT COULD POTENTIALLY CAUSE MORE CUSTOMER OUTAGES. PG&E DETERMINED THAT CLOSING VALVES WAS THE FASTEST AND SAFEST METHOD AND CHOSE TO CLOSE NEARBY VALVES FOR SHUTTING IN GAS FLOW. REPAIR CREW REPLACED THE 4X4X2-INCH TEE AND THE DAMAGED 2-INCH DISTRIBUTION MAIN. ABOUT 2,500 PEOPLE WERE EVACUATED FROM OFFICE BUILDINGS ON A TWO-BLOCK AREA OF MARKET AND FIRST AND SAN PEDRO STREETS. SANTA CLARA STREET WAS CLOSED BETWEEN FIRST AND SAN PEDRO STREETS, ACCORDING TO THE VALLEY TRANSPORTATION AUTHORITY. BUS LINES 22, 522, 68, 17, 168, AND 181 WERE REROUTED, VTA OFFICIALS SAID. SEVERAL SAN FRANCISCO BAY AREA NEWS STATIONS WERE OBSERVED ON SCENE (I.E., KTVU, NBC BAY AREA). THIS INCIDENT WAS REPORTED TO THE CPUC AND DOT DUE TO THE ESTIMATED DAMAGES EXPECTED TO EXCEED $50,000 AND MAJOR MEDIA OBSERVED ON SCENE.
2025-03-31 10:13 | NO | NO | NO | 20140112 | 16164 | 2014-12-10 09:42 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2014-11-24 10:03 |  |  | 2014 | 1705 GRANVILLE AVENUE | MUNCIE | DELAWARE | IN | 47303 | 40.2087 | -85.3824 | [9 empty] | 2014-11-24 12:23 | 1101854 |  | NATURAL GAS |  | 15 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2014-11-24 10:10 |  |  |  | 2014-11-24 10:10 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 10 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1967 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | HOLE CAUSED BY ELECTRICAL ARC | [5 empty] | CLASS 3 LOCATION | 50000 | 61257.225433526 | 2000 | 2450.28901734104 | 1600 | 1960.231213872832 | 0 | 0 |  |  | 70 | 52.34676007005253940455341506129597197898 |  | 0 | 53670 | 27246.0346078441367481611208406304728546 | 65720.092424809924539404553415061295972 | 1 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | JOHN SPINKS | MANAGER QUALITY ASSURANCE | jaspinks@vectren.com | 937-440-1844 | 937-440-1818 |  |  |  | JAMES FRANCIS | DIRECTOR ENGINEERING AND ASSET MANAGEMENT | 812-491-4369 | jmfrancis@vectren.com | ON 11/24/14 AT 10:03 AM, PROPRIETOR AT 1705 GRANVILLE AVENUE, MUNCIE, INDIANA ( A PLUMBING AND HEATING COMPANY) CALLED VECTREN AND REPORTED A FIRE NEAR THE GAS METER. VECTREN FIRST RESPONDER ARRIVED AT 10:10 AM AND WORKED WITH FIRE DEPARTMENT TO SECURE THE SITE. A VECTREN CONSTRUCTION CREW WAS DISPATCHED AND SQUEEZED OFF THE SERVICE STOPPING THE FLOW OF GAS AT 11:05 AM. THE GAS SERVICE WAS THEN CUT/CAPPED AND RETIRED AT THE MAIN. THE BUILDING STRUCTURE AND CONTENTS SUSTAINED DAMAGE. BASED UPON OUR INVESTIGATION OF THIS INCIDENT, WE HAVE CONCLUDED THAT AN ENERGIZED WIRE THAT RAN BETWEEN THE AFFECTED BUILDING AND AN ADJACENT COMMUNICATION TOWER USED BY THE PROPRIETOR HAD BEEN PLACED AGAINST THE OPERATOR'S SERVICE LINE. THE WIRE SHORTED TO GROUND CREATING AN ELECTRICAL ARC MELTING A .5 INCH BY .5 INCH HOLE IN THE PLASTIC SERVICE LINE AND WAS THE PROXIMATE CAUSE OF THE INCIDENT. THE SUBJECT WIRE WAS NOT OWNED OR CONTROLLED BY VECTREN.
2025-03-31 10:13 | NO | NO | NO | 20140113 | 15985 | 2014-12-16 09:55 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2014-11-19 21:15 |  |  | 2014 | 2808 AVENUE F | ROSENBERG | FT BEND | TX | 77471 | 29.6068 | -95.7924 | [9 empty] | 2014-11-19 22:52 | 1101512 |  | NATURAL GAS |  | 6.35 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 250 | 2014-11-19 21:15 |  |  |  | 2014-11-19 21:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1925 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 27173 | 33290.85173410403996 | 2596 | 3180.47514450866992 | 0 | 0 |  |  | 42 | 31.40805604203152364273204903677758318739 |  | 0 | 29811 | 15134.3840595041695968966725043782837128 | 36502.7349346547414036427320490367775832 | 0 | 0 | 168 |  |  |  |  | 42.6 | 42.6 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESGOLDS OF SYSTEM | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | A DENT AT THE FAILURE SITE CAUSED A CRACK TO INITIATE AT THE INNER SURFACE OF THE PIPE. OVER TIME THERMAL AND GROUND STRESSES ALLOWED THE CRACK TO PROPAGATE. | [154 empty] | LESLIE J. DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steve.yarbrough@centerpointenergy.com | SMELL OF GAS REPORTED INSIDE AND OUTSIDE RESIDENCE AT 2808 AVENUE F, INVESTIGATION RESULTED IN GAS BEING DETECTED INSIDE THE SANITARY SEWER SYSTEM. APPROXIMATELY 80 HOMES WERE EVACUATED OF APPROXIMATELY (250) PERSONNEL WHILE ONGOING INVESTIGATION WAS CONDUCTED. SOURCE OF GAS LEAK WAS DISCOVERED AND SECURED AT JENETTA & AVENUE F AND THE GAS WAS SHUT OFF AT 0800 AM ON 11/20/2014. PERMANENT REPAIRS WERE COMPLETED AND THE GAS RESTORED TO THE MAIN AT 1500 HOURS ON 11/20/2014 WITH CUSTOMER RELITES AT THAT TIME. PREVIOUSLY UNKNOWN 3RD-PARTY DAMAGE TO PIPE AT 800 JENETTA & AVE F AT UNKNOWN TIME RESULTED IN STRESS FACTORS CAUSING THE PIPE TO CRACK AND LEAK.
2025-03-31 10:13 | NO | NO | NO | 20140114 | 15986 | 2014-12-16 18:36 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-11-16 19:35 |  |  | 2014 | 1384 ESSEX WAY | SAN JOSE | SANTA CLARA | CA | 95117 | 37.2993 | -121.9563 | [9 empty] | 2014-11-16 | 1101208 |  | NATURAL GAS |  | 25.91 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO |  | 2014-11-16 19:35 |  |  |  | 2014-11-16 20:11 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | STEEL | [9 empty] | OTHER | [8 empty] | VEHICLE IMPACT | CLASS 3 LOCATION | 50000 | 61257.225433526 | 7000 | 8576.01156069364 | 0 | 0 | 0 | 0 |  |  | 98 | 73.28546409807355516637478108581436077058 |  | 0 | 57098 | 28990.6257149509605674255691768826619965 | 69906.5224583177135551663747810858143608 | 0 | 0 | 5 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VEHICLE IMPACT INCIDENT | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | (925) 328-5756 | lcd1@pge.com | ON NOVEMBER 16, 2014 AT 1935 HOURS, PG&E WAS NOTIFIED THAT A VEHICLE STRUCK A FIVE-METER MANIFOLD, RESULTING IN AN UNINTENTIONAL RELEASE OF GAS WHICH SUBSEQUENTLY IGNITED. THERE WERE TWO EXISTING 4-INCH CONCRETE BOLLARDS INSTALLED BESIDE THE METER MANIFOLD. A VEHICLE STRUCK THE METER MANIFOLD WHILE DRIVING INTO THE ALLEY WAY (COMING FROM ESSEX WAY). THE DRIVER FLED THE SCENE WITH THE VEHICLE. THE SERVICE RISER WAS NOT DAMAGED FROM THE INCIDENT. PG&E'S GAS SERVICE REPRESENTATIVE (GSR) WAS ON SITE AT 2011 HOURS ON NOVEMBER 16, 2014. FIVE SERVICE ACCOUNTS EXPERIENCED GAS SERVICE INTERRUPTION AND GAS SERVICE WAS AVAILABLE FOR RELIGHT BY 1253 HOURS ON NOVEMBER 17, 2014. (THE FIFTH METER SERVES A UTILITY ROOM FOR THE MULTI-UNIT RESIDENCE.) THE SAN JOSE FIRE DEPARTMENT STOPPED THE FLOW OF GAS BY CLOSING THE SERVICE VALVE AND EXTINGUISHED THE FIRE PRIOR TO THE ARRIVAL OF THE GSR. THE REGULATOR, 5-METER MANIFOLD, AND METERS WERE REPLACED. THERE WERE NO INJURIES, NO FATALITIES AND NO MEDIA ASSOCIATED WITH THIS INCIDENT. UNINTENTIONAL RELEASE OF NATURAL GAS WAS LESS THAN 3 MMCF. THE DAMAGES RESULTING FROM THE ENSUING FIRE ARE ESTIMATED TO EXCEED $50,000, THUS MEETING THE CRITERIA TO REPORT BOTH TO THE CPUC AND DOT.
2025-03-31 10:13 | NO | YES | NO | 20140115 | 30562 | 2014-12-18 16:34 | SUPPLEMENTAL FINAL | 12582 | ATMOS ENERGY CORPORATION - MISSISSIPPI | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2014-11-12 16:45 |  |  | 2014 | 516 WEST JEFFERSON ST | KOSCIUSKO | ATTALLA | MS | 39090 | 33.0555 | -89.6013 | [9 empty] | 2014-11-12 19:16 | 1100900 |  | NATURAL GAS |  | 2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2014-11-12 16:45 |  |  |  | 2014-11-12 17:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | OTHER | INVESTOR OWNED | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | REGUALTOR DIAPHRAGM | [9 empty] | OTHER | [8 empty] | REGULATOR DIAPHRAGM FAILED | CLASS 3 LOCATION | 115000 | 140891.6184971098 | 8846 | 10837.62832369941992 | 3701 | 4534.25982658959452 | 6821 | 8356.71069364161692 | CLEANUP |  | 8 | 5.98248686514886164623467600700525394046 |  | 0 | 134376 | 68186.2909906900486157898423817863397548 | 164626.1998279055802216462346760070052539 | 1 | 0 | 0 |  |  |  |  | 250 | 60 | 60 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  | YES | [73 empty] | DEAN G. MORRIS | MANAGER OF COMPLIANCE | dean.morris@atmosenergy.com | 6015925360 |  |  |  |  | DAVE DOGGETTE | VICE PRESIDENT OF TECH SERVICES | 601-420-5030 | dave.doggette@atmosenergy.com | DURING A CHANGE OF WEATHER FROM VERY WARM WEATHER TO VERY COLD WEATHER, METAL PARTICLES IN THE LINE WERE ENTRAINED IN THE GAS STREAM. THE METAL PARTICLES CUT AND DAMAGED THE RUBBER DIAPHRAGM CONTROLLING PRESSURE AND SETTLED IN THE PRESSURE REILEF PILOT. RISING PRESSURE CAUSED THE SERVICE REGULATOR AT A GROCERY STORE TO FAIL, WHICH THEN CAUSED EXCESSIVE PILOT LIGHT FLAMES AT THE APPLIANCES INSIDE THE STORE. THESE FLAMES CAUSED A FIRE, WHICH DAMAGED THE BUILDING AND CONTENTS. THE STORE WAS CLOSED AT THAT TIME. THERE WERE NO EVACUATIONS. THERE WERE NO INJURIES OR DEATHS.
2025-03-31 10:13 | NO | YES | YES | 20140116 | 16738 | 2014-12-18 17:40 | SUPPLEMENTAL | 12342 | MEMPHIS LIGHT GAS & WATER DIVISION | P.O. BOX 430 | MEMPHIS | TN | 38101 | 2014-11-25 10:35 |  |  | 2014 | 4624 WINTER PARK | MEMPHIS | SHELBY | TN | 38141 | 35.022 | -89.8454 | [9 empty] | 2014-11-25 12:10 | 1101962 |  | NATURAL GAS |  | 60 |  | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2 | 0 | 0 | 0 | 0 | 2 | YES |  |  |  |  | NO | 0 | 2014-11-25 10:35 |  |  |  | 2014-11-25 10:50 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1983 | [5 empty] | 2.375 | ASTM D2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | OTHER | [8 empty] | EMPLOYEE RELEASED GAS THROUGH A SQUEEZE OFF TOOL. | CLASS 3 LOCATION | 0 | 0 | 9000 | 11026.30057803468 | 4000 | 4900.57803468208 | 0 | 0 |  |  | 118 | 88.24168126094570928196147110332749562172 |  | 0 | 13118 | 6678.064174334991866900175131348511383538 | 16015.1202939777057092819614711033274956 | 0 | 0 | 22 |  |  |  |  | 90 | 90 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT DID NOT HAPPEN AT OR NEAR A PRESSURE REGULATOR STATION, WHICH IS WHERE IS WHERE OUR SCADA MONITORING IS LOCATED. THE RELEASE OF GAS WAS NOT GREAT ENOUGHT OT AFFECT OUR SCADA. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | EMPLOYEES FAILED TO FOLLOW PROCEEDURES BY NOT TAKING APPROPIATE STEPS TO MINIMIZE THE ESCAPE OF GAS TO PREVENT PERSONNEL FROM A POTIENTAL HAZARD. |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | CLIFTON PHILLIPS | LEAD GAS SYSTEM INTEGRITY ENGINEER | cphillips@mlgw.org | 901.320.1061 |  |  |  |  | VIRGIL L DEANES JR | MANAGER GAS ENGINEERING AND OPERATIONS | 901.320.1401 | vdeanes@mlgw.org | 11/21/2014 4:28 PM CUSTOMER CALLS IN GAS LEAK DUE TO ODOR OUTSIDE 4:29 PM EMPLOYEE A002244 IN CALL CENTER RECEIVES AND CREATES A LEAK MAINTENANCE 4:31 PM GAS LEAK CALL WAS DISPATCHED TO CUSTOMER SERVICE TECH 65252 4:36 PM CUSTOMER SERVICE TECH 65252 EN-ROUTE 4:53 PM ON SITE AND EVALUATES THE LEAK, GIVES GRADE 1 LEAK MAINTENANCE FOR REPAIRS TO BE MADE BY DISTRIBUTION 6:05 PM GAS DISTRIBUTION RECEIVES GRADE 1 LEAK MAINTENANCE WORK REQUEST, GIVE TO CREW 6370 6:50 PM GAS DIST. ARRIVES AND MAKES TEMPORARY REPAIR BY PLACING A BOLT ON FITTING OVER A LEAKING PE BUTT FUSE AND MAKES A NOTE THAT THE JOB IS INCOMPLETE, 6370 10:45 PM CREW 6370 DEPARTED 11/24/2014 SUPERVISOR STATED CREW WAS ON SITE AT WINTER PARK TO PREP/ENLARGE EXCAVATION FOR PLANNED OUTAGE (PERMANENT REPAIR) ON 11/25,. ACCESS TO CLEARANCE ORDER 6894 WAS GIVEN. 11/25/2014 8:00 AM CREW 3710 CONTINUED WORK REQUEST TO MAKE PERMANENT REPAIRS AT 4624 WINTER PARK 9:24 AM THE CLEARANCE ORDER 6894 WAS ACTIVATED TO CLOSE VALVES AND SQUEEZE OFF MAIN TO REPLACE LEAKING INLINE TEES. NARRATIVE OF MAINTENANCE EVENTS: CUSTOMERS TO BE AFFECTED BY THE MAINTENANCE WERE TURNED OFF. VALVE WAS CLOSED AND SQUEEZE OFF TOOL WAS INSTALLED. EVIDENCE INDICATES A THREE (3) FOOT SECTION WITH TWO INLINE TEES WERE CUT FROM MAIN AND REMOVED FROM EXCAVATION. EVIDENCE ALSO INDICATES THAT NEW INLINE TEES WERE ELETROFUSED ABOVE GROUND. EMPLOYEE STATEMENTS INDICATE, PRIOR TO INSTALLING NEW TEES, AN EMPLOYEE WAS OPENING THE SQUEEZE OFF TOOL AND ROTATING ITS POSITION ON THE PIPE WHEN AN IGNITION OCCURRED. STATEMENTS INDICATE THAT 2 EMPLOYEES WERE IN THE EXCAVATION AT THE TIME OF IGNITION AND 3 WERE IN CLOSE VACINITY OF THE EXCAVATION. 10:35 AM CREW 3710 CREW LEADER RADIOS INTO THE CONTROL ROOM AND TELL DISPATCH HE NEEDS THE AMBULANCE, HE HAS GOT TWO PEOPLE DOWN AND BURNED 11:45AM CREWS 3890 & 3810 RECEIVED AND ACTIVATED CLEARENCE ORDER #6898 TO MAKE THE PERMANENT REPAIRS AFTER ALL PREVIOUS CREW MEMBERS HAD BEEN TRANSPORTED TO THE HOSPITAL. 11:49 AM CREWS 3890 & 3910 REQUEST FOR CUSTOMER SERVICE TECH TO COME AND LOCK OFF GAS METERS TO 22 HOMES IN A GAS FIRE HAS CAUSED FOR A 2INCH MAIN TO BE VALVED OFF. 5:25 PM BOTH CREWS HAD COMPLETED THE MAINTENANCE OPERATED VALVES TO OPEN POSITION, AND REQUESTED CUSTOMER SERVICE FOR RELIGHTS.
2025-03-31 10:13 | NO | NO | NO | 20140117 | 16199 | 2014-12-19 16:52 | SUPPLEMENTAL FINAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2014-11-20 19:47 |  |  | 2014 | 40 NOTTINGHAM WAY | MAHOPAC | PUTNAM | NY | 10541 | 41.359 | -73.7383 | [9 empty] | 2014-11-21 14:57 | 1101674 |  |  |  | 16.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2014-11-20 19:47 |  |  |  | 2014-11-20 20:37 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1989 | [8 empty] | OTHER | ALUMINUM CASED METER AND REGULATOR | [9 empty] | OTHER | [8 empty] | INVESTIGATION DETERMINED THAT GAS WAS NOT THE CAUSE OF THE INCIDENT. | CLASS 3 LOCATION | 0 | 0 | 100 | 122.514450867052 | 2950 | 3614.176300578034 | 0 | 0 |  |  | 0 | 0 |  | 0 | 3050 | 1547.6252408477846 | 3736.690751445086 | 0 | 0 | 1 |  |  |  |  | 112 | 112 | 120 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | INVESTIGATION DETERMINED THAT GAS WAS NOT THE CAUSE OF THE INCIDENT. | [47 empty] | LENORE J CLARKE | SECTION ENGINEER GAS SYSTEM SAFETY AND COMPLIANCE | lclarke@cenhud.com | 845 486 5521 | 845 486 5697 |  |  |  | LAWRENCE R. CAMBALIK | MANAGER GAS MECHANICAL AND ENGINEERING | 845 486 5741 | lcambalik@cenhud.com | INVESTIGATION DETERMINED THAT GAS WAS NOT THE CAUSE OF THIS INCIDENT
2025-03-31 10:13 | NO | YES | NO | 20140120 | 15992 | 2014-12-23 11:09 | ORIGINAL FINAL | 30769 | MISSOURI GAS ENERGY | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2014-11-25 12:22 |  |  | 2014 | 243 N MULLEN RD AT LARKSPUR | BELTON | CASS | MO | 64012 | 38.8164 | -94.512 | [9 empty] | 2014-11-25 16:14 | 1101993 |  | NATURAL GAS |  | 5460 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 25 | 2014-11-25 12:22 |  |  |  | 2014-11-25 12:43 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2002 | [5 empty] | 8 | API 5L X-42 | UNKNOWN | STEEL |  | OTHER | ERW | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 2.1 | 2.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 73327 | 89836.17138728322004 | 500 | 612.57225433526 | 0 | 0 |  |  | 31695 | 23701.8651488616462346760070052539404553 |  | 0 | 105522 | 59386.7698961359844863817863397548161121 | 114150.6087904801262746760070052539404553 | 0 | 0 | 0 |  |  |  |  | 50 | 50 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | GRADER/SCRAPER | ROAD WORK | NO |  |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED |  |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MARK D. LAUBER | MANAGER OF PIPELINE SAFETY COMPLIANCE | mark.lauber@thelacledegroup.com | 314-658-5413 | 314-535-9414 |  |  |  | CRAIG R. HOEFERLIN | VICE PRESIDENT OF OPERATION SERVICES | 314-658-5410 | craig.hoeferlin@thelacledegroup.com | CONTRACTOR HIT 8" STEEL MAIN WHILE SCARIFYING OLD ROAD BASE WORKING POT ASH INTO THE BASE. THE MAIN WAS ONLY 12" DEEP AT THE TIME OF THE DAMAGE DUE TO PRIOR GRADING WORK HAVING ALREADY REMOVED EXISTING, ADDITIONAL COVER. THE 8" STEEL MAIN IS A ONE-WAY FEED INTO THE TOWN OF BELTON, MO. THE DAMAGED PIPE WAS NOT SHUT DOWN (THOUGH PRESSURE ON THE LINE WAS CUT BACK FROM 50 TO 30 PSI) UNTIL A 6" PLASTIC BYPASS COULD BE INSTALLED TO CARRY THE GAS LOAD. NO CUSTOMERS WERE OUT OF SERVICE AT ANY TIME.
2025-03-31 10:13 | NO | NO | NO | 20140121 | 16313 | 2014-12-30 15:04 | SUPPLEMENTAL FINAL | 3240 | DELMARVA POWER & LIGHT COMPANY | 630 MARTIN LUTHER KING JR. | WILMINGTON | DE | 19801 | 2014-12-01 13:30 |  |  | 2014 | 8 LOWER VALLEY LN. | NEWARK | NEW CASTLE | DE | 19711 | 39.7016 | -75.6921 | [9 empty] | 2014-12-01 15:00 | 1102340 |  | NATURAL GAS |  | 40.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 6 | 2014-12-01 13:30 |  |  |  | 2014-12-01 14:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | OTHER | NATURAL GAS, INVESTOR OWNED | OUTSIDE METER/REGULATOR SET |  | 1978 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.14 | [6 empty] | OTHER | [8 empty] | A MOTOR VEHICLE DRIVEN BY A THRID PARTY RESIDENT OF THE NEIGHBORHOOD HIT THE METER SET LOCATED AGAINST HIS HOUSE, BENDING BACK AND PARTIALLY BREAKING 3/4" STEEL PIPE NIPPLE AT OUTLET OF SHUT-OFF VALVE AT TOP OF RISER. | CLASS 3 LOCATION | 85000 | 104137.2832369942 | 1000 | 1225.14450867052 | 2000 | 2450.28901734104 | 0 | 0 |  |  | 175 | 130.866900175131348511383537653239929947 |  | 0 | 88175 | 44773.8533789552298704028021015761821366 | 107943.5836631808913485113835376532399299 | 0 | 0 | 30 |  |  |  |  | 28 | 28 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DONALD J. BRIDGE | SR. SUPERVISING ENGINEER | don.bridge@delmarva.com | 302-429-3543 | 302-429-3272 |  |  |  | ROBERT G. KITSON | MANAGER GAS ENGINEERING | 302-429-3848 | robert.kitson@delmarva.com | THIS IS THE FINAL REPORT AND IS UNCHANGED FROM THE INITIAL REPORT. THIRD PARTY VEHICLE OWNER'S VEHICLE WAS PARKED IN FRONT OF THIRD PARTY VEHICLE OWNER'S ROW HOME. THIRD PARTY VEHICLE OWNER WAS OPERATING THE VEHICLE AND STATED IN A NEWS REPORT THAT HE THOUGHT HE PLACED THE GEAR SELECTOR IN REVERSE, BUT THE CAR MOVED FORWARD JUMPING THE LANDSCAPED AREA BETWEEN HIS HOME AND THE PARKING AREA AND PROCEEDING TO STRIKE THE GAS METERSET IN FRONT OF HIS HOME CAUSING THE PIPE NIPPLE ABOVE THE RISER SHUT-OFF VALVE TO BEND BACK AND PARTIALLY BREAK RELEASING GAS AND IGNITING. THE CAR WAS ABANDONED IN PLACE, THE FIRE SPREAD TO THE ENTIRE CAR AND TO THE FRONT OF VEHICLE OWNER'S ROW HOME, PARTIALLY DAMAGING HIS ROW HOME AND TWO ADJACENT ROW HOMES. FIRE DISPATCH CALLED DELMARVA POWER TO REPORT THE FIRE INVOLVING THE STRUCK GAS METER. A DELMARVA POWER CREW RESPONDED WITHIN APPROXIMATELY 30 MINUTES AND HAD GAS TO THE MAIN FEEDING THE DAMAGED SERVICE AND 29 OTHER SERVICES TURNED OFF WITHIN APPROXIMATELY 56 MINUTES. AFTER THE FIRE WAS EXTINGUISHED, SERVICES TO THE THREE DAMAGED HOMES WERE CUT OFF AT THE GAS MAIN, RETIRING THE SERVICES. ONCE THE FIRE WAS FULLY EXTINGUISHED AND CONDITIONS WARRANTED, THE GAS TO THE MAIN WAS TURNED BACK ON AND SERVICES TO THE REMAINING 27 ROW HOMES WERE RESTORED. ACCORDING TO NEW CASTLE COUNTY POLICE REPORT NO: 32-14-131736, THE DRIVER RECEIVED A SINGLE VIOLATION OF INATTENTIVE DRIVING. THE ESTIMATED COST OF PUBLIC AND NON-OPERATOR PRIVATE PROPERTY DAMAGE AS NOTED IN PART D IS BASED ON INFORMATION REPORTED IN THE MEDIA REFLECTING POLICE AND FIRE OFFICIALS' STATEMENTS AT THE INCIDENT SCENE.
2025-03-31 10:13 | NO | YES | NO | 20140122 | 16585 | 2014-12-31 11:01 | SUPPLEMENTAL FINAL | 15329 | PEOPLES GAS LIGHT & COKE CO | 200 E RANDOLPH STREET | CHICAGO | IL | 60601 | 2014-12-02 09:27 |  |  | 2014 | 2148 WEST 107TH PLACE | CHICAGO | COOK | IL | 60643 | 41.6986 | -87.6762 | [9 empty] | 2014-12-02 10:03 | 1102396 |  | NATURAL GAS |  | 110 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 20 | 2014-12-02 08:26 |  |  |  | 2014-12-02 08:36 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1967 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | COPPER | [10 empty] | MECHANICAL PUNCTURE | 0.5 | 1.2 | [7 empty] | CLASS 4 LOCATION | 301040 | 368817.5028901733408 | 1000 | 1225.14450867052 | 20000 | 24502.8901734104 | 0 | 0 |  |  | 300 | 224.343257443082311733800350262697022767 |  | 0 | 322340 | 163616.4593570419083721190893169877408056 | 394769.8808296973431117338003502626970228 | 0 | 0 | 63 |  |  |  |  | 22 | 22 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 6 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | YES | PRIVATE LANDOWNER | [10 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | WATER | YES | 478339647 | DIGGER |  | CONTRACT LOCATOR | YES |  |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | EXCAVATOR NO CALL TO OPERATOR AND UNAUTHORIZED TEMPORARY REPAIR | [169 empty] | SHAWN BARTELS | COMPLIANCE SPECIALIST | srbartels@peoplesgasdelivery.com | 312-240-5421 |  |  |  |  | TOM WEBB | COMPLIANCE MANAGER | 312-240-4650 | tjwebb@peoplesgasdelivery.com | ON DECEMBER 2, 2014, THE CHICAGO DEPARTMENT OF WATER MANAGEMENT (CDWM) WAS DIGGING AND DAMAGED A GAS SERVICE TO 2149 WEST 107TH PLACE. CDWM FAILED TO TIMELY REPORT THE DAMAGE. AS A RESULT GAS WAS ALLOWED TO MIGRATE TO NEARBY SEWERS. CDWM EVENTUALLY CALLED PEOPLES GAS (PGL) AT APPROXIMATELY 08:26. A PGL FIRST RESPONDER ARRIVED ONSITE AT 08:36 AND BEGAN RESPONDING TO THE EMERGENCY BY VENTING SEWERS, ISOLATING SERVICES, AND ASSISTING THE FIRE DEPARTMENT. CDWM CONTINUED TO WORK AFTER BEING INSTRUCTED TO EVACUATE THE AREA BY PGL. DUCT TAPE WAS FOUND ILLEGALLY WRAPPED AROUND THE GAS SERVICE LEADING TO 2149 W 107TH PLACE, WHICH APPEARS TO BE AN EFFORT MADE BY CDWM TO CONTROL THE GAS LEAK. ADDITIONAL PGL CREWS ARRIVED AT 08:53 AND BEGAN WORKING TO ISOLATE THE GAS LEAK. AT APPROXIMATELY 09:27, THE HOME AT 2148 WEST 107TH PLACE EXPLODED. WITH ASSISTANCE FROM THE CHICAGO FIRE DEPARTMENT, PGL CREWS ISOLATED THE SERVICE FOR 2149 WEST 107TH PLACE TO CONTROL THE EMERGENCY. PGL CREWS MADE REPAIRS TO THE SERVICE AT 2149 WEST 107TH PLACE ON DECEMBER 4, 2014. PGL CONSIDERS THIS INCIDENT CLOSED.
2025-03-31 10:13 | NO | YES | YES | 20150001 | 30418 | 2015-01-02 16:30 | SUPPLEMENTAL FINAL | 15259 | UGI PENN NATURAL GAS | 1 UGI DRIVE | DENVER | PA | 17517 | 2014-12-04 03:51 |  |  | 2014 | 413 SMITH STREET | DUNMORE | LACKAWANNA | PA | 18512 | 41.4141 | -75.6252 | [9 empty] | 2014-12-04 05:27 | 1102577 |  | NATURAL GAS |  | 395 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 45 | 2014-12-04 02:23 |  |  |  | 2014-12-04 02:50 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 47 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2014 | [5 empty] | 2 | ASTM D2513 | CHARTER PLASTICS - TITUSVILLE, PA | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | OTHER | HOLE - 2.25" X 1.5" OVAL | [5 empty] | CLASS 3 LOCATION | 509000 | 623598.55491329468 | 5000 | 6125.7225433526 | 15000 | 18377.1676300578 | 0 | 0 |  |  | 1300 | 972.154115586690017513134851138353765324 |  | 0 | 530300 | 269323.4805921397424658493870402802101576 | 649073.5992022917700175131348511383537653 | 5 | 0 | 120 |  |  |  |  | 51 | 51 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 8 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE CAUSE OF THE INCIDENT WAS THE FAILURE OF A HIGH PRESSURE (~100 PSIG) CAST IRON WATER MAIN FROM WHICH A JET OF WATER EMANATED, IMPINGING ON THE ADJACENT POLYETHYLENE GAS DISTRIBUTION LINE, CAUSING ABRASION WITH SAND AND GRAVEL UNTIL THE PIPEWALL WAS ERODED. | [154 empty] | FRANK BENNETT | DIRECTOR ENGINEERING AND TECHNICAL SERVICES | fbennett@ugi.com | 610-796-3567 |  |  |  |  | HANS BELL | CHIEF OPERATING OFFICER | 610-796-3450 | hbell@ugi.com | ON DECEMBER 4, 2014, BETWEEN 1:00 AM AND 2:23 AM, A 2" MEDIUM-PRESSURE (60 PSIG MAOP) HIGH-DENSITY PLASTIC MAIN INSTALLED IN MAY OF 2014 ON SMITH ST., IN DUNMORE, PA, AND OWNED BY UGI PENN NATURAL GAS, INC., WAS CAUSED TO LEAK AFTER ITS SIDEWALL WAS ERODED BY THE ABRASIVE EFFECT OF SAND AND GRAVEL MOBILIZED BY A HIGH-PRESSURE JET OF WATER EMANATING FROM AN 1880 CAST IRON WATER MAIN WHICH WAS OPERATED AT 100 PSI BY PA AMERICAN WATER COMPANY. POST INCIDENT INVESTIGATION INDICATED THAT THE WATER MAIN WAS HEAVILY CORRODED AND A THIN SECTION ON THE TOP OF IT RUPTURED SPONTANEOUSLY. THE WATER MAIN WAS LOCATED APPROXIMATELY TWO FEET BENEATH THE GAS MAIN. ESCAPING GAS MIGRATED TO 413 SMITH STREET, AND AT 3:51 AM THE GAS IGNITED CAUSING AN EXPLOSION AND FIRE, AND RESULTING IN A FATALITY AT 413 SMITH STREET. 413 AND 411 SMITH ST. WERE TOTALLY DESTROYED AND ADJACENT STRUCTURES INCURRED MINOR PROPERTY DAMAGES. 5/30/2018 UPDATED COST ESTIMATE OF DAMAGES AND SUBMITTED REPORT AS FINAL.
2025-03-31 10:13 | NO | YES | YES | 20150002 | 16014 | 2015-01-14 09:56 | SUPPLEMENTAL FINAL | 8080 | INDIANA NATURAL GAS CORP | PO BOX 520 | WASHINTON | IN | 47501 | 2014-12-20 07:47 |  |  | 2014 | 13417 W STATE ROAD 46 | COLUMBUS | BARTHOLOMEW | IN | 47201-8729 | 39.2002 | -86.0673 | [9 empty] | 2014-12-20 10:10 | 1103941 |  | NATURAL GAS |  | 63 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-12-20 08:38 |  |  |  | 2014-12-20 08:43 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | FARM TAP METER/REGULATOR SET |  | 2001 | [8 empty] | STEEL |  |  |  | 0.138 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 2 LOCATION | 25000 | 30628.612716763 | 3000 | 3675.43352601156 | 2000 | 2450.28901734104 | 0 | 0 |  |  | 300 | 224.343257443082311733800350262697022767 |  | 0 | 30300 | 15430.0740005871494921190893169877408056 | 36978.6785175586823117338003502626970228 | 0 | 0 | 2 |  |  |  |  | 190 | 190 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | PHILLIP S. ROSS | GENERAL MANAGER | phil_r@indiananatural.com | 812-723-2151 | 812-723-2188 |  |  |  | PHILLIP S. ROSS | GENERAL MANAGER | 812-723-2151 | phil_r@indiananatural.com | ON SATURDAY, DECEMBER 20, 2014 A DRIVER OF A PASSENGER VEHICLE LOST CONTROL WHILE DRIVING WEST ON A RURAL SECTION OF INDIANA STATE ROAD 46 WEST, WEST OF COLUMBUS, INDIANA. THE VEHICLE WAS OBSERVED TO FISHTAIL ON AN ICE COVERED BRIDGE OVER WOLF CREEK. IT SKIDDED OFF THE NORTH SIDE OF THE HIGHWAY WHILE SPINNING 180-DEGREES AND ROLLING OVER ON ITS SIDE. THE VEHICLE CAME TO REST ON TOP OF AN ABOVE GROUND 1-INCH 190 PSI TO 3/4-INCH 20 PSI SERVICE LINE/REGULATOR ASSEMBLY OWNED BY INDIANA NATURAL GAS CORPORATION. THE FORCE OF THE IMPACT SHEARED THE 1-INCH GAS LINE DOWNSTREAM OF THE SHUTOFF VALVE FOR THE FARM TAP, CAUSING A GAS LEAK. THE GAS DID NOT IGNITE. BARTHOLOMEW COUNTY FIRE DEPARTMENT EMERGENCY RESPONDERS ARRIVED ON SCENE AND FOUND THE SOLE OCCUPANT OF THE VEHICLE UNRESPONSIVE AND WITHOUT A PULSE. THEY WERE UNABLE TO IMMEDIATELY EXTRICATE THE OCCUPANT FROM THE VEHICLE DUE TO HIS SIZE. NOTING A GAS LEAK, THEY RETREATED, DONNED SELF-CONTAINED BREATHING APPARATUS AND TRIED AGAIN UNSUCCESSFULLY TO REMOVE THE OCCUPANT FROM THE VEHICLE. EMERGENCY RESPONDERS NOTIFIED DISPATCH THAT THEY NEEDED THE LOCAL GAS COMPANY TO RESPOND TO THE GAS LEAK. BARTHOLOMEW COUNTY DISPATCH CONTACTED INDIANA NATURAL GAS'S ON-CALL SERVICE PERSON WHO ARRIVED ON THE SCENE FIVE MINUTES LATER (SEE ATTACHED TIME LINE). HE AND ANOTHER RESPONDING INDIANA NATURAL GAS SERVICE PERSON UTILIZED CGI'S TO MONITOR THE ESCAPING GAS, DISCUSSED THE SITUATION OF WITH EMERGENCY RESPONDERS AND THEN EXCAVATED AND SHUT OFF THE SERVICE TEE FOR THE 1-INCH LINE TO STOP GAS FLOW AND MAKE THE SITUATION SAFE. THE OCCUPANT OF THE VEHICLE WAS PRONOUNCED DEAD AT THE SCENE. BARTHOLOMEW COUNTY PERSONNEL THEORIZED THAT THE BLOWING GAS COULD HAVE CAUSED THE DRIVER OF THE VEHICLE TO ASPHYXIATE. INDIANA NATURAL GAS CONTACTED INDIANA PIPELINE SAFETY ON-CALL PERSONNEL AT 10:00 AM TO REPORT THE INCIDENT. INDIANA NATURAL GAS CONTACTED THE NATIONAL RESPONSE CENTER AT 10:15 AM TO REPORT THE INCIDENT. AN INCIDENT NUMBER OF 1103941 WAS ASSIGNED BY THE NRC.
2025-03-31 10:13 | NO | NO | NO | 20150003 | 16003 | 2015-01-21 11:27 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2014-12-28 01:58 |  |  | 2014 | OCOTILLO ROAD & ELLSWORTH LOOP ROAD | QUEEN CREEK | MARICOPA | AZ | 85142 | 33.2488 | -111.6351 | [9 empty] | 2014-12-28 03:32 | 1104372 |  | NATURAL GAS |  | 111 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-12-28 01:58 |  |  |  | 2014-12-28 02:39 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2006 | [8 empty] | STEEL |  | SEAMLESS | SEAMLESS | 0.035 | [6 empty] | OTHER | [8 empty] | DISTRICT REGULATOR STATION SENSE LINE DAMAGED BY VEHICLE. | CLASS 3 LOCATION | 0 | 0 | 80000 | 98011.5606936416 | 1739 | 2130.52630057803428 | 0 | 0 |  |  | 416 | 311.089316987740805604203152364273204904 |  | 0 | 82155 | 41763.6248684827793370718038528896672504 | 100453.1763112073750856042031523642732049 | 0 | 0 | 0 |  |  |  |  | 175 | 175 | 720 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | SHAWN BRINK | ADMINISTRATOR DIVISION COMPLIANCE | shawn.brink@swgas.com | 602-484-5489 | 602-484-5322 |  |  |  | LYNN A. MALLOY P.E. | GENERAL MANAGER OPERATIONS | 602-484-5477 | lynn.malloy@swgas.com | P/L # 2014-1600 SOUTHWEST GAS CORPORATION (SWG) RESPONDED TO A CALL BY THE FIRE DEPARTMENT AT 01:58 REGARDING AN ABOVE GROUND PIPE THAT HAD BEEN HIT BY A VEHICLE AND WAS LEAKING AT OCOTILLO ROAD AND ELLSWORTH LOOP ROAD IN QUEEN CREEK. UPON ARRIVAL, SWG WAS ADVISED THAT A COLLISION BETWEEN TWO AUTOMOBILES CAUSED INJURIES TO THREE PEOPLE AND THEY WERE BEING TRANSPORTED TO THE HOSPITAL DUE TO THE ACCIDENT. THE VEHICLE ACCIDENT ALSO DAMAGED DR # 426130 AND GAS WAS BLOWING FROM A BROKEN SENSE LINE. SWG CREWS RESPONDED AND CONTROLLED THE FLOW OF GAS BY UTILIZING TWO ABOVE GROUND STATION VALVES AT THE REGULATOR STATION. NOTIFICATION WAS MADE TO PHMSA VIA THE NATIONAL RESPONSE CENTER (NRC) AT 03:32 HOURS REPORT NUMBER 1104372 CONCERNING AN ESTIMATED DAMAGE EXCEEDING $50,000. THERE WERE NO FATALITIES AS A RESULT OF THE INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20150004 | 16004 | 2015-01-22 11:32 | ORIGINAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2014-12-06 12:56 |  |  | 2014 | 11812 MILLWRIGHT PARKWAY | AUSTIN | WILLIAMSON | TX | 78750-1613 | 30.4485 | -97.8057 | [9 empty] | 2014-12-23 08:41 | 1104119 |  |  |  | 28 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2014-12-06 12:56 |  |  |  | 2014-12-06 13:35 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1980 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | A PERDENALES ELECTRIC COOPERATIVE TRANSFORMER MALFUNCTIONED CAUSING ARCING AT THE METERS AT 11812 MILLWRIGHT PARKWAY, AUSTIN, TEXAS AND 10302 ANDERSON MILL RD., AUSTIN, TEXAS. THE ARCING CAUSED A RELEASE OF GAS THAT IGNITED AND CAUSED A LARGE STRUCTURAL FIRE AT 11812 MILLWRIGHT PARKWAY AND A SMALL FIRE AT 10302 ANDERSON MILL RD.; EXPERT OPINIONS FROM VARIOUS ENTITIES ARE IN AGREEMENT ON THIS SUCCESSION OF EVENTS. | CLASS 3 LOCATION | 1000000 | 1225144.50867052 | 5185 | 6352.3742774566462 | 928 | 1136.93410404624256 | 0 | 0 |  |  | 168 | 125.63222416812609457092819614711033275 |  | 0 | 1006281 | 510636.1758333925171515866900175131348511 | 1232759.44927619101485457092819614711033 | 0 | 0 | 1 |  |  |  |  | 51 | 51 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | A PERDENALES ELECTRIC COOPERATIVE TRANSFORMER MALFUNCTIONED CAUSING ARCING AT THE METERS AT 11812 MILLWRIGHT PARKWAY, AUSTIN, TEXAS AND 10302 ANDERSON MILL RD., AUSTIN, TEXAS. THE ARCING CAUSED A RELEASE OF GAS THAT IGNITED AND CAUSED A LARGE STRUCTURAL FIRE AT 11812 MILLWRIGHT PARKWAY AND A SMALL FIRE AT 10302 ANDERSON MILL RD.; EXPERT OPINIONS FROM VARIOUS ENTITIES ARE IN AGREEMENT ON THIS SUCCESSION OF EVENTS. | [47 empty] | AMY MARK | REGULATORY COMPLIANCE SPECIALIST | amy.mark@onegas.com | 512-370-8378 | 512-370-8400 |  |  |  | MARK MONTGOMERY | DIRECTOR OF ENGINEERING AND COMPLIANCE | 512-370-8348 | mark.montgomery@onegas.com | A PERDENALES ELECTRIC COOPERATIVE TRANSFORMER MALFUNCTIONED CAUSING ARCING AT THE METERS AT 11812 MILLWRIGHT PARKWAY, AUSTIN, TEXAS AND 10302 ANDERSON MILL RD., AUSTIN, TEXAS. THE ARCING CAUSED A RELEASE OF GAS THAT IGNITED AND CAUSED A LARGE STRUCTURAL FIRE AT 11812 MILLWRIGHT PARKWAY AND A SMALL FIRE AT 10302 ANDERSON MILL RD.; EXPERT OPINIONS FROM VARIOUS ENTITIES ARE IN AGREEMENT ON THIS SUCCESSION OF EVENTS.
2025-03-31 10:13 | NO | YES | YES | 20150005 | 16005 | 2015-01-22 16:21 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2014-12-27 23:02 |  |  | 2014 | 925 S. BUCKNER BLVD. | DALLAS | DALLAS | TX | 75217 | 32.7274 | -96.6832 | [9 empty] | 2014-12-28 01:15 | 1104368 |  | NATURAL GAS |  | 17.7 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | NO | 0 | 2014-12-27 23:25 |  |  |  | 2014-12-27 23:25 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1982 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER |  |  |  | VEHICULAR DAMAGE TO METER SET |  |  |  |  | LEAK CAUSED BY VEHICULAR DAMAGE TO METER SET | CLASS 3 LOCATION | 0 | 0 | 82 | 100.46184971098264 | 3033 | 3715.86329479768716 | 0 | 0 |  |  | 118 | 88.24168126094570928196147110332749562172 |  | 0 | 3233 | 1662.236139652909646900175131348511383538 | 3904.566825769615509281961471103327495622 | 1 | 0 | 0 |  |  |  |  | 25 | 25 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ALFONSO HERNANDEZ | OPERATIONS SUPERVISOR | alfonso.hernandez@atmosenergy.com | 214-792-7952 | 214-426-7062 |  |  |  | L. A. TREADWAY | COMPLIANCE DIRECTOR | 214-206-2044 | andy.treadway@atmosenergy.com | ONE VEHICLE ACCIDENT. VEHICLE STRUCK GAS METER AND METER LOOP CAUSING NATURAL GAS TO IGNITE. DALLAS FIRE DEPARTMENT AND DALLAS POLICE DEPARTMENT WERE ON-SITE PRIOR TO ATMOS ENERGY PERSONNEL. AS SOON AS EMERGENCY RESPONDERS MOVED THE VEHICLE TO A SAFE LOCATION, AN ATMOS ENERGY CREW WAS ABLE TO SHUT THE GAS OFF AT THE MAIN BY DISCONNECTING THE SERVICE LINE FROM THE MAIN.
2025-03-31 10:13 | NO | YES | NO | 20150006 | 16217 | 2015-01-28 21:49 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2014-12-29 15:00 |  |  | 2014 | 51ST. AVE. & SAN LEANDRO ST. | OAKLAND | ALAMEDA | CA | 94601 | 37.7659 | -122.2114 | [9 empty] | 2014-12-30 | 1104593 |  | NATURAL GAS |  | 365 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2014-12-29 15:00 |  |  |  | 2014-12-29 15:00 |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 66 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | BLOW OFF VALVE | 1989 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER |  |  |  | LEAKING BLOW OFF VALVE |  |  |  |  | LEAKING BLOW OFF VALVE | CLASS 3 LOCATION | 0 | 0 | 325000 | 398171.965317919 | 0 | 0 | 0 | 0 |  |  | 1500 | 1121.716287215411558669001751313485113835 |  | 0 | 326500 | 165948.539559775847460595446584938704028 | 399293.6816051344115586690017513134851138 | 0 | 0 | 0 |  |  |  |  | 135 | 135 | 198 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  |  | YES | [7 empty] | YES |  |  |  | NO | [11 empty] | YES | YES | PAINT | [250 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 925-328-6107 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | ON DECEMBER 29, 2014, PG&E CREWS WERE PERFORMING ROUTINE MAINTENANCE ON TRANSMISSION LINE L-105N, WHEN A LEAK WAS OBSERVED ON A NEARBY 6-INCH BLOW OFF VALVE. THE 6-INCH BLOW OFF VALVE IS LOCATED NEAR 51ST AVENUE AND SAN LEANDRO STREET IN OAKLAND IN A VALVE FRAME AND COVER WITH LIMITED ACCESS. PG&E CREWS EXCAVATED THE VALVE TO DETERMINE THE NATURE OF THE LEAK AND THE METHOD OF REPAIR. ON DECEMBER 30, 2014 IT WAS ESTIMATED THAT THE COST OF REPAIRS, INCLUDING THE USE OF COMPRESSED NATURAL GAS (CNG), EXCEEDED $50,000, REQUIRING A REPORT TO THE DOT AND CPUC. THERE WERE NO INJURIES, NO FATALITIES, NO IGNITION, NO EVACUATIONS AND NO MEDIA ASSOCIATED WITH THIS EVENT. ON DECEMBER 30 AT APPROXIMATELY 1400 HOURS, PG&E PLACED EIGHT INDUSTRIAL CUSTOMERS ON CNG. NO CUSTOMERS LOST GAS SERVICE AS A RESULT OF THE EVENT. PG&E DE-PRESSURIZED A ONE MILE SECTION OF L-105N AT 1815 HOURS. REPAIRS TO THE BLOW OFF VALVE WERE COMPLETED BY 0200 HOURS ON DECEMBER 31, AND AT 0430 HOURS PRESSURE WAS RESTORED TO THE ISOLATED SECTION OF L-105N. THE CAUSE OF THE LEAK WAS DUE TO ATMOSPHERIC CORROSION OF THE FLANGE BOLTS ALLOWING GAS TO ESCAPE THROUGH THE GASKET JOINT.
2025-03-31 10:13 | NO | NO | NO | 20150007 | 31948 | 2015-01-28 | SUPPLEMENTAL FINAL | 12582 | ATMOS ENERGY CORPORATION - MISSISSIPPI | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2014-12-29 02:37 |  |  | 2014 | 409 WEST HILL DR. | JACKSON | HINDS | MS | 39209 | 32.3417 | -90.2748 | [9 empty] | 2014-12-29 02:37 | 1104428 |  | NATURAL GAS |  | 3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 8 | 2014-12-29 01:47 |  |  |  | 2014-12-29 02:12 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1967 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  |  |  | 0.113 | [6 empty] | LEAK |  |  | OTHER | POSSIBLE LEAK ON FITTING | [5 empty] | CLASS 3 LOCATION | 70000 | 85760.1156069364 | 2000 | 2450.28901734104 | 787 | 964.18872832369924 | 25 | 30.628612716763 | APPROXIMATE VEHICLE EXPENSE FOR COMPANY RESPONDER'S VEHICLES |  | 9 | 6.73029772329246935201401050788091068301 |  | 0 | 72821 | 36952.3534724261017487635726795096322242 | 89211.9522630411947093520140105078809107 | 0 | 0 | 2 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | NUT FOLLOWER |  | OTHER |  | UNKNOWN |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | UNKNOWN CAUSE. SINCE QUESTION 25 IS MANDATORY, YET WE DON'T KNOW THE ACTUAL CAUSE OF THIS FAILURE, WE SPECULATED "MATERIAL DEFECT" MAY HAVE BEEN A CAUSE. |  | YES |  |  |  | OTHER | FITTING MAY HAVE FAILED TO CONTAIN GAS FOR REASONS THAT COULD NOT BE DETERMINED. | NO | [86 empty] | DEAN G MORRIS | MANAGER OF COMPLIANCE | dean.morris@atmosenergy.com | 6015925360 | 6019614019 |  |  |  | JAMIE E. MCKENZIE | VP OF OPERATIONS | 601-420-5013 | jamie.mckenzie@atmosenergy.com | WE RECEIVED A REPORT OF A FIRE AT A RESIDENCE LOCATED AT 409 W. HILL DR. IN JACKSON, MS. THE RESPONDING SERVICE TECHNICIAN ARRIVED ON SCENE IN 15 MINUTES. THE OPERATIONS SUPERVISOR WAS SUBSEQUENTLY NOTIFIED. SOME OF THE EXTERIOR WALLS HAD BEEN DISPLACED OUTWARD INDICATING A POSSIBLE EXPLOSION. WE NOTIFIED THE NATIONAL RESPONSE CENTER AND THE DIRECTOR OF PIPELINE SAFETY (MPSC). DUE TO HEAVY RAINS SATURATING THE SOIL, PERFORMANCE OF LEAK SURVEYS AROUND THE PREMISE WERE DIFFICULT. ULTIMATELY A LEAK WAS FOUND BEHIND THE LEFT REAR CORNER OF THE HOUSE ALONGSIDE THE SIDE STREET (MAGNOLIA DR.). THE SATURATED SOIL CAUSED GAS TO MIGRATE ALONG THE ROOTS OF A TREE TOWARDS THE RESIDENCE. IN HASTE TO SECURE THE SCENE AND STOP THE LEAK, THE CONSTRUCTION CREW SHUT OFF THE SERVICE TAP AND DISLODGED A MECHANICAL FITTING CONNECTED TO THE TAP. AS A RESULT, IT IS IMPOSSIBLE TO KNOW FOR CERTAIN THE SPECIFIC SOURCE OF THE LEAK.
2025-03-31 10:13 | NO | YES | NO | 20150008 | 30682 | 2015-02-05 17:19 | SUPPLEMENTAL FINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2015-01-09 16:17 |  |  | 2015 | 805 SOUTH MIDKIFF | MIDLAND | MIDLAND | TX | 79701 | 31.9822 | -102.1121 | [9 empty] | 2015-01-09 20:50 | 1105290 |  | NATURAL GAS |  | 557 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | YES | 0 | 2015-01-09 17:37 |  |  |  | 2015-01-09 17:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1952 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 113000 | 136872.178302695526 | 7500 | 9084.436613010765 | 2000 | 2422.516430136204 | 0 | 0 |  |  | 1400 | 1403.286384976525821596244131455399061033 |  | 0 | 123900 | 62752.308178690839530516431924882629108 | 149782.417730819020821596244131455399061 | 2 | 0 | 0 |  |  |  |  | 20 | 20 | 44 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2011-06-07 | NO | [12 empty] | NO | YES | OTHER | [12 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO | [7 empty] | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | MIKE CLUP | COMPLIANCE MANAGER - ATMOS ENERGY WEST TEXAS | mike.culp@atmosenergy.com | 806-798-4440 | 806-798-4495 |  |  |  | MIKE CLUP | COMPLIANCE MANAGER - ATMOS ENERGY WEST TEXAS | 806-798-4440 | mike.culp@atmosenergy.com | ON JANUARY 9, 2015, THE COMPANY WAS NOTIFIED THAT AN EXPLOSION OCCURRED IN THE ALLEY AT 805 SOUTH MIDKIFF IN MIDLAND TEXAS AT APPROXIMATELY 16:00 HOURS. WE RECEIVED NOTIFICATION AT APPROXIMATELY 17:38 AND ARRIVED ON SIGHT AT APPROXIMATELY 17:45. COMPANY FORCES REMAINED ON SIGHT UNTIL THE ALLEY SECTION OF PIPE WAS ABANDONED IN PLACE EARLY THE NEXT MORNING. A PORTION OF PIPE IN THE ALLEY WAS LATER REMOVED FOR INSPECTION AND INCLUDED A DENT OF UNKNOWN ORIGIN THAT HAD CRACKED. IN SECTION G3 - 1 THE DATE OF THE LAST LEAK SURVEY WAS RECOREDED AS UNKNOWN DUE TO A FORM ERROR. THE DATE OF THE LAST LEAK SURVEY OF THIS MAIN WAS 06/07/2011.
2025-03-31 10:13 | NO | YES | NO | 20150009 | 16016 | 2015-02-09 16:15 | ORIGINAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2014-12-14 09:53 |  |  | 2014 | 7340 BRIGHTON RD | COMMERCE CITY | ADAMS | CO | 80022-1503 | 39.8304 | -104.9242 | [9 empty] | 2014-12-14 10:43 | 1103397 |  | NATURAL GAS |  | 3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 10 | 2014-12-14 09:53 |  |  |  | 2014-12-14 10:20 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1966 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 75000 | 91885.838150289 | 55000 | 67382.9479768786 | 2500 | 3062.8612716763 | 0 | 0 |  |  | 10 | 7.47810858143607705779334500875656742557 |  | 0 | 132510 | 67239.8174955879896497373029772329246935 | 162339.1255074253360770577933450087565674 | 2 | 0 | 0 |  |  |  |  | 13 | 13 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | OTHER COMPRESSION TYPE FITTING | COUPLING, NUT-TYPE |  |  | NORTON MCMURRAY |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | NONE OF THE ADDITIONAL FACTORS APPLY. |  |  | YES |  |  |  |  | NO | [86 empty] | JON MOE | MANAGER GAS DISTRIBUTION ENGINEERING | jonathan.t.moe@xcelenergy.com | 303-571-3477 |  |  |  |  | MARK NOLAN | PRINCIPAL ENGINEER | 303-571-3931 | mark.nolan@xcelenergy.com | A MINOR EXPLOSION OCCURRED IN A COMMERCIAL BUILDING, AND A LEAKING COMPRESSION COUPLING WAS DISCOVERED NEARBY. THERE WAS NO SUSTAINING FIRE, SO THE EVENT WAS NOT DISCOVERED UNTIL NOTICED BY THE CUSTOMER'S EMPLOYEE. THE TIME INDICATED IN RESPONSE A.4. IS THE TIME THAT WE WERE NOTIFIED.
2025-03-31 10:13 | NO | NO | NO | 20150010 | 16017 | 2015-02-11 16:18 | ORIGINAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2015-01-11 22:46 |  |  | 2015 | 621 LAKE ST | SANDPOINT | BONNER | ID | 83864-1642 | 48.2719 | -116.5566 | [9 empty] | 2015-01-12 05:00 | 1105416 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2015-01-11 22:46 |  |  |  | 2015-01-11 23:04 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2006 | [8 empty] | OTHER | SERVICE REGULATOR | [9 empty] | OTHER | [8 empty] | WATER ENTERED REGULATOR VENT AND FROZE, CAUSING A MALFUNCTION OF THE REGULATOR | CLASS 3 LOCATION | 60000 | 72675.49290408612 | 100 | 121.1258215068102 | 500 | 605.629107534051 | 2000 | 2422.516430136204 | INCIDENT INVESTIGATION BY INTERNAL PERSONNEL |  | 1 | 1.00234741784037558685446009389671361502 |  | 0 | 62601 | 31405.2705008346427568075117370892018779 | 75825.7666106810255755868544600938967136 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS |  | NO | [218 empty] | TIMOTHY HARDING | GAS DISTRIBUTION ENGINEER | tim.harding@avistacorp.com | 509-495-2784 | 509-777-5583 |  |  |  | KAREN TERPAK | MANAGER OF INTEGRITY MANAGEMENT AND COMPLIANCE | 509-495-2856 | karen.terpak@avistacorp.com | AN AVISTA FIRST RESPONDER WAS CALLED TO A STRUCTURE FIRE. WHEN HE ARRIVED HE NOTICED THAT THE RESIDENTIAL REGULATOR AND METER SET WERE COVERED IN ICE. HE COULD HEAR WHAT SOUNDED LIKE HIGH GAS FLOW THROUGH THE METER SET. HE TURNED OFF THE VALVE ON THE SERVICE RISER. AFTER THE STRUCTURE WAS SAFE TO ENTER, THE GAS SERVICE WAS BRIEFLY TURNED BACK ON SO A PRESSURE MEASUREMENT COULD BE TAKEN ON THE CUSTOMER'S DOWNSTREAM SYSTEM. THE GAS PRESSURE WAS MEASURED AT 12.9 PSIG ON THE SYSTEM THAT WOULD TYPICALLY OPERATE AT 0.25 PSIG. THIS HIGHER PRESSURE WAS DUE TO ICE ENTERING THE SERVICE REGULATOR VENT AND CAUSING IT TO MALFUNCTION.
2025-03-31 10:13 | NO | YES | YES | 20150011 | 30664 | 2015-02-17 11:56 | SUPPLEMENTAL FINAL | 2784 | CORDOVA, WATER WORKS & GAS BOARD FO THE CITY OF | 20 MILL STREET | CORDOVA | AL | 35550 | 2015-01-27 16:30 |  |  | 2015 | 5 MCCRORY STREET | CORDOVA | WALKER | AL | 35550-1127 | 33.7601 | -87.1864 | [9 empty] | 2015-01-27 17:13 | 1106740 |  | NATURAL GAS |  | 475 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | YES | 6 | 2015-01-27 16:00 |  |  |  | 2015-01-27 16:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1952 | [5 empty] | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 7 | 0.8 |  | CLASS 3 LOCATION | 10000 | 12112.58215068102 | 1000 | 1211.258215068102 | 500 | 605.629107534051 | 3000 | 3633.774645204306 | EMPLOYEE TIME SPENT ON REPAIRING CUSTOMER SEWERS. |  | 1000 | 1002.347417840375586854460093896713615023 |  | 0 | 15500 | 8201.399015421544807511737089201877934272 | 18565.591536327854586854460093896713615 | 1 | 0 | 74 |  |  |  |  | 22 | 22 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [56 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | SUBSIDENCE |  |  |  |  | NO | [218 empty] | PHILLIP REED | SUPERINDENTDENT | hattie.cordova@gmail.com | 205-483-9235 | 205-483-0106 |  |  |  | PHILLIP REED | SUPERINTENDENT | 205-483-9235 | hattie.cordovawater@gmail.com | A PERSON REPORTED A GAS SMELL IN THE AREA IF 5 MCCRORY STREET. TIM FARLEY AND CHRIS HUGGINS RESPONDED AT 4:00 PM AND CARRIED A COMBUSTIBLE GAS INDICATOR. PHILLIP REED RESPONDED AT 4:15 PM. A GAS LEAK WAS DETERMINED TO BE BEHIND THE HOUSE AT 5 MCCRORY STREET AFTER MAKING A BAR-HOLE AND CHECKING IT WITH THE CGI. THE TRACK-HOE WAS BROUGHT AND DIGGING STARTED AT ABOUT 4:20 PM AT THE BAR-HOLE WHICH WAS ALINGED WITH THE SERVICE LINE. ABOUT TWO FEET HAD BEEN EXCAVATED WHEN THE HOUSE EXPLODED AT 4:30 PM. HILLIARD MINOR, THE RESIDENT AT 5 MCCRORY STREET WAS INSIDE THE HOUSE AND WAS KILLED. WHEN THE GAS MAIN HAD BEEN SHUT-DOWN AND EXCAVATED THE NEXT DAY, IT WAS FOUND THAT THE GAS PIPELINE WAS ABOUT FOUR FEET DEEP AND WAS LAYING ON AN OLD BRICK BUILDING FOUNDATION. THE SOIL SUBSIDENCE CAUSED THE PIPELINE TO REST ON THE BRICK OF THE FOUNDATION AND CAUSE A CIRCUMFERENTIAL CRACK. TIM FARLEY AND CHRIS HUGGINS WERE INJURED. PHILLIP REED ATTEMPTED TO SHUT DOWN THE GAS MAIN BUT WAS UNABLE AND WAS CARRIED TO THE HOSPITAL. ONLY CHRIS HUGGINS WAS HOSPITALIZED OVERNIGHT. FORMER EMPLOYEE JOEY GRIFFIN CAME AND HELPED TO SHUT DOWN THE GAS MAIN AT ABOUT 9:00PM.
2025-03-31 10:13 | NO | NO | NO | 20150012 | 16019 | 2015-02-19 09:25 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2015-02-06 05:15 |  |  | 2015 | 9806 ROCKCREST DR | HOUSTON | HARRIS | TX | 77041 | 29.8354 | -95.5337 | [9 empty] | 2015-02-06 07:18 | 1107473 |  | NATURAL GAS |  | 8.06 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2015-02-06 02:44 |  |  |  | 2015-02-06 02:44 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1979 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 0.7 | 0.1 |  | CLASS 3 LOCATION | 47000 | 56929.136108200794 | 250 | 302.8145537670255 | 1548 | 1875.027716925421896 | 0 | 0 |  |  | 48 | 48.11267605633802816901408450704225352113 |  | 0 | 48846 | 24524.8447887055644387605633802816901408 | 59155.0910549495794241690140845070422535 | 0 | 0 | 0 |  |  |  |  | 20 | 20 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF SYSTEM | [12 empty] | YES | 1 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LESLIE J. DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steve.yarbrough@centerpointenergy.com | RESIDENT LIVING AT 9806 ROCKCREST, HOUSTON, TEXAS 77041 WHILE OPERATING A GO-CART COLLIDED WITH THE METER-SET AT THAT LOCATION. THE COLLISION CAUSED A LARGE CRACK ON THE THREADS OF THE SERVICE RISER AT THE LOCK WING VALVE. AN UNIDENTIFIED IGNITION SOURCE IGNITED ESCAPING GAS FROM CRACKED RISER AND EXPLOSION/FIRE OCCURRED.
2025-03-31 10:13 | NO | NO | NO | 20150013 | 16020 | 2015-02-19 17:37 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2015-01-20 14:56 |  |  | 2015 | 2160 TULLY ROAD | SAN JOSE | SANTA CLARA | CA | 95122 | 37.3265 | -121.8183 | [9 empty] | 2015-01-21 17:07 | 1106278 |  | NATURAL GAS |  | 240.27 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 12 | 2015-01-20 14:56 |  |  |  | 2015-01-20 15:28 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 0.7 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 93000 | 112647.014001333486 | 0 | 0 | 0 | 0 |  |  | 1027 | 1029.410798122065727699530516431924882629 |  | 0 | 94027 | 47607.2800215267544413145539906103286385 | 113676.4247994555517276995305164319248826 | 12 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 10982 | USAN |  | UTILITY OWNER | YES | YES | 17 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | INVESTIGATION REGARDING LOCATE AND MARK OF FACILITIES IS CURRENTLY ONGOING. | [169 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT APPROXIMATELY 1456 HOURS, PG&E WAS NOTIFIED OF A THIRD-PARTY DIG-IN AT 2160 TULLY ROAD IN SAN JOSE (NEAR THE EASTRIDGE SHOPPING CENTER). A PG&E GAS SERVICE REPRESENTATIVE ARRIVED ON SCENE AT APPROXIMATELY 1528 HOURS. THE THIRD-PARTY (QUATTUOR CONSTRUCTION INC.; REPORTED USA TICKET #010982) WAS BORING AN UNDERGROUND CONDUIT, STRIKING A 1.25-INCH STEEL SERVICE LINE. INVESTIGATION REGARDING LOCATE AND MARK OF FACILITIES IS CURRENTLY ONGOING. PG&E REPAIR CREWS ARRIVED ONSITE AT APPROXIMATELY 1551 HOURS. GAS WAS SHUT IN AT APPROXIMATELY 1807 HOURS BY EXCAVATING AND SQUEEZING THE 4-INCH STEEL DISTRIBUTION MAIN IN ONE LOCATION. A SHELTER-IN-PLACE ORDER WAS INITIALLY ISSUED, BUT THE SAN JOSE FIRE DEPARTMENT DECIDED TO EVACUATE 12 NEARBY BUSINESSES OUT OF PRECAUTION. TULLY ROAD WAS CLOSED BETWEEN QUIMBY ROAD AND CAPITOL EXPRESSWAY AS CREWS MADE REPAIRS. APPROXIMATELY 12 CUSTOMERS (BUSINESSES) LOST GAS SERVICE AS A RESULT OF THE INCIDENT. THERE WERE NO INJURIES, NO FATALITIES AND NO IGNITION AS A RESULT OF THIS INCIDENT. LESS THAN 3MMCF OF NATURAL GAS WAS UNINTENTIONALLY RELEASED DURING THE INCIDENT. MAJOR SAN FRANCISCO BAY AREA MEDIA WERE OBSERVED ON SCENE DURING THE INCIDENT (KRON 4, CBS BAY AREA, KGO 7). BY 1015 HOURS ON JANUARY 21, REPAIRS WERE COMPLETED. PG&E GAS SERVICE REPRESENTATIVES BEGAN RELIGHT EFFORTS AT APPROXIMATELY 1110 HOURS. ON JANUARY 21, 2015 IT WAS DETERMINED THAT DAMAGES WERE EXPECTED TO EXCEED $50,000 AND SUBSEQUENTLY THE DOT WAS NOTIFIED.
2025-03-31 10:13 | NO | YES | NO | 20150014 | 16021 | 2015-02-20 15:52 | ORIGINAL | 15469 | PHILADELPHIA GAS WORKS | 800 W. MONTGOMERY AVENUE | PHILADELPHIA | PA | 19122 | 2015-02-16 01:50 |  |  | 2015 | 7912-14 ARDLEIGH ST. | PHILADELPHIA | PHILADELPHIA | PA | 19118 | 40.0723 | -75.1978 | [9 empty] | 2015-02-16 05:52 | 110822 |  | NATURAL GAS |  | 4 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 10 | 2015-02-16 05:10 |  |  |  | 2015-02-16 02:17 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 30 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1906 | [5 empty] | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 279800 | 338910.0485760549396 | 1000 | 1211.258215068102 | 5000 | 6056.29107534051 | 0 | 0 |  |  | 16 | 16.03755868544600938967136150234741784038 |  | 0 | 285816 | 143391.2143834847689089201877934272300469 | 346193.6354251489976093896713615023474178 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | NO | [218 empty] | JOSEPH HAWKINSON | DIRECTOR FIELD SERVICES AND MAINTENANCE | joseph.hawkinson@pgworks.com | 2156846342 |  |  |  |  | RAY WELTE | VICE PRESIDENT FIELD OPERATIONS | 215-684-6033 | raymond.welte@pgworks.com | ON FEBRUARY 16TH, 2015 PGW RECEIVED A PHONE CALL AT 1:50 AM FROM THE PHILADELPHIA FIRE DEPARTMENT (PFD) CONCERNING A POSSIBLE EXPLOSION. PGW DISPATCHED FIRST RESPONDERS AT 1:59 WITH THE FIRST PGW EMPLOYEE ARRIVING ON LOCATION AT 2:17. UPON ARRIVAL, PGW CONFIRMED WITH THE PFD THAT AN EXPLOSION HAD OCCURRED AT 7912-14 ARDLEIGH ST. AKA 199 E. BENEZET ST. THE PFD EVACUATED A TOTAL OF TEN (10) PEOPLE WITH NO INJURIES REPORTED. ADDITIONAL PGW RESOURCES CONTINUED TO ARRIVE AND PERFORM HOUSE CHECKS AND LEAK MIGRATION CHECKS. THE INITIAL REPORT HAD THE FOLLOWING READINGS: 7912-14 ARDLEIGH - 50% GAS @ FFW, 192 BENEZET - 2% LEL @ FFW, 196 BENEZET - 25% LEL IN ATMOSPHERE & 10% LEL @ FFW. AFTER THE FIRST PGW DISTRIBUTION CREW ARRIVED (2:31), THEY MADE BAR HOLES TO VENTILATE THE GAS AND LOCATE THE LEAK. THE PGW FIELD SERVICE TECHNICIANS CONTINUED TO MAKE HOUSE CHECKS AND MONITOR GAS READINGS. THE DISTRIBUTION CREW COMPLETED THEIR INVESTIGATION AND BEGAN AN OPENING OVER A 1906 6' CAST IRON MAIN. AT 2:59 P.E.C.O. ARRIVED AND AT 3:00 THEY CUT OFF THE ELECTRIC TO 7912-14 ARDLEIGH ST. AT 5:10 A 6' CAST IRON BROKEN MAIN WAS REPORTED. AT 5:44 THE CAST IRON MAIN WAS TEMPORARILY WRAPPED AND THE JOB WAS DECLARED SAFE. AT 7:25 A STAINLESS STEEL SLEEVE WAS INSTALLED OVER THE BROKEN MAIN. ON FEBRUARY 20TH, 2015 PGW CUT OUT THE SECTION OF 6' CAST IRON PIPE THAT INCLUDED THE BROKEN MAIN WITH A STAINLESS STEEL SLEEVE. THE REMOVED MAIN WAS TRANSPORTED TO AN EVIDENCE LOCKER AT PGW'S MAIN OFFICE (1800 N. 9TH ST., PHILADELPHIA PA 19122) FOR FUTURE ANALYSIS.
2025-03-31 10:13 | NO | YES | YES | 20150016 | 16709 | 2015-02-25 15:10 | SUPPLEMENTAL FINAL | 5330 | FLORIDA PUBLIC UTILITIES CO | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2015-02-24 15:50 |  |  | 2015 | 1499 W. PALMETTO PARK RD. | BOCA RATON | PALM BEACH | FL | 33486 | 26.3512 | -80.1153 | [9 empty] | 2015-02-24 21:00 | 1108997 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | NO |  |  |  |  | NO | 20 | 2015-02-24 16:00 |  |  |  | 2015-02-24 16:15 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1978 | [5 empty] | 1.66 | API 5L | UNKNOWN | STEEL |  |  |  | 0.14 | [6 empty] | OTHER | [8 empty] | WORKER CUT THE 1 1/4" STEEL PIPE WITH A WHEELED CUTTER DURING THE COURSE OF RETIRING THE INACTIVE SERVICE. RELEASE WAS INTENTIONAL AND EXPECTED BUT WORKER WAS INJURED DURING COURSE OF PERFORMING THE TASK. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 1000 | 1211.258215068102 | 50000 | 60562.9107534051 | MINIMUM MEDICAL CARE FOR INJURED WORKER FOR CONTRACTOR |  | 100 | 100.234741784037558685446009389671361502 |  | 0 | 51100 | 25677.7311007039796807511737089201877934 | 61874.4037102572395586854460093896713615 | 0 | 0 | 0 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | OPERATOR'S CONTRACTOR'S EMPLOYEE DID NOT UTILIZE APPROPRIATE PPE. OPERATOR'S PROCEDURE FOR CUT AND CAP ACTIVITIES WAS MINIMAL AND NOT COMPREHENSIVE ENOUGH. | YES |  |  |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | MICHAEL MCCARTY | COMPLIANCE AND MEASUREMENT MANAGER | mmccarty@fpuc.com | 863 224-0417 | 863 294-0629 |  |  |  | MICHAEL MCCARTY | COMPLIANCE AND MEASUREMENT MANAGER | 863 224-0417 | mmccarty@fpuc.com | AT APPROXIMATELY 15:50 ON TUESDAY, 2/24/2015, AN EMPLOYEE OF A CONTRACTOR PERFORMING AN INACTIVE SERVICE RETIREMENT FOR FLORIDA PUBLIC UTILITIES WAS INJURED. THE WORKER USING A WHEELED PIPE CUTTER CUT INTO AN 1 1/4" COATED STEEL SERVICE LINE WITH APPROXIMATELY 54 PSIG TO CAP THE SERVICE. THE ESCAPING GAS BLEW SAND AND SMALL PEBBLES IN THE EXCAVATED HOLE STRIKING THE WORKER AND CAUSING SEVERE INJURY TO HIS LEG AND HANDS. THE WORKER WAS TRANSPORTED TO A LOCAL HOSPITAL AND UNDERWENT SURGERY FOR HIS INJURIES AND IS HOSPITALIZED AT THIS TIME (2/25/15). TECHNICIANS FROM FLORIDA PUBLIC UTILITIES ARRIVED ON SCENE AT 16:15 AND PROCEEDED TO PERFORM A SQUEEZE OFF ON THE STEEL LINE. THE LINE WAS STOPPED AND CAPPED AT 16:58 ON 2/24/15. SUPPLEMENTAL AND FINAL - 12/5/2017 AFTER RECOMMENDATIONS FROM PHMSA THRU THE FLORIDA PUBLIC SERVICE COMMISSION, FLORIDA PUBLIC UTILITIES SUBMITS THIS CHANGE TO THIS REPORT REGARDING PART G. THE CAUSE WAS CHANGED FROM G-8, OTHER INCIDENT CAUSE, TO G-7, INCORRECT OPERATION. ALTHOUGH THE RELEASE OF GAS WAS EXPECTED, THE OUTCOME AND INJURY WERE NOT ANTICIPATED. IT WAS DETERMINED THAT THE OPERATOR'S PROCEDURE FOR ABANDONMENT OF GAS FACILITIES WAS NOT ROBUST ENOUGH TO COVER ALL SITUATIONS ENCOUNTERED IN THE FIELD. THE CONTRACTOR EMPLOYEE ALSO DID NOT UTILIZE ADEQUATE PPE. THE OPERATOR REVISED IT'S PROCEDURE ON 8/25/15 AND REVIEWED THIS PROCEDURE WITH IT'S EMPLOYEES AND CONTRACTORS. ALSO CHANGED IS PART C (2)(A) FROM UNKNOWN TO 1978. AN AS BUILT WITH THE DATE INSTALLED SHOW THE SERVICE WAS INSTALLED ON 2/17/1978.
2025-03-31 10:13 | NO | NO | NO | 20150017 | 16028 | 2015-02-25 19:38 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2015-01-26 10:15 |  |  | 2015 | 992 EL CAMINO REAL | SAN BRUNO | SAN MATEO | CA | 94066 | 37.6323 | -122.4184 | [9 empty] | 2015-01-26 | 1106634 |  | NATURAL GAS |  | 27 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2015-01-26 10:29 |  |  |  | 2015-01-26 10:46 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | METER IS POT ALUMINUM | [9 empty] | OTHER | [8 empty] | VEHICLE IMPACT ON METER SET | CLASS 3 LOCATION | 50000 | 60562.9107534051 | 6200 | 7509.8009334222324 | 0 | 0 | 0 | 0 |  |  | 184 | 184.431924882629107981220657276995305164 |  | 0 | 56384 | 28364.2859167897504525821596244131455399 | 68257.1436117099615079812206572769953052 | 2 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | WINI CHEN | PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | (925) 328-5756 | lcd1@pge.com | AT 1029 HOURS ON JANUARY 26, 2015, PG&E WAS NOTIFIED OF A STRUCTURE FIRE AT 992 EL CAMINO REAL (PIZZA PARLOR) IN SAN BRUNO DUE TO VEHICLE IMPACT (FOLLOWING A HIGH SPEED POLICE CHASE) WITH THE GAS METER SET AND RISER. THE VEHICLE IMPACT RESULTED IN AN UNINTENTIONAL RELEASE OF NATURAL GAS AND SUBSEQUENT IGNITION. PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ONSITE AT 1046 HOURS. REPAIR CREW ARRIVED AT 1110 HOURS. GAS WAS SHUT-IN AT 1140 HOURS BY EXCAVATING, SQUEEZING, AND CAPPING THE 2-INCH STEEL GAS DISTRIBUTION MAIN. PG&E ALSO REMOVED THE METER SET TO 990 EL CAMINO REAL, WHICH WAS LOCATED ON THE DAMAGED WALL OF 992 EL CAMINO REAL. THE FIRE WAS CONTAINED AT APPROXIMATELY 1215 HOURS. SENIORE'S PIZZA (992 EL CAMINO REAL) WAS DESTROYED FROM THE INCIDENT. AT APPROXIMATELY 1245 HOURS, SOUTHBOUND EL CAMINO REAL REOPENED. THREE CUSTOMERS (992 AND 990 EL CAMINO REAL) LOST GAS SERVICE AS A RESULT OF THE INCIDENT AND WILL BE RESTORED ONCE NEW SERVICE IS REQUESTED. ON JANUARY 27, 2015, A SPECIAL LEAK SURVEY OF PG&E'S GAS FACILITIES IN THE AREA WAS CONDUCTED AND NO LEAKS WERE DETECTED. THERE WERE NO INJURIES AND NO FATALITIES REPORTED DURING THE INCIDENT. LESS THAN 3 MMCF OF GAS WAS UNINTENTIONALLY RELEASED. SAN FRANCISCO MAJOR MEDIA (I.E., KRON 4, KGO 7, AND KTVU) WERE OBSERVED ON SCENE. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO THE UNINTENTIONAL RELEASE AND IGNITION OF NATURAL GAS FROM PG&E FACILITIES, AND DAMAGES ARE ESTIMATED TO EXCEED $50,000.
2025-03-31 10:13 | NO | NO | NO | 20150018 | 16214 | 2015-02-27 11:53 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2015-01-29 23:33 |  |  | 2015 | 13067 BESS AVE | BALDWIN PARK | LOS ANGELES | CA | 91706 | 34.0655 | -117.9894 | [9 empty] | 2015-01-30 07:29 | 1106936 |  | NATURAL GAS |  | 53 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2015-01-29 23:33 |  |  |  | 2015-01-29 23:53 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1947 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 56000 | 67830.460043813712 | 200 | 242.2516430136204 | 0 | 0 |  |  | 318 | 318.746478873239436619718309859154929577 |  | 0 | 56518 | 28488.5347430808302647887323943661971831 | 68391.4581657005718366197183098591549296 | 0 | 0 | 589 |  |  |  |  | 47 | 47 | 52 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | (626) 893-4536 | 626-969-8694 |  |  |  | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | (909) 376-7208 | tbauer@semprautilities.com | ON JANUARY 29, 2015, LA COUNTY FIRE DEPARTMENT REPORTED A POWER LINE POLE WAS KNOCKED OVER CAUSING A GAS LEAK ON A 2 IN. STEEL MAIN. CREW RESPONDED AND CONTROLLED THE GAS. NO INJURIES RESULTED FROM THIS INCIDENT. ALL REPAIRS TO THE DAMAGED MAIN WERE COMPLETED AND THE AFFECTED CUSTOMERS WERE RESTORED. INVESTIGATION OF THE INCIDENT SHOWED THAT A VEHICLE STRUCK THE POWER LINE AND LEFT THE SCENE BEFORE EMERGENCY RESPONDERS ARRIVED. THE HIGH VOLTAGE CABLE FROM THE POLE MADE CONTACT WITH A STOP SIGN, TRANSFERRED ELECTRICITY TO THE STOP SIGN THROUGH THE GROUND, WHILE ARCING THE 2 IN. STEEL MAIN BELOW THE STOP SIGN CAUSING AN IGNITING LEAK. IT WAS LATER DETERMINED THAT THE ASSOCIATED COST, MOSTLY FROM RESTORING SERVICES TO 589 CUSTOMERS, EXCEEDED $50,000. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO A GAS LEAK AND THE ASSOCIATED DAMAGE EXCEEDING $50,000.
2025-03-31 10:13 | NO | YES | NO | 20150019 | 16110 | 2015-03-05 16:35 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 5241 SPRING MOUNTAIN ROAD | LAS VEGAS | NV | 89103 | 2015-02-03 13:05 |  |  | 2015 | 2398 SOUTH BOULDER HIGHWAY | HENDERSON | CLARK COUNTY | NV | 89002 | 35.997 | -114.9331 | [9 empty] | 2015-02-03 13:17 | 1107258 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-02-03 08:34 |  |  |  | 2015-02-03 08:34 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 55 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1978 | [5 empty] | 4 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 383 | 463.911896371083066 | 231183 | 280022.307934089024666 | 0 | 0 |  |  | 0 | 0 |  | 0 | 231566 | 116168.980093342224304 | 280486.219830460107732 | 71 | 1 | 5009 |  |  |  |  | 47 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [28 empty] | YES | [11 empty] | YES |  |  |  | OTHER | SLOW CRACK GROWTH | NO | [86 empty] | BOWDIE YOUNG | COMPLIANCE SPECIALIST | bowdie.young@swgas.com | (702) 365-2213 | (702) 221-4116 |  |  |  | THOMAS CARDIN | DIRECTOR OF GAS OPERATIONS | (702) 365-2028 | thomas.cardin@swgas.com | DURING A LEAK SURVEY, SOUTHWEST GAS DISCOVERED A HAZARDOUS LEAK ON A 4-INCH ALDYL A MAIN AND 4-INCH ALDYL A SOCKET FUSION TEE AT 2398 SOUTH BOULDER HIGHWAY IN HENDERSON, NEVADA. THE FLOW OF GAS TO THE SECTION OF PIPE WAS DISCONTINUED IN ORDER TO COMPLETE THE REPAIR, RESULTING IN AN OUTAGE OF FIVE THOUSAND AND EIGHTY-ONE ACTIVE CUSTOMERS. THE COSTS OF SOUTHWEST GAS' EMERGENCY RESPONSE, LEAK LOCATING, FACILITY REPAIR AND SERVICE RESTORATION RESULTED IN THE INCIDENT MEETING PHMSA/DOT NOTIFICATION CRITERIA. PART A, 10: ESTIMATED VOLUME OF GAS RELEASED: 0.026 THOUSAND CUBIC FEET (MCF) PART C, 2A: YEAR 4-INCH ALDYL A MAIN INSTALLED, 1978 YEAR 4-INCH ALDYL A SOCKET FUSION TEE INSTALLED, 1984 PART G5: ADDITIONAL CAUSE: FUSION JOINT: 19. SPECIFY: SOCKET, HEAT FUSION 20. YEAR INSTALLED: 1984 21. OTHER ATTRIBUTES: 4-INCH ALDYL A 22A. FIRST MATERIAL BEING JOINED: POLYETHYLENE (PE) 22B. SECOND MATERIAL BEING JOINED: POLYETHYLENE (PE) 4-INCH ALDYL A MAIN - SLOW CRACK GROWTH RESULTING FROM PIPE DEFLECTION CREATING A STRESS CONCENTRATOR AT THE ENTRANCE TO THE SOCKET FUSED HEADER. 4-INCH ALDYL A SOCKET FUSION - SLOW CRACK GROWTH RESULTING FROM NON-FUSION FROM DEBRIS AT THE PIPE TO SOCKET FUSION INTERFACE AT THE PIPE END-POINT. THIS WAS DRIVEN BY PIPE DEFLECTION CREATING A STRESS CONCENTRATOR AT THE PIPE END-POINT INTERFACE WITH THE SOCKET-FUSED FITTING
2025-03-31 10:13 | NO | NO | NO | 20150021 | 16060 | 2015-03-10 10:47 | SUPPLEMENTAL FINAL | 15826 | POWELL CLINCH UTIL DIST | 203 FIRST ST. P.O. BOX 428 | ROCKY TOP | TN | 37769 | 2015-03-09 15:53 |  |  | 2015 | 169 BATLEY ROAD | Not Within a Municipality | ANDERSON COUNTY | TN | 37716 | 36.042 | -84.2669 | [9 empty] | 2015-03-10 09:38 | 1110125 |  | NATURAL GAS |  | 80 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2015-03-09 15:53 |  |  |  | 2015-03-09 16:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 28 |  | NO | [11 empty] | OTHER | UTILITY DISTRICT | MAIN |  | 1999 | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 89000 | 107801.981141061078 | 0 | 0 | 5000 | 6056.29107534051 | 0 | 0 |  |  | 390 | 390.915492957746478873239436619718309859 |  | 0 | 94390 | 47518.3013070325951549295774647887323944 | 114249.1877093593344788732394366197183099 | 0 | 0 | 20 |  |  |  |  | 40 | 40 | 43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | [7 empty] | YES | [6 empty] | UTILITY | BACKHOE/TRACKHOE | WATER | NO | [5 empty] | YES | 6 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | STEPHEN HARRIS | ENGINEERING MANAGER | steveh@powellclinch.com | 865-426-2822 | 865-426-2006 |  |  |  | STEPHEN HARRIS | ENGINEERING MANAGER | 865-426-2822 | steveh@powellclinch.com | IN THE PROCESS OF THE LOCAL WATER UTILITY REPAIRING A LEAK, THEY SEVERED A 2" DISTRIBUTION MAIN. THE BACKHOE CAUSED AN IGNITION OF THE ESCAPING NATURAL GAS. THE BACKHOE WAS DESTROYED BUT NO ONE WAS INJURED.
2025-03-31 10:13 | NO | YES | YES | 20150022 | 16039 | 2015-03-10 15:42 | ORIGINAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2015-02-09 16:22 |  |  | 2015 | 10901 SE 29TH | MIDWEST CITY | OKLAHOMA | OK | 73130 | 35.4359 | -97.3375 | [9 empty] | 2015-02-09 21:06 | 1107747 |  | NATURAL GAS |  | 11 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO |  |  |  |  | NO | 0 | 2015-02-09 16:22 |  |  |  | 2015-02-09 16:37 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1989 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.133 | [6 empty] | OTHER | [8 empty] | VEHICLE STRUCK A COMMERCIAL METER | CLASS 3 LOCATION | 6176 | 7480.730736260597952 | 28 | 33.915230021906856 | 477 | 577.770168587484654 | 0 | 0 |  |  | 54 | 54.12676056338028169014084507042253521127 |  | 0 | 6735 | 3401.706483112409131605633802816901408451 | 8146.542895433369743690140845070422535211 | 1 | 0 | 0 |  |  |  |  | 49.2 | 49.2 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS A RESULT OF VEHICULAR DAMAGE BY A 3RD PARTY. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | RUSSELL WEATHERS | AREA SUPERVISOR | russell.weathers@onegas.com | 405-551-6543 |  |  |  |  | RICHARD LAMIRAND | COMPLIANCE MANAGER | 918-947-7459 | richard.lamirand@onegas.com | A DRIVER WAS HEADING EASTBOUND ON SE 29TH ST. AND HAD A MEDICAL CONDITION CAUSING HIM TO STEER ACROSS THE WESTBOUND LANE OF SE 29TH ST. LEAVING THE ROADWAY. ONCE HE LEFT THE ROADWAY HE STRUCK AN ONG COMMERCIAL METER SET AND CONTINUED ON AND HIT A TREE. THE DRIVER WAS TRANSPORTED BY AMBULANCE TO THE HOSPITAL AND WAS LATER ADMITTED FOR AN OVERNIGHT STAY. THE SERVICE WAS DISCONTINUED THE DAY OF THE EVENT AND THE SERVICE WAS REBUILT WITH THE METER SET RELOCATED CLOSER TO THE CUSTOMER'S STRUCTURE FEBRUARY 20, 2015. THE INCIDENT OCCURRED AT 16:22 ON FEBRUARY 9, 2015 AND NOTIFICATION WAS MADE TO THE OKLAHOMA CORPORATION COMMISSION AT 17:51 UPON LEARNING THAT DAMAGES EXCEEDED THE $5,000 STATE REPORTING THRESHOLD. ONG BECAME AWARE OF THE OVERNIGHT HOSPITAL STAY AT 20:57 AND TELEPHONICALLY REPORTED THE INCIDENT TO THE NATIONAL RESPONSE CENTER AT 21:06.
2025-03-31 10:13 | NO | NO | NO | 20150024 | 16041 | 2015-03-12 12:15 | ORIGINAL | 11856 | COLONIAL GAS CO - LOWELL DIV | 40 SYLVAN RD | WALTHAM | MA | 02451 | 2015-02-11 12:03 |  |  | 2015 | 7 BANDON CIRCLE | WESTFORD | MIDDLESEX COUNTY | MA | 01886 | 42.573 | -71.4042 | [9 empty] | 2015-02-12 08:10 | 1107960 |  | NATURAL GAS |  | 31.57 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2015-02-11 11:59 |  |  |  | 2015-03-11 11:59 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2013 | [8 empty] | UNKNOWN | [10 empty] | LEAK |  |  | OTHER | FALLING ICE CAUSED LEAK | [5 empty] | CLASS 1 LOCATION | 50000 | 60562.9107534051 | 500 | 605.629107534051 | 1500 | 1816.887322602153 | 0 | 0 |  |  | 138 | 138.323943661971830985915492957746478873 |  | 0 | 52138 | 26214.6326678999612394366197183098591549 | 63123.7511272032758309859154929577464789 | 0 | 0 | 2 |  |  |  |  | 52.8 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SCADA SYSTEM DID NOT INDICATE ANY ABNORMAL CONDITIONS WITH THIS EVENT | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS | ,, | NO | [218 empty] | CHRISTTOPHER ARONSON | SENIOR COUNSEL | christopher.aronson@nationalgrid.com | 781-907-1854 |  |  |  |  | CHRISTOPHER S. ARONSON | SENIOR | 781-907-1854 | christopher.aronson@nationalgrid.com | RECEIVED CALL FROM THE PUBLIC ON 2/11/15 REPORTING GAS ODOR AT 7 BANDON CIRCLE, WESTFORD, MA. FIRE DEPARTMENT ARRIVED FIRST AND REPORTED GAS BLOWING AT METER. WHILE FIRE DEPARTMENT WAS ONSITE AN IGNITION OCCURRED AND ONE PERSON WAS EXVACUATED FROM PROPERTY. NO INJURIES. NATIONAL GRID ARRIVED AT 11:59. FIRE DEPARTMENT REQUESTED THAT GAS BE SHUT OFF. THE RISER WAS NOT ACCESIBLE DUE TO THE FIRE AND THE SERVICE SHUTOFF WAS BURIED UNDER SNOW AND WAS ALSO TOO CLOSE TO FIRE. GAS WAS SHUT OFF AT THE MAIN AT APPROXIMATELY 1:00 PM. IT WAS DETERMINED THAT THE REGULATOR WAS DAMAGED BY FALLING ICE FROM THE ROOF WHICH CAUSED THE RELEASE OF GAS.
2025-03-31 10:13 | NO | YES | YES | 20150025 | 16236 | 2015-03-12 14:08 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-02-11 00:52 |  |  | 2015 | 400 EAST SOUTH STREET | JACKSON | JACKSON COUNTY | MI | 49203-4441 | 42.2263 | -84.3936 | [9 empty] | 2015-02-11 01:55 | 1107846 |  | NATURAL GAS |  | 60.77 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO |  |  |  |  | NO | 3 | 2015-02-10 16:58 |  |  |  | 2015-02-10 16:58 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 42 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1932 | [5 empty] | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 22693 | 27487.082674540438686 | 487 | 589.882750738165674 | 0 | 0 |  |  | 453 | 454.063380281690140845070422535211267606 |  | 0 | 23633 | 12048.6722243164675538028169014084507042 | 28531.0288055602945008450704225352112676 | 0 | 0 | 0 |  |  |  |  | 0.5 | 0.5 | 0.97 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATOR EMPLOYEES WERE PERFORMING A DISCRETIONARY LEAK SURVEY AND DISCOVERED A SMALL CRACK IN THE MAIN | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | NO | [218 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 517-788-0509 |  |  |  |  | ALAN CHICHESTER | GAS REGULATORY SERVICES ENGINEER | 989-791-5841 | alan.chichester@cmsenergy.com | ON FEBRUARY 10, 2015 AT APPROXIMATELY 4:58 P.M. DURING A DISCRETIONARY LEAK SURVEY OF A 4" CI MAIN ON EGGLESTON STREET, JACKSON, MI A CRACK IN THE MAINLINE WAS DISCOVERED. THE LEAK REPAIR WAS COMPLETED AT APPROXIMATELY 8:28 P.M. CE CONTINUED ADDITIONAL LEAK SURVEYING AND MONITORING THE AREA TO INVESTIGATE FOR RESIDUAL GAS. GAS WAS DISCOVERED AT THE FOUNDATION OF THREE HOMES AT APPROXIMATELY 11:15 P.M. AND RESIDENTS WERE EVACUATED. THE RESIDENT LOCATED AT 400 E. SOUTH ST. SUSTAINED A FALL DURING THE EVACUATION ON FEBRUARY 11, 2015 AT APPROXIMATELY 12:52 A.M. THE EMS WAS CONTACTED AND THE RESIDENT WAS TRANSPORTED TO THE HOSPITAL. DURING THE INITIAL HOSPITAL EVALUATION AN UNRELATED HEALTH CONCERN WAS IDENTIFIED AND THE PATIENT WAS ADMITTED. THE RESIDENT REMAINED IN THE HOSPITAL FOR TWO DAYS. A MEMBER OF THE GENERAL PUBLIC WAS TAKEN TO THE HOSPITAL FOR A FALL WHICH OCCURRED DURING AN EVACUATION RESULTING FROM A NATURAL GAS LEAK. DUE TO THE HIPPA PRIVACY RULE NO ADDITIONAL INFORMATION WAS AVAILABLE REGARDING THE HEALTH OR HOSPITALIZATION OF THE RESIDENT. SINCE CONSUMERS ENERGY STAFF WAS UNABLE TO ASCERTAIN THE SPECIFIC CAUSE OF THE HOSPITALIZATION, THE INCIDENT WAS REPORTED TO COMPLY WITH THE DEFINITION OF A REPORTABLE GAS INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20150027 | 16234 | 2015-03-18 17:02 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-02-16 14:00 |  |  | 2015 | 2637 KINGSTOWNE DRIVE | COMMERCE TOWNSHIP | OAKLAND | MI | 48390 | 42.555 | -83.4517 | [9 empty] | 2015-02-16 15:48 | 1108266 |  | NATURAL GAS |  | 43.51 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2015-02-16 14:00 |  |  |  | 2015-02-16 13:34 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1970 | [5 empty] | 1.125 | UNKNOWN | UNKNOWN | COPPER | [10 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 300000 | 363377.4645204306 | 3693 | 4473.176588246500686 | 730 | 884.21849699971446 | 0 | 0 |  |  | 324 | 324.760563380281690140845070422535211268 |  | 0 | 304747 | 153019.3425275914959176338028169014084507 | 369059.6201690570968361408450704225352113 | 0 | 0 | 55 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | DRILLING | ELECTRIC | NO | [5 empty] | YES | 8 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 517-788-0509 |  |  |  |  | ALAN CHICHESTER | GAS REGULATORY SERVICES ENGINEER | 989-791-5841 | alan.chichester@cmsenergy.com | CONSUMERS ENERGY WAS NOTIFIED AT APPROXIMATELY 13:01 ON FEBRUARY 16, 2015 A NATURAL GAS SERVICE LINE (1 1/8" COPPER SERVICE LINE) LOCATED AT 2637 KINGSTOWNE DRIVE WAS PUNCTURED BY A GROUNDING ROD BEING INSTALLED (USING MOTORIZE EQUIPMENT) BY AN ELECTRICAL CONTRACTOR WORKING ON-SITE. AT APPROXIMATELY 14:00 WHILE ON-SITE INVESTIGATING THE DAMAGES AND PERFORMING THE STANDARD PRECAUTIONARY ACTIONS NECESSARY TO MAKE THE AREA SAFE THE CE EMPLOYEE WAS INFORMED BY AN ELECTRICIAN WORKING ONSITE OF A FIRE NEAR THE FURNACE IN ONE OF THE UNITS. DAMAGE TO THE SERVICE LINE ALLOWED GAS TO MIGRATE THROUGH A BASEMENT FLOOR DRAIN AND IGNITE AT 2633 KINGSTOWNE DRIVE. THE FIRE COMPLETELY DESTROYED THE UNIT AND SEVERELY DAMAGED SEVEN (7) ADDITIONAL UNITS LOCATED IN THE BUILDING. THE KINGSTOWNE CONDOMINIUM COMPLEX IS CENTRALLY METERED AND SHUTTING OFF GAS TO THE METER IMPACTED SERVICE TO MULTIPLE UNITS, LEAVING APPROXIMATELY FIFTY-FIVE (55) CUSTOMERS WITHOUT GAS SERVICE. PRIOR TO THE START OF THE FIRE, 3 RESIDENTS WERE EVACUATED. RESTORATION OF GAS SERVICE TO THE REMAINING STRUCTURES BEGAN THE EVENING OF FEBRUARY 16TH AND WAS COMPLETED THE FOLLOWING DAY. THE SOURCE OF IGNITION IS UNKNOWN AT THIS POINT.
2025-03-31 10:13 | NO | YES | NO | 20150028 | 30796 | 2015-03-20 19:03 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2015-02-22 02:47 |  |  | 2015 | 45 SHAWMUT RD | CANTON | NORFOLK | MA | 02021-1408 | 42.1885 | -71.152 | [9 empty] | 2015-03-02 12:12 | 1109420 |  | NATURAL GAS |  | 283 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2015-02-22 02:47 |  |  |  | 2015-02-22 03:03 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1997 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.121 |  | 3408 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 1000000 | 1211258.215068102 | 4500 | 5450.661967806459 | 4098 | 4963.736165349081996 | 1000000 | 1211258.215068102 | CONTENT COST WHICH WAS REFERENCED ON NFIRS REPORT |  | 1774 | 1778.164319248826291079812206572769953052 |  | 0 | 2010372 | 1009291.88829206627948852582159624413146 | 2434708.99258860836728707981220657276995 | 1 | 0 | 0 |  |  |  |  | 76 | 76 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | A THIRD PARTY BURIED THE METER SET WITH SNOW WHILE CLEARING SNOW OFF OF THE ROOF. | [154 empty] | MEGGAN BIRMINGHAM | COMPLIANCE OPERATIONS MANAGER | mbirmingham@nisource.com | 508.468.9956 |  |  |  |  | MEGGAN BIRMINGHAM | COMPLIANCE OPERATIONS MANAGER | 508.468.9956 | mbirmingham@nisource.com | NATURAL GAS RELEASED FROM A METER SET THAT WAS BROKEN BECAUSE A THIRD PARTY BURIED IT WITH SNOW WHILE CLEARING SNOW OFF OF A ROOF. THE RELEASE OF GAS RESULTED IN AN EXPLOSION/FIRE THAT CAUSED STRUCTURAL DAMAGE TO THE PROPERTY. PART C SUBPART 4 & 2A ARE ASSOCIATED WITH THE SERVICE LINE. THE NON-OPERATOR PROPERTY DAMAGE AND OTHER COSTS WERE OBTAINED FROM THE NATIONAL FIRE INVESTIGATION REPORT SYSTEM (NFIRS) REPORT. THERE WAS A BREAKDOWN IN THE NOTIFICATION PROCESS WHICH RESULTED IN A DELAYED NRC CALL BEING MADE. THE COMPANY HAS SINCE IMPLEMENTED ANNUAL TRAINING TO PROVIDE CONTINUOUS EDUCATION ON THE REPORTING REQUIREMENTS AT BOTH A STATE AND FEDERAL LEVEL.
2025-03-31 10:13 | NO | NO | NO | 20150029 | 16509 | 2015-03-23 15:34 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 55 BEARFOOT ROAD | NORTHBORO | MA | 01532 | 2015-02-22 13:51 |  |  | 2015 | 130 WOODBURY STREET | PROVIDENCE | PROVIDENCE | RI | 02903 | 41.8453 | -71.392 | [9 empty] | 2015-02-22 17:30 | 1108791 |  | NATURAL GAS |  | 23.11 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 5 | 2015-02-22 13:49 |  |  |  | 2015-02-22 14:22 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | OTHER | UTILITY | MAIN |  | 1929 | [5 empty] | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 50000 | 60562.9107534051 | 1000 | 1211.258215068102 | 7000 | 8478.807505476714 | 0 | 0 |  |  | 140 | 140.328638497652582159624413145539906103 |  | 0 | 58140 | 29226.4880804655219530516431924882629108 | 70393.3051124475685821596244131455399061 | 0 | 0 | 1 |  |  |  |  | 0.34 | 0.34 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SCADA SYSTEM DID NOT INDICATE ANY ABNORMAL CONDITIONS RELATED TO THIS EVENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | YES |  |  |  | YES | PIPE WAS IN FROZEN GROUND. | [213 empty] | JAMES FOLEY | MANAGER - DISPATCH -SCHEDULING | james.foley3@nationalgrid.com | 877-304-1203 |  |  |  |  | CORINNE BYRNES | PRIN. PROGRAM MANAGER FEDERAL PROGRAMS | 631-770-3549 | corinne.byrnes@nationalgrid.com | NATIONALGRID WAS CONTACTED BY THE PROVIDENCE FIRE DEPARTMENT AT 13:51 REQUESTING THE GAS TO BE SHUT OFF TO 130 WOODBURY ST. POSSIBLE DISTURBANCE AND ODOR IN AREA. NATIONALGRID'S REPRESENTATIVE ARRIVED AT 14:22 AND SHUT OFF GAS SERVICE TO 130 WOODBURY ST. NATIONALGRID'S REPRESENTATIVE REPORTED 5 PEOPLE SELF EVACUATED BUILDING AND THAT THERE HAD BEEN A FIRE AND A DISTURBANCE. NATIONALGRID SUPERVISOR ONSITE REQUESTED ELETRICAL SERVICE TO 130 WOODBURY ST. BE DISCONNECTED AT 15:40. MEDIA AND PUC REGULATOR ONSITE AT THIS TIME. NATIONALGRID MONITORED AND INVESTIGATED THIS INCIDENT AND AT 21:30 LOCATED A 6" BROKEN MAIN AT 130 WOODBURY ST.AND STARTED TO MAKE REPAIRS. NATIONALGRID CONTINUED TO MONITOR THE AREA WHILE REPAIRS WERE BEING MADE. AT 23:45 REPAIRS HAD BEEN COMPLETED AND BACK FILLING OF THE EXCAVATION AND PURGING OF RESIDUAL GAS FROM THE AREA STARTED. MONITORING AND PURGING CONTINUED UNTIL 16:00 THE FOLLOWING DAY. THE AREA WAS SECURE AT THIS TIME AND ALL NATIONALGRID PERSONNEL LEFT THE SITE.. NOTE - SUPPLEMENTAL REPORT FILED ON 3/7/2017 TO CORRECT LAT/LONG COORDINATES. NOTE - WITH THE CONCURRENCE OF STEPHEN BELL, PHMSA CORRECTED THE LATITUDE ON 4/9/2024
2025-03-31 10:13 | NO | YES | YES | 20150030 | 16252 | 2015-03-25 15:31 | SUPPLEMENTAL FINAL | 13299 | NEW JERSEY NATURAL GAS CO | 1415 WYCKOFF ROAD | WALL | NJ | 07719 | 2015-02-24 10:32 |  |  | 2015 | 59 OAK AV | STAFFORD TOWNSHIP | OCEAN | NJ | 08092 | 39.6859 | -74.2699 | [9 empty] | 2015-02-24 12:29 | 1108949 |  | NATURAL GAS |  | 456 |  | NO | [5 empty] | 0 | YES | 2 | 0 | 0 | 0 | 0 | 2 | YES |  |  |  |  | YES | 0 | 2015-02-24 10:32 |  |  |  | 2015-02-24 09:24 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 34 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1981 | [5 empty] | 2 | API-5L-A25 | UNKNOWN | STEEL |  | OTHER | ELECTRIC WELDED | 0.154 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 7.5 | 0.5 |  | CLASS 3 LOCATION | 274000 | 331884.750928659948 | 0 | 0 | 62050 | 75158.5722449757291 | 131921 | 159790.394989999083942 | FINAL ROAD RESTORATION, LIKELY TO EXCEED $50,000. |  | 8340 | 8359.577464788732394366197183098591549296 |  | 0 | 476311 | 242498.6245464021413986478873239436619718 | 575193.2956284234934363661971830985915493 | 1 | 0 | 334 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | YES | 7 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | MATERIAL FAILURE OF PIPE OR WELD | BUTT WELD | [146 empty] | BUTT WELD |  |  | OTHER | INADEQUATE WELD PENETRATION OF THE BUTT WELD JOINT | [23 empty] | YES |  | YES |  | YES | [8 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | MOBEEN KHAN | DIRECTOR - SYSTEM ENHANCEMENT | mukhan@njng.com | 732-919-8035 | 732-919-0936 |  |  |  | MOBEEN KHAN | DIRECTOR - SYSTEM ENHANCEMENT | 732-919-8035 | mukhan@njng.com | ON TUESDAY, FEBRUARY 24, 2015, A DATALOGGER (PRESSURE GAUGE) USED FOR FLOW STUDIES INDICATED A SUDDEN LOW PRESSURE AT 8:42 A.M. ON CYPRESS LANE IN STAFFORD. AT 9:05 A.M. NEW JERSEY NATURAL GAS ("NJNG") RECEIVED THE FIRST OF SEVERAL "NO GAS" CALLS. THE COMPANY SENT A CREW TO THE AREA. BEFORE THEY REACHED CYPRESS LANE, THE CREW WAS FLAGGED DOWN BY A POLICE OFFICER AT THE INTERSECTION OF OAK AVENUE AND ROUTE 9, WHO INFORMED THEM THAT THERE WAS A GAS ODOR ON OAK AVENUE. THEREAFTER, AT 9:15 A.M. A FIRST RESPONDER WAS DISPATCHED TO OAK AVENUE AND ARRIVED AT ABOUT 9:24 A.M. A STRONG GAS ODOR WAS IDENTIFIED NEAR 59 OAK AVENUE. IT WAS CONFIRMED THAT NO ONE WAS IN THE BUILDING. POLICE AND FIRE PERSONNEL WERE ALREADY ON SITE AND HAD EVACUATED NEIGHBORING HOMES. SOON THEREAFTER, THREE ADDITIONAL CREWS ARRIVED AT 59 OAK AVENUE. A LEAK IN THE STREET WAS LOCATED AND THE CREWS BEGAN JACKHAMMERING THE PAVEMENT. AT 10:32 A.M., AN EXPLOSION OCCURRED INSIDE 59 OAK AVENUE. PRIOR TO THE INCIDENT APPROXIMATELY FIVE INDIVIDUALS WERE EVACUATED BY FIRE AND POLICE. A REQUEST FOR EMERGENCY ASSISTANCE WAS MADE IMMEDIATELY. SEVEN NJNG EMPLOYEES WERE TAKEN TO THE HOSPITAL. FIVE WERE TREATED AND RELEASED AND TWO WERE ADMITTED. THE AREA WAS MADE SAFE AT 11:30 A.M. BY SHUTTING A VALVE TO THE STREET, WHICH AFFECTED ABOUT 335 CUSTOMERS. AT 14:30 (2:30 P.M.), NJNG RECEIVED PERMISSION TO RE-ENTER THE AREA AND REMOVE DEBRIS. THE STREET WAS OPENED IN THE LOCATION WHERE THE LEAK WAS FOUND AND A TWO-INCH (2") COATED STEEL MAIN WAS FOUND TO BE BROKEN AT THE WELD JOINT. THE BREAK WAS 360° AROUND THE PIPE AND THE PIPE ENDS WERE SEPARATED. APPROXIMATELY TWO FEET OF PIPE ON EACH SIDE OF THE BREAK WAS REMOVED FOR METALLURGICAL EVALUATION. NJNG BELIEVES THAT THERE WERE THREE PRIMARY CONTRIBUTING CAUSES FOR THE FAILURE: (I) A POOR QUALITY WELD, LACKING ADEQUATE PENETRATION; (II) ENVIRONMENTALLY ASSISTED CRACKING OF THE WELD (E.G., CORROSION); AND (III) EXTERNAL STRESS ON THE GAS MAIN, POSSIBLY FROM POST-INSTALLATION IMPACT, DIFFERENTIAL SOIL SETTLEMENT BELOW THE PIPE, SOIL DISPLACEMENT FROM ADJACENT CONSTRUCTION, ETC. WITH REFERENCE TO QUESTION NUMBER 2 IN PART D ABOVE, PLEASE BE ADVISED THAT NJNG HAS RECEIVED NUMEROUS PROPERTY DAMAGE CLAIMS, INCLUDING THE OWNER OF 59 OAK AVENUE, IN THE AMOUNT OF $199,000 AND SEVEN NEIGHBORING PROPERTIES, TOTALING APPROXIMATELY $75,000. THE COMPANY HAS RECEIVED NOTICE OF OTHER CLAIMS FROM OTHER INSURANCE CARRIERS BUT THESE CARRIERS HAVE NOT INDICATED A LOSS AMOUNT. THE AMOUNT OF MONEY THAT THE COMPANY ULTIMATELY PAYS ON THESE CLAIMS WILL DEPEND ON A FINDING OF LIABILITY AGAINST THE COMPANY AS WELL AS WHETHER THE AMOUNT OF THE DAMAGES CLAIMED CAN BE PROVEN BY THE CLAIMANT AND VERIFIED BY THE COMPANY. A NEW PLASTIC MAIN WAS INSTALLED AND PRESSURIZED ON FEBRUARY 25, 2015 AT APPROXIMATELY 4:30 A.M. SERVICE WAS RESTORED TO ALL CUSTOMERS ON FEBRUARY 25, 2015 BY 18:30 (6:30 P.M.). SUBSEQUENTLY THE ENTIRE 2" STEEL MAIN AND THE 2"HDPE MAIN HAS BEEN REPLACED WITH 4" HDPE PIPE. THIS INSTALLATION WAS COMPLETED OCTOBER 27, 2015
2025-03-31 10:13 | YES | NO | NO | 20150031 | 16048 | 2015-03-25 19:46 | ORIGINAL FINAL | 4483 | ENSTAR NATURAL GAS CO | 3000 SPENARD ROAD | ANCHORAGE | AK | 99503 | 2015-03-14 05:53 |  |  | 2015 | 915 INGRA STREET | ANCHORAGE | Not Within a County or Parish | AK | 99510 | 61.2129 | -149.8835 | [9 empty] | 2015-03-14 08:39 | 1110627 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 10 | 2015-03-14 05:53 |  |  |  | 2015-03-14 06:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1983 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 3408 | OTHER | [8 empty] | FIRE BURNED A HOLE IN THE PLASTIC TUBING INSIDE THE RISER | CLASS 3 LOCATION | 50000 | 60562.9107534051 | 5000 | 6056.29107534051 | 5000 | 6056.29107534051 | 0 | 0 | NA |  | 100 | 100.234741784037558685446009389671361502 |  | 0 | 60100 | 30192.7325294114756807511737089201877934 | 72775.7276458701575586854460093896713615 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | DAVE BREDIN | DIRECTOR OF OPERATIONS | dave.bredin@enstarnaturalgas.com | 907-264-3745 | 907-562-0053 |  |  |  | DAVE BREDIN | DIRECTOR OF OPERATIONS | 907-264-3745 | dave.bredin@enstarnaturalgas.com | THIS WAS A FIRE FIRST SITUATION. THE FIRE STARTED UNDER A NEARBY PICNIC TABLE THAT HAD SMOKING MATERIALS AROUND IT. THE FIRE IS BELEIVED TO HAVE STARTED UNDER THE PICNIC TABLE AND SPREAD TO THE GAS METER LOCATION. THE PLASTIC SERVICE LINE INSIDE THE RISER MELTED, RELEASING NATURAL GAS THAT CAUGHT FIRE. THE FIRE WAS EXTIGUISHED BY PINCHING OFF THE PLASTIC SERVICE LINE.
2025-03-31 10:13 | NO | YES | NO | 20150032 | 16050 | 2015-03-26 19:54 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2015-02-27 13:51 |  |  | 2015 | ELK-GROVE FLORIN RD AND GERBER RD | SACRAMENTO | SACRAMENTO | CA | 95829 | 38.4818 | -121.3673 | [9 empty] | 2015-02-27 16:10 | 1109272 |  | NATURAL GAS |  | 293 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-02-27 13:51 |  |  |  | 2015-02-27 14:05 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2008 | [5 empty] | 8 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 163600 | 198161.8439851414872 | 0 | 0 | 0 | 0 |  |  | 1260 | 1262.95774647887323943661971830985915493 |  | 0 | 164860 | 83241.0024965489679774647887323943661972 | 199424.8017316203604394366197183098591549 | 768 | 0 | 0 |  |  |  |  | 54 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 413394 | USA NORTH 811 |  | UTILITY OWNER | YES | YES | 8 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CHARLES CHANG | GAS ENGINEER | cyc8@pge.com | 9253285727 |  |  |  |  | LARRY DENISTON | MANAGER | 9253285756 | lcd1@pge.com | AT 1351 HOURS ON FEBRUARY 27, 2015, PG&E WAS NOTIFIED OF A THIRD-PARTY DIG-IN NEAR THE INTERSECTION OF ELK GROVE-FLORIN ROAD AND GERBER ROAD IN SACRAMENTO. THE THIRD-PARTY (WESTERN ENGINEERING) WAS USING A BACKHOE TO DIG NEW UNDERGROUND SERVICES (SEWER MANHOLES) WHEN THEY STRUCK AN 8-INCH PLASTIC DISTRIBUTION MAIN, CAUSING AN UNINTENTIONAL RELEASE OF NATURAL GAS. WESTERN ENGINEERING PROVIDED A VALID USA TICKET (#413394). PG&E FACILITIES WERE PROPERLY LOCATED AND MARKED, BUT THE EXCAVATOR FAILED TO HAND DIG, EXPOSE, AND PROTECT THE FACILITIES BEFORE USING MECHANICAL EQUIPMENT. PG&E WAS ONSITE AT 1405 HOURS. GAS WAS SHUT IN BY 1737 HOURS BY EXCAVATING AND SQUEEZING THE DISTRIBUTION MAIN. FIRE DEPARTMENT, POLICE, AND SACRAMENTO MEDIA (CHANNEL 10 AND 3) WERE OBSERVED ON SCENE. TRAFFIC WAS BLOCKED ON GERBER ROAD (EAST OF ELK GROVE-FLORIN ROAD) AND REROUTED FROM THE AREA. THE INCIDENT WAS REPORTED TO THE CPUC AND DOT DUE TO DAMAGES LIKELY EXCEEDING $50,000. THERE WERE NO INJURIES OR FATALITIES REPORTED. ADDITIONALLY, THERE WAS NO IGNITION AND THE ESTIMATED VOLUME OF GAS RELEASED WAS LESS THAN THREE MILLION CUBIC FEET. APPROXIMATELY 768 RESIDENTIAL CUSTOMERS LOST GAS SERVICE DURING THE INCIDENT. PG&E RESTORED GAS SERVICE TO ALL THE AVAILABLE CUSTOMERS (I.E. APPROXIMATELY 431 CUSTOMERS) BY 0200 HOURS ON FEBRUARY 28, 2015. BY MARCH 1, 2015, PG&E RESTORED GAS SERVICE FOR APPROXIMATELY 323 ADDITIONAL CUSTOMERS. AS OF MARCH 26, 2015, SERVICE WAS RESTORED FOR AN ADDITIONAL EIGHT CUSTOMERS; THE REMAINING SIX HOMES ARE VACANT.
2025-03-31 10:13 | NO | YES | NO | 20150033 | 16051 | 2015-03-30 09:06 | ORIGINAL | 11856 | COLONIAL GAS CO - LOWELL DIV | 55 BEARFOOT ROAD | NORTHBORO | MA | 01532 | 2015-03-09 16:24 |  |  | 2015 | 85 ROUNSEVELL ROAD | TEWKSBURY | MIDDLESEX | MA | 01876 | 42.6012 | -71.1854 | [9 empty] | 2015-03-09 20:00 | 1110092 |  | NATURAL GAS |  | 21.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2015-03-09 16:46 |  |  |  | 2015-03-09 16:46 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | OTHER | UTILITY | OUTSIDE METER/REGULATOR SET |  | 2011 | [8 empty] | UNKNOWN | [10 empty] | LEAK |  |  | OTHER | REGULATOR BROKEN AT METER | [5 empty] | CLASS 3 LOCATION | 425000 | 514784.74140394335 | 1000 | 1211.258215068102 | 3500 | 4239.403752738357 | 0 | 0 |  |  | 118 | 118.276995305164319248826291079812206573 |  | 0 | 429618 | 215575.3146599698541032863849765258215962 | 520353.6803670549733192488262910798122066 | 0 | 0 | 1 |  |  |  |  | 55.66 | 55.66 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SCADA SYSTEM DID NOT INDICATE ANY ABNORMAL CONDITIONS RELATED TO THIS EVENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS | ,, | YES |  |  |  | YES | SNOW / ICE FALLING OFF ROOF | [213 empty] | JAMES FOLEY | MANAGER - DISPATCH -SCHEDULING | james.foley3@nationalgrid.com | 877-304-1203 |  |  |  |  | JAMES FOLEY | MANAGER -DISPATCH-SCHEDULEING | 877-304-1203 | james.foley3@nationalgrid.com | SUMMARY OF EVENTS * CALL RECEIVED FROM TEWKSBURY POLICE REQUESTING GAS TO BE TURNED OFF WORKING FIRE. 16:35 * TECH ARRIVED TO WORKING FIRE. 16:46 * TECH SHUT OFF GAS AT GATE IN DRIVEWAY 17:00 * AFTER FIRE WAS EXTINGUISHED, SERVICE PERSON CHECKED GAS MAIN & SERVICE NO READS REPORTED 19:00- 19:30 * SERVICE PERSON CHECKED MANHOLES IN AREA & PUT BAR HOLES NO READS REPORTED 19:00-19:30 * METER SET IN REAR OF HOUSE WAS INSPECTED, SERVICE REGULATOR DAMAGE FROM FALLEN SNOW AND ICE WAS NOTED. (SERVICE RISER HAD BEEN SHUTOFF BY FIRE DEPT) 18:30 -19:30 * DPU DIRECTOR REQUESTED DAMAGED METER FIT BE REMOVED AND STORED 20:00 * AREA SECURED AND SAFE 22:00 * DOL TEST WAS DONE AND DETERMINED TO BE NORMAL * ON 3/11/15 A POST INCIDENT SERVICE PRESSURE TEST WAS CONDUCTED IN THE PRESENCE OF THE DPU REGULATOR AND THE SERVICE PRESSURE TEST WAS VERIFIED AS BEING SECURE AND SAFE.
2025-03-31 10:13 | NO | YES | NO | 20150034 | 16052 | 2015-03-31 14:13 | ORIGINAL FINAL | 13800 | NORTHERN UTILITIES, INC. (NH) | 325 WEST ROAD | PORTSMOUTH | NH | 03801 | 2015-02-20 08:11 |  |  | 2015 | 68 LOCKE ROAD | HAMPTON | ROCKINGHAM COUNTY | NH | 03842-4013 | 42.9351 | -70.82 | [9 empty] | 2015-02-20 10:25 | 1108592 |  | NATURAL GAS |  | 1.44 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2015-02-20 08:11 |  |  |  | 2015-02-20 08:03 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2010 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 4 LOCATION | 150000 | 181688.7322602153 | 3500 | 4239.403752738357 | 4500 | 5450.661967806459 | 0 | 0 |  |  | 14 | 14.03286384976525821596244131455399061033 |  | 0 | 158014 | 79276.3396357444289953051643192488262911 | 191392.8308446098812582159624413145539906 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEM PRESSURE OPERATING UNDER MAOP AND NEVER REACHED MAOP, INCIDENT AT SINGLE RESIDENCE METER FIT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | HOME OWNER REMOVED SNOW FROM ROOF AND PILLED ON TOP OF METER FIT 7 FEET HIGH | [47 empty] | MEL CIULLA | MANAGER GAS DISTRIBUTION OPERATIONS | ciulla@unitil.com | 603-294-5148 |  |  |  |  | MEL CIULLA | MANAGER GAS DISTRIBUTION OPERATIONS | 603-294-5148 | ciulla@unitil.com | HOME OWNER HAD HIS ROOF SHOVELED TO REMOVE SNOW, HOUSE IS A RANCH STYLE L SHAPED, ADDRESS, 68 LOCKE ROAD HAMPTON NH, THIS HOUSE SITS ON A CORNER LOT, LOCKE ROAD & EDGEWOOD ROAD, AND GAS SERVICE COMES OFF EDGEWOOD ROAD. ALL OF THE SNOW REMOVED FROM THE ROOF WAS PILED ON TOP OF THE RESIDENTIAL 250 INTERMEDIATE PRESSURE METER FIT, THE METER FIT WAS CONNECTED TO A 3/4 INCH ANODLESS RISER, SERVICE LINE WAS A 1/2 INCH HIGH DENSITY PL, 3408. METER FIT SUPPORTED BY A DRIVEN BRACKET CONNECTED TO THE INLET OF THE METER BAR. WHEN OUR SERVICE TECHNICIAN ARRIVED ON SITE THE HOME OWNER EXPLAINED THEY HAD A FIRE, OUR TECHNICIAN WAS UNABLE TO SEE THE METER FIT, BUT HE KNEW THE APPROXIMATE LOCATION. WHEN THE FIRE DEPARTMENT ARRIVED THEY DIG OUT THE BACK DOOR AND METER FIT SO OUR TECHNICIAN WAS ABLE TO TURN OFF THE RISER VALVE, THIS SERVICE HAD A FLOW LIMITER (550 CFH). THE WEIGHT OF THE SNOW, APPROXIMATELY SEVEN (7) FEET HIGH PUSHED THE FIT ASSEMBLY DOWN CAUSING THE THREAD TO FAIL ON THE OUT LET OF THE RISER VALVE. THE HOME OWNER'S KITCHEN WAS ON THE OTHER SIDE OF THE WALL FROM THE METER FIT, HOME OWNER TURNED ON HIS GARBAGE DISPOSAL IGNITING THE NATURAL GAS AS A FLASH, THE HOME OWNER HAD MINOR BURNS ON HIS ARMS AND FACE, FIRE DEPARTMENT TREATED HIM ON SITE, THIS CAUSED EXTENSIVE FIRE AND WATER DAMAGE TO THE RESIDENCE MAKING THE RESIDENCE INHABITABLE, THE SERVICE WAS ABANDONED AT THE MAIN ON EDGEWOOD ROAD.
2025-03-31 10:13 | NO | YES | YES | 20150035 | 16057 | 2015-04-03 10:39 | ORIGINAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 1 METROTECH CENTER | BROOKLYN | NY | 11201 | 2015-03-05 21:00 |  |  | 2015 | 442 PACIFIC STREET | BROOKLYN | KINGS | NY | 11217-2203 | 40.6853 | -73.9833 | [9 empty] | 2015-03-06 09:18 | 1109783 |  | NATURAL GAS |  | 1084.47 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES |  |  |  |  | YES | 0 | 2015-03-05 08:50 |  |  |  | 2015-03-05 09:06 |  | NO | PRIVATE PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2002 | [5 empty] | 6 | PLASTIC | UNKNOWN | PLASTIC |  |  |  |  | OTHER | MD PLDB |  | 0.579 |  |  | LEAK |  |  | OTHER | CON EDISON ELECTRICAL BURNOUT | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 150 | 181.6887322602153 | 71996 | 87205.746452043071592 | 7253 | 8785.255833888943806 | PAVING COSTS |  | 4932 | 4943.577464788732394366197183098591549296 |  | 0 | 84331 | 44404.9428624322374306478873239436619718 | 101116.2684829809630923661971830985915493 | 0 | 0 | 6 |  |  |  |  | 0.31 | 0.31 | 0.36 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A CONSOLIDATED EDISON ELECTRICAL BURN OUT THAT DAMAGED THE GAS MAIN. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | CONSOLIDATED EDISON ELECTRICAL BURN OUT | [47 empty] | DAVID ANGELONE | MANAGER | david.angelone@nationalgrid.com | 718 403 3347 |  |  |  |  | ROBERT DEMARINIS | VP MAINT AND CONSTR NY GAS | 516-545-4337 | robert.demarinis@nationalgrid.com | DISPATCH WAS NOTIFIED ON 3/5/15 AT 12:30 BY CMS REGARDING AN OUTSIDE LEAK INVESTIGATION FINDING OF 7% GAS READING IN A SEWER MANHOLE AT THE INTERSECTION OF PACIFIC ST AND NEVINS ST. FIELD OPERATIONS WAS NOTIFIED AND RESPONDED TO THE LOCATION TO PERFORM A LEAK INVESTIGATION. WHILE CONDUCTING THE INVESTIGATION IT WAS DETERMINED A CON ED BURNOUT WAS THE CAUSE OF THE LEAK. THE BURNOUT DAMAGED A 6" LOW PRESSURE PLASTIC MAIN. NATIONAL GRID AND CON ED HAD CREWS AT THE LOCATION TRYING TO REMEDY THE SITUATION. GAS FROM THE DAMAGED MAIN WAS MIGRATING INTO THE NEARBY CON ED MANHOLE WHEN A FLASH/FIRE OCCURRED AT APPROXIMATELY 21:00. THE CON ED EMPLOYEE WORKING IN THE MANHOLE WAS USING A LIGHT BULB THAT SUDDENLY BROKE AND THEN BECAME A SOURCE OF IGNITION SETTING THE MANHOLE ON FIRE. FIELD OPERATIONS WAS NOT ABLE TO SAFELY SECURE THE GAS AT THE DESIRED LOCATION BECAUSE OF THE ENERGIZED CABLE LINES IN CLOSE PROXIMITY OF THE DAMAGED MAIN AND THE FIRE IN THE MANHOLE. REMOTE OPENINGS WERE NOW NECESSARY AS A CONTINGENCY TO SECURE THE GAS OR UNTIL SUCH TIME AS CON ED WAS ABLE TO DE-ENERGIZE THEIR CABLE LINES IN ORDER FOR THE FD TO EXTINGUISH THE FIRE ALLOWING FIELD OPERATIONS TO SAFELY SECURE. CON ED DE-ENERGIZED THEIR LINES AT APPROXIMATELY 8:00 ON 3/6/2015 AND THE FD WAS ABLE TO EXTINGUISH THE FIRE AT 9:00. FIELD OPERATIONS WAS NOW ABLE TO SAFELY SECURE THE GAS AT 10:30.
2025-03-31 10:13 | NO | YES | YES | 20150036 | 16317 | 2015-04-04 16:37 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2015-03-05 08:42 |  |  | 2015 | 5204 TRENTON | DETROIT | WAYNE | MI | 48210 | 42.3314 | -83.1483 | [9 empty] | 2015-03-05 14:37 | 1109728 |  | NATURAL GAS |  | 1 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 11 | 2015-03-05 08:42 |  |  |  | 2015-03-05 09:29 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1923 | [5 empty] | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 10000 | 12112.58215068102 | 13320 | 16133.95942470711864 | 47679 | 57751.580436232035258 | 150 | 181.6887322602153 | MATERIALS |  | 10 | 10.02347417840375586854460093896713615023 |  | 0 | 71159 | 35702.3652617038872240751173708920187793 | 86189.8342180587929538685446009389671362 | 0 | 0 | 3 |  |  |  |  | 2 | 2 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | NO | [218 empty] | FRENAE F. SMITH | MANAGER | smithff@dteenergy.com | 313-389-7762 | 313-389-7757 |  |  |  | FRENAE F. SMITH | MANAGER | 313-389-7755 | smithff@dteenergy.com | ON MARCH 5, 2015 AT 08:42 DTE GAS WAS NOTIFIED OF A CUSTOMER LEAK COMPLAINT AT THE RESIDENCE OF 5204 TRENTON IN DETROIT, MI. THE DTE SERVICE TECHNICIAN ARRIVED ON THE SCENE AT 09:29 AND WAS INFORMED THERE WAS AN ODOR IN THE BASEMENT AND A 19-YEAR OLD MALE WAS INJURED THE DAY BEFORE AND WAS TAKEN TO THE HOSPITAL TO TREAT BURNS HE RECEIVED FROM THE WAIST UP. THE TECHNICIAN BEGAN HIS LEAK INVESTIGATION AND FOUND COMBUSTIBLE READS IN THE BASEMENT FLOOR DRAIN AT 5204 TRENTON. THE SERVICE TECHNICIAN ALSO REPORTED WINDOWS WERE BLOWN OUT AND SOME BURNING HAD OCCURRED IN THE BASEMENT AT 5204 TRENTON. THE SERVICE TECHNICIAN ALSO FOUND COMBUSTIBLE READINGS IN THE BASEMENT FLOOR DRAINS AT ADDRESSES 5196 AND 5210 TRENTON. A TOTAL OF ELEVEN PEOPLE WERE EVACUATED FROM THE THREE HOMES. THE DTE GAS DISTRIBUTION CREW PERFORMED UNDERGROUND LEAK CHECKS OVER THE SERVICE LINES AND THE DISTRIBUTION MAIN IN THE AREA AROUND 5204 TRENTON. THE CREW REPORTED A 100 FOOT SPREAD OF 98% NATURAL GAS READINGS OVER THE 6-INCH CAST IRON MAIN AND AT THE BUILDING WALLS OF ADDRESSES 5204, 5196 AND 5210 TRENTON. THE DISTRIBUTION CREW FOUND A CIRCUMFERENTIAL CRACK IN THE 6-INCH CAST IRON MAIN. THE DISTRIBUTION CREW REPAIRED THE LEAK WITH A 6-INCH BY 18-INCH REPAIR CLAMP. THE FROST DEPTH WAS APPROXIMATELY 48 INCHES CAUSING THE MAIN TO BREAK AND DIFFICULT TO PINPOINT THE LEAK. THE 19-YEAR OLD MALE THAT WAS INJURED LATER DIED.
2025-03-31 10:13 | NO | NO | NO | 20150037 | 16178 | 2015-04-08 13:58 | SUPPLEMENTAL FINAL | 6690 | GREAT PLAINS NATURAL GAS CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2015-03-13 03:17 |  |  | 2015 | 1903 PEBBLE LAKE ROAD | FERGUS FALLS | OTTER TAIL | MN | 56537 | 46.2644 | -96.0553 | [9 empty] | 2015-03-13 07:25 | 1110499 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 4 | 2015-03-13 03:23 |  |  |  | 2015-03-13 03:36 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 20 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1971 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 75000 | 90844.36613010765 | 1500 | 1816.887322602153 | 2500 | 3028.145537670255 | 0 | 0 |  |  | 0 | 0 |  | 0 | 79000 | 39631.679207543576 | 95689.398990380058 | 0 | 0 | 1 |  |  |  |  | 15 | 15 | 33 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | [197 empty] | THREADED CONNECTION FAILURE | [12 empty] | OTHER | A NUT FOLLOWER/COMPRESSION FITTING AT THE BOTTOM OF THE RISER CONNECTING TO THE PVC SERVICE LINE WAS FOUND TO BE LEAKING DURING THE LEAK INVESTIGATION OF THE INCIDENT. WHAT CAUSED THE LEAK TO OCCUR IS UNKNOWN. | [69 empty] | MATT KLINGENSTEIN | STAFF ENGINEER | matt.klingenstein@mdu.com | 701.222.7973 |  |  |  |  | DARYL ANDERSON | DIRECTOR OF DISTRIBUTION | 701.222.7994 | daryl.anderson@mdu.com | THIS SERVICE LINE HAD BEEN INSTALLED SINCE 1971. NO INDICATIONS OF A LEAK WERE FOUND IN THE PRIOR TWO LEAK SURVEYS, CONDUCTED IN 2008 & 2012 RESPECTIVELY. DAY TIME HIGH TEMPERATURES THE WEEK OF THE 13TH OF MARCH, 2015 WERE ABNORMALLY WARM (ALMOST 20 DEGREES ABOVE NORMAL). THUS, IT IS HIGHLY LIKELY THAT THE GROUND WAS BEGINNING TO THAW. THE LEAK INVESTIGATION INDICATED THAT THERE WAS A LEAK AT THE RISER. AFTER EXCAVATING THE, 3/4" CONTINENTAL ,RISER AND COMPLETING FURTHER TESTING A LEAK WAS FOUND AT THE NUT FOLLOWER/COMPRESSION CONNECTION BETWEEN THE RISER AND THE PVC SERVICE LINE. AN INSIDE LEAK ON NON-JURISDICTIONAL PIPING WAS ALSO IDENTIFIED DURING THE LEAK INVESTIGATION. IN THE ABSENCE OF ANY OTHER IDENTIFIABLE SOURCE, THE RISER LEAK MAY BE THE SOURCE OF FUEL FOR THE EXPLOSION THAT OCCURRED, HOWEVER A MIGRATION PATH FOR THE GAS TO ENTER THE PREMISE WAS NOT IDENTIFIED.
2025-03-31 10:13 | NO | YES | NO | 20150038 | 16062 | 2015-04-08 15:48 | ORIGINAL FINAL | 2568 | COLORADO SPRINGS, CITY OF | PO BOX 1103 | COLORADO SPRINGS | CO | 80947 | 2015-03-10 16:17 |  |  | 2015 | INTERSECTION OF POWERS BLVD AND OLD RANCH RD | COLORADO SPRINGS | EL PASO | CO | 80908 | 38.9846 | -104.7648 | [9 empty] | 2015-03-11 10:47 | 1110260 |  | NATURAL GAS |  | 1833 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-03-10 16:18 |  |  |  | 2015-03-10 16:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2015 | [5 empty] | 6 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 48 | 18.8 | [7 empty] | CLASS 3 LOCATION | 196480 | 237988.01409658068096 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 3860 | 3869.061032863849765258215962441314553991 |  | 0 | 200340 | 102146.6058381594143969953051643192488263 | 241857.075129444530725258215962441314554 | 5 | 0 | 1406 |  |  |  |  | 49 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | COLORADO SPRINGS UTILITIES DID NOT INVESTIGATE THE CONTROLLER BECAUSE THE CONTROLLER FOLLOWED STANDARD OPERATING PROCEDURES. THE CONTROLLER RECOGNIZED THE ALARM, WITNESSED THE RAPID PRESSURE LOSS VIA SCADA AND CONTACTED FIRST RESPONDERS TO START THE FIELD INVESTIGATION. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | GRADING | NO | [5 empty] | YES | 48 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JESSICA NESVOLD | SR GAS REGULATORY COMPLIANCE ENGINEER | jnesvold@csu.org | 7196683582 |  |  |  |  | MARK JOHNSON | ECOM MANAGER | 719-668-3630 | mjohnson@csu.org | EXCAVATOR HIT CORRECTLY MARKED PLASTIC 6-INCH GAS MAIN WHILE EXCAVATING HILLSIDE. EXCAVATOR HAD NOT CALLED FOR LOCATES AND WAS DIGGING ON ANOTHER EXCAVATOR'S MARKS. EXCAVATOR FAILED TO POT-HOLE MARKED UTILITY, FAILED TO USE NON-MECHANIZED EQUIPMENT WITHIN 18-INCHES OF A MARKED UTILITY, AND FAILED TO CONTACT FACILITY OWNER FOR INSPECTOR.
2025-03-31 10:13 | NO | YES | NO | 20150040 | 16064 | 2015-04-01 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2015-03-02 19:58 |  |  | 2015 | 9430 ELOISE ST. | DALLAS | DALLAS | TX | 75217 | 32.7376 | -96.6592 | [9 empty] | 2015-03-02 21:48 | 1109474 |  | NATURAL GAS |  | 47 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | YES | 12 | 2015-03-02 21:37 |  |  |  | 2015-03-02 21:18 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | CONNECTION | 1951 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 100000 | 121125.8215068102 | 1915 | 2319.55948185541533 | 4377 | 5301.677207353082454 | 0 | 0 |  |  | 187 | 187.438967136150234741784037558685446009 |  | 0 | 106479 | 53496.5622254656943710046948356807511737 | 128934.497163154848018741784037558685446 | 0 | 0 | 5 |  |  |  |  | 20 | 20 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOW POINT OF THIS SYSTEM WAS MONITORED BY CONTROLLER WITH NO CONTROL CAPABILITIES | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [14 empty] | NO | YES | CITY STREET | [12 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO | [7 empty] | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | TOMMY LOONEY | OPERATIONS SUPERVISOR | tommy.looney@atmosenergy.com | 469-261-7387 | 214-426-7062 |  |  |  | JEFFREY S. KNIGHTS | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2701 | jeff.knights@atmosenergy.com | AT 7:58 PM ON MARCH 2, 2015, ATMOS ENERGY DISPATCH WAS NOTIFIED OF AN EVENT AT 1504 MEMORY LANE IN DALLAS. ATMOS ENERGY'S FIRST RESPONDER ARRIVED ON-SITE AT 9:17 PM AND UPON LEARNING THAT HOMES HAD BEEN EVACUATED BY DALLAS FIRE DEPARTMENT PERSONNEL THE ATMOS ENERGY FIRST RESPONDER BEGAN BAR TESTING AND CHECKING SEWER VENTS IN THE IMMEDIATE AREA. SOON A SECOND ATMOS ENERGY RESPONDER AND TWO ATMOS ENERGY SUPERVISORS ARRIVED TO ASSIST WITH THE INVESTIGATION. AT APPROXIMATELY 11:25 PM ATMOS ENERGY BEGAN A LEAK SURVEY OF THE AREA WITH A LEAK THEREAFTER PINPOINTED IN THE AREA OF THE SERVICE TAP TO 1504 MEMORY LANE. IN THE EARLY MORNING HOURS OF MARCH 3, 2015, ATMOS ENERGY REQUESTED EMERGENCY LINE LOCATES WHICH WERE MADE ALLOWING ATMOS ENERGY'S EXCAVATION OF THE SERVICE TAP TO 1504 MEMORY LANE TO BEGIN AT APPROXIMATELY 2:20 AM. A LEAK WAS DISCOVERED AT THE SERVICE TAP CONNECTION AND THE SERVICE LINE TO 1504 MEMORY LANE WAS RETIRED AT 2:43 AM. ATMOS ENERGY THEN BEGAN AN EXCAVATION TO RETIRE THE SERVICE LINE TO 9430 ELOISE STREET AND THIS RETIREMENT WAS COMPLETED AT 4:47 AM. ON MARCH 10, 2015, UNDER THE OBSERVATION OF RAILROAD COMMISSION PERSONNEL ATMOS ENERGY AND BAKER RISK PERFORMED STRATEGIC EXCAVATION OF THE 1504 MEMORY LANE SERVICE LINE. PREVIOUS DAMAGE DUE TO THIRD PARTY EXCAVATION WAS OBSERVED ON THE SERVICE LINE. BETWEEN DECEMBER 13, 2011, AND MARCH 2, 2015, ATMOS ENERGY IS AWARE OF FIVE LOCATE REQUESTS (LOCATE NUMBERS 1475052478, 1475382044, 120450096, 120196080, AND 13474488) IN PROXIMITY TO 1504 MEMORY LANE. THE THIRD PARTY EXCAVATION DAMAGE TO THE SERVICE LINE CAUSED THE CONNECTION FAILURE AT THE SERVICE TAP.
2025-03-31 10:13 | NO | NO | NO | 20150041 | 16246 | 2015-04-10 18:01 | SUPPLEMENTAL FINAL | 30769 | MISSOURI GAS ENERGY | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2015-03-13 12:20 |  |  | 2015 | SEC OF RANGELINE & NEWMAN RD. | JOPLIN | JASPER | MO | 64801 | 37.0981 | -94.4761 | [9 empty] | 2015-03-23 15:47 | 1111554 |  | NATURAL GAS |  | 5436 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-03-13 12:23 |  |  |  | 2015-03-13 12:43 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 62 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1973 | [5 empty] | 4 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 6 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 12652 | 15324.838937041626504 | 500 | 605.629107534051 | 0 | 0 |  |  | 28556 | 28623.0328638497652582159624413145539906 |  | 0 | 41708 | 33075.9033084751644833051643192488262911 | 44553.5009084254427622159624413145539906 | 0 | 0 | 0 |  |  |  |  | 30 | 30 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 150640341 |  |  | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | PATRICK SEAMANDS | MANAGER OF PIPELINE SAFETY AND COMPLIANCE | patrick.seamands@thelacledegroup.com | (314) 349-2936 |  |  |  |  | BOB GARDNER | DIRECTOR OF COMPLIANCE AND PIPELINE INTEGRITY | (205) 326-2584 | bob.gardner@alagasco.com | A 4-INCH STEEL MAIN WAS HIT AND PUNCTURED BY AN EXCAVATING CONTRACTOR'S BORE MACHINE BACK-REAMER WHILE INSTALLING FIBER OPTIC FACILITIES. THE EXCAVATING CONTRACTOR HAND DUG ON BOTH SIDES OF THE LOCATE MARKING AND COULD NOT LOCATE THE GAS MAIN. THE LOCATE CONTRACTOR HAD NOT BEEN ABLE TO CORRECTLY LOCATE THE FACILITY. THE COMPANY WELDED ONE SHORT STOP ON EACH END OF THE DAMAGE AND BYPASSED THE MAIN WHILE THE REPAIR WAS MADE. FOUR FEET OF PRE-TESTED STEEL PIPE WAS ATTACHED TO THE EXISTING MAIN WITH TWO 4-INCH POSI-HOLD COUPLINGS. THE COMPANY ESTIMATED REPAIR COSTS TO BE BELOW $50,000 AND DID NOT ANTICIPATE LOSSES TO BE OVER THREE MILLION CUBIC FEET (MMCF); HOWEVER, GAS LOSS CALCULATIONS CONDUCTED ON MARCH 19, 2015 TOTALED 10.873 MMCF. THE COMPANY REPORTED THE INCIDENT TO THE NATIONAL RESPONSE CENTER IMMEDIATELY AFTER REVIEWING THE GAS LOSS CALCULATIONS ON MARCH 23, 2015.
2025-03-31 10:13 | NO | YES | NO | 20150042 | 16192 | 2015-04-13 09:39 | SUPPLEMENTAL FINAL | 5300 | FLORENCE GAS DEPT, CITY OF | 110 W. COLLEGE ST. / P.O. BOX 937 | FLORENCE | AL | 35631 | 2015-04-10 03:03 |  |  | 2015 | 443 CALHOUN DIRVE | FLORENCE | ALABAMA | AL | 35630 | 34.8299 | -87.6892 | [9 empty] | 2015-04-10 05:01 | 1113159 |  |  |  | 1.2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2015-04-10 03:20 |  |  |  | 2015-04-10 03:35 |  | NO | PRIVATE PROPERTY | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | 1959 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 100000 | 121125.8215068102 | 200 | 242.2516430136204 | 500 | 605.629107534051 | 200 | 242.2516430136204 | ADDITIONAL LEAK SURVEY |  | 5 | 5.01173708920187793427230046948356807512 |  | 0 | 100905 | 50622.8188342998913840375586854460093897 | 122220.9656374606936779342723004694835681 | 0 | 0 | 17 |  |  |  |  | 21 | 21 | 26 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | YES |  |  |  | YES | SEVERE THUNDERSTORM | [213 empty] | MICHAEL DOYLE | MANAGER | mdoyle@florenceal.org | 2567185100 | 2567671818 |  |  |  | MICHAEL DOYLE | MANAGER | 2567185100 | mdoyle@florenceal.org | IT APPEARS THAT LIGHTNING STRUCK THE BACK YARD CHAIN FENCE AT 443 CALHOUN DR. AROUND 3:03 AM ON APRIL 10, 2015 AND ARCHED OVER TO THE GAS METER AND RISER. INCIDENT WAS REPORTED (#1113159) TO NATIONAL RESPONSE CENTER (NRC) BY K. DAVIS AT 5:01 AM. DURING THE INCIDENT TWO GAS VALVES WERE TURNED OFF AFFECTING 21 (17 ACTIVE, 2 INACTIVE, AND 2 RISER ONLY) RESIDENTIAL CUSTOMERS. THREE RESIDENTS WERE EVACUATED AND ONE FLORENCE FIREMAN WAS INJURED WITH A SPRAINED BACK, TREATED AND RELEASED FROM THE HOSPITAL. A 3/4" WELDED SERVICE LINE WAS KILLED 11' SOUTH OF SOUTH BACK OF THE CURB OF CALHOUN DRIVE ON APRIL THE 10TH. AFTER THE HOME WAS DESTROYED, FIRE INVESTIGATION CONFIRMED THAT SEVERE THUNDERSTORMS HAD BEEN IN THE AREA THAT MORNING.
2025-03-31 10:13 | NO | NO | NO | 20150043 | 30797 | 2015-04-16 16:20 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2015-02-16 14:29 |  |  | 2015 | 59 LONE ST | MARSHFIELD | PLYMOUTH | MA | 02050 | 42.1047 | -70.7598 | [9 empty] | 2015-04-02 15:45 | 1112400 |  | NATURAL GAS |  | 13.97 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 11 | 2015-02-16 14:29 |  |  |  | 2015-02-16 14:47 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1996 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.121 |  | 3408 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 50000 | 60562.9107534051 | 1000 | 1211.258215068102 | 1000 | 1211.258215068102 | 600 | 726.7549290408612 | PRESSURE TESTING |  | 82 | 82.19248826291079812206572769953051643192 |  | 0 | 52682 | 26463.7078805180196582159624413145539906 | 63794.3746008450759981220657276995305164 | 1 | 0 | 0 |  |  |  |  | 67 | 67 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | RISER AFTER THE INSULATED UNION BROKE DUE TO SNOW/ICE LOAD | [154 empty] | MEGGAN BIRMINGHAM | COMPLIANCE OPERATIONS MANAGER | mbirmingham@nisource.com | [5 empty] | MEGGABN BIRMINGHAM | COMPLIANCE OPERATIONS MANAGER | 508.468.9956 | mbirmingham@nisource.com | THERE WAS A BUILD UP OF SNOW AND ICE ON THE METER SET CAUSING THE RISER AFTER THE INSULATED UNION TO BREAK RESULTING IN A RELEASE OF GAS. THE RELEASE OF GAS IGNITED RESULTING IN A FIRE AND PROPERTY DAMAGE. PART C SUBPART 2A & 4 ARE ASSOCIATED WITH THE SERVICE LINE. THE COMPANY WAS UNABLE TO DETERMINE HOW THE SNOW BUILD UP OCCURRED (I.E. WHETHER IT WAS ASSOCIATED WITH NATURAL FORCE OR A 3RD PARTY).THERE WAS A BREAKDOWN IN THE NOTIFICATION PROCESS WHICH RESULTED IN A DELAYED NRC CALL BEING MADE. THE COMPANY HAS SINCE IMPLEMENTED ANNUAL TRAINING TO PROVIDE CONTINUOUS EDUCATION ON THE REPORTING REQUIREMENTS AT BOTH A STATE AND FEDERAL LEVEL.
2025-03-31 10:13 | NO | YES | NO | 20150044 | 16125 | 2015-04-20 16:58 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2015-03-21 14:47 |  |  | 2015 | 3418 SUNNINGDALE WAY | UPPER ARLINGTON | FRANKLIN | OH | 43221 | 40.0271 | -83.0579 | [9 empty] | 2015-03-21 15:45 | 1111378 |  | NATURAL GAS |  | 163 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 18 | 2015-03-21 14:47 |  |  |  | 2015-03-21 12:38 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 38 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1960 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.166 | [6 empty] | OTHER | [8 empty] | UNPLUGGED ELBOW. | CLASS 3 LOCATION | 9000000 | 10901323.935612918 | 1755 | 2125.75816744451901 | 3200 | 3876.0262882179264 | 0 | 0 |  |  | 320 | 320.751173708920187793427230046948356808 |  | 0 | 9005275 | 4517783.90144243565669840375586854460094 | 10907646.47124228936559779342723004694836 | 0 | 0 | 8 |  |  |  |  | 7 | 7 | 9.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | SEE NARRATIVE | [47 empty] | ROB SMITRH | OPERATION COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB SMITH | OPERATION COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | ON MARCH 21, 2015, A COLUMBIA GAS OF OHIO, INC. ("COLUMBIA" OR "COMPANY") SERVICE TECHNICIAN RESPONDED TO AN ODOR-OF-GAS CALL AT 3418 SUNNINGDALE WAY, UPPER ARLINGTON, OHIO. THE TECHNICIAN VERIFIED THAT NO ONE WAS AT HOME, AND TURNED OFF BOTH THE CURB VALVE TO THE ACTIVE SERVICE LINE AND THE METER VALVE. NO LEAKS WERE FOUND IN THE METER SET ASSEMBLY, BUT SUBSURFACE READINGS INDICATED THE PRESENCE OF GAS AT THE FOUNDATION OF THE HOUSE. WHILE THE TECHNICIAN WAS ON THE PREMISES, AN EXPLOSION OCCURRED, FOLLOWED BY A FIRE. THE FIRE CONTINUED AT THE FOUNDATION OF THE HOUSE. ALTHOUGH THE FIRE APPEARED TO BE GAS-FED, IT CONTINUED AFTER THE COMPANY PHYSICALLY DISCONNECTED THE ACTIVE, PLASTIC SERVICE LINE. IN THE COURSE OF SEARCHING FOR POSSIBLE SOURCES OF THE FIRE, THE COMPANY DISCOVERED A DISCONTINUED CUSTOMER-OWNED STEEL SERVICE LINE, WHICH WAS ACCESSED THROUGH A CURB BOX THAT WAS INCORRECTLY LABELED "WATER." THE VALVE ON THAT LINE WAS PARTIALLY OPEN, AND THE COMPANY BELIEVES THAT IT WAS INADVERTENTLY OPERATED BY A THIRD PARTY ON THE PREVIOUS DAY. THE LINE TERMINATED AT AN ELBOW APPROXIMATELY 38 INCHES BELOW THE SURFACE, NEAR THE BLOCK FOUNDATION OF THE HOUSE. SUBSEQUENT TESTING SHOWED A CORROSION LEAK APPROXIMATELY FOUR FEET FROM THE INCORRECTLY LABELED CURB BOX, AND ADDITIONAL EXAMINATION OF THAT FACILITY REVEALED THAT THE ELBOW AT THE TERMINATION OF THE DISCONTINUED CUSTOMER-OWNED SERVICE LINE WAS UNCAPPED. COLUMBIA'S RECORDS DO NOT SHOW TWO SERVICE LINES AT THIS ADDRESS, AND SUBSEQUENT GAS MAIN CAMERA INSPECTIONS, INCLUDING GAS LINE VALVES AND CUSTOMER SERVICE CONNECTIONS TO THE MAIN, CONDUCTED BY COLUMBIA ON SUNNINGDALE WAY AND THE IMMEDIATELY SURROUNDING STREETS CONFIRMED THAT THE DISCONTINUED AND CONNECTED GAS SERVICE LINE IS AN ANOMALY BECAUSE ALL OTHER GAS MAIN OPENINGS ARE ACCOUNTED FOR IN THE COMPANY'S RECORDS. THE COMPANY IS UNABLE TO RULE OUT AN UNAUTHORIZED INSTALLATION OF FACILITIES BY A THIRD PARTY. AT THIS POINT IN THE INVESTIGATION, COLUMBIA HAS ENOUGH INFORMATION TO FINALIZE ITS INCIDENT REPORT, AND SUBMITS THAT THE INADVERTENT OPERATION OF A GAS VALVE BY A THIRD-PARTY, WHICH WAS ACCESSED THROUGH A CURB BOX THAT WAS INCORRECTLY LABELED "WATER," WHICH ULTIMATELY ALLOWED GAS TO FLOW TO A DISCONTINUED, UNCAPPED SERVICE LINE IS THE LIKELY SERIES OF EVENTS THAT CAUSED THE INCIDENT. THE COMPANY HAS MADE MULTIPLE ATTEMPTS TO INTERVIEW THE WATER DEPARTMENT AND/OR THE OPERATOR OF ITS SYSTEM IN THAT AREA TO DETERMINE WHETHER IT HAS INFORMATION OR DOCUMENTATION CONCERNING ANY FACTORS THAT CONTRIBUTED TO THIS EVENT, AND HAS BEEN UNSUCCESSFUL IN SECURING AN INTERVIEW. THE COMPANY WILL CONTINUE TO WORK WITH LOCAL AUTHORITIES AS THEY COMPLETE THEIR INVESTIGATIONS.
2025-03-31 10:13 | NO | YES | NO | 20150045 | 16071 | 2015-04-23 16:50 | ORIGINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2015-03-25 16:25 |  |  | 2015 | INTERSECTION DORSETT STREET @ FULGHAM DRIVE | DOUGLASVILLE | DOUGLAS | GA | 30134 | 33.757 | -84.7345 | [9 empty] | 2015-03-25 19:25 | 1111730 |  | NATURAL GAS |  | 30 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2015-03-25 16:25 |  |  |  | 2015-03-25 16:56 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1985 | [5 empty] | 2.375 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | 2406 | OTHER | [8 empty] | SECTION OF PIPE DAMAGED DUE TO BLASTING | CLASS 3 LOCATION | 0 | 0 | 2300 | 2785.8938946566346 | 4000 | 4845.032860272408 | 175000 | 211970.18763691785 | DAMAGE TO NEARBY BACKHOE |  | 300 | 300.704225352112676056338028169014084507 |  | 0 | 181600 | 91230.3644612699542422535211267605633803 | 219901.8186171990052760563380281690140845 | 0 | 0 | 0 |  |  |  |  | 45 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | EXPLOSIVES | ROAD WORK | YES | 2275400082 |  |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@aglresources.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R. LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@aglresources.com | A 2-INCH PLASTIC NATURAL GAS MAIN WAS RUPTURED BY BLASTING OPERATIONS WHILE PERFORMING ROAD CONSTRUCTION WORK. THE COMPANY WAS NOTIFIED THROUGH ONE-CALL OF EXCAVATION IN THE AREA WHERE THE PIPELINE WAS CORRECTLY LOCATED AND MARKED, HOWEVER, THERE WAS NO INDICATION OF BLASTING AS AN EXCAVATION TYPE ON THE LOCATE REQUEST. ADDITIONALLY, THERE IS NO EVIDENCE TO DATE OF THE EXCAVATOR ATTEMPTING TO PROTECT THE PIPE DURING BLASTING OR REQUESTING ASSISTANCE FROM THE COMPANY IN THAT REGARD. THE ESCAPING GAS IGNITED WHEN A NEARBY BACKHOE BEGAN DIGGING IN THE AREA AFTER THE BLASTING OPERATION WAS COMPLETE THUS BURNING THE BACKHOE.
2025-03-31 10:13 | NO | NO | NO | 20150049 | 16080 | 2015-05-06 16:54 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2015-04-14 14:47 |  |  | 2015 | VAR. LOC'S IN NORTHERN QUEENS | NEW YORK | QUEENS | NY | 11211 | 40.7138 | -73.8283 | [9 empty] | 2015-04-14 17:36 | 113602 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-04-14 14:47 |  |  |  | 2015-04-14 15:25 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | OTHER | VARIOUS ODOR COMPLAINTS |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | CUSTOMER GAS ODOR COMPLAINTS | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | MALODOROUS CONDITION IDENTIFIED BY VAR. CUSTOMER REPORTED GAS ODOR COMPLAINTS IN NORTHERN QUEENS. SUBSEQUENT INVESTIGATION REVEALED EXCESS ODORANT INJECTION FROM LNG LIQEFACTION PROCESS. | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 82832 | 100330.940470521024864 | 0 | 0 |  |  | 0 | 0 |  | 0 | 82832 | 41554.066482522145408 | 100330.940470521024864 | 0 | 0 | 0 |  |  |  |  | 13.5 | 13.5 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS NOT THE RESULT OF ANY OPERATION THAT THE CONTROL ROOM CAN DETECT UNDER PRESENT OPERATING CONDITIONS AND ALARMS. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | LIQUEFACTION PLANT FEED GAS PURIFICATION PROCESS REINJECTION SYSTEM (MERCAPTAN/MOISTURE) REQUIRES ADJUSTMENT TO ENSURE PROPER INJECTION RATIO INTO DISTSRIBUTION SYSTEM. | [47 empty] | CORINNE BYRNES | PRIN PROG MGR- OPERATIONS CODES AND POLICY | corinne.byrnes@nationalgrid.com | 5169030596 | 5165456116 |  |  |  | CORINNE BYRNES | PRIN PROG MGR- OPERATIONS CODES AND POLICY | 5169030596 | corinne.byrnes@nationalgrid.com | MULTIPLE GAS ODOR COMPLAINTS WERE RECEIVED AND INVESTIGATED BY 70 FIRST RESPONDER CREWS. THE NATIONAL RESPONSE CENTER WAS NOTIFIED OUT OF AN ABUNDANCE OF CAUTION DUE TO THE CALL VOLUME. SUBSEQUENT CHEMICAL ANALYSIS OF THE GAS REVEALED EXCESS ODORANT CONCENTRATIONS. IT WAS LATER DETERMINED THAT THE LIQUEFACTION PLANT FEED GAS PURIFICATION PROCESS REINJECTION SYSTEM (MERCAPTAN/MOISTURE) REQUIRES ADJUSTMENT TO ENSURE PROPER INJECTION RATIO INTO DISTRIBUTION SYSTEM.
2025-03-31 10:13 | NO | YES | NO | 20150050 | 30798 | 2015-05-08 16:37 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2015-02-19 10:28 |  |  | 2015 | 298 KINGS TOWN WAY | DUXBURY | PLYMOUTH | MA | 02332 | 42.0307 | -70.7389 | [9 empty] | 2015-04-13 14:59 | 1113473 |  | NATURAL GAS |  | 54 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 24 | 2015-02-19 10:28 |  |  |  | 2015-02-19 10:49 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1997 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.121 |  | 3408 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | 400000 | 484503.2860272408 | 1000 | 1211.258215068102 | 4381 | 5306.522240213354862 | 100000 | 121125.8215068102 | CONTENT COST WHICH WAS REFERENCED ON NFIRS REPORT. |  | 227 | 227.53286384976525821596244131455399061 |  | 0 | 505608 | 253743.3631141709476593051643192488262911 | 612374.4208531822221202159624413145539906 | 1 | 0 | 0 |  |  |  |  | 69 | 69 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | NIPPLE BROKE DUE TO SNOW/ICE LOAD | [154 empty] | MEGGAN BIRMINGHAM | COMPLIANCE OPERATIONS MANAGER | mbirmingham@nisource.com | [5 empty] | MEGGAN BIRMINGHAM | COMPLIANCE OPERATIONS MANAGER | 508.468.9956 | mbirmingham@nisource.com | 3/4" CLOSE STEEL NIPPLE BROKE AT THE ENTRANCE TO THE HIGH PRESSURE SHUT OFF DUE TO A BUILD UP OF SNOW ON THE FITTING. PART C SUBPART 2A & 4 ARE ASSOCIATED WITH THE SERVICE LINE. THE COMPANY WAS UNABLE TO DETERMINE HOW THE SNOW LOAD OCCURRED ON THE FITTING (I.E. WHETHER IT WAS DUE TO NATURAL FORCES OR A 3RD PARTY). GAS WAS RELEASED AND RESULTED IN AN IGNITION. THE SERVICE WAS CUT OFF AT THE CURB AS THE FINAL REMEDIATION. THE NON-OPERATOR PROPERTY DAMAGE AND OTHER COSTS WERE OBTAINED FROM THE NATIONAL FIRE INVESTIGATION REPORTING SYSTEM (NFIRS) REPORT. THERE WAS A BREAKDOWN IN THE NOTIFICATION PROCESS WHICH RESULTED IN A DELAYED NRC CALL BEING MADE. THE COMPANY HAS SINCE IMPLEMENTED ANNUAL TRAINING TO PROVIDE CONTINUOUS EDUCATION ON THE REPORTING REQUIREMENTS AT BOTH A STATE AND FEDERAL LEVEL.
2025-03-31 10:13 | NO | YES | NO | 20150051 | 16086 | 2015-05-26 14:13 | ORIGINAL FINAL | 22763 | WISCONSIN GAS LLC DBA WE ENERGIES | 231 W. MICHIGAN STREET | MILWAUKEE | WI | 53203 | 2015-04-29 10:05 |  |  | 2015 | 316 S. MAIN STREET | MEDFORD | TAYLOR | WI | 54451 | 45.136 | -90.3428 | [9 empty] | 2015-04-29 11:38 | 115011 |  | NATURAL GAS |  | 339 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 60 | 2015-04-29 09:32 |  |  |  | 2015-04-29 10:05 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 38 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1963 | [5 empty] | 4 | API 5L | ACME - NEWPORT STEEL COMPANY | STEEL |  | OTHER | ERW | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 9 | 3 | [7 empty] | CLASS 3 LOCATION | 112500 | 136266.549195161475 | 3000 | 3633.774645204306 | 2500 | 3028.145537670255 | 0 | 0 |  |  | 1836 | 1840.309859154929577464788732394366197183 |  | 0 | 119836 | 60899.0797648065750985915492957746478873 | 144768.7792371909655774647887323943661972 | 4 | 0 | 9 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | THE INCIDENT WAS CLEARLY THE RESULT OF 3RD PARTY EXCAVATION DAMAGE. | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | AUGER | UNKNOWN/OTHER | YES | 20151715490 |  |  | CONTRACT LOCATOR | NO | YES | 6 | NOTIFICATION ISSUE | EXCAVATOR PROVIDED INCORRECT NOTIFICATION INFORMATION | [170 empty] | CHRISTOPHER GIGOT | ENGINEER | christopher.gigot@we-energies.com | (414) 221-5347 |  |  |  |  | TIM STROMMEN | MANAGER REGULATORY COMPLIANCE | 414-221-5173 | tim.strommen@we-energies.com | ON WEDNESDAY, APRIL 29TH, 2015, AT 9:32 A.M., WE ENERGIES WAS NOTIFIED BY A LOCAL FIRE DEPARTMENT THAT A GAS MAIN HAD BEEN STRUCK BY A CONTRACTOR PERFORMING SOIL BORINGS AT 316 S. MAIN STREET IN MEDFORD, WISCONSIN. WE ENERGIES DISPATCHED A FIRST RESPONDER TO THE SITE AT 9:34 A.M. AND DETERMINED THE VALVES REQUIRED TO STOP THE FLOW OF GAS. WHILE THE FIRE DEPARTMENT WAS EVACUATING BUILDINGS WITHIN A 2 BLOCK RADIUS OF THE DAMAGED GAS MAIN, THE GAS IGNITED AT APPROXIMATELY 9:45 A.M. IT IS BELIEVED THAT THE SOIL BORING MACHINE, WHICH WAS LEFT ON, WAS THE SOURCE OF IGNITION. THE FIRST EMPLOYEE FROM WE ENERGIES ARRIVED ON SITE AT 10:05 A.M. AND THE GAS WAS SHUT OFF AT 10:37 A.M. ONCE THE GAS WAS SHUT OFF AND THE SITE WAS DEEMED SAFE, WE ENERGIES EMPLOYEES ASSESSED WHETHER OR NOT THIS EVENT MET THE CRITERIA OF A REPORTABLE INCIDENT. IT WAS DETERMINED THAT THERE WERE NO INJURIES OR FATALITIES AND THAT THE AMOUNT OF GAS RELEASED WAS WELL BELOW 3 MMCF; HOWEVER, PROPERTY DAMAGE OF MORE THAN $50,000 OCCURRED. A PHONE NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER AT 11:38 A.M. OF A POSSIBLE NATURAL GAS INCIDENT PER 49 CFR PART 191.3. THE WISCONSIN PUBLIC SERVICE COMMISSION PIPELINE SAFETY MANAGER WAS ALSO INFORMED OF THE INCIDENT. AFTER THE FIRE HAD BEEN COMPLETELY EXTINGUISHED AND THE DEBRIS HAD BEEN REMOVED, WE ENERGIES REPLACED THE DAMAGE SECTION OF 4 INCH STEEL MAIN. THE MAIN REPAIR WAS COMPLETED BY ABOUT 4:00 P.M. AND RESTORING SERVICE TO THE 13 CUSTOMERS AFFECTED PROCEEDED THROUGH THE EVENING. INVESTIGATION OF THE INCIDENT DETERMINED THAT THE SOIL BORING CONTRACTOR PROVIDED AN INADEQUATE DESCRIPTION OF THE AREA REQUIRING UTILITY LOCATES TO THE ONE CALL SYSTEM.
2025-03-31 10:13 | NO | YES | NO | 20150052 | 16194 | 2015-06-01 17:09 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-05-02 16:47 |  |  | 2015 | 4487 E. M-71 | CORUNNA | SHIAWASSEE | MI | 48817 | 42.9682 | -84.082 | [9 empty] | 2015-05-02 19:56 | 1115334 |  | NATURAL GAS |  | 12525 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 60 | 2015-05-02 16:47 |  |  |  | 2015-05-02 17:17 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | EMERGENCY VALVE ASSEMBLY (PLUG VALVES) | 2013 | [8 empty] | OTHER | 2" THREADED NIPPLE | [9 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 30519 | 36966.389465663404938 | 5140 | 6225.86722545004428 | 0 | 0 | N/A |  | 93443 | 93662.3497652582159624413145539906103286 |  | 0 | 129102 | 104532.0946043598162603192488262910798122 | 136854.6064563716651804413145539906103286 | 0 | 0 | 0 |  |  |  |  | 315 | 315 | 350 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELEASE WAS THE RESULT OF A THIRD PARTY DAMAGE AND THE OPERATOR WAS NOTIFIED BY 911-DISPATCHER. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 517-788-0509 |  |  |  |  | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | 989-791-5841 | alan.chichester@cmsenergy.com | ON SATURDAY, MAY 2, 2015 AT APPROXIMATELY 16:47 AN ABOVE-GRADE 10" HIGH PRESSURE DISTRIBUTION EMERGENCY VALVE ASSEMBLY WAS STRUCK BY A FARMER OPERATING CULTIVATION EQUIPMENT IN A FIELD NEAR 4487 E. M-71, CORUNNA, SHIAWASSEE COUNTY, MICHIGAN. A 2" THREADED NIPPLE WAS TORN OFF AS A RESULT OF THE DAMAGE, CAUSING BLOWING GAS. CONSUMERS ENERGY PERSONNEL ARRIVED ON SITE AT APPROXIMATELY 17:17 TO ADDRESS THE IMMEDIATE PUBLIC SAFETY HAZARD, SECURE THE SITE, ASSESS DAMAGE TO COMPANY FACILITIES, AND DETERMINE NEXT STEPS. LOCAL POLICE AND AND FIRE PERSONNEL BLOCKED TRAFFIC IN BOTH DIRECTION ON HIGHWAY E. M-71, AND APPROXIMATELY 60 RESIDENCES WERE EVACUATED. TEMPORARY SHELTER FOR WAS PROVIDED TO EVACUATED RESIDENTS. BASED ON AN ANALYSIS OF REPAIR OPTIONS AND POTENTIAL SERVICE INTERRUPTIONS FROM ISOLATING THE DAMAGED SECTION, A PRESSURE REDUCTION WAS PERFORMED TO TAKE THE AFFECTED SEGMENT FROM 315 PSIG TO 150 PSIG. THE GRADUAL PRESSURE REDUCTION ALLOWED SERVICE TO BE MAINTAINED TO SEVERAL THOUSAND CUSTOMERS IN PREPARATION FOR VALVING OPERATION. THE PRESSURE REDUCTION WAS COMPLETED AT 00:28 HOURS ON MAY 3. A REVISED RESPONSE PLAN WAS DEVELOPED AT 4:00 HOURS TO FURTHER REDUCE SERVICE INTERRUPTIONS BY BACKFEEDING THE DOWNSTREAM 60 PSIG (MEDIUM PRESSURE) SYSTEM FROM TWO ADJACENT SYSTEMS. AT APPROXIMATELY 12:00 HOURS ON MAY 3, PRESSURE ON THE DAMAGED HIGH PRESSURE SYSTEM WAS FURTHER REDUCED TO BELOW 15 PSIG, ALLOWING CONSUMERS ENERGY PERSONNEL TO REPLACE THE DAMAGED THREADED VALVE ASSEMBLY AND COMPLETE REPAIRS TO THE DAMAGED FACILITY. AT 14:45 ON MAY 3, BLOWING GAS WAS STOPPED FOR COMPLETION OF FINAL REPAIRS. REPAIRS WERE COMPLETED AND NORMAL OPERATION WAS RESTORED AT 16:00.
2025-03-31 10:13 | NO | YES | YES | 20150054 | 16337 | 2015-06-05 17:52 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2015-05-09 13:37 |  |  | 2015 | INTERSECTION OF E 54 STREET AND LEXINGTON AVENUE | NEW YORK | NEW YORK | NY | 10019-3513 | 40.7568 | -73.9696 | [9 empty] | 2015-05-09 22:27 | 1116018 |  | NATURAL GAS |  | 0.7 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | NO |  |  |  |  | YES | 0 | 2015-05-09 13:37 |  |  |  | 2015-05-09 14:03 |  | NO | PUBLIC PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 16 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 78000 | 94478.140775311956 | 45000 | 54506.61967806459 | 0 | 0 |  |  | 3 | 3.00704225352112676056338028169014084507 |  | 0 | 123003 | 61707.8012158099570704225352112676056338 | 148987.7674956300671267605633802816901408 | 0 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | [197 empty] | NON-THREADED CONNECTION FAILURE | [14 empty] | OTHER SEAL OR PACKING | [68 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | (718) 319-2310 | (718) 904-4607 |  |  |  | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | (718) 319-2310 | fagank@coned.com | ON THE EVENING OF MAY 8, 2015, CON EDISON WAS NOTIFIED THAT NEW YORK CITY DEPARTMENT OF TRANSPORTATION (NYCDOT) EMPLOYEES WERE INJURED WHILE REPAIRING A POTHOLE NEAR A NEW YORK CITY DEPARTMENT OF ENVIRONMENTAL PROTECTION (NYCDEP) WATER VALVE BOX AT THE INTERSECTION OF EAST 54TH STREET AND LEXINGTON AVENUE. FIRE DEPARTMENT CITY OF NEW YORK (FDNY) INITIALLY REPORTED TO CON EDISON THAT THERE WAS A SMOKING MANHOLE AT THE LOCATION. THE ELECTRIC CREW THAT RESPONDED FOUND THAT THE WATER VALVE COVER HAD BEEN BLOWN OFF ITS CASTING. THEY DETERMINED THAT THERE WAS NO ELECTRIC INVOLVEMENT, CONDUCTED A PRELIMINARY INVESTIGATION WHICH DETECTED TRACE METHANE, AND REQUESTED A GAS CREW TO RESPOND. A GAS EMERGENCY MECHANIC WAS DISPATCHED AT 22:52 HOURS TO INVESTIGATE AND FOUND NO INDICATIONS OF GAS IN THE WATER VALVE BOX. ON MAY 9, 2015 AT 1:18 HOURS, ANOTHER GAS EMERGENCY MECHANIC WAS DISPATCHED TO INVESTIGATE AND ALSO FOUND NO INDICATIONS OF NATURAL GAS IN THE WATER VALVE BOX. AT 13:37 HOURS, THE NYCDEP REPORTED TO THE GAS EMERGENCY RESPONSE CENTER (GERC) THAT THEY WERE RECEIVING GAS READINGS IN THE WATER VALVE BOX, WHICH HAD BEEN SUBSEQUENTLY BACKFILLED. A GAS EMERGENCY MECHANIC RESPONDED, INVESTIGATED AND REPORTED A 7% GAS READING IN THE WATER VALVE BOX. CON EDISON'S CHEMICAL LAB PERSONNEL WERE DISPATCHED TO THE LOCATION AND AT 20:32 HOURS THEY REPORTED FINDING A CONCENTRATION OF 5.9% NATURAL GAS-IN-AIR IN THE WATER VALVE BOX. CON EDISON DISPATCHED AN EMERGENCY CONSTRUCTION CREW TO RESPOND, VENTILATE AND INVESTIGATE FOR A POSSIBLE GAS LEAK. THE LEAK INVESTIGATION REVEALED POSITIVE GAS READINGS OVER A 16" LOW PRESSURE CAST IRON GAS MAIN, LOCATED IN THE ROADWAY APPROXIMATELY 50' WEST AND 15' SOUTH OF THE WATER VALVE BOX. A LEAKING HUB ON THE 16" MAIN WAS EXPOSED AND SEALED. A RETIRED, OUT-OF-SERVICE 8" STEEL GAS MAIN ON THE NORTH SIDE OF EAST 54TH STREET BETWEEN LEXINGTON AND THIRD AVENUES WAS EXPOSED AND FOUND TO CONTAIN 90% GAS-IN-AIR. THE LEAK INVESTIGATION FOUND POSITIVE GAS READINGS NEAR THE NORTHWEST CORNER OF EAST 54 STREET AND THIRD AVENUE IN THE AREA OF A 16" LOW PRESSURE CAST IRON GAS MAIN. THREE HUB CONNECTIONS ON THAT 16" LOW PRESSURE GAS MAIN WERE EXCAVATED, FOUND TO BE LEAKING AND WERE REPAIRED. THE AREA WAS MONITORED, CONFIRMED CLEAR AND NO ADDITIONAL READINGS WERE DETECTED. THE FDNY FIRE MARSHAL INVESTIGATED, AND CONCLUDED THIS WAS A NATURAL GAS EVENT WITH AN UNKNOWN SOURCE OF IGNITION. CIG, PSC, DOT AND DEP WERE NOTIFIED. THIS WAS A SERIOUS LEVEL INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20150055 | 16213 | 2015-06-05 19:43 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2015-05-08 07:34 |  |  | 2015 | 9503 RUSH ST | SOUTH EL MONTE | LOS ANGELES | CA | 91733 | 34.0519 | -118.062 | [9 empty] | 2015-05-08 14:28 | 1115909 |  | NATURAL GAS |  | 71 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-05-08 07:34 |  |  |  | 2015-05-08 07:51 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1948 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | HP WATER BORE HOLE INTO 6"MAIN | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 190000 | 230139.06086293938 | 0 | 0 | 0 | 0 |  |  | 424 | 424.99530516431924882629107981220657277 |  | 0 | 190424 | 95709.8423681754632863849765258215962441 | 230564.0561681036992488262910798122065728 | 43 | 6 | 47 |  |  |  |  | 40 | 40 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HIGH PRESSURE WATER BORED A HOLE INTO A 6" STEEL NATURAL GAS MAIN. | [154 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | ON MAY 8, 2015, DURING INVESTIGATION OF A CUSTOMER COMPLAINT OF NO GAS, IT WAS DISCOVERED THAT A 6" STEEL GAS MAIN AT 9503 RUSH ST IN SOUTH EL MONTE CONTAINED WATER. INITIAL REPORT TO DOT INDICATED A 2" STEEL GAS MAIN AT 9703 ALPACA ST. CREWS PERFORMED REPAIRS, REMOVED WATER AND RESTORED CUSTOMERS. NO INJURIES OR IGNITION RESULTED FROM THIS INCIDENT. INVESTIGATION OF THE INCIDENT SHOWED THAT A BLOWN TRANSFORMER EARLIER IN THE DAY CAUSED A POWER OUTAGE THAT LIKELY ENERGIZED A TRACER WIRE ON A 1" PLASTIC WATER SERVICE LINE, BURNING A HOLE IN THE WATER SERVICE LINE. WATER PRESSURE FROM THE ESCAPING WATER BORED HOLES INTO THE 6" STEEL GAS MAIN CAUSING THE GAS LEAK. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO A GAS LEAK AND THE ASSOCIATED DAMAGE EXCEEDING $50,000.
2025-03-31 10:13 | NO | YES | YES | 20150056 | 16251 | 2015-06-10 19:05 | SUPPLEMENTAL FINAL | 2432 | FLORIDA CITY GAS | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2015-05-10 01:43 |  |  | 2015 | 340 SW S MACEDA BLVD. | PORT ST LUCIE | ST LUCIE | FL | 34983 | 27.3167 | -80.3735 | [9 empty] | 2015-05-10 09:38 | 1116034 |  | NATURAL GAS |  | 675 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO |  |  |  |  | NO | 200 | 2015-05-10 01:43 |  |  |  | 2015-05-10 02:30 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1993 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | VARIOUS SIZES OF BROKEN AND DAMAGED PIPES INSIDE THE STATION DUE TO VEHICULAR DAMAGE | CLASS 3 LOCATION | 0 | 0 | 998483 | 1209420.736355843689266 | 465542 | 563891.571959234341284 | 206515 | 250142.99028478908453 | TRUCKED LNG/CNG TO MAINTAIN PRESSURE TO PARTS OF SYSTEM. MARGIN LOSS. |  | 3850 | 3859.03755868544600938967136150234741784 |  | 0 | 1674390 | 841624.3342044201034689201877934272300469 | 2027314.33615855256108938967136150234742 | 358 | 3 | 6075 |  |  |  |  | 105 | 105 | 150 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY VEHICULAR DAMAGE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LETICIA QUEZADA | DIR COMPLIANCE AND QA | lquezad@aglresources.com | (630)388-2316 |  |  |  |  | LETICIA QUEZADA | DIR COMPLIANCE AND QA | (630)514-2036 | lquezad@aglresources.com | NOTE: THE LOCATION OF THIS INCIDENT WAS ORIGINALLY REPORTED TO THE NRC AS503 S MACEDO. THE DRIVER OF SPORT UTILITY VEHICLE, TRAVELLING AT A HIGH RATE OF SPEED, LOST AND WENT AIRBORNE OVE THE 6-FOOT HIGH FENCE OF A GATE STATION, CAUSING DAMAGE TO THE REGULATING FACILITIES. THE DAMAGE CAUSED A REPID DEPRESSURIZATION, RESULTING IN A SYTEM OUTAGE AFFECTING 6,436 CUSTOMERS.
2025-03-31 10:13 | NO | YES | NO | 20150057 | 16308 | 2015-06-11 21:13 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-05-12 14:10 |  |  | 2015 | 2415 N. CEDAR STREET | HOLT | INGHAM | MI | 48842 | 42.6515 | -84.5301 | [9 empty] | 2015-05-12 16:26 | 1116320 |  | NATURAL GAS |  | 21.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2015-05-12 14:10 |  |  |  | 2015-05-12 14:33 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1983 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.1 | 3.1 | [7 empty] | CLASS 3 LOCATION | 125000 | 151407.27688351275 | 854 | 1034.414515668159108 | 898 | 1087.709877131155596 | 0 | 0 |  |  | 162 | 162.380281690140845070422535211267605634 |  | 0 | 126914 | 63737.4847222203596908169014084507042254 | 153691.7815580022055490704225352112676056 | 1 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OPERATOR RECEIVED NOTIFICATION FROM 911 DISPATCH | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 517-788-0509 |  |  |  |  | ALAN CHICHESTER | GAS REGULATORY SERVICES ENGINEER | 989-791-5841 | alan.chichester@cmsenergy.com | ON MAY 12, 2015 AT APPROXIMATELY 14:10 A MOTORIST TRAVELING NORTHWEST ON N. CEDAR STREET IN HOLT, MICHIGAN CROSSED A TURN LANE, TWO LANES OF ONCOMING TRAFFIC, A CURB, A GRASS SHOULDER, AND A PARKING LOT BEFORE COLLIDING WITH A VACANT COMMERCIAL BUILDING. THE GAS METER STAND WAS DAMAGED AS A RESULT OF THE COLLISION, AND THE GAS SERVICE RISER BROKE, RESULTING IN BLOWING GAS. THIS GAS IGNITED, AND THE RESULTING FIRE DAMAGED THE STRUCTURE AND THE VEHICLE. POLICE AND FIRE DEPARTMENTS BLOCKED TRAFFIC ON CEDAR STREET BETWEEN DELHI COMMERCE AND FAY STREET. THE MOTORIST WAS TRANSPORTED BY AMBULANCE TO THE HOSPITAL FOR TREATMENT. THE MOTORIST'S DOG WAS REPORTABLY KILLED AS A RESULT OF THE CRASH. THE NATURAL GAS SERVICE LINE WAS RETIRED AND THE METER REMOVED AT THE PROPERTY OWNER'S REQUEST ON OCTOBER 28, 2015 IN PREPARATION FOR DEMOLITION.
2025-03-31 10:13 | NO | NO | NO | 20150058 | 16097 | 2015-06-12 18:57 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2015-05-16 11:36 |  |  | 2015 | CAHUENGA BLVD AND YUCCA ST | LOS ANGELES | LOS ANGELES | CA | 90028 | 34.1038 | -118.3295 | [9 empty] | 2015-05-16 11:47 | 1116739 |  | NATURAL GAS |  | 3185 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 100 | 2015-05-17 11:36 |  |  |  | 2015-05-17 12:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 64 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2006 | [5 empty] | 6 | ASTM D2513 | POLY PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 2.8 | 2.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 37081 | 44914.665872940290262 | 0 | 0 | 0 | 0 |  |  | 19113 | 19157.8661971830985915492957746478873239 |  | 0 | 56194 | 36324.4554404242391259718309859154929577 | 64072.5320701233888535492957746478873239 | 1 | 0 | 46 |  |  |  |  | 30 | 30 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | WATER | YES | 51270007 | DIGALERT - 811 |  | UTILITY OWNER | YES | YES | 17 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-335-7915 | tbauer@semprautilities.com | ON MAY 16, 2015, A LADWP EMPLOYEE WAS EXCAVATING WITH A BACKHOE TO INSTALL A WATER QUALITY SAMPLING POINT WHEN HE STRUCK A 6" PLASTIC GAS MAIN. CREW RESPONDED AND CONTROLLED THE GAS. NO INJURIES OR FURTHER DAMAGE RESULTED FROM THE GAS LEAK. ALL REPAIRS TO THE DAMAGED MAIN WERE COMPLETED AND THE AFFECTED CUSTOMERS WERE RESTORED. INVESTIGATION OF THE INCIDENT SHOWED THAT LADWP HAD A VALID USA TICKET BUT MARKS WERE OFF IN THE IMMEDIATE VICINITY OF THE DAMAGE, LIKELY DUE TO INTERFERENCE THE LOCATOR RECEIVED FROM A NEARBY UNDERGROUND POWER SOURCE. THIS INCIDENT WAS INITIALLY REPORTED TO CPUC DUE TO MEDIA COVERAGE, BUT WAS LATER REPORTED TO DOT AND CPUC DUE TO THE AMOUNT OF GAS RELEASED EXCEEDING 3,000,000 CUBIC FEET. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2025-03-31 10:13 | NO | YES | NO | 20150059 | 16099 | 2015-06-16 09:27 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2015-05-15 09:58 |  |  | 2015 | SR 37 BETWEEN BURRER DR. & SUNSET AVE. | SUNBURY | DELAWARE | OH | 43074 | 40.2437 | -82.862 | [9 empty] | 2015-05-18 15:04 | 1116843 |  | NATURAL GAS |  | 1790 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-05-15 09:58 |  |  |  | 2015-05-15 10:17 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 70 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 5.188 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.305 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 7248 | 8779.199542813603296 | 128698 | 155886.509762834591196 | 2500 | 3028.145537670255 | 0 | 0 |  |  | 8682 | 8702.380281690140845070422535211267605634 |  | 0 | 147128 | 77503.9765785876328268169014084507042254 | 176396.2351250085903370704225352112676056 | 1 | 0 | 0 |  |  |  |  | 120 | 120 | 125 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DRILLING | ROAD WORK | YES | 513300076 | OHIO UTILITIES PROTECTION SERVICE (OUPS) |  | CONTRACT LOCATOR | YES |  |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | SIGNAL BLEED OFF MADE LOCATING DIFFICULT AND CONFLICTING RECORDS | [169 empty] | ROB SMITH | OPERATION COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB SMITH | OPERATION COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | ON FRIDAY MAY 15, 2015, COLUMBIA GAS OF OHIO INC. (COLUMBIA) RECEIVED A CALL REGARDING A LEAK ON A DAMAGED STEEL PIPELINE. COLUMBIA RESPONDED, ESTABLISHED A PERIMETER AND REDUCED THE SYSTEM OPERATING PRESSURE FROM 120 PSIG TO 35 PSIG. COLUMBIA EXCAVATED THE DAMAGED STEEL MAIN AND FOUND THAT IT WAS FLATTENED WITH A CRACK IN THE SIDE OF THE PIPE DUE TO A GUARD RAIL INSTALLATION. COLUMBIA REPAIR CREWS MADE A TEMPORARY REPAIR TO STOP THE LEAK AND DECIDED NOT TO RETURN THE SYSTEM BACK TO NORMAL OPERATING PRESSURE UNTIL A PERMANENT REPAIR COULD BE COMPLETED. COLUMBIA MONITORED THE DAMAGE 24/7 AND CONDUCTED PERIODIC PRESSURE MONITORING UNTIL THE PERMANENT REPLACEMENT WAS COMPLETE. ON MONDAY, MAY 18, 2015, COLUMBIA DETERMINED THAT THE COST OF REPAIR WOULD EXCEED THE $50,000 DOLLAR REPORTING CRITERIA AND A NOTIFICATION WAS MADE TO THE NATIONAL RESPONSE CENTER AND THE PUBLIC UTILITIES COMMISSION OF OHIO. THE DAMAGE TO COLUMBIA'S FACILITY OCCURRED AS A RESULT OF THE MISMARKING OF THE GAS MAIN. THE STEEL GAS MAIN COULD NOT BE CONDUCTIVELY LOCATED DUE TO SIGNAL BLEED OFF AND A DISCREPANCY IN FACILITY RECORDS. THE DISCREPANCY IN COLUMBIA'S INVENTORY RECORDS HAS BEEN CORRECTED. PLEASE CONSIDER THIS REPORT FINAL.
2025-03-31 10:13 | NO | NO | NO | 20150060 | 16157 | 2015-06-26 09:46 | SUPPLEMENTAL FINAL | 14180 | OHIO VALLEY GAS CORP | 111 ENERGY PARK DRIVE | WINCHESTER | IN | 47394 | 2015-05-26 09:15 |  |  | 2015 | 10047 OLD IN RT 37 | TELL CITY | PERRY | IN | 47586 | 37.9845 | -86.7119 | [9 empty] | 2015-05-26 12:06 | 1117562 |  | NATURAL GAS |  | 67.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2015-05-26 09:15 |  |  |  | 2015-05-26 09:24 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1988 | [5 empty] | 3 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 5 | 2.5 | [7 empty] | CLASS 2 LOCATION | 18795 | 22765.59815220497709 | 1089 | 1319.060196209163078 | 34509 | 41799.309743785131918 | 0 | 0 |  |  | 354 | 354.830985915492957746478873239436619718 |  | 0 | 54747 | 27615.4030712515883018591549295774647887 | 66238.7990781147650437464788732394366197 | 3 | 1 | 181 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  | NO |  |  | YES | YES | [8 empty] | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | TRENCHER | ELECTRIC | YES | 1505122387 | INDIANA 811 |  | UTILITY OWNER | YES | YES | 24 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | WILLIAM D. FIELDS | COMPLIANCE MANAGER | bfields@ovgc.com | 765-584-6842 | 765-584-0826 |  |  |  | WILLIAM D. FIELDS | COMPLIANCE MANAGER | 765-584-6842 | bfields@ovgc.com | CONTRACTOR (J&L SCHWARTZ CONSTRUCTION) WAS INSTALLING AN ELECTRIC SERVICE TO A REMODELED HOME. PROPERTY OWNER HAD CALLED IN A ONE CALL LOCATE REQUEST. THE GAS MAIN WAS ADEQUATELY MARKED AND A PIPELINE MARKER POST IS BY THE DAMAGE SITE. THE CONTRACTOR DUG ACROSS THE NATURAL GAS MAIN AND A TELEPHONE CABLE WITH A RENTED TRENCHER AND CUT BOTH FACILITIES. THE GAS IGNITED AND BURNED THE RENTED TRENCHER BEYOND REPAIR. THERE WERE NO INJURIES.
2025-03-31 10:13 | NO | NO | NO | 20150061 | 16140 | 2015-06-26 15:01 | SUPPLEMENTAL FINAL | 603 | CENTERPOINT ENERGY RESOURCES CORP. | 10825 E GEDDES AVE SUITE 410 | CENTENNIAL | CO | 80112 | 2015-05-28 02:34 |  |  | 2015 | NORTH OF AR RIVER @ I-430 | NORTH LITTLE ROCK | PULASKI | AR | 72118 | 34.8036 | -92.3688 | [9 empty] | 2015-05-29 11:40 | 1117951 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-05-28 02:34 |  |  |  | 2015-05-28 03:36 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | OVERHEAD CROSSING |  |  |  | YES | YES | UNCASED | [9 empty] | OTHER | PUBLICLY TRADED LDC | MAIN |  | 1975 | [5 empty] | 10 | GRADE B | REPUBLIC | STEEL |  | OTHER | UNKNOWN | 0.344 | [6 empty] | OTHER | [8 empty] | LEAK DEVELOPED DUE TO OUTSIDE STRESS CAUSED BY FLOODING / BANK EROSION. | CLASS 2 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | UNABLE TO ACCESS DAMAGE |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 200 | 200 | 280 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  | ,, | YES |  |  |  | YES | HEAVY RAINS CAUSING FLOODING AND EXTREME FLOW RATES ON THE ARKANSAS RIVER | [213 empty] | JAY REBER | DISTRICT OPERATIONS MANAGER | jay.reber@centerpointenergy.com | 501-377-4980 | 501-377-4721 |  |  |  | KEITH KITTINGER | REGIONAL OPERATIONS MANAGER | 501-377-4669 | keith.kittinger@centerpointenery.com | CURRENTLY THIS SECTION OF MAIN IS VALVED OFF AND BLIND PLATED. BIDS HAVE BEEN LET FOR REPLACEMENT OF THE DAMAGED SECTION AND WE ANTICIPATE COMPLETION OF THE PROJECT WITH GAS REINSTATED BY THE END OF THE YEAR. THIS IS OUR FINAL REPORT.
2025-03-31 10:13 | NO | NO | NO | 20150062 | 16103 | 2015-06-26 16:54 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2015-06-08 13:11 |  |  | 2015 | 6000 WALLISVILLE RD | HOUSTON | HARRIS | TX | 77020 | 29.7874 | -95.3105 | [9 empty] | 2015-06-08 14:27 | 1119070 |  | NATURAL GAS |  | 71 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-06-08 13:11 |  |  |  | 2015-06-08 13:11 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2015 | [5 empty] | 2 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 941 | 1139.793980379083982 | 1164 | 1409.904562339270728 | 0 | 0 |  |  | 417 | 417.978873239436619718309859154929577465 |  | 0 | 2522 | 1442.663597069606908732394366197183098592 | 2967.677415957791329718309859154929577465 | 0 | 0 | 0 |  |  |  |  | 35 | 35 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF THE SYSTEM | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 1564880991 | TEXAS 811 |  | UTILITY OWNER | NO |  |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO UNLOCATABLE FACILITY | [170 empty] | LESLIE J DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | REGION OPERATIONS DIRECTOR | 713-207-5700 | steve.yarbrough@centerpointenergy.com | CITY OF HOUSTON CONTRACTOR WORKING WITH A VALID ONE-CALL TICKET ON DRAINAGE SYSTEM, DAMAGED AN UNMARKED 2" PLASTIC MAIN WITH BACKHOE. RAIL TRAFFIC AT THE UNION PACIFIC RAIL YARD WAS SHUT DOWN FOR APPROX. 2 HOURS.
2025-03-31 10:13 | NO | YES | NO | 20150063 | 16167 | 2015-07-01 14:18 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2015-06-03 04:30 |  |  | 2015 | 6801 S 52ND | LINCOLN | LANCASTER | NE | 68516 | 40.744 | -96.6489 | [9 empty] | 2015-06-03 09:23 | 1118494 |  | NATURAL GAS |  | 16 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2015-06-03 05:03 |  |  |  | 2015-06-03 05:44 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1992 | [8 empty] | UNKNOWN | [10 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 250000 | 302814.5537670255 | 1300 | 1574.6356795885326 | 250 | 302.8145537670255 | 0 | 0 |  |  | 85 | 85.199530516431924882629107981220657277 |  | 0 | 251635 | 126273.1044863651235286384976525821596244 | 304777.2035308974900248826291079812206573 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 66 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | NATHAN STEWART | STATE COMPLIANCE SPECIALIST | nathan.stewart@blackhillscorp.com | 402-437-1734 | 402-437-6734 |  |  |  | NATHAN STEWART | STATE COMPLIANCE SPECIALIST | 402-437-1734 | nathan.stewart@blackhillscorp.com | AT APPROXIMATELY 0430 HOURS THE RESIDENTIAL STRUCTURE AT 6801 SOUTH 52ND STREET WAS STRUCK BY LIGHTNING, THE ENERGY SOURCE EXITED THE STRUCTURE THROUGH THE CUSTOMERS' GAS PIPING CAUSING A HOLE TO BE BLOWN IN THE SIDE WALL OF THE COPPER PIPE AND A RELEASE OF NATURAL GAS AT 2 PSIG WAS IGNITED. THE CLOSE PROXIMITY OF THE INITIAL FIRE CAUSED HEAT BUILDUP AT THE METER/REGULATING FACILITY. WITHIN A SHORT TIME SPAN THE METER/REGULATOR FAILED RELEASING GAS AT 50 PSIG. THIS RELEASE OF GAS FUELED THE FIRE, MAGNIFYING THE INTENSITY AND SPREAD. OCCUPANTS WERE ABLE TO EXIT THE STRUCTURE WITHOUT INJURY. BLACK HILLS ENERGY (BHE) WAS NOTIFIED OF THE FIRE AT 05:03 BY EMERGENCY RESPONSE CREWS. BLACK HILLS TECHNICIAN WAS DISPATCHED TO THE SCENE AT 05:07 AND ARRIVED ON THE SCENE AT 05:44 AND BEGAN WORKING WITH EMERGENCY RESPONDERS ON THE PROPER RESPONSE. ADDITIONAL CREWS WERE DISPATCHED BY BHE AT 06:01 TO DISCONNECT GAS SERVICE TO THE STRUCTURE. THIS WORK WAS COMPLETED AT 07:46. BLACK HILLS REPORTED THIS INCIDENT TO THE NRC AT 0923 (CDT) WHEN IT WAS CONCLUDED THAT THIS INCIDENT LIKELY MET THE CRITERIA FOR A REPORTABLE INCIDENT. SERVICE HAS NOT BEEN RESTORED THE THE STRUCTURE AS OF THE DATE OF THIS REPORT.
2025-03-31 10:13 | NO | YES | YES | 20150064 | 16210 | 2015-07-01 15:57 | SUPPLEMENTAL FINAL | 30750 | MIDAMERICAN ENERGY COMPANY | 666 GRAND AVENUE, SUITE 500 | DES MOINES | IA | 50309-2580 | 2015-06-04 10:35 |  |  | 2015 | 7538 NORTHEAST 114TH AVENUE | Not Within a Municipality | POLK | IA | 50035 | 41.7688 | -93.4564 | [9 empty] | 2015-06-04 13:26 | 1118659 |  | NATURAL GAS |  | 1.37 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2015-06-04 10:36 |  |  |  | 2015-06-04 11:30 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2015 | [5 empty] | 0.5 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 2406 | MECHANICAL PUNCTURE | 28 | 0.5 | [7 empty] | CLASS 2 LOCATION | 1000 | 1211.258215068102 | 813 | 984.752928850366926 | 652 | 789.740356224402504 | 975 | 1180.97675969139945 | EMERGENCY RESPONSE COST - NON OPERATOR |  | 6 | 6.01408450704225352112676056338028169014 |  | 0 | 3446 | 1731.297259698777500845070422535211267606 | 4172.74234434131313352112676056338028169 | 0 | 0 | 1 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INDIVIDUAL RESIDENTIAL SERVICE FAILURE WOULD NOT HAVE BEEN DETECTABLE BY THE CONTROL ROOM | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | NO | [5 empty] | YES | 4 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CHRISTOPHER R. PAYER | GAS STANDARDS ENGINEER | crpayer@midamerican.com | 712-277-7941 | 712-252-7369 |  |  |  | ADAM L. WRIGHT | VICE PRESIDENT GAS DELIVERY | 515-252-6945 | alwright@midamerican.com | A THIRD PARTY CONTRACTOR (C & M PLUMBING LLC) INSTALLING A DRAIN LINE FROM A GARAGE TO A POND DAMAGED A 1/2 INCH PLASTIC NATURAL GAS SERVICE LINE (60 PSIG) WITH A MINI-EXCAVATOR. THE BLOWING GAS CAUGHT FIRE AND ONE CONTRACTOR EMPLOYEE WAS INJURED FROM FIRE WITH 2ND DEGREE BURNS TO THE FACE AND ARMS. PROPERTY DAMAGE WAS LIMITED TO THE SERVICE LINE AND CONTRACTOR EQUIPMENT. AN AMBULANCE RESPONDED TO THE SITE FOR THE CONTRACTOR AND HE WAS TAKEN THE HOSPITAL FOR MEDICAL TREATMENT. THE INJURED CONTRACTOR, CLINT MAHON, WAS ADMITTED. THE PLASTIC SERVICE WAS SQUEEZED OFF SHORTLY AFTER OPERATOR CREWS ARRIVED AND WAS RESTORED THAT AFTERNOON. LOCATES WERE NOT REQUESTED OR PERFORMED PRIOR TO THE INITIAL EXCAVATION BY C & M PLUMBING LLC. THE EXACT TIME THE CONTRACTOR HIT THE PLASTIC SERVICE LINE IS NOT KNOWN. THE LOCAL TIME OF THE INCIDENT IS SHOWN ON LINE 4 IN PART A AS 10:35 WHICH IS WHEN 911 WAS NOTIFIED OF THE INCIDENT. AT 10:36, MIDAMERICAN ENERGY COMPANY WAS NOTIFIED OF THE DAMAGED PIPE. AT 13:00, MIDAMERICAN ENERGY COMPANY DETERMINED THE INJURED PARTY WAS ADMITTED TO THE HOSPITAL. MIDAMERICAN ENERGY COMPANY THEN PROMPTLY NOTIFIED THE IOWA UTILITIES BOARD AND THE NATIONAL RESPONSE CENTER AT 13:26.
2025-03-31 10:13 | NO | YES | YES | 20150065 | 16209 | 2015-07-02 10:07 | SUPPLEMENTAL FINAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDENCE BLVD | VIRGINIA BEACH | VA | 23452 | 2015-06-05 09:30 |  |  | 2015 | 2097 GENERAL BOOTH BLVD | VIRGINIA BEACH | Not Within a County or Parish | VA | 23454-5801 | 36.769 | -76.0133 | [9 empty] | 2015-06-05 11:22 | 1118741 |  | NATURAL GAS |  | 68 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | NO | 20 | 2015-06-05 09:49 |  |  |  | 2015-06-05 10:22 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1990 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | METER ASSEMBLY PIPING DAMAGED BY A PASSENGER VAN | CLASS 3 LOCATION | 1000000 | 1211258.215068102 | 3513 | 4255.150109534242326 | 3436 | 4161.883226973998472 | 0 | 0 |  |  | 291 | 291.683098591549295774647887323943661972 |  | 0 | 1007240 | 505422.7321253935706869859154929577464789 | 1219966.93150320179009377464788732394366 | 1 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELEASE OF GAS WAS TOO SMALL TO BE DETECTED BY THE SCADA SYSTEM ALARMS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | BILL ROBINSON | MANAGER DISTRIBUTION QUALITY ASSURANCE PROGRAM | brobinso@aglresources.com | 757-616-7530 | 757-616-7513 |  |  |  | KERRY CAMPBELL | VICE PRESIDENT OPERATIONS VIRGINIA NATURAL GAS | 757-466-5559 | kcampbell@aglresources.com | A PASSENGER VAN LOST CONTROL IN THE INTERSECTION OF GENERAL BOOTH BOULEVARD AND LONDON BRIDGE ROAD IN VIRGINIA BEACH AND CRASHED INTO THE MCDONALD'S RESTAURANT ON THE CORNER, HITTING AND DAMAGING THE VIRGINIA NATURAL GAS METER ADJACENT TO THE BUILDING. IT IS NOTED THAT THE METER SET WAS INSTALLED IN A VEHICLE-SAFE LOCATION AND DID HAVE VEHICLE PROTECTION POSTS. THE VEHICLE CAUGHT FIRE AND DESTROYED THE VAN; THE COMPANY'S METER SET ASSEMBLY; AND THE RESTAURANT. SUPPLEMENTAL REPORT: THE FIRE DAMAGED STRUCTURE WAS REBUILT AND GAS SERVICE WAS RESTORED ON 12/14/15 (UPDATED PART A, 13B).
2025-03-31 10:13 | NO | YES | YES | 20150066 | 16242 | 2015-07-06 12:50 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-06-06 11:38 |  |  | 2015 | S. DORT HIGHWAY & I-69 | FLINT | GENESEE | MI | 48503 | 43.0127 | -83.6541 | [9 empty] | 2015-06-06 16:35 | 1118894 |  | NATURAL GAS |  | 5883 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | NO | 3 | 2015-06-06 11:38 |  |  |  | 2015-06-06 12:06 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1997 | [5 empty] | 8 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.784 |  | 2406 | MECHANICAL PUNCTURE | 14 | 2 | [7 empty] | CLASS 3 LOCATION | 50000 | 60562.9107534051 | 7883 | 9548.348509381848066 | 668 | 809.120487665492136 | 0 | 0 |  |  | 43890 | 43993.0281690140845070422535211267605634 |  | 0 | 102441 | 70069.2210552581134256901408450704225352 | 114913.4079194665247090422535211267605634 | 3 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PIPELINE WAS DAMAGED DURING ROAD RECONSTRUCTION AND REPORTED BY THE DAMAGING PARTY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 51381293 |  |  | CONTRACT LOCATOR | NO | YES | 116 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 517-788-0509 |  |  |  |  | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | 989-791-5841 | alan.chichester@cmsenergy.com | ON SATURDAY JUNE 6, 2015 AT APPROXIMATELY 11:38 HOURS A CONTRACTOR PERFORMING ROAD RECONSTRUCTION AT THE INTERSECTION OF DORT HIGHWAY AND I-69 IN FLINT, MICHIGAN (GENESEE COUNTY) MADE CONTACT WITH AN 8" PLASTIC GAS DISTRIBUTION MAIN, CAUSING A GOUGE IN ITS UPPER QUADRANT, AND RESULTING IN BLOWING GAS. THE FLINT FIRE DEPARTMENT ARRIVED ON SITE AT APPROXIMATELY 11:50 ASSESSED THE SITUATION AND LEFT BEFORE CE PERSONNEL ARRIVE. CONSUMERS ENERGY (CE) WAS NOTIFIED AND PERSONNEL ARRIVED ON-SITE AT APPROXIMATELY 12.06 TO ASSESS THE POTENTIAL PUBLIC HAZARD, SECURE THE SITE AND ASSESS THE DAMAGE TO CE FACILITIES TO DETERMINE NEXT STEPS. AT APPROXIMATELY 13:20 THE ESCAPING GAS IGNITED RESULTING IN A FIREBALL INJURING TWO MOTORISTS TRAVELING NORTHBOUND ON DORT HWY. ONE MOTORIST WAS TRANSPORTED BY EMS TO THE LOCAL HOSPITAL AND THE SECOND MOTORIST WAS TRANSPORTED TO THE LOCAL HOSPITAL BY PRIVATE VEHICLE. BOTH MOTORISTS SUSTAINED INJURIES THAT REQUIRED OVERNIGHT HOSPITALIZATION. THE FIRE DEPARTMENT/EMS RETURNED TO THE SITE AT APPROXIMATELY 13:27 TO ASSIST THE INJURED MOTORISTS AND REQUESTED POLICE SUPPORT TO BLOCK HIGHWAY TRAFFIC.THE NORTHBOUND LANES OF DORT HWY AND A SECTION OF EAST AND WESTBOUND I-69 WERE BLOCKED AS A RESULT OF THE IGNITION. RAILROAD OPERATORS WERE ALSO NOTIFIED TO DIVERT RAIL TRAFFIC FROM THE DAMAGE SITE. THE PIPELINE WAS SQUEEZED OFF AT THE NORTH AND SOUTH SIDES OF THE DAMAGE AREA AND BLOWING GAS WAS STOPPED AT APPROXIMATELY 16:18, THE FIRE WAS EXTINGUISHED AT APPROXIMATELY 16:31. THE VEHICLES DRIVEN BY THE INJURED MOTORIST AS WELL AS A CRANE BEING UTILIZED AT THE CONSTRUCTION SITE MAY HAVE INCURRED HEAT DAMAGE.
2025-03-31 10:13 | NO | YES | YES | 20150067 | 16169 | 2015-07-10 15:56 | SUPPLEMENTAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2015-06-17 08:30 |  |  | 2015 | 102 S. MANNSTON STREET | GETTYSBURG | POTTER | SD | 57442 | 45.0111 | -99.9605 | [9 empty] | 2015-06-17 11:18 | 1120065 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 4 | 2015-06-17 08:44 |  |  |  | 2015-06-17 09:29 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 34 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1993 | [5 empty] | 2 | SDR 11 MDPE 2406 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 3 LOCATION | 160000 | 193801.31441089632 | 30000 | 36337.74645204306 | 10000 | 12112.58215068102 | 0 | 0 |  |  | 0 | 0 |  | 0 | 200000 | 100333.3650823888 | 242251.6430136204 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2013-01-01 | NO | [12 empty] | YES | YES | OTHER | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 1423888976 | PORTAL TICKET |  | UTILITY OWNER | NO | YES | 168 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | MATT KLINGENSTEIN | STAFF ENGINEER | matt.klingenstein@mdu.com | 701.222.7973 |  |  |  |  | PAT DARRAS | VP OPERATIONS | 701.222.6711 | pat.darras@mdu.com | HOME OWNER HIRED A CONTRACTOR TO INSTALL SOME "GEO LOCK EARTH ANCHORS" TO STABILIZE THE BOWING/SHEERING OF FOUNDATION WALLS. CONTRACTOR INDICATED THAT ALL WORK WOULD BE COMPLETED INSIDE A 10' PERIMETER OF THE HOME. THIS WORK WAS COMPLETE IN SEPTEMBER OF 2014. ONE OF THE ANCHORS EXTENDED IN EXCESS OF 10 FEET FROM THE HOUSE AND PUNCTURED THE MAIN IN THE ALLEY. GAS MIGRATED VIA THE ANCHOR PATH TO THE FOUNDATION AND INTO THE HOUSE. SOMETHING IGNITED THE GAS AND BOTH AN EXPLOSION AND FIRE ENSUED.
2025-03-31 10:13 | NO | YES | YES | 20150068 | 16430 | 2015-07-14 14:14 | SUPPLEMENTAL FINAL | 22435 | WEST TEXAS GAS INC | 303 VETERANS AIRPARK LANE | MIDLAND | TX | 79705 | 2015-06-25 20:30 |  |  | 2015 | INTERSECTION OF SOUTH MAIN STREET AND 8TH STREET | WHITE DEER | CARSON | TX | 79097 | 35.4297 | -101.1692 | [9 empty] | 2015-06-29 15:49 | 1121341 |  | NATURAL GAS |  | 125 |  | NO | [5 empty] | 0 | YES | 1 | 3 | 0 | 0 | 0 | 4 | YES |  |  |  |  | NO | 0 | 2015-06-25 20:30 |  |  |  | 2015-06-25 20:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | UNKNOWN | OTHER | [8 empty] | CONTRACT EMPLOYEE WAS ATTEMPTING TO REMOVE A TEMPORARY INTERNAL PIPE PLUG FROM A SYSTEM THAT WAS PRESSURIZED AND VENTING GAS WAS IGNITED. | CLASS 3 LOCATION | 0 | 0 | 5000 | 6056.29107534051 | 20000 | 24225.16430136204 | 0 | 0 |  |  | 500 | 501.173708920187793427230046948356807512 |  | 0 | 25500 | 13005.2856587727784037558685446009389671 | 30782.6290856227377934272300469483568075 | 48 | 0 | 400 |  |  |  |  | 13 | 13 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | CONTRACT EMPLOYEE WAS ATTEMPTING TO REMOVE A TEMPORARY INTERNAL PIPE PLUG FROM A SEGMENT OF SYSTEM THAT WAS PRESSURIZED AND VENTING GAS WAS ACCIDENTLY IGNITED. | [47 empty] | RAY REED | DIRECTOR OF INTGRITY MANAGEMENT | rreed@westtexasgas.com | (806)358-1321 | (806)354-0797 |  |  |  | RICHARD HATCHETT | VICE PRESIDENT | (432)682-4349 | rhatchett@westtexasgas.com | ON JUNE 26, 2015 AT APPROXIMATELY 8:30 PM, A CONTRACT EMPLOYEE WAS ATTEMPTING TO REMOVE A 2" TEMPORARY INTERNAL PIPE PLUG FROM A SYSTEM THAT WAS PRESSURIZED. DURING THIS PROCESS THE VENTING GAS WAS ACCIDENTLY IGNITED BY AN UNKNOWN SOURCE.
2025-03-31 10:13 | NO | YES | NO | 20150069 | 16116 | 2015-07-14 15:07 | ORIGINAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2015-06-14 |  |  | 2015 | KINGS HIGHWAY AND EAST 98TH STREET | BROOKLYN | KINGS | NY | 11212 | 40.662 | -73.9196 | [9 empty] | 2015-06-16 11:00 | 1119934 |  | NATURAL GAS |  | 0.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-06-14 21:00 |  |  |  | 2015-06-14 21:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1972 | [5 empty] | 12.75 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS | SEAMLESS | 0.375 | [6 empty] | MECHANICAL PUNCTURE | 2.5 | 2.5 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 1000000 | 1211258.215068102 | 28500 | 34520.859129440907 | 0 | 0 |  |  | 10 | 10.02347417840375586854460093896713615023 |  | 0 | 1028510 | 515973.6022366538875680751173708920187793 | 1245789.09767172131075586854460093896714 | 60 | 10 | 1297 |  |  |  |  | 0 | 0.25 | 0.64 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ABNORMAL CONDITIONS DETECTED IN THE SURROUNDING AREA. THE INCIDENT WAS DETECTED AS A RESULT OF CUSTOMER CALLS OF NO GAS WITHIN THE 1-MILE BOUNDARY OF FLOODING. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | 60" STEEL WATER MAIN, OPERATING IN THE RANGE OF 90 TO 105 PSI, RUPTURED IN CLOSE PROXIMITY TO NATIONAL GRID 12" STEEL LP MAIN . JETTING CAUSED BY THE WATER PRESSURE BORE A 2.5" HOLE INTO 12" STEEL LP MAIN. | [154 empty] | CORINNE BYRNES | PRIN PROG MGR OPERATIONS CODES AND POLICY | corinne.byrnes@nationalgrid.com | 5164924469 |  |  |  |  | CORINNE BYRNES | PRIN PROG MGR- OPERATIONS CODES AND POLICY | 5164924469 | corinne.byrnes@gmail.com | A 60" STEEL WATER MAIN, OPERATING IN THE RANGE OF 90 TO 105 PSI, RUPTURED IN CLOSE PROXIMITY (6" BELOW) TO NATIONAL GRID 12" STEEL LP MAIN . JETTING CAUSED BY THE WATER PRESSURE BORE A 2.5" HOLE INTO 12" STEEL LP MAIN. THE RAPID ESCAPE OF THE WATER FLOODED THE GAS MAIN, RESULTING IN A 1-MILE PIPELINE OUTAGE, ALONG WITH 98 SERVICE OUTAGES AFFECTING 1367 CUSTOMERS. NATIONAL GRID RECEIVED MULTIPLE SERVICE CALLS FROM CUSTOMERS STARTING AT 3 PM ON 6/14/2015, RESPONDED TO THOSE CALLS, AND BY 9 PM DETERMINED THE CAUSE OF THE MULTIPLE OUTAGES.
2025-03-31 10:13 | NO | YES | YES | 20150070 | 16117 | 2015-07-14 21:47 | ORIGINAL FINAL | 6243 | HAWAI`IGAS | 515 KAMAKEE STREET (P.O. BOX 3000) | HONOLULU | HI | 96802-3000 | 2015-06-15 21:30 |  |  | 2015 | 645 KAPAHULU AVE | HONOLULU | HONOLULU | HI | 96815 | 21.2795 | -157.814 | [9 empty] | 2015-06-16 00:08 | 1119900 |  | SYNTHETIC GAS |  | 160 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2015-06-15 21:38 |  |  |  | 2015-06-15 22:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 8 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1977 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 9.5 | 0.5 | [7 empty] | CLASS 4 LOCATION | 500000 | 605629.107534051 | 100000 | 121125.8215068102 | 10000 | 12112.58215068102 | 0 | 0 |  |  | 3900 | 3909.154929577464788732394366197183098592 |  | 0 | 613900 | 309632.9606843844315492957746478873239437 | 742776.6661211196847887323943661971830986 | 2 | 0 | 8 |  |  |  |  | 12 | 12 | 17 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATION DAMAGE CAUSED BY THIRD PARTY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY | 2014-01-01 | NO |  |  | YES | YES | YES | YES | [6 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | MILLING EQUIPMENT | MILLING | YES | 15001196 |  |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CHRISTOPHER HALL | IMP ENGINEER | chall@hawaiigas.com | 808-594-5553 |  |  |  |  | THOMAS YOUNG | EXECUTIVE VP AND COO | 808-535-5935 | tkyoung@hawaiigas.com | INCIDENT SUMMARY ON 06/15/2015, ROAD BUILDERS ("RB") WAS COLD PLANING A PORTION OF KAPAHULU AVENUE IN HONOLULU WITH AN ASPHALT MILLING MACHINE. BETWEEN 2115 AND 2130, THE MACHINE STRUCK A HAWAII GAS ("HG") UNDERGROUND MAIN LINE, CAUSING AN APPROXIMATELY 9.5-INCH TEAR IN THE MAIN. THE DAMAGED SEGMENT WAS 4-INCH STEEL PIPE COATED WITH XTC ("SUBJECT SEGMENT"). THE SUBJECT SEGMENT BEGAN TO LEAK GAS AND AT AN UNVERIFIED TIME, THE GAS IGNITED AROUND THE MACHINE. TWO RB EMPLOYEES WERE INJURED IN CONNECTION WITH THE FIRE AND ONE REQUIRED INPATIENT HOSPITALIZATION. THE HONOLULU FIRE DEPARTMENT ("HFD") RESPONDED AND DIRECTED WATER AT THE MACHINE TO PREVENT ITS FUEL TANKS FROM OVERHEATING. HG STOPPED THE FLOW OF GAS TO THE SUBJECT SEGMENT AT APPROXIMATELY 0253 ON 06/16/2015, THE FIRE DISSIPATED SHORTLY THEREAFTER AND HFD ANNOUNCED AN "ALL CLEAR" AT APPROXIMATELY 0300. HG PRE-INCIDENT ACTIVITY HG INSTALLED THE SUBJECT SEGMENT IN 1977. ON 02/09/2015, RB SUBMITTED ONE CALL TICKET 15001196 (THE "TICKET") TO THE HAWAII ONE CALL CENTER STATING THAT RB WOULD BE EXCAVATING AN AREA OF KAPAHULU AVENUE (THE "EXCAVATION AREA"), INCLUDING THE SUBJECT SEGMENT. HG RESPONDED TO THE TICKET BY REVIEWING EXCAVATION AREA MAPS AND DETERMINING THAT AN UNDERGROUND MAIN WAS LOCATED THEREIN. ON 02/19/2015, HG PERFORMED CONDUCTIVE AND INDUCTIVE TONING IN THE EXCAVATION AREA AND MARKED THE APPROXIMATE LOCATION OF THE MAIN LINE ON THE ROADWAY SURFACE WITH YELLOW PAINT. HG RESPONSE TO INCIDENT HG WAS ALERTED TO THE INCIDENT IN TWO WAYS: 1) THE HG SYNTHETIC NATURAL GAS PLANT RECORDED A PRESSURE IRREGULARITY IN THE GAS PIPELINE AND NOTIFIED HG DISPATCH AT APPROXIMATELY 2130; AND 2) HFD NOTIFIED HG DISPATCH AT APPROXIMATELY 2138. AN HG OPERATIONS SUPERINTENDENT ARRIVED AT THE SCENE AT APPROXIMATELY 2200. OTHER HG PERSONNEL WERE NOTIFIED BETWEEN 2145 AND 2215, AND BEGAN ARRIVING AT THE HG KAMAKEE BASEYARD BETWEEN 2215 AND 2300. THE HG SUPERVISORY TEAM CONCLUDED THAT THE MAIN LINE WOULD NEED TO BE EXCAVATED AND STOPPED AT THREE LOCATIONS: NORTH, SOUTH AND WEST OF THE INCIDENT. HG PERSONNEL INSTALLED LINE STOPPERS AT THE NORTH AND SOUTH SITES AND PINCHED THE LINE AT THE WEST SITE. GAS FLOW TO THE SUBJECT SEGMENT WAS STOPPED AT APPROXIMATELY 0253 ON 06/16/15. STATUTORY AND REGULATORY CONTEXT (1) HAWAII ONE CALL STATUTE THE HAWAII ONE CALL STATUTE REQUIRES AN EXCAVATOR TO PROVIDE EXCAVATION LOCATION TO THE ONE CALL CENTER PRIOR TO EXCAVATING, AND THE CENTER NOTIFIES UTILITY OPERATORS ABOUT THE PROPOSED EXCAVATION. THE OPERATOR LOCATES AND MARKS ON THE ROADWAY THE APPROXIMATE LOCATION OF INSTALLATIONS THAT MAY BE AFFECTED BY THE EXCAVATION, BUT IS NOT REQUIRED TO MARK DEPTH UNDER THE STATUTE. THE EXCAVATOR MUST THEN USE HAND TOOLS TO DETERMINE THE EXACT LOCATION OF THE INSTALLATION. HERE, HG RESPONDED TO THE TICKET BY REVIEWING MAPS, PERFORMING TONING AND MARKING THE ALIGNMENT--BUT NOT DEPTH--OF THE GAS MAIN IN THE EXCAVATION AREA WITH YELLOW PAINT. HG WAS IN FULL COMPLIANCE WITH THE ONE CALL STATUTE. RB DOES NOT APPEAR TO HAVE HAND EXCAVATED AND LOCATED THE SUBJECT SEGMENT IN COMPLIANCE WITH THE STATUTE. (2) SUBJECT SEGMENT DEPTH FEDERAL REGULATIONS IN 1977 REQUIRED 24-INCH COVER FOR A MAIN LINE. A MAIN LINE CAN BE INSTALLED WITH LESS THAN 24-INCH COVER IF AN UNDERGROUND STRUCTURE PREVENTS SUCH INSTALLATION AND THE LINE IS PROVIDED WITH ADDITIONAL PROTECTION. ON 06/16/2015, THE SUBJECT SEGMENT WAS MEASURED AT APPROXIMATELY 8 INCHES BELOW THE ROADWAY SURFACE. IF THE SUBJECT SEGMENT WAS INSTALLED WITH LESS THAN 24-INCH COVER IN 1977, THE ABOVE EXCEPTION APPLIES. CITY RECORDS INDICATE THAT A CONDUIT STRUCTURE RUNS DIRECTLY BELOW THE SUBJECT SEGMENT, PREVENTING INSTALLATION OF THE SUBJECT SEGMENT AT 24-INCH DEPTH. THE SUBJECT SEGMENT WAS ENCASED IN CONCRETE, PROVIDING THE ADDITIONAL PROTECTION REQUIRED FOR MAINS INSTALLED WITH LESS THAN 24-INCH COVER. PLEASE CONTACT HG FOR ADDITIONAL NARRATIVE DETAIL IN PDF FORMAT.
2025-03-31 10:13 | NO | YES | NO | 20150071 | 16318 | 2015-07-15 16:15 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2015-06-16 11:15 |  |  | 2015 | 1195 LONG POINT DRIVE | LAKE TOWNSHIP | ROSCOMMON | MI | 48629 | 44.3701 | -84.7721 | [9 empty] | 2015-07-13 16:43 | 1122665 |  | NATURAL GAS |  | 2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2015-06-16 11:15 |  |  |  | 2015-06-16 11:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1968 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.062 |  | 3408 | LEAK |  |  | OTHER | SEVERED | [5 empty] | CLASS 3 LOCATION | 500000 | 605629.107534051 | 17 | 20.591389656157734 | 1260 | 1526.18535098580852 | 131 | 158.674826173921362 | SUPPORT COST FOR PROCESSING DAMAGES |  | 10 | 10.02347417840375586854460093896713615023 |  | 0 | 501418 | 251549.0318966215007200751173708920187793 | 607344.5825750452913718685446009389671362 | 0 | 0 | 2 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | HOMEOWNER HIT OUTSIDE METER MANIFOLD WITH RIDING LAWN MOWER CAUSING NATURAL GAS LEAK. | [154 empty] | ROBERT FRECKELTON | MANAGER | freckeltonr@dteeenergy.com | 313-389-7755 | 313-389-7755 |  |  |  | FRENAE SMITH | MANAGER | 313-389-7762 | smithff@dteeenergy.com | ON JUNE 16, 2015, DTE GAS RECEIVED AN EMERGENCY ORDER STATING "HOME ON FIRE WITH GAS LEAK" AT 1195 LONG POINT, LAKE TOWNSHIP, ROSCOMMON COUNTY, MI. HOMEOWNER HIT OUTSIDE METER MANIFOLD WITH RIDING LAWN MOWER CAUSING NATURAL GAS LEAK. AS A RESULT, THE GAS IGNITED AND BURNED DOWN THE HOMES AT 1195 AND 1205 LONG POINT DRIVE TO CATCH FIRE.
2025-03-31 10:13 | NO | YES | NO | 20150072 | 16195 | 2015-07-17 15:37 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-06-18 11:46 |  |  | 2015 | 1716 STUTZ DR. | TROY | OAKLAND | MI | 48084 | 42.5519 | -83.1804 | [9 empty] | 2015-06-18 13:41 | 1120188 |  | NATURAL GAS |  | 103 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 50 | 2015-06-18 11:46 |  |  |  | 2015-06-18 12:06 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 10 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1986 | [5 empty] | 1.125 | ASTMD3350 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 300000 | 363377.4645204306 | 3855 | 4669.40041908753321 | 300 | 363.3774645204306 | 0 | 0 |  |  | 768 | 769.802816901408450704225352112676056338 |  | 0 | 304923 | 153296.5859592261653481690140845070422535 | 369180.0452209399722607042253521126760563 | 5 | 0 | 0 |  |  |  |  | 25 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTRACTOR RESPONSIBLE FOR THE DAMAGE NOTIFIED CONSUMERS ENERGY DISPATCH OF THE DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | MILLING EQUIPMENT | ROAD WORK | YES | 51550867 |  |  | CONTRACT LOCATOR | YES | YES | 3 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | DATA NOT COLLECTED | [169 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 517-788-0509 |  |  |  |  | ALAN M. CHICHESTER | GAS REGULATORY SERVICES ENGINEER | 989-791-5841 | alan.chichester@cmsenergy.com | ON JUNE 18, 2015 AT APPROXIMATELY 11:46 LOIS KAY CONTRACTING (SUB-CONTRACTOR FOR FENTON EXCAVATING AND CONSTRUCTION, INC.) WAS OPERATING A ROAD TEC RX-700 MILLING MACHINE TO REMOVE THE ASPHALT SURFACE OF THE ROADWAY WHEN CONTACT WAS MADE WITH A 1-1/8" PLASTIC SERVICE LINE AT 1716 STUTZ RD., TROY, MI (OAKLAND COUNTY) CAUSING A RELEASE OF GAS. THE ESCAPING GAS IGNITED AND THE MILLING MACHINE WAS ENGULFED IN FLAMES. LOIS KAY EMPLOYEES WERE AWARE THE GAS SERVICE HAD BEEN HIT AND EXITED THE MACHINE PRIOR TO THE IGNITION. NO INJURIES OCCURRED AS A RESULT OF THE FIRE. CONSUMERS ENERGY DISTRIBUTION PERSONNEL ARRIVED ONSITE AT APPROXIMATELY 12:46. THE MAIN WAS SQUEEZED OFF EAST OF THE SERVICE TEE AT 1716 STUTZ (DAMAGED SERVICE) STOPPING THE FLOW OF GAS AT 13:00. THE MAIN WAS A ONE-WAY FEED AND SERVICE WAS INTERRUPTED TO FIVE CUSTOMERS WEST OF THE SQUEEZE OFF LOCATION. GAS WAS RESTORED AT 15:30 AND SERVICE RESTORATION BEGAN IMMEDIATELY FOLLOWING. TAGS TO CONTACT CONSUMERS ENERGY TO HAVE SERVICE RESTORED WERE LEFT AT THOSE LOCATIONS IN WHICH ENTRY WAS UNAVAILABLE.
2025-03-31 10:13 | NO | YES | NO | 20150073 | 16122 | 2015-07-17 17:40 | ORIGINAL FINAL | 2288 | CHATTANOOGA GAS CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2015-06-18 10:28 |  |  | 2015 | 3901 HIXSON PIKE | CHATTANOOGA | HAMILTON | TN | 37415 | 35.1145 | -85.264 | [9 empty] | 2015-06-18 12:00 | 1120168 |  | NATURAL GAS |  | 39.64 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 20 | 2015-06-18 10:28 |  |  |  | 2015-06-18 10:28 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 18 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1970 | [5 empty] | 1.25 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.14 | [6 empty] | OTHER | [8 empty] | 1-1/4 INCH STEEL PIPE WAS PULLED OUT OF COMPRESSION FITTING | CLASS 3 LOCATION | 0 | 0 | 5411 | 6554.118201733499922 | 500 | 605.629107534051 | 500000 | 605629.107534051 | DAMAGE TO MILLING MACHINE, TRANSFORMER, AND POWER LINES |  | 100 | 100.234741784037558685446009389671361502 |  | 0 | 506011 | 253891.4883156768366647511737089201877934 | 612889.0895851025884806854460093896713615 | 7 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  | YES | [6 empty] | YES |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | MILLING EQUIPMENT | MILLING | YES | 151627229 |  |  | CONTRACT LOCATOR | YES | YES | 24 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@aglresources.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R. LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@aglresources.com | A SPOTTED AND EXPOSED FOR EXCAVATION 1-1/4 INCH STEEL NATURAL GAS SERVICE WAS PULLED OUT OF A COMPRESSION FITTING BY A MILLING MACHINE DURING MILLING OPERATIONS TO REPAVE ASPHALT PAVING BEHIND A STRIP SHOPPING CENTER. THE ESCAPING GAS IGNITED BURNING THE MILLING MACHINE, TRANSFORMER, AND POWER LINES ABOVE THE INCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20150074 | 16170 | 2015-07-17 17:51 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2015-06-18 09:26 |  |  | 2015 | 14360 SE EASTGATE WAY | BELLEVUE | KING | WA | 98007 | 47.5805 | -122.1489 | [9 empty] | 2015-06-18 10:14 | 1120179 |  | NATURAL GAS |  | 13 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 2 | 0 | 2 | YES |  |  |  |  | NO | 55 | 2015-06-18 09:26 |  |  |  | 2015-06-18 09:33 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1981 | [5 empty] | 1.25 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3406 | LEAK |  |  | OTHER | HEAT MELTED PE PIPE; LEAKED | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 6301 | 7632.138013144110702 | 2530 | 3064.48328412229806 | 0 | 0 |  |  | 141 | 141.330985915492957746478873239436619718 |  | 0 | 8972 | 4560.959171832595773859154929577464788732 | 10837.9522831819017197464788732394366197 | 2 | 0 | 0 |  |  |  |  | 26.5 | 28 | 32 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | TWO EMPLOYEES OF MACDONALD-MILLER CONTRACTORS (NON-OPERATOR CONTRACTORS) WERE SOLDERING ON A COPPER WATER PIPE IN AN OPEN EXCAVATION OUTSIDE OF THE BUILDING. THE HEAT PRODUCED WHILE SOLDERING THE COPPER WATER PIPE MELTED A NEARBY 1 1/4" PE GAS MAIN THAT RAN PERPENDICULAR TO THE WATER PIPE. GAS ESCAPED FROM THE MELTED PE PIPE AND IGNITED, AND THE WORKERS WERE TRANSPORTED TO THE HOSPITAL WITH BURNS. | [154 empty] | STEPHANIE SILVA | GAS COMPLIANCE PROGRAM MANAGER | stephanie.silva@pse.com | 425.462.3923 |  |  |  |  | CHERYL MCGRATH | MANAGER COMPLIANCE PROGRAMS | 425.462.3207 | cheryl.mcgrath@pse.com | TWO EMPLOYEES OF MACDONALD-MILLER CONTRACTORS (NOT AFFILIATED WITH OPERATOR) WERE SOLDERING ON A COPPER WATER PIPE IN AN OPEN EXCAVATION OUTSIDE OF THE BUILDING. THE HEAT PRODUCED WHILE SOLDERING THE COPPER WATER PIPE MELTED A NEARBY 1 1/4" PE GAS MAIN THAT RAN PERPENDICULAR TO THE WATER PIPE. GAS ESCAPED FROM THE MELTED PE PIPE AND IGNITED, AND THE WORKERS WERE TRANSPORTED TO THE HOSPITAL WITH BURNS. THE FIRE DEPARTMENT EVACUATED APPROXIMATELY 55 PEOPLE FROM THE BUILDING. THE PE MAIN WAS SQUEEZED SHUTTING OFF THE FLOW OF GAS. A PERMANENT REPAIR OF THE PE MAIN WAS COMPLETED BY REPLACING THE SECTION THAT HAD MELTED. THE BUILDING SUSTAINED SOME DAMAGE FROM THE FIRE BUT COSTS TO THE BUILDING OWNER ARE UNKNOWN AT THIS TIME. NO MAJOR STRUCTURAL DAMAGE TO THE BUILDING.
2025-03-31 10:13 | YES | NO | NO | 20150075 | 16216 | 2015-07-17 18:11 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2015-06-18 14:32 |  |  | 2015 | 2421 OREGON STREET | UNION CITY | ALAMEDA COUNTY | CA | 94587 | 37.59 | -122.0328 | [9 empty] | 2015-06-18 19:07 | 1120254 |  | NATURAL GAS |  | 0.5 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 10 | 2015-06-18 18:00 |  |  |  | 2015-06-18 16:44 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | METER SET MELTED FROM HEAT OF THE FIRE | CLASS 3 LOCATION | 50000 | 60562.9107534051 | 5000 | 6056.29107534051 | 0 | 0 | 0 | 0 |  |  | 5 | 5.01173708920187793427230046948356807512 |  | 0 | 55005 | 27596.3115478916617840375586854460093897 | 66624.2135658348118779342723004694835681 | 0 | 0 | 4 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 925-328-6107 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | ON JUNE 18, 2015 AT 1632 HOURS, PG&E WAS NOTIFIED OF A STRUCTURE FIRE AT 2421 OREGON STREET (AT ALVARADO NILES ROAD) IN UNION CITY. THE FIRE APPEARS TO HAVE STARTED IN A CARPORT AREA, WHICH THEN MIGRATED TO THE OPPOSITE SIDE OF THE BUILDING WHERE THE METER SET IS LOCATED. THE FIRE MELTED A 5-METER MANIFOLD AND REGULATOR, CAUSING AN UNINTENTIONAL RELEASE OF GAS WHICH SUBSEQUENTLY IGNITED. THIS IS A FIRE FIRST INCIDENT AS PG&E'S FACILITIES WERE SECONDARILY INVOLVED. THE ALAMEDA COUNTY FIRE REPORT STATES "EXTERIOR INVESTIGATION OF UTILITIES DID NOT PROVIDE ANY EVIDENCE OF FAILURE OF ELECTRIC OR GAS SYSTEM." PG&E'S GAS SERVICE REPRESENTATIVE ARRIVED ON SITE AT 1644 HOURS AND OBSERVED THAT GAS HAD ALREADY BEEN SHUT OFF AT THE SERVICE VALVE BY FIRE OFFICIALS. THE GSR REMOVED THE REGULATOR, PLUGGED THE SERVICE VALVE, CONDUCTED A LEAK TEST OF THE VALVE AND DID NOT DETECT ANY LEAKS. THE APARTMENT COMPLEX WAS DAMAGED FROM THE FIRE AND TWO NEARBY BUILDINGS WERE EVACUATED. A SPECIAL LEAK SURVEY OF THE SURROUNDING AREA WAS PERFORMED AND NO LEAKS WERE DETECTED. THE TOTAL COST OF DAMAGES IS ESTIMATED TO EXCEED $50,000. ONE FATALITY WAS REPORTED AS A RESULT OF THIS INCIDENT. BAY AREA NEWS MEDIA WAS ALSO OBSERVED ONSITE DURING THE INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20150076 | 16126 | 2015-07-24 18:21 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2015-06-25 15:20 |  |  | 2015 | 8239 DON AVENUE | STOCKTON | SAN JOAQUIN COUNTY | CA | 95209 | 38.0251 | -121.3456 | [9 empty] | 2015-06-25 16:54 | 1120986 |  | NATURAL GAS |  | 30 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 10 | 2015-06-25 15:22 |  |  |  | 2015-06-25 15:41 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | VEHICLE IMPACT | CLASS 3 LOCATION | 50000 | 60562.9107534051 | 7000 | 8478.807505476714 | 0 | 0 | 0 | 0 |  |  | 165 | 165.387323943661971830985915492957746479 |  | 0 | 57165 | 28748.0020062272868732394366197183098592 | 69207.1055828254759718309859154929577465 | 0 | 0 | 4 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | WINI CHEN | COMPLIANCE PROGRAM MANAGER | wcce@pge.com | 925-328-5798 |  |  |  |  | LARRY DENISTON | MANAGER OF GAS OPERATIONS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | PG&E WAS NOTIFIED ABOUT A VEHICLE IMPACT INCIDENT AND FIRE AT 1522 HOURS ON JUNE 25, 2015. THE INCIDENT OCCURRED AT 8239 DON AVENUE IN STOCKTON. THE VEHICLE DROVE THROUGH A FENCE, STRUCK THE METER SET AND SERVICE RISER, CAUSING AN UNINTENTIONAL RELEASE OF NATURAL GAS AND IGNITION. THIS METER DID NOT MEET THE REQUIREMENTS FOR ADDITIONAL METER PROTECTION. PG&E GAS SERVICE REPRESENTATIVE ARRIVED ON SCENE AT 1541 HOURS. ACCORDING TO STOCKTON POLICE, THE DRIVER OF THE VEHICLE SUSTAINED INJURIES (I.E., SCRAPES, BRUISES, ETC.) DUE TO THE VEHICLE IMPACT THAT DID NOT RESULT IN IN-PATIENT HOSPITALIZATION. GAS WAS SHUT IN AT 1647 HOURS BY EXCAVATING AND SQUEEZING THE PLASTIC SERVICE LINE. THE SERVICE LINE WAS CUT OFF BELOW GROUND, AT THE POINT WHERE IT BRANCHES OFF FROM THE ADJACENT SERVICE LINE. FOUR CUSTOMERS (TWO DUPLEX BUILDINGS) LOST GAS SERVICE AS A RESULT OF THE INCIDENT. TWO CUSTOMERS HAD GAS SERVICE RESTORED BY 1900 HOURS. GAS SERVICE FOR THE TWO CUSTOMERS AT 8239 DON AVENUE WILL BE RESTORED ONCE THE DUPLEX STRUCTURE IS REPAIRED AND AT THE REQUEST OF THE CUSTOMERS. FIRE OFFICIALS, POLICE, AMBULANCE (EMT PERSONNEL), AND LOCAL MEDIA (STOCKTON 10 NEWS) WERE OBSERVED ON SCENE. THERE WERE NO FATALITIES REPORTED, AND NO INJURIES DUE TO THE ESCAPING NATURAL GAS. THE INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO DAMAGES FROM THE FIRE ESTIMATED TO EXCEED $50,000. AFTER THE INCIDENT, A LEAK SURVEY OF PG&E'S GAS FACILITIES WAS PERFORMED AND NO LEAKS WERE DETECTED.
2025-03-31 10:13 | NO | NO | NO | 20150077 | 16128 | 2015-07-29 15:45 | ORIGINAL | 1184 | BAY CITY MUNICIPAL GAS SYSTEM | 1100 6TH STREET | BAY CITY | TX | 77414 | 2015-07-25 15:05 |  |  | 2015 | 615 2ND STREET | BAY CITY | MATAGORDA | TX | 77414 | 28.9774 | -95.9821 | [9 empty] | 2015-07-25 17:20 | 1123830 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2015-07-25 15:05 |  |  |  | 2015-07-25 15:20 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 11 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 9000 | 10901.323935612918 | 150 | 181.6887322602153 | 300 | 363.3774645204306 | 0 | 0 |  |  | 2 | 2.00469483568075117370892018779342723005 |  | 0 | 9452 | 4742.605960236767513615023474178403755869 | 11448.3948272292446511737089201877934272 | 0 | 0 | 1 |  |  |  |  | 25 | 25 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | TRENCHER | IRRIGATION | NO | [5 empty] | YES | 2 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | LEO GARZA | OPERATIONS MANAGER | leo@baycitygas.com | 979.245.2194 | 979.244.1422 |  |  |  | KEVIN HECHT | DIRECTOR | 9792452194 | kevin@baycitygas.com | LAWN SPRINKLER SYSTEM BEING INSTALLED AT PRIVATE RESIDENCE. LOCATE REQUESTS WERE RECEIVED, KNOWN LINES WERE MARKED. INSTALLER USING WALK-BEHIND TRENCH HIT AND CUT AN UNKNOWN SERVICE LINE AT APPROXIMATELY 11 INCHES OF DEPTH. INSTALLER EVACUATED PERSONNEL AND TRENCHER LATER IGNITED ESCAPING GAS, DESTROYING TRENCHER. NO OTHER PROPERTY DAMAGES, NO INJURIES. LINE WAS SQUEEZED OFF BY GAS COMPANY PERSONNEL AND LATER REPAIRED TO RESTORE SERVICE TO RESIDENCE.
2025-03-31 10:13 | NO | NO | NO | 20150078 | 16294 | 2015-08-05 14:50 | SUPPLEMENTAL FINAL | 30769 | MISSOURI GAS ENERGY | 3420 BROADWAY | KANSAS CITY | MO | 64111 | 2015-07-06 07:35 |  |  | 2015 | PLEASANT VALLEY STREET & I-35 | PLEASANT VALLEY | CLAY | MO | 64068 | 39.2132 | -94.4791 | [9 empty] | 2015-07-06 10:45 | 1121959 |  | NATURAL GAS |  | 4471 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-07-06 07:54 |  |  |  | 2015-07-06 08:10 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1959 | [5 empty] | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 11 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 26301 | 31857.302314506150702 | 500 | 605.629107534051 | 0 | 0 |  |  | 23483 | 23538.1244131455399061032863849765258216 |  | 0 | 50284 | 35219.3157803537740547981220657276995305 | 56001.0558351857416081032863849765258216 | 20 | 0 | 190 |  |  |  |  | 30 | 30 | 33 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOTIFICATION FROM THE THIRD PARTY OF DIRECT CAUSE OF MECHANICAL PUNTURE FROM GRADER. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | INTERSTATE HIGHWAY | [12 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | YES | 151820607 |  |  | CONTRACT LOCATOR | YES | YES | 9 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | PATRICK SEAMANDS | MANAGER OF PIPELINE SAFETY AND COMPLIANCE | patrick.seamands@thelacledegroup.com | (314) 349-2936 |  |  |  |  | CRAIG R. HOEFERLIN | VICE PRESIDENT OF OPERATIONS SERVICES | (314) 349-2972 | craig.hoeferlin@thelacledegroup.com | A CONTRACTOR OPERATING A GRADER FAILED TO OBSERVE FACILITY LOCATION MARKS AND PUNCTURED AN APPROXIMATELY 22 SQUARE INCH HOLE IN A 12 INCH STEEL MAIN. IT IS OUR UNDERSTANDING THE CONTRACTOR WAS UNDER THE IMPRESSION THE 12 INCH STEEL MAIN WAS RELOCATED AS A RESULT OF A RECENT MAIN RELOCATION PROJECT. THE CONSTRUCTION PLANS DID NOT INDICATE THE 12 INCH STEEL MAIN WAS TO BE RELOCATED. EMERGENCY RESPONDERS WERE ON-SITE AND ASSISTED IN TRAFFIC CONTROL. GAS WAS MADE SAFE BY CLOSING A 6 INCH VALVE ON CHURCH ROAD, NORTH OF THE DAMAGE, STOPPLING A 6 INCH THREE-WAY TEE, NORTHEAST OF DAMAGE AT PLEASANT VALLEY ROAD AND LIBERTY PARKWAY, CLOSING THE OUTLET VALVE OF REGULATOR STATION #007, SOUTH OF DAMAGE AT HIGHWAY 69 AND SQUEEZING OFF A 6 INCH PLASTIC MAIN ON PLEASANT VALLEY ROAD, WEST OF CHURCH ROAD. A 30 INCH LONG FULL CIRCUMFERENTIAL BAND AND A 48 INCH LONG SLEEVE WERE WELDED OVER THE DAMAGED SECTION OF PIPE. REPAIRS WERE COMPLETED AT 16:27 ON JULY 6, 2016, AND SERVICE TECH BEGAN RELIGHTING 210 CUSTOMERS WHO LOST SERVICE.
2025-03-31 10:13 | NO | NO | NO | 20150079 | 16130 | 2015-08-05 17:11 | ORIGINAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2015-07-07 18:47 |  |  | 2015 | VAR. LOC'S IN NORTHERN QUEENS | QUEENS | QUEENS | NY | 11211 | 40.7138 | -73.8283 | [9 empty] | 2015-07-07 21:02 | 1122119 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-07-07 18:47 |  |  |  | 2015-07-07 19:17 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | OTHER | VARIOUS ODOR COMPLAINTS |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | CUSTOMER GAS ODOR COMPLAINTS | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | MALODOROS CONDITION IDENTIFIED BY VAR. CUSOTMER REPORTED GAS ODOR COMPLAINTS IN NORTHERN QUEENS. SUBSEQUENT INVESTIGATION REVEALED EXCESS ODORANT INJECTION FROM LNG LIQUEFACTION PROCESS. | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 60385 | 73141.82731688733927 | 0 | 0 |  |  | 0 | 0 |  | 0 | 60385 | 30293.15125250023844 | 73141.82731688733927 | 0 | 0 | 0 |  |  |  |  | 10.5 | 12 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT THE RESULT OF ANY OPERATION THAT THE CONTROL ROOM CAN DETECT UNDER PRESENT OPERATING CONDITIONS AND ALARMS. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | LIQUEFACTION PLANT FEED GAS PURIFICATION PROCESS REINJECTION SYSTEM (MERCAPTAN/MOISTURE) REQUIRES ADJUSTMENT TO ENSURE PROPER INJECTION RATIO INTO DISTRIBUTION SYSTEM. | [47 empty] | CORINNE BYRNES | PRIN PROG MGR OPERATIONS CODES AND POLICY | corinne.byrnes@nationalgrid.com | 5165452425 |  |  |  |  | CORINNE BYRNES | PRIN PROG MGR- OPERATIONS CODES AND POLICY | 5164924469 | corinne.byrnes@gmail.com | MULTIPLE GAS ODOR COMPLAINTS WERE RECEIVED AND INVESTIGATED BY CUSTOMER CALL CENTER. THE NATIONAL RESPONSE CENTER WAS NOTIFIED OUT OF AN ABUNDANCE OF CAUTION DUE TO THE CALL VOLUME. SUBSEQUENT CHEMICAL ANALYSIS OF HTE GAS REVEALED EXCESS ODORANT CONCENTRATIONS. IT WAS LATER DETERMINED THAT THE LIQUEFACTION PANT FEED GAS PURIFICATION PROCESS REINJECTION SYSTEM (MERCAPTAN/MOISTURE) REQUIRES ADJUSTMENT TO ENSURE PROPER INJECTION RATIO INTO DISTRIBUTION SYSTEM.
2025-03-31 10:13 | NO | NO | NO | 20150080 | 16131 | 2015-08-06 16:54 | ORIGINAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2015-07-07 11:00 |  |  | 2015 | 1215 AND 1217 REBECCA AVE | NORTH BRADDOCK | ALLEGHANY | PA | 15104 | 40.3996 | -79.8584 | [9 empty] | 2015-07-07 13:04 | 1122076 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | YES | 2 | 2015-07-07 10:59 |  |  |  | 2015-07-07 11:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | LEAK ON HOUSE LINE PIPING OWNED BY THE CUSTOMER/HOME OWNER | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | LEAK ON INTERIOR HOUSE LINE | [5 empty] | CLASS 3 LOCATION | 47400 | 57413.6393942280348 | 0 | 0 | 7100 | 8599.9333269835242 | 0 | 0 |  |  | 8 | 8.01877934272300469483568075117370892019 |  | 0 | 54508 | 27348.2598253265348544600938967136150235 | 66021.5915005542820046948356807511737089 | 0 | 0 | 1 |  |  |  |  | 0.4 | 0.4 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | 911 CALL PLACED AFTER THE EXPLOSION |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | LEAK OCCURRED ON HOUSE LINE PIPING OWNED BY THE CUSTOMER/HOME OWNER. | [47 empty] | WAYNE DADIG | MANAGER PROCESS WORK MANAGEMENT | wayne.dadig@peoples-gas.com | 412 258-4604 | 412 258-4641 |  |  |  | PAUL BECKER | VICE PRESIDENT OPERATIONS AND ENGINEERING | 412 473-4161 | paul.becker@peoples-gas.com | THERE WAS AN EXPLOSION AT 1215-17 REBECCA AVENUE AT APPROX. 11:00 AM ON JULY 7TH, 2015. TWO INDIVIDUALS WERE PRESENT AT THE TIME BUT THEY DID NOT SEEK MEDICAL ATTENTION. THE HOUSE WAS DESTROYED AND WILL BE TORN DOWN. THE ALLEGHENY COUNTY FIRE MARSHALL INVESTIGATED AND HAS CONCLUDED THAT IT WAS A NATURAL GAS EXPLOSION. IT WAS DETERMINED THAT THE GAS ESCAPED FROM A LEAK ON INTERNAL PIPING NEAR AN OLD FURNACE. HOURLY REMOTE METER READS SHOW USUAL LOADS FROM JUNE 22 UNTIL EARLIER IN THE MORNING ON JULY 7. A CATASTROPHIC LEAK OCCURRED ON THE INTERIOR PIPING APPROXIMATELY 9 AM AND THE GAS FLOWED UNRESTRICTED UNTIL THE TIME OF THE EXPLOSION. ALL GAS ODOR TESTS SHOWED EXCELLENT RESULTS. NO ODOR OR LEAK CALLS WERE RECEIVED BY PEOPLES PRIOR TO THE INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20150081 | 16135 | 2015-08-13 19:39 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2015-07-14 11:00 |  |  | 2015 | GREEN RIVER RD & DOMINGUEZ RANCH RD | CORONA | RIVERSIDE | CA | 92282 | 33.8789 | -117.6504 | [9 empty] | 2015-07-14 14:37 | 1122771 |  | NATURAL GAS |  | 861 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-07-14 11:00 |  |  |  | 2015-07-14 11:14 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 80 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1980 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 6 | 6 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 251042 | 304076.684827126462284 | 200 | 242.2516430136204 | 0 | 0 |  |  | 5166 | 5178.126760563380281690140845070422535211 |  | 0 | 256408 | 130829.8469726828457156056338028169014085 | 309497.0632307034629656901408450704225352 | 7 | 0 | 826 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | YES | 51061283 | DIGALERT - 811 |  | UTILITY OWNER | YES | YES | 50 | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | (626) 893 4536 |  |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | ON JULY 14, 2015, A CONTRACTOR WAS GRADING EARTH FOR STREET WIDENING WHEN HE STRUCK A 6 IN. STEEL GAS MAIN CAUSING A LEAK. CREWS RESPONDED AND CONTROLLED THE LEAK. NO INJURIES RESULTED FROM THE GAS LEAK. ALL REPAIRS TO THE DAMAGED MAIN WERE COMPLETED AND ALL THE AFFECTED CUSTOMERS WERE RESTORED. INVESTIGATION OF THE INCIDENT SHOWED THAT THERE WAS A VALID USA TICKET FOR THE CONTRACTOR AND THAT THE 6 IN. MAIN WAS PROPERLY MARKED. MARKS WERE VISIBLE BEFORE AND AFTER THE DAMAGE AREA BUT NOT VISIBLE IN THE APPROXIMATE AREA WHERE THE DAMAGE OCCURRED LIKELY DUE TO THE CONTRACTOR REMOVING THE MARKS WHILE GRADING WAS PERFORMED. THIS INCIDENT WAS REPORTED TO CPUC AND DOT DUE TO A RELEASE OF GAS AND THE ASSOCIATED COST OF THE DAMAGE EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2025-03-31 10:13 | NO | YES | NO | 20150082 | 16139 | 2015-08-14 10:50 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2015-07-16 11:39 |  |  | 2015 | 8070 FAIR OAKS COURT | JONESBORO | CLAYTON | GA | 30236 | 33.5339 | -84.3088 | [9 empty] | 2015-07-16 13:27 | 1122973 |  | NATURAL GAS |  | 206 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2015-07-16 11:35 |  |  |  | 2015-07-16 11:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1998 | [8 empty] | OTHER | METER SET | [9 empty] | OTHER | [8 empty] | METER BYPASS VALVE WITH AN END CAP ASSEMBLY INADVERTENTLY SEPARATED FROM PIPE DURING MAINTENANCE WORK | CLASS 3 LOCATION | 500000 | 605629.107534051 | 500 | 605.629107534051 | 1000 | 1211.258215068102 | 0 | 0 |  |  | 588 | 589.380281690140845070422535211267605634 |  | 0 | 502088 | 252131.1242116955498028169014084507042254 | 608035.3751383432938450704225352112676056 | 1 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@aglresources.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R. LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@aglresources.com | WHILE PERFORMING ROUTINE MAINTENANCE WORK AN EMPLOYEE LOOSENED A METER BYPASS VALVE WITH AN END CAP ASSEMBLY ON A METER SET WHILE UNDER PRESSURE WHERE THE VALVE INADVERTENTLY SEPARATED FROM THE PIPE. THE ESCAPING GAS IGNITED RESULTING IN A FIRE AT THE BUILDING WALL.
2025-03-31 10:13 | NO | YES | NO | 20150083 | 16260 | 2015-08-17 12:04 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2015-07-18 01:30 |  |  | 2015 | 7901 PICKFAIR DR | BLOOMINGTON | HENNEPIN | MN | 55438-1379 | 44.8444 | -93.3871 | [9 empty] | 2015-07-22 15:08 | 1123568 |  | NATURAL GAS |  | 5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2015-07-18 01:30 |  |  |  | 2015-07-18 02:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1977 | [8 empty] | COPPER | [10 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 604000 | 731599.961901133608 | 800 | 969.0065720544816 | 2000 | 2422.516430136204 | 700 | 847.8807505476714 | LEAK DETECTION EXPENSES |  | 0 | 0 |  | 0 | 607500 | 304762.59643775598 | 735839.365653871965 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK WAS ON A RESIDENTIAL RISER. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | STEVE OLINGER | OPERATIONS SPECIALIST I | steve.olinger@centerpointenergy.com | 6123600585 |  |  |  |  | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 6123215366 | dean.headlee@centerpointenergy.com | LIGHTNING CAUSED A PINHOLE LEAK IN THE COPPER RISER AND SUBSEQUENT SIGNIFICANT DAMAGE TO THE 7901 PICKFAIR DR, BLOOMINGTON, MN RESIDENCE. THE TOTAL DOLLAR AMOUNTS EXCEED $50K.
2025-03-31 10:13 | NO | NO | NO | 20150084 | 16141 | 2015-08-20 15:59 | ORIGINAL FINAL | 180 | ALABAMA GAS CORPORATION | 605 RICHARD ARRINGTON JR BLVD N | BIRMINGHAM | AL | 35203 | 2015-07-21 14:45 |  |  | 2015 | 66 THE DOWNS | TUSCALOOSA | TUSCALOOSA | AL | 35401 | 33.1895 | -87.5501 | [9 empty] | 2015-07-21 15:20 | 1123458 |  | NATURAL GAS |  | 25.91 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2015-07-21 13:04 |  |  |  | 2015-07-21 13:20 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 32 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2013 | [5 empty] | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2.3 | 0.8 | [7 empty] | CLASS 3 LOCATION | 68000 | 82365.558624630936 | 646 | 782.472806933993892 | 100 | 121.1258215068102 | 0 | 0 |  |  | 262 | 262.615023474178403755868544600938967136 |  | 0 | 69008 | 34730.5218520699717075680751173708920188 | 83531.7722765459184957558685446009389671 | 0 | 0 | 8 |  |  |  |  | 20 | 20 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY EXCAVATION DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 151941995 |  |  | CONTRACT LOCATOR | YES | YES | 2 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | RANDY A. WILSON | MANAGER REGULATORY COMPLIANCE | randy.wilson@alagasco.com | 205-326-2987 | 205-326-8483 |  |  |  | ROBERT N. GARDNER | DIRECTOR QUALITY ASSURANCE AND COMPLIANCE | 205-326-2584 | bob.gardner@alagasco.com | ON JULY 21, 2015 AT 13:04 CT, A THIRD PARTY CONTRACTOR DAMAGED A 2" PLASTIC MAIN WITH A MINI-EXCAVATOR. THIS DAMAGE RESULTED IN A RELEASE OF NATURAL GAS AND A FIRE THAT DESTROYED THE MINI-EXCAVATOR AND DAMAGED SIDING ON A NEARBY RESIDENCE. ALAGASCO DETERMINED IT WAS A REPORTABLE INCIDENT AT 14:45 CT. THE CONTRACTOR HAD A VALID LOCATE AND THE MARKS WERE DETERMINED TO BE ACCURATE AT THE TIME OF THE INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20150085 | 16370 | 2015-08-24 12:08 | SUPPLEMENTAL FINAL | 32198 | MINNESOTA ENERGY RESOURCES CORPORATION | 2685 145TH STREET WEST | ROSEMOUNT | MN | 55068 | 2015-07-24 06:29 |  |  | 2015 | 3740 156TH ST WEST | ROSEMOUNT | DAKOTA | MN | 55068 | 44.7228 | -93.1411 | [9 empty] | 2015-07-24 12:57 | 1123738 |  | NATURAL GAS |  | 0.25 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 20 | 2015-07-24 06:45 |  |  |  | 2015-07-24 06:55 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1986 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | LIGHTNING STRIKE | [5 empty] | CLASS 3 LOCATION | 132000 | 159886.084388989464 | 1500 | 1816.887322602153 | 2480 | 3003.92037336889296 | 0 | 0 | NONE |  | 150 | 150.352112676056338028169014084507042254 |  | 0 | 136130 | 68355.7394265583986411267605633802816901 | 164857.2441976365662980281690140845070423 | 0 | 0 | 4 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  | ,, | YES |  |  |  | YES | THUNDERSTORM | [213 empty] | LINDSAY K LYLE | ENGINEERING MANAGER | lklyle@minnesotaenergyresources.com | 651-322-8909 | 920-272-4000 |  |  |  | LINDSAY K LYLE | ENGINEERING MANAGER | 651-322-8909 | lklyle@minnesotaenergyresources.com | A CALL INTO OUR CALL CENTER RESULTED IN A DISPATCH OF A LOCAL TECHNICIAN TO 3740 156TH ST W, ROSEMOUNT. A SECOND CALL WAS FROM ADDRESS 3660 156TH ST W, ROSEMOUNT FOR THE SAME ISSUE. LIGHTNING STRUCK THE METERS SET THAT FED A 4 UNIT DUPLEX. ALL 4 UNITS WERE EVACUATED, RESULTING IN 8-10 OCCUPANTS AT EACH COMPLEX. MERC EMPLOYEE ARRIVED AT 0655 WITH 3 MORE ARRIVING BY 0705. THERE WAS BLOWING GAS BELOW THE REGULATOR AT 60 PSI FEEDING A FIRE AT 3740 AND 3750 156TH ST W. THE DOUBLE METER SET WAS MELTED AND FEEDING THE FIRE. FACILITIES WERE LOCATED AND THE SERVICE LINE (PLASTIC) WAS PINCHED OFF AT 0720. THE REMAINING FIRE WAS EXTINGUISHED. BAR HOLES WERE CONDUCTED THROUGHOUT THE NEIGHBORHOOD WITH NO ADDITIONAL LEAKS FOUND. FIRE DEPTS FROM ROSEMOUNT AND APPLE VALLEY, ROSEMOUNT POLICE, MNOPS, AND THE STATE FIRE MARSHALL RESPONDED TO THE INCIDENT. 156TH STREET WAS CLOSED. THE INSIDE FIRE WAS OUT WHEN MERC ARRIVED AND THE FIRE WAS CONTAINED TO THE METER SET. REPORT WAS FILED WITH MNOPS AND NRC REPORT FOLLOWED. SERVICE LINE WAS PARTIALLY ABANDONED ON 7/24/2015 AND COMPLETELY ABANDONED ON 10/22/2015. NEW SERVICE WAS INSTALLED AFTER THE RECONSTRUCTION.
2025-03-31 10:13 | NO | NO | NO | 20150086 | 16534 | 2015-08-31 16:56 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-08-02 22:15 |  |  | 2015 | 800 N. PENNSYLVANIA AVENUE | LANSING | EATON | MI | 48906 | 42.7423 | -84.5375 | [9 empty] | 2015-08-02 23:59 | 1124593 |  | NATURAL GAS |  | 23.07 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 12 | 2015-08-02 22:15 |  |  |  | 2015-08-02 23:04 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1987 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | OTHER | [8 empty] | PLASTIC RISER SEVERED FROM METER BY VEHICLE IMPACT | CLASS 3 LOCATION | 80000 | 96900.65720544816 | 3259 | 3947.490522906944418 | 206 | 249.519192304029012 | 0 | 0 |  |  | 172 | 172.403755868544600938967136150234741784 |  | 0 | 83637 | 42031.1051510830233308920187793427230047 | 101270.0706765276780309389671361502347418 | 0 | 0 | 6 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VEHICLE STRUCK GAS METER RESULTING IN RELEASE OF GAS. THE GAS IGNITED AND AN EXPLOSION OCCURRED. THE OPERATOR WAS NOTIFIED BY EMERGENCY RESPONDER - 911 OPERATOR | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST I | carmella.king@cmsenergy.com | 517-788-0509 |  |  |  |  | JULIE A. HEGEDUS | DIRECTOR DOET REGULATORY AND COMPLIANCE | 248-217-6993 | julie.hegedus@cmsenergy.com | ON SUNDAY, AUGUST 2, 2015 AT APPROXIMATELY 22:15 A VEHICLE TRAVELING NORTH ON PENNSYLVANIA AVE. WAS REAR-ENDED AT THE INTERSECTION OF PENNSYLVANIA AVE. AND MAY ST., CAUSING THE VEHICLE TO EXIT THE ROADWAY AND STRIKE THE GAS METER LOCATED AT 800 N. PENNSYLVANIA AVE., LANSING, MICHIGAN (EATON COUNTY). THE METER STAND AND THE SERVICE RISER WERE DAMAGED AS A RESULT OF THE COLLISION CAUSING A RELEASE OF GAS. AT APPROXIMATELY 22:23 THE RELEASED GAS IGNITED AND AN EXPLOSION OCCURRED RESULTING IN A COMPLETE LOSS OF THE STRUCTURE. THE DRIVER EXITED THE VEHICLE AND THE OCCUPANTS OF THE HOME EVACUATED BEFORE THE EXPLOSION OCCURRED. NO FATALITIES OR INJURIES OCCURRED AS A RESULT OF THE INCIDENT. THE LANSING POLICE AND FIRE DEPARTMENTS WERE ONSITE AND HAD TRAFFIC BLOCKED AS A SAFETY PRECAUTION. TWO ADDITIONAL STRUCTURES LOCATED DIRECTLY TO THE NORTH AND EAST SUSTAINED DAMAGES AS A RESULT OF THE EXPLOSION. THE OCCUPANTS OF THE STRUCTURE TO THE EAST WERE EVACUATED WITHOUT INJURY AFTER THE EXPLOSION OCCURRED. THE PROPERTY TO THE NORTH WAS UNOCCUPIED. CONSUMERS ENERGY GAS SERVICE WORKERS PERFORMED BAR TESTING TO ENSURE THERE WAS NO EVIDENCE OF GAS MIGRATION TO ADJACENT STRUCTURES AND NO GAS WAS DETECTED. THE 1 1/4" PLASTIC DISTRIBUTION MAIN WAS SQUEEZED SOUTH OF THE INCIDENT LOCATION SHUTTING GAS DOWN AT APPROXIMATELY 00:15. THE TEMPORARY SHUT-DOWN RESULTED IN AN INTERRUPTION OF SERVICE TO SIX CUSTOMERS. SERVICE TO THE IMPACTED CUSTOMERS WAS RESTORED ON AUGUST 3, 2015 AT APPROXIMATELY 14:00 FOLLOWING THE DEMOLITION OF THE DAMAGED STRUCTURE.
2025-03-31 10:13 | NO | YES | NO | 20150087 | 16293 | 2015-09-04 17:25 | SUPPLEMENTAL FINAL | 30769 | MISSOURI GAS ENERGY | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2015-08-07 03:30 |  |  | 2015 | E. TRUMAN RD. AND WABASH | KANSAS CITY | JACKSON | MO | 64127 | 39.0948 | -94.5528 | [9 empty] | 2015-08-07 08:01 | 1124968 |  | NATURAL GAS |  | 4066 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2015-08-07 04:07 |  |  |  | 2015-08-07 04:45 |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 43 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1902 | [5 empty] | 16 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 124360 | 150632.07162586916472 | 500 | 605.629107534051 | 0 | 0 |  |  | 21357 | 21407.1338028169014084507042253521126761 |  | 0 | 146217 | 82440.9719336113841780281690140845070423 | 172644.8345362201171284507042253521126761 | 0 | 0 | 466 |  |  |  |  | 44 | 23 | 25 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM RESPONDED TO THE ALARMS BY TAKING PROMPT REMEDIAL ACTION. ADDITIONALLY, THE LOCAL WATER UTILITY CONFIRMED MISTAKENLY OPERATING THE GAS VALVE IN LINE WITH THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | THE LOCAL WATER UTILITY MISTAKENLY OPERATED A GAS VALVE BYPASSING A REGULATOR. THE SYSTEM BECAME OVERPRESSURIZED CREATING SEVERAL CRACKS AND A HOLE IN A 16 INCH CAST IRON MAIN. | [47 empty] | PATRICK SEAMANDS | MANAGER OF PIPELINE SAFETY AND COMPLIANCE | patrick.seamands@thelacledegroup.com | (314) 349-2936 |  |  |  |  | CRAIG R. HOEFERLIN | VICE PRESIDENT OF OPERATIONS SERVICES | (314) 349-2972 | craig.hoeferlin@thelacledegroup.com | THE LOCAL WATER UTILITY WORKER MISTAKENLY OPERATED (OPENED) A NATURAL GAS DISTRIBUTION SYSTEM VALVE, BYPASSING A REGULATOR STATION. THE SYSTEM BECAME OVERPRESSURIZED, CREATING SEVERAL CRACKS AND A HOLE IN A 16-INCH CAST IRON MAIN. NATURAL GAS SERVICE WAS MAINTAINED TO ALL CUSTOMERS SERVED BY THE LINE WHILE IT WAS BEING REPAIRED. SUBSEQUENT TO THE EVENT, THE LID OF THE ASSOCIATED VALVE BOX WAS MARKED WITH YELLOW PAINT AND A VALVE CAP LABELED "GAS VALVE" WAS PLACED OVER THE VALVE KEY.
2025-03-31 10:13 | NO | YES | NO | 20150088 | 16151 | 2015-09-10 11:53 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2015-08-12 08:20 |  |  | 2015 | 715 MONTANA AVE | SANTA MONICA | LOS ANGELES | CA | 90403 | 34.0273 | -118.5016 | [9 empty] | 2015-08-12 12:53 | 1125441 |  | NATURAL GAS |  | 38 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2015-08-12 08:20 |  |  |  | 2015-08-12 08:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2001 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.8 | 0.8 | [7 empty] | CLASS 3 LOCATION | 200000 | 242251.6430136204 | 995 | 1205.20192399276149 | 200 | 242.2516430136204 | 0 | 0 |  |  | 228 | 228.535211267605633802816901408450704225 |  | 0 | 201423 | 101144.265389460298432112676056338028169 | 243927.6317918943875238028169014084507042 | 6 | 0 | 0 |  |  |  |  | 39 | 39 | 43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-376-7208 | tbauer@semprautilities.com | ON AUGUST 12, 2015, A DRIVER WAS BACKING HER VEHICLE OUT OF A PARKING SPACE WHEN SHE STRUCK ANOTHER VEHICLE. THE DRIVER REPORTEDLY PANIC, INADVERTENTLY STEPPED ON THE GAS PEDAL INSTEAD OF THE BRAKE AND ACCELERATED FORWARD. THE VEHICLE JUMPED THE PARKING STOP, WENT OVER THE CURB, STRUCK AND SHEARED OFF A SERVICE RISER, AND CRASHED INTO A BUILDING. THIS RESULTED IN A GAS LEAK AND IGNITION TO HER VEHICLE AND THE BUILDING. CREW RESPONDED AND CONTROLLED THE LEAK. THE DRIVER SUFFERED MINOR SCRAPES AS A RESULT OF THE IMPACT AND EXITING VEHICLE. GAS SERVICE WILL NOT BE RESTORED UNTIL THE BUILDING OWNERS AND THEIR PLUMBERS CONFIRMED THAT THE BUILDING HOUSELINE HAS BEEN REPAIR. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO A RELEASE OF GAS AND THE COST ASSOCIATED WITH THE DAMAGE EXCEEDED $50,000.
2025-03-31 10:13 | YES | NO | NO | 20150089 | 16152 | 2015-09-15 21:50 | ORIGINAL FINAL | 18112 | SAN DIEGO GAS & ELECTRIC CO | 8326 CENTURY PARK COURT | SAN DIEGO | CA | 92123 | 2015-08-16 11:54 |  |  | 2015 | 869 39TH ST | SAN DIEGO | SAN DIEGO | CA | 92102 | 32.7148 | -117.1098 | [9 empty] | 2015-08-16 14:14 | 1125822 |  | NATURAL GAS |  | 32 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2015-08-16 11:54 |  |  |  | 2015-08-16 12:24 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1957 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | FIRE MELTED THE MSA CAUSING A GAS RELEASE. | CLASS 3 LOCATION | 140000 | 169576.15010953428 | 920 | 1114.35755786265384 | 200 | 242.2516430136204 | 0 | 0 |  |  | 190 | 190.446009389671361502347417840375586854 |  | 0 | 141310 | 70971.3961110537250734272300469483568075 | 171123.2053198002256015023474178403755869 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 626-893-4536 | kle2@semprautilities.com | ON AUGUST 16, 2015, FIRE DEPARTMENT REPORTED A STRUCTURE FIRE AT 871 39TH ST, SAN DIEGO. INITIAL REPORT SHOWS 874 QUAIL ST, SAN DIEGO. THE FIRE REPORTEDLY MELTED THE METER CAUSING GAS TO ESCAPE. CREW RESPONDED AND CONTROLLED THE GAS VIA A NEARBY CONTROL HOLE IN THE ALLEY. NO INJURIES RESULTED FROM THIS INCIDENT. RESTORE WILL NOT TAKE PLACE UNTIL THE CUSTOMER'S PLUMBER CONFIRMED THAT THE HOUSELINE IS REPAIRED AND FREED FROM LEAK. CAUSE OF THE FIRE IS UNDETERMINED. THIS INCIDENT WAS REPORTED TO CPUC AND DOT DUE TO A GAS LEAK, MEDIA COVERAGE, AND THE ASSOCIATED DAMAGE EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2025-03-31 10:13 | NO | YES | YES | 20150090 | 16165 | 2015-09-16 11:32 | SUPPLEMENTAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2015-08-18 20:25 |  |  | 2015 | 3400 11TH STREET | BREMERTON | KITSAP | WA | 98312-2636 | 47.5708 | -122.6601 | [9 empty] | 2015-08-18 22:00 | 1126041 |  | NATURAL GAS |  | 53 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | YES | 65 | 2015-08-18 20:04 |  |  |  | 2015-08-18 20:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1978 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 1000000 | 1211258.215068102 | 500 | 605.629107534051 | 6051 | 7329.323459377085202 | 0 | 0 |  |  | 384 | 384.901408450704225352112676056338028169 |  | 0 | 1006935 | 505309.3011232458141580845070422535211268 | 1219578.06904346384042735211267605633803 | 1 | 0 | 0 |  |  |  |  | 56 | 56 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | INDIVIDUALS COMING DOWN FROM A SECOND STORY WINDOW WERE SEEN USING THE METER AS A STEP STOOL/LADDER. THE STRESS ON THE METER CAUSED THE METER TO BE PULLED AWAY FROM THE RISER BELOW THE METER STOP. CAUSING A RELEASE OF NATURAL GAS TO OCCUR AS INDIVIDUALS WERE LEAVING THE SCENE. | [154 empty] | PATTI CHARTREY | PIPELINE SAFETY SPECIALIST | patti.chartrey@cngc.com | 360.405.4231 | 360.377.2091 |  |  |  | MIKE EUTSEY | MANAGER OF STANDARDS AND COMPLIANCE | 509-734-4576 | mike.eutsey@cngc.com | ON 08.18.15 AT 19:51, TWO INDIVIDUALS WERE OBSERVED JUMPING OUT OF A TWO STORY WINDOW ONTO CNGC'S GAS METER. AT 19:54 A CALL WAS RECEIVED AT 911 FOR GAS ODOR AT 3400 11TH STREET, BREMERTON, WA. AT 19:55 FIRE DEPT & POLICE DEPT WERE DISPATCHED TO SCENE. CNGC RECEIVED A CALL OF A BLOWING GAS LINE BELOW THE METER AT 20:04, CNGC EMPLOYEE WAS DISPATCHED AT 20:05. AT APPROXIMATELY 20:20 CNGC EMPLOYEE ARRIVED ON SCENE. CNGC EMPLOYEE WAS AT THE METER SET WHEN THE EXPLOSION OCCURRED AT 20:25. METER SET WAS LOCATED AT THE BUILDING WALL. THE MOTEL'S LAUNDRY ROOM CONTAINING 2 NG DRYERS AND 1 NG WATER HEATER WERE LOCATED ON THE OTHER SIDE OF THE BUILDING WALL, MOSTLY BELOW GRADE. VENTING AND AIR INTAKE VENTS WERE IN THE VICINITY OF THE BLOWING GAS. THE CLOTHES DRYER WAS IN OPERATION AT THE TIME OF THE EXPLOSION. CNGC EMPLOYEE WAS INJURED. BLOWING NATURAL GAS ENTERED THE LAUNDRY ROOM AND WAS IGNITED BY THE DRYER IN OPERATION.
2025-03-31 10:13 | NO | YES | YES | 20150091 | 16158 | 2015-09-25 21:46 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2015-08-26 15:51 |  |  | 2015 | 2000 BLOCK OF WHITE OAK LANE | SANTA CLARA | SANTA CLARA COUNTY | CA | 95051 | 37.3602 | -121.9964 | [9 empty] | 2015-08-26 22:25 | 1126788 |  | NATURAL GAS |  | 100 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 1 | 2 | YES |  |  |  |  | NO | 15 | 2015-08-26 16:26 |  |  |  | 2015-08-26 16:26 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | VEHICLE STRUCK GAS FACILITIES, CAUSING UNINTENTIONAL RELEASE OF NATURAL GAS AND SUBSEQUENT IGNITION | CLASS 3 LOCATION | 50000 | 60562.9107534051 | 8000 | 9690.065720544816 | 0 | 0 | 0 | 0 |  |  | 537 | 538.260563380281690140845070422535211268 |  | 0 | 58537 | 29594.5984091040196056338028169014084507 | 70791.2370373301976901408450704225352113 | 4 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | WINI CHEN |  | wcce@pge.com | [5 empty] | LARRY DENISTON | MANAGER OF GAS REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT 1610 HOURS ON AUGUST 26, 2015, PG&E WAS NOTIFIED OF A VEHICLE IMPACT INCIDENT AT 2055 WHITE OAK LANE IN SANTA CLARA. THE VEHICLE STRUCK A 3-METER MANIFOLD OF A COMMERCIAL BUILDING RESULTING IN AN UNINTENTIONAL RELEASE OF GAS THAT SUBSEQUENTLY IGNITED. THE BUILDING THAT CAUGHT ON FIRE IS A SMALL STRIP MALL CONSISTING OF FOUR BUSINESSES AT 2035, 2041, 2045, AND 2055 WHITE OAK LANE IN SANTA CLARA. THE FACILITY IMPACTED BY THE INCIDENT WAS LOCATED BEHIND A CHAIN-LINK FENCE MORE THAN FIVE FEET FROM THE ROADWAY, ON THE SIDE OF 2055 WHITE OAK LANE, ADJACENT TO THE PARKING LOT OF 2065 WHITE OAK LANE. UPON ARRIVAL, THE FIRE OFFICIALS EVACUATED THE BUILDING. A PG&E GAS SERVICE REPRESENTATIVE ARRIVED ON SITE A 1626 HOURS AND CREWS ARRIVED ONSITE AT 1712 HOURS. GAS WAS SHUT IN AT 2041 HOURS BY EXCAVATING AND SQUEEZING THE 1-INCH PLASTIC SERVICE. BAY AREA MAJOR MEDIA WERE OBSERVED ON SITE AT APPROXIMATELY 1711 HOURS. DAMAGES RESULTING FROM THE FIRE ARE ESTIMATED TO EXCEED $50,000, MAKING THE INCIDENT REPORTABLE TO BOTH THE DOT AND CPUC. POLICE NOTED THAT THIS WAS A HIT-AND-RUN COLLISION AND NOTED THERE ARE NO FATALITIES. TWO INDIVIDUALS (INCLUDING ONE FIREFIGHTER) WERE TAKEN TO THE HOSPITAL.
2025-03-31 10:13 | NO | YES | NO | 20150092 | 16159 | 2015-09-30 11:18 | ORIGINAL | 18440 | SOUTH JERSEY GAS CO | 101 SOUTH LINCOLN PLACE | ATLANTIC CITY | NJ | 08401 | 2015-09-15 08:04 |  |  | 2015 | 111 N. BROADWAY AVENUE | PENNSVILLE | SALEM | NJ | 08070-1618 | 39.661 | -75.5142 | [9 empty] | 2015-09-15 09:25 | 1128507 |  | NATURAL GAS |  | 9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2015-09-15 08:10 |  |  |  | 2015-09-15 08:17 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 29 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1933 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | OTHER | [8 empty] | STRUCK SERVICE | CLASS 3 LOCATION | 300000 | 363377.4645204306 | 1000 | 1211.258215068102 | 11000 | 13323.840365749122 | 7000 | 8478.807505476714 | MISCELLANEOUS ITEMS |  | 26 | 26.06103286384976525821596244131455399061 |  | 0 | 319026 | 160055.8252876307932769953051643192488263 | 386417.431639588387765258215962441314554 | 1 | 0 | 1 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT DID NOT RESULT IN OBSERVABLE PRESSURE CHANGES IN THE SYSTEM. | [12 empty] | NO |  |  | YES | 6 | 1 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 152240790 |  |  | CONTRACT LOCATOR | YES | YES |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | PRIMARY CAUSE UNDER INVESTIGATION. | [169 empty] | DAVID J. NEWMAN | MANAGER COMPLIANCE AND QA QC | dnewman@sjindustries.com | 609-561-9000 | 856-881-7378 |  |  |  | DAVID J. NEWMAN | MANAGER COMPLIANCE AND QA QC | 609-561-9000 | dnewman@sjindustries.com | ON TUESDAY SEPTEMBER 15, 2015, KLINE CONSTRUCTION, A CONTRACTOR WORKING FOR SOUTH JERSEY GAS COMPANY, WAS SCHEDULED TO RENEW A GAS SERVICE TO THE BUILDING LOCATED AT 111-113 N. BROADWAY AVENUE IN PENNSVILLE, NJ. THE GAS SERVICE RENEWAL WAS PART OF A PROJECT TO REPLACE THE GAS MAINS AND SERVICES IN THIS SECTION OF PENNSVILLE. THE PROJECT CONSISTED OF REPLACING 4" BARE STEEL MAIN ON N. BROADWAY AVENUE ALONG WITH ALL EXISTING SERVICES. THE NEW MAIN IS 6" PE PLASTIC AND THE SERVICES WILL ALL BE PE PLASTIC. THE OPERATING PRESSURE OF THE SYSTEM IS 60 PSIG MAOP. ON THE MORNING OF 9/15/15, KLINE'S SERVICE INSTALLATION CREW STRUCK AN UNMARKED GAS SERVICE TO 111 N. BROADWAY. THERE WAS AN APPARENT IGNITION OF NATURAL GAS INSIDE THE STRUCTURE AT 111 N. BROADWAY WHEN THE SERVICE WAS PULLED APART FROM THE INSIDE METER SET. THERE WERE TWO SERVICES ON THE PROPERTY, ONE MARKED AND ONE NOT MARKED.
2025-03-31 10:13 | NO | NO | NO | 20150093 | 16160 | 2015-10-01 10:59 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2015-09-04 17:20 |  |  | 2015 | 15158 FM 916 | MAYPEARL | ELLIS | TX | 76064 | 32.2997 | -97.0458 | [9 empty] | 2015-09-05 12:00 | 1127650 |  | NATURAL GAS |  | 2100 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-09-04 17:20 |  |  |  | 2015-09-04 18:00 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 37 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1962 | [5 empty] | 10 | SMLS | UNKNOWN | STEEL |  | OTHER | SMLS | 0.203 | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 67500 | 81759.929517096885 | 0 | 0 | 0 | 0 |  |  | 10000 | 10023.4741784037558685446009389671361502 |  | 0 | 77500 | 43134.8111847897880751173708920187793427 | 91783.4036955006408685446009389671361502 | 0 | 0 | 8 |  |  |  |  | 16 | 16 | 240 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS DUE TO 3RD PARTY, NO CONTROLLER ISSUES WERE PRESENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  | NO |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | IRRIGATION | NO | [5 empty] | YES | 16 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JOSHUA LENAMOND | OPERATIONS SUPERVISOR | joshua.lenamond@atmosenergy.com | 469-261-2303 |  |  |  |  | ANDY TREADWAY | COMPLIANCE DIRECTOR | 214-206-2044 | andy.treadway@atmosenergy.com | CONTRACTOR WAS INSTALLING A WELL FOR A LANDOWNER USING A BACKHOE, AND HIT A 10 INCH (HP DISTRIBUTION) TRANSMISSION LINE. NO NOTIFICATION WAS MADE TO THE ONE-CALL CENTER.
2025-03-31 10:13 | NO | YES | NO | 20150094 | 16611 | 2015-10-08 13:56 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2015-09-08 12:32 |  |  | 2015 | 10218 DODGE ROAD | MONTROSE | GENESEE | MI | 48457 | 43.1475 | -83.8818 | [9 empty] | 2015-09-08 13:26 | 1127887 |  | NATURAL GAS |  | 17.26 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2015-09-08 12:32 |  |  |  | 2015-09-08 12:32 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1991 | [5 empty] | 0.625 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 185000 | 224082.76978759887 | 11403 | 13811.977426421567106 | 1437 | 1740.578055052862574 | 0 | 0 |  |  | 128 | 128.300469483568075117370892018779342723 |  | 0 | 197968 | 99368.4501855083906313615023474178403756 | 239763.6257385568677551173708920187793427 | 0 | 0 | 2 |  |  |  |  | 58 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | BASED ON AN INCIDENT INVESTIGATION THERE WAS NO CONTROL ROOM ISSUE THAT CONTRIBUTED TO THE INCIDENT. THEREFORE NO ADDITIONAL INVESTIGATION WAS NECESSARY. | [12 empty] | YES | 10 | 0 | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 734-513-6256 |  |  |  |  | JASON PIONK | SR. ENG. TECH ANAL LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON TUESDAY, SEPTEMBER 8, 2015 AT APPROXIMATELY 09:19 CONSUMERS ENERGY PERSONNEL RESPONDED TO AN OUTSIDE LEAK INVESTIGATION AT 10223 DODGE RD., MONTROSE, MI (GENESEE COUNTY). THE HOMEOWNER INDICATED A LIGHTNING STRIKE OCCURRED AT APPROXIMATELY 07:34 AND AFTERWARDS A STRONG ODOR OF GAS WAS PRESENT NEAR THE HOME. THE RESPONDING GAS SERVICE WORKER (GSW) PERFORMED A SERIES OF LEAK TEST AT 10223 DODGE RD., INCLUDING BAR HOLE TESTING THE SERVICE LINE AND THE MAIN. NO GAS READS WERE DETECTED AT THIS LOCATION. THE GSW PROCEEDED TO CHECK FOR GAS READINGS ALONG THE SERVICE LINE AS WELL AS THE BUILDING PERIMETER (DOORS AND WINDOWS) AT 10218 DODGE RD. USING A SENSIT GOLD CGI COMBUSTIBLE GAS INDICATOR. NO READS WERE DETECTED DURING THIS PORTION OF THE INVESTIGATION. THE GSW EXPANDED THE LEAK INVESTIGATION TO THE LIGHTNING STRIKE LOCATION AT 10209 DODGE RD., AND FOUND 100% GAS READS AT THE EDGE OF PAVEMENT ON BOTH SIDES OF DODGE ROAD AS WELL AS WATER BUBBLING FROM A CRACK IN THE PAVEMENT NEAR THE CENTER OF THE ROAD ABOVE THE SERVICE LINE. AT APPROXIMATELY 11:15 CONSUMERS ENERGY DISTRIBUTION CREW ARRIVED ON-SITE AND BEGAN PREPARATION TO REPLACE THE SERVICE LINE LOCATED AT 10209 DODGE RD. AT APPROXIMATELY 12:32 AN EXPLOSION AND SUBSEQUENT FIRE OCCURRED AT 10218 DODGE RD. RESULTING IN A COMPLETE LOSS OF PROPERTY. THE PROPERTY WAS UNOCCUPIED AND NO INJURIES OCCURRED AS A RESULT OF THE INCIDENT. AFTER THE INCIDENT, CONSUMERS ENERGY CONDUCTED BAR HOLE TESTING IN THE VICINITY OF 10218 DODGE ROAD. THIS TESTING INDICATED THAT GAS HAD MIGRATED FROM THE LEAK LOCATION AT 10209 DODGE ROAD ALONG THE MAIN TO A LOCATION APPROXIMATELY 20' WEST OF THE IDENTIFIED LEAK. THE HIGHEST SUSTAINED READS WERE OBTAINED APPROXIMATELY 20 FEET FROM THE LEAK LOCATION AND APPROXIMATELY 60 FEET FROM THE BUILDING WALL. THE INITIAL READ TAKEN AT 16:00, APPROXIMATELY 3.5 HOURS AFTER THE EXPLOSION WAS 55%. A READ TAKEN AT THE SAME LOCATION 2 HOURS LATER (22%) INDICATES THE MIGRATING GAS WAS VENTING AT THIS LOCATION. THIS LOCATION WAS MONITORED THE NEXT SEVERAL DAYS AND CONTINUED TO VENT. LOWER RESIDUAL GAS READINGS WERE ALSO OBTAINED, BUT AT NO TIME (PRE OR POST-INCIDENT) WERE THERE ANY GAS READINGS AT THE BUILDING WALL OF 10218 DODGE ROAD. BASED ON THE INCIDENT INVESTIGATION SUMMARIZE ABOVE AND OUR INABILITY TO PERFORM AN INVESTIGATION OF THE CUSTOMER'S FUEL LINE AND GAS APPLIANCE(S), CONSUMERS ENERGY FOUND NO CONCLUSIVE EVIDENCE THAT THE EXPLOSION AND FIRE AT 10218 DODGE RD., WAS THE RESULT OF A RELEASE AND/OR MIGRATION OF CONSUMERS ENERGY'S JURISDICTIONAL GAS.
2025-03-31 10:13 | YES | NO | NO | 20150095 | 16172 | 2015-10-13 10:43 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2015-09-15 15:11 |  |  | 2015 | 11852 MILL VALLEY ST | PARKER | DOUGLAS COUNTY | CO | 80138 | 39.5012 | -104.7189 | [9 empty] | 2015-09-15 15:45 | 1128547 |  | NATURAL GAS |  | 15 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2015-09-15 14:21 |  |  |  | 2015-09-15 14:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2004 | [8 empty] | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | BUILDING FIRE MELTED THE BUILDING REGULATOR AND METER. ESCAPING GAS CAUGHT FIRE. | CLASS 3 LOCATION | 500000 | 605629.107534051 | 1000 | 1211.258215068102 | 5000 | 6056.29107534051 | 0 | 0 |  |  | 30 | 30.0704225352112676056338028169014084507 |  | 0 | 506030 | 253871.230559852114704225352112676056338 | 612926.7272469948232676056338028169014085 | 0 | 0 | 2 |  |  |  |  | 25 | 25 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | JONATHAN MOE | MANAGER GAS ENGINEERING | jonathan.t.moe@xcelenergy.com | 303-571-3477 |  |  |  |  | MARK NOLAN | PRINCIPAL ENGINEER | 303-571-3931 | mark.nolan@xcelenergy.com | A BUILDING FIRE AT 11844 MILL VALLEY ST MELTED THE BUILDING REGULATOR AND METER ATTACHED TO THE HOME. THE LEAKING GAS WAS THEN IGNITED BY THE FIRE WHICH CONTRIBUTED TO THE FIRE IN THE ADJACENT BUILDING 11852 MILL VALLEY ST. NO INJURIES WERE REPORTED AND THE ORIGINAL SOURCE OF THE FIRE IS NOT ATTRIBUTED TO THE GAS FACILITIES. NOTE: RESPONSE TO A.13 IS FOR THE INDIVIDUAL SERVICE THAT WAS CUT-OFF. NO OTHER PIPELINE MAIN WAS SHUT DOWN. THE SERVICE WILL LIKELY BE RENEWED AT SOME POINT IN THE FUTURE AFTER THE HOME IS RE-BUILT.
2025-03-31 10:13 | NO | YES | YES | 20150096 | 16219 | 2015-10-19 10:10 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2015-09-21 08:00 |  |  | 2015 | 113 ARABIAN ROAD | WAXAHACHIE | ELLIS | TX | 75165 | 32.3491 | -96.7845 | [9 empty] | 2015-09-21 09:00 | 1129019 |  | NATURAL GAS |  | 1595 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | NO |  |  |  |  | YES | 20 | 2015-09-21 08:10 |  |  |  | 2015-09-21 08:30 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2008 | [5 empty] | 0.75 | 2406 | POLYPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | LEAK |  |  | OTHER | 3RD PARTY BORED INTO 3/4" SERV | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8000 | 8018.779342723004694835680751173708920188 |  | 0 | 8000 | 7417.840375586854460093896713615023474178 | 8018.779342723004694835680751173708920188 | 0 | 0 | 17 |  |  |  |  | 25 | 25 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS DUE TO 3RD PARTY, NO CONTROLLER ISSUES WERE PRESENT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | UTILITY | BORING | TELECOMMUNICATIONS | YES | 1575144185 | TEXAS 811 |  | CONTRACT LOCATOR | YES | YES | 24 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JOSHUA LENAMOND | OPERATIONS SUPERVISOR | joshua.lenamond@atmosenergy.com | 469-261-2303 |  |  |  |  | ANDY TREADWAY | COMPLIANCE DIRECTOR | 214-206-2044 | andy.treadway@atmosenergy.com | 3RD PARTY CONTRACTOR BORED IN TO 3/4" SERVICE. THE EXCAVATOR OPERATED MECHANIZED EQUIPMENT WITHIN THE TOLERANCE ZONE CAUSING DAMAGE TO A SERVICE LINE WHICH RESULTED IN THE RELEASE OF PRODUCT. THERE WAS EVIDENCE THAT THE EXCAVATOR FAILED TO VERIFY THE LOCATION OF UTILITY LINES WITHIN THE BORE PATH THROUGH POT HOLE VERIFICATION.
2025-03-31 10:13 | NO | YES | NO | 20150097 | 16278 | 2015-10-23 09:35 | SUPPLEMENTAL FINAL | 1088 | BALTIMORE GAS & ELECTRIC CO | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2015-09-23 19:19 |  |  | 2015 | 12218 SLEEPY-HORSE LANE | COLUMBIA | HOWARD | MD | 21044 | 39.2095 | -76.8977 | [9 empty] | 2015-09-23 20:50 | 129242 |  | NATURAL GAS |  | 70 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 10 | 2015-09-23 19:19 |  |  |  | 2015-09-23 19:19 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | 1994 | [8 empty] | STEEL |  | OTHER | FITTING | 0.154 | [6 empty] | OTHER | [8 empty] | OUTSIDE FORCE - PIPE DAMAGE / BREAK AS A RESULT OF VEHICLE IMPACT | CLASS 3 LOCATION | 2000000 | 2422516.430136204 | 500 | 605.629107534051 | 2500 | 3028.145537670255 | 0 | 0 |  |  | 70 | 70.16431924882629107981220657276995305164 |  | 0 | 2003070 | 1004903.55740341021697652582159624413146 | 2426220.36910065713229107981220657276995 | 0 | 0 | 6 |  |  |  |  | 0.25 | 0.25 | 0.35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SMALL AMOUNT OF RELEASE AT EVENT LOCATION | [12 empty] | YES | 1 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | STEVE TROCH | MANAGER-GAS ENGINEERING -ASSET PERFORMANCE | steve.troch@bge.com | 410-470-9560 | 410-470-9549 |  |  |  | STEVE TROCH | MANAGER-GAS ENGINEERING -ASSET PERFORMANCE | 410-470-9560 | steve.troch@bge.com | THE RESIDENT OF 12218 SLEEPY-HORSE LANE STATED THAT SHE BACKED OUT OF HER GARAGE UNAWARE THAT HER CAR DOOR WAS PARTIALLY OPEN AND HER CAR DOOR STRUCK AN UNDETERMINED PIPE/OBJECT INSIDE THE GARAGE. BGE LATER RECEIVED A REPORT OF AN OUTSIDE GAS ODOR FROM THE RESIDENT OF 12220 SLEEPY-HORSE LANE. BGE RESPONDED TO THE ODOR CALL AND FOUND HIGH LEVELS OF GAS AND A BREACHED GAS METER/REGULATOR SET INSIDE THE GARAGE OF 12218 SLEEPY-HORSE LANE. THE GAS MECHANIC EVACUATED THE RESIDENTS OF 12220 SLEEPY-HORSE LANE. SHORTLY THEREAFTER, THE IGNITION OCCURRED. HOWARD COUNTY FIRE INVESTIGATION REPORT 15MA012 DATED 12/17/2015 STATED; AS A RESULT OF A SYSTEMATIC ORIGIN AND CAUSE INVESTIGATION, THE SPECIFIC POINT OF ORIGIN COULD NOT BE READILY IDENTIFIED; THEREFORE, THE AREA OF ORIGIN IS IDENTIFIED AS THE STRUCTURE OF 12218 SLEEPY HORSE LANE. BASED ON THE INFORMATION PRESENTLY AVAILABLE, IT IS THE OPINION OF THIS INVESTIGATOR THAT THE SOURCE OF IGNITION WAS UNDETERMINED. THERE WAS A SEVERED NATURAL GAS PIPE INSIDE OF THE GARAGE AND GAS WAS FREE FLOWING INSIDE OF THE GARAGE, WHICH PROVIDED THE FUEL FOR THE IGNITION. THE AREA OF ORIGIN CONTAINED MULTIPLE COMPETENT AND POTENTIAL SOURCES OF ACCIDENTAL IGNITION. THESE INCLUDED ENERGIZED ELECTRICAL DEVICES. AS A RESULT, THE SPECIFIC SOURCE OF IGNITION OF THIS FIRE COULD NOT BE CONCLUSIVELY DETERMINED WITHIN THE LIMITS OF THIS INVESTIGATION. DURING THIS INVESTIGATION, HOWEVER, NO SOURCES OF INCENDIARY IGNITION WERE OBSERVED OR INDICATED IN THE AREA OF ORIGIN. IT IS THE OPINION OF THIS INVESTIGATOR THAT THE EXPLOSION AND FIRE WAS ACCIDENTAL IN NATURE.
2025-03-31 10:13 | NO | YES | YES | 20150099 | 16783 | 2015-10-28 13:38 | SUPPLEMENTAL | 2120 | CARTERSVILLE GAS DEPT, CITY OF | 19 NORTH ERWIN ST PO BOX1390 | CARTERSVILLE | GA | 30120 | 2015-09-30 11:26 |  |  | 2015 | 13 COURRANT STREET | CARTERSVILLE | BARTOW | GA | 30120 | 34.1768 | -84.7958 | [9 empty] | 2015-09-30 13:50 | 1129766 |  |  |  | 1.6 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2015-09-30 11:26 |  |  |  | 2015-09-30 11:31 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | INTENTIONAL RELEASE OF GAS | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 38 | 46.027812172587876 | 93 | 112.647014001333486 | 0 | 0 |  |  | 18 | 18.04225352112676056338028169014084507042 |  | 0 | 149 | 82.4084949740350865352112676056338028169 | 176.71707969504812256338028169014084507 | 0 | 0 | 0 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | FAILURE TO PREVENT ACCIDENTAL IGNITION. USE OF ELECTRIC BAND SAW IN A GASEOUS ENVIRONMENT. |  |  | YES |  |  | DECOMMISSIONING | YES | NO, BUT THEY WERE PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | GREG THACKER | REGULATORY COMPLIANCE SUPERVISOR | gthacker@cityofcartersville.org | 770-387-5642 | 770-387-5638 |  |  |  | GREG THACKER | REGULATORY COMPLIANCE SUPERVISOR | 770-387-5642 | gthacker@cityofcartersville.org | ON SEPTEMBER 30, 2015, CREW FORMAN, WELDER 1, SERVICE WORKER A AND SERVICE WORKER B WERE RETIRING A SERVICE AT 13 COURRANT STREET. THE SERVICE WAS EXCAVATED BY THE CREW FORMAN. THE WELDER 1 (INJURED EMPLOYEE) ON THE CREW RETIRED THE SERVICE BY CUTTING THE SERVICE ABOUT 4 INCHES FROM THE TAPPING TEE WITH A SET OF FOUR WHEEL CUTTERS, AND THEN INSERTED A LEAK SCREW IN THE SERVICE, AND WELDED IT UP. AFTER WELDING THE LEAK SCREW IN, THEY CHECKED FOR LEAKS AND NO LEAKS WERE FOUND. WELDER 1 (INJURED EMPLOYEE) THEN BUFFED THE TEE AND MAIN OFF WITH A BUFFER TO PREPARE IT TO BE RE-COATED AND CHECKED FOR LEAKS A SECOND TIME. AFTER CHECKING FOR LEAKS AGAIN WELDER 1 (INJURED EMPLOYEE) FOUND A SMALL LEAK ON THE TAPPING TEE. WELDER 1 (INJURED EMPLOYEE) TRIED TO WELD THE LEAK UP BUT WAS UNSUCCESSFUL. AFTER FAILING TO REPAIR THE LEAK ON THE TAPPING TEE THE CREW FORMAN INSTRUCTED WELDER 1 (INJURED EMPLOYEE) TO REMOVE THE TAPPING TEE AND INSTALL A LEAK SCREW IN THE MAIN TO ELIMINATE THE LEAK. WELDER 1 (INJURED EMPLOYEE) USED AN ELECTRIC BAND SAW TO CUT THE TEE OFF THE MAIN. WHILE CUTTING THE TEE OFF THE MAIN THE GAS IGNITED, AND WELDER 1 (INJURED EMPLOYEE) ESCAPED OUT OF THE HOLE WHILE RECEIVING BURNS TO HIS LEFT ARM, NECK, AND FACE. IN THE PRECONSTRUCTION MEETING, THE GAS DISTRIBUTION/CONSTRUCTION SUPERINTENDENT INSTRUCTED THE CREW FORMAN NOT TO USE THE ELECTRIC BAND SAW WHILE RETIRING THIS SERVICE. THE DISTRIBUTION/CONSTRUCTION SUPERINTENDENT TOLD THE CREW FORMAN THIS WHILE GIVING INSTRUCTIONS FOR THE DAY OF SEPTEMBER 30, 2015. THE REGULATORY COMPLIANCE SUPERVISOR WAS A WITNESS TO THIS CONVERSATION. AT 11:26AM THE CREW FORMAN CALLED THE REGULATORY COMPLIANCE SUPERVISOR AND TOLD HIM THAT WELDER 1 THE INJURED EMPLOYEE HAD RECEIVED BURNS AND THE REGULATORY COMPLIANCE SUPERVISOR ARRIVED WITHIN FIVE MINUTES, AND TOOK WELDER 1 (INJURED EMPLOYEE) TO THE EMERGENCY ROOM. SERVICE WORKER A CALLED WELDER 2 WHO ARRIVED WITH IN TWENTY MINUTES TO THE JOB SITE. WELDER 2 INSTALLED AND WELDED A LEAK SCREW IN THE MAIN TO STOP THE FLOW OF GAS. GAS WAS RELEASED FOR NO MORE THAN TWENTY MINUTES. AT APPROXIMATELY 12:05PM IT WAS DETERMINED THAT THE INJURED EMPLOYEE WOULD NEED HOSPITALIZATION AND WAS TRANSFERRED TO GRADY HOSPITAL IN ATLANTA AROUND 1:30PM. THE INJURED EMPLOYEE WAS HOSPITALIZED, NO PROPERTY DAMAGE, AND NO EVACUATIONS. THE REGULATORY COMPLIANCE SUPERVISOR CONTACTED CHRIS SWAN WITH THE PUBLIC SERVICE COMMISSION AT 12:39PM AS PER COMMISSION RULE. THE REGULATORY COMPLIANCE SUPERVISOR CONTACTED THE OFFICE OF PIPELINE SAFETY NATIONAL RESPONSE CENTER AT 1:50PM AND REPORTED THE INCIDENT. THE NATIONAL RESPONSE CENTER GAVE THE REGULATORY COMPLIANCE SUPERVISOR A CONFIRMATION NUMBER OF: 1129766. PUBLIC SERVICE COMMISSION INSPECTOR LYNN BUFFINGTON ARRIVED AT OUR OFFICE AT 2:20PM TO INVESTIGATE THE INCIDENT. THE CREW WAS WORKING ON A .75 INCH STEEL SERVICE ATTACHED TO A 2 INCH STEEL MAIN WITH AN OPERATING PRESSURE OF 30 PSIG. NO CUSTOMERS WERE AFFECTED.
2025-03-31 10:13 | NO | YES | NO | 20150100 | 16188 | 2015-11-04 14:31 | SUPPLEMENTAL FINAL | 13062 | NATIONAL FUEL GAS DISTRIBUTION CORP - NEW YORK | 6363 MAIN ST. | WILLIAMSVILLE | NY | 14221 | 2015-10-05 15:32 |  |  | 2015 | 56 COURT STREET | LANCASTER | ERIE | NY | 14086-2324 | 42.9006 | -78.662 | [9 empty] | 2015-10-05 16:16 | 1130150 |  | NATURAL GAS |  | 2.88 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2015-10-05 14:14 |  |  |  | 2015-10-05 14:25 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2003 | [5 empty] | 1.125 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 12.5 |  |  | 2406 | MECHANICAL PUNCTURE | 0.3 | 0.5 | [7 empty] | CLASS 3 LOCATION | 200000 | 242251.6430136204 | 1000 | 1211.258215068102 | 900 | 1090.1323935612918 | 0 | 0 |  |  | 15 | 15.03521126760563380281690140845070422535 |  | 0 | 201915 | 101300.440501375718952112676056338028169 | 244568.0688335173994338028169014084507042 | 0 | 0 | 1 |  |  |  |  | 43 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | CALL RECEIVED FROM LANCASTER 911 |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE REGULATOR STATION FEEDING THE DISTRIBUTION SYSTEM IS MANUALLY SET. THE SYSTEM IS MONITORED BY SCADA BUT THE LEAK ON THE SERVICE WAS NOT SIGNIFICANT ENOUGH TO BE NOTICED. THE CONTROLLER'S ACTIONS WOULD NOT HAVE AFFECTED THE OUTCOME. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | TRENCHER | DRAINAGE | YES | 928554223100 | DIG SAFELY NEW YORK, INC. |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | STEVEN M MONNIE | ASSOCIATE ENGINEER | monnies@natfuel.com | 814-871-8204 | 814-871-8659 |  |  |  | CRAIG K SWIECH | SUPERINTENDENT | 716-827-5551 | swiechc@natfuel.com | AT APPROXIMATELY 2:14 PM ON MONDAY, OCTOBER 5, 2015, A CONTRACTOR USING A TRENCHER TO INSTALL DRAINAGE STRUCK A 1" CTS PLASTIC NATURAL GAS SERVICE LINE WHICH RESULTED IN A FIRE DAMAGING 2 RESIDENCES. THERE WERE NO INJURIES OR FATALITIES. THE ONE-CALL CENTER WAS NOTIFIED PRIOR TO THE EXCAVATION ACTIVITY. INVESTIGATION INTO THE INCIDENT SHOWS THE SERVICE LINE WAS ACCURATELY LOCATED AND THE EXCAVATOR USED INSUFFICIENT EXCAVATION PRACTICES WHICH CAUSED THE SERVICE LINE TO BE DAMAGED. THE SERVICE LINE TO THE SINGLE AFFECTED RESIDENCE WAS SHUT DOWN AT 15:00 ON 10/5/2015 AND PERMANENTLY DISCONNECTED.
2025-03-31 10:13 | NO | YES | NO | 20150101 | 16189 | 2015-11-06 10:05 | ORIGINAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2015-10-06 16:12 |  |  | 2015 | 5205 S. 193RD E. AVE | BROKEN ARROW | WAGONER | OK | 74014 | 36.0863 | -95.7615 | [9 empty] | 2015-10-07 11:18 | 1130296 |  | NATURAL GAS |  | 2536.79 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-10-06 16:12 |  |  |  | 2015-10-06 16:12 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 150 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1978 | [5 empty] | 2.375 | API 5L | UNKNOWN | STEEL |  | SEAMLESS | SEAMLESS | 0.125 | [6 empty] | MECHANICAL PUNCTURE | 2.5 | 0.5 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 59944 | 72607.662444042306288 | 38426 | 46543.808172206887452 | 0 | 0 |  |  | 13156 | 13186.8826291079812206572769953051643192 |  | 0 | 111526 | 61547.6041134255134396244131455399061033 | 132338.3532453571749606572769953051643192 | 0 | 0 | 0 |  |  |  |  | 380 | 380 | 440 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LINE WAS PUNCTURED BY THE OPERATOR'S CONTRACTED EXCAVATOR. | [12 empty] | YES | 1 | 0 | YES | 3 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 1510051414244 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JOHNNY WILSON | REGULATORY COMPLIANCE SPECIALIST | jlwilson@onegas.com | (918)831 8238 | (918)831 8214 |  |  |  | RICHARD LAMIRAND | MANAGER - REGULATORY COMPLIANCE | (918)899-2797 | richard.lamirand@onegas.com | ONG'S CONTRACTOR DAMAGED ITS 2" LINE WHILE EXCAVATING TO ACCESS AND STOP GAS FLOW THROUGH A 2" GATE VALVE, AS PART OF A REGULATOR STATION REBUILD PROJECT. THE VALVE COULD NOT BE ACCESSED USING THE VALVE CHAMBER DUE TO DEBRIS INSIDE. EXCAVATION WORK WAS PERFORMED TO ACCESS THE VALVE LOCATED AT AN APPROXIMATE DEPTH OF 12.5 FEET. LIMITED MOBILITY IN THE WORK AREA, ALONG WITH SUBSTANTIAL ROCK, CEMENT, AND BRICK PRESENT IN THE EXCAVATION AREA COMPLICATED THE EXCAVATOR AND SPOTTER'S EFFORTS TO PROPERLY LOCATE AND EXPOSE THE VALVE.
2025-03-31 10:13 | NO | YES | YES | 20150103 | 16197 | 2015-11-13 09:53 | ORIGINAL | 11064 | LAFAYETTE GAS & UTILITIES DEPT, CITY OF | 200 EAST LOCUST ST. | LAFAYETTE | TN | 37083 | 2015-10-23 16:00 |  |  | 2015 | 718 BRATTONTOWN CIRCLE | LAFAYETTE | MACON | TN | 37083 | 36.3156 | -86.0333 | [9 empty] | 2015-10-23 18:30 | 1131542 |  | NATURAL GAS |  | 488 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 0 | 2015-10-23 16:00 |  |  |  | 2015-10-23 16:10 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | 1994 | [8 empty] | OTHER | 3/4 X 3/4 ANODELESS GAS RISER | [9 empty] | OTHER | [8 empty] | THE SUBJECT BROKE THE LOCK OUT OF THE RISER VALVE AND DUCT TAPPED A GARDEN HOSE TO THE VALVE AND RUN IT UNDER THE MOBILE HOME UP THROUGH THE FLOOR OF THE LIVING ROOM | CLASS 2 LOCATION | 24600 | 29796.9520906753092 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 320 | 320.751173708920187793427230046948356808 |  | 0 | 24920 | 12637.717520157296578403755868544600939 | 30117.7032643842293877934272300469483568 | 0 | 0 | 0 |  |  |  |  | 20 | 20 | 54 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THEFT OF SERVICES | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | THEFT OF SERVICES | [47 empty] | JEFF HARPER |  | jharper@lafayettecityhall.org | 615-666-4580 | 615-666-2922 |  |  |  | JEFF HARPER | GAS SUPERINTENDENT | 615-666-4580 | jharper@lafayettecityhall.org | THE SUBJECT THAT LIVED AT 718 BRATTONTOWN CIRCLE WAS APPARENTLY TRYING TO BURN DOWN HIS RESIDENTS. HE HAD BROKE THE BROOKS BARRLE LOCK OUT OF THE RISER VALVE AND DUCT TAPPED A GARDEN HOSE TO THE VALVE AND RUN IT UNDER THE FLOOR UP IN TO THE LIVING ROOM. THE SUBJECT TOLD POLICE THAT HE HAD ATTEMTED TO LIGHT A CIGARETTE AND THATS WHEN THE EXPLOSION OCCURED. THE SERVICE HAD BEEN SHUT OFF AND LOCKED SINCE 3/19/2008
2025-03-31 10:13 | NO | YES | NO | 20150104 | 16201 | 2015-11-27 12:59 | ORIGINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2015-06-11 11:00 |  |  | 2015 | 2045 SHELBY-GANGES RD. | SHELBY | RICHLAND | OH | 44875-9397 | 40.9015 | -82.5896 | [9 empty] | 2015-10-30 15:45 | 1132136 |  | NATURAL GAS |  | 47249.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-07-04 21:23 |  |  |  | 2015-07-04 22:06 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | FARM TAP METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.179 | [6 empty] | OTHER | [8 empty] | STEEL PIPE NIPPLE WAS SHEARED OFF WHERE IT THREADED INTO THE REGULATOR | CLASS 2 LOCATION | 0 | 0 | 200 | 242.2516430136204 | 2000 | 2422.516430136204 | 0 | 0 |  |  | 207000 | 207485.9154929577464788732394366197183099 |  | 0 | 209200 | 193040.2867342161359549295774647887323944 | 210150.6835661075708788732394366197183099 | 0 | 0 | 1 |  |  |  |  | 137.1 | 140 | 495 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ROB R. SMITH | OPERATIONS COMPLIANCE MANAGER | rrsmith@nisource.com | 6148182110 | 6148182151 |  |  |  | ROB R. SMITH | OPERATIONS COMPLIANCE MANAGER | 6148182110 | rrsmith@nisource.com | ON JUNE 11, 2015 A RURAL FARM TAP METER SETTING WAS ACCIDENTALLY DAMAGED BY AN AGRICULTURAL SPRAYER. THE SPRAYER SHEARED OFF A STEEL PIPE NIPPLE WHERE IT WAS THREADED INTO THE REGULATOR. THE DAMAGE TO THIS REMOTE METER SETTING AND SUBSEQUENT RELEASE OF GAS WERE NOT REPORTED TO COLUMBIA UNTIL JULY 4, 2015. COLUMBIA PERSONNEL PROMPTLY RESPONDED AND MADE THE SITUATION SAFE ON JULY 4, 2015. ON OCTOBER 30, 2015, COLUMBIA ENGINEERS PERFORMED THE GAS LOSS CALCULATION AND DETERMINED THAT THIS EVENT MET THE REPORTING CRITERIA AS SET FORTH IN CFR 49 PART 191.3.
2025-03-31 10:13 | NO | NO | NO | 20150105 | 16202 | 2015-11-30 23:58 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2015-10-29 13:19 |  |  | 2015 | 2700 21ST STREET | SACRAMENTO | SACRAMENTO | CA | 95818 | 38.5558 | -121.4873 | [9 empty] | 2015-10-29 18:00 | 1132079 |  | NATURAL GAS |  | 427.53 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 13 | 2015-10-29 13:19 |  |  |  | 2015-10-29 13:39 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 32 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6 | SDR 13 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.491 |  | 2406 | MECHANICAL PUNCTURE | 1.5 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 50000 | 60562.9107534051 | 0 | 0 | 0 | 0 |  |  | 1838 | 1842.314553990610328638497652582159624413 |  | 0 | 51838 | 26787.5900968882798122065727699530516432 | 62405.2253073957103286384976525821596244 | 0 | 0 | 50 |  |  |  |  | 54 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | WATER | NO | [5 empty] | YES | 10 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 925-328-6107 |  |  |  |  | LARRY DENISTON | MANAGER REGULATORY COMPLIANCE | 925-328-5756 | lcd1@pge.com | AT 1319 HOURS ON 10/29/15, PG&E WAS NOTIFIED OF A THIRD PARTY DIG-IN NEAR 2700 21ST STREET IN SACRAMENTO. PG&E'S GAS SERVICE REPRESENTATIVE ARRIVED ON-SITE AT 1339 HOURS. THE CONTRACTOR, ZLUTKA UTILITIES PERFORMING BORING OPERATIONS STRUCK A 6-INCH GAS DISTRIBUTION MAIN. THE EXCAVATOR DID NOT HAVE A VALID USA TICKET. NO INJURIES, FATALITITES, OR IGNITION. FIRE DEPARTMENT EVACUATED 3 APARTMENT BUILDINGS AND 10 HOMES AND SHUT OFF GAS SERVICE AT THE SERVICE VALVES. MEDIA (KCRA 3) WAS OBSERVED ON THE SCENE AT APPROXIMATELY 1455 HOURS. THE FLOW OF GAS WAS COMPLETELY STOPPED AT 1648 HOURS BY SQUEEZING AND ISOLATING THE DAMAGED PIPE. REPAIRS ON THE PIPE WERE COMPLETED ON 10/30/15 AT 0300 HOURS AND THE PIPELINE WAS RESTORED TO NORMAL OPERATION ON 10/30/15 AT 0500 HOURS. GAS SERVICE TO THE CUSTOMERS WAS RESTORED BY 10/30/15 AT 0300 HOURS (THE GAS SERVICE LINES SERVING THESE 3 APARTMENT BUILDINGS WERE NOT CONNECTED TO THE PORTION OF THE GAS MAIN THAT WAS DAMAGED AND ISOLATED). THE AMOUNT OF UNINTENTIONAL GAS RELEASE IS LESS THAN THE 3 MMCF. THIS INCIDENT IS BEING REPORTED TO THE DOT AND CPUC DUE TO SIGNIFICANT PUBLIC AND MEDIA ATTENTION, AND DAMAGES ARE EXPECTED TO BE GREATER THAN $50,000.
2025-03-31 10:13 | NO | YES | NO | 20150106 | 16204 | 2015-12-03 15:26 | ORIGINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2015-11-03 14:30 |  |  | 2015 | WEST 22 ST AND NEPTUNE AVE | BROOKLYN | KINGS | NY | 11224 | 40.5784 | -73.9893 | [9 empty] | 2015-11-03 20:05 | 1132503 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-11-03 14:30 |  |  |  | 2015-11-03 14:59 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6.625 | UNKNOWN | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | OTHER | [8 empty] | NO RELEASE OF GAS | CLASS 1 LOCATION | 0 | 0 | 0 | 0 | 122850 | 148803.0717211163307 | 0 | 0 |  |  | 0 | 0 |  | 0 | 122850 | 61629.7695018573204 | 148803.0717211163307 | 0 | 0 | 177 |  |  |  |  | 10 | 12 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | YES | 6 | 0 | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | ALL NEW PIPE INSTALLED PREVIOUSLY BY AN ALLIANCE RESOURCE. ON 11.03.2015, THE PROJECT ENGINEER INSTRUCTED THE IN-HOUSE MECHANICAL CREW TO JOIN PIPE SEGMENTS. THE PROJECT ENGINEER STATED BACK FEED WAS PREVIOUSLY ESTABLISHED BY ANOTHER MECHANICAL CREW. PRIOR TO STOPPING FLOW, THE CREW LEAD FOLLOWED STEPS OF THE SOP AND INFORMED GSO OF GAUGE READINGS MONITORED FOR ~30 MINUTES. APP. 50 MINS. LATER, PRESSURE DROPPED AND CUSTOMERS NOTIFIED CREW OF AN INTERRUPTION OF SERVICE. | [47 empty] | CORINNE BYRNES | PRIN PROG MGR OPERATIONS CODES AND POLICY | corinne.byrnes@nationalgrid.com | 5164924469 |  |  |  |  | CORINNE BYRNES | PRIN PROG MGR- OPERATIONS CODES AND POLICY | 6317703549 | corinne.byrnes@nationalgrid.com | TWO ADJACENT CONSTRUCTION PROJECTS WERE IN PROGRESS PRIOR TO THE STATED INCIDENT. A CONSTRUCTION CREW WAS PERFORMING A SCHEDULED SOP FOR TIE IN OF A NEW 6" HP MAIN AT THE INTERSECTION OF WEST 22 ST & NEPTUNE AVE WHEN THEY LOST GAS PRESSURE TO THE MAIN CAUSING AN UNPLANNED SUPPLY INTERRUPTION TO 177 SERVICES. AN INCIDENT ASSESSMENT IS CURRENTLY IN PROGRESS TO ESTABLISH ROOT CAUSE ANALYSIS. ON 11.03.2015, THE PROJECT ENGINEER ON SITE INSTRUCTED THE IN-HOUSE MECHANICAL CREW TO JOIN PIPE SEGMENTS. THE PROJECT ENGINEER STATED TO CREW LEAD A BACK FEED WAS PREVIOUSLY ESTABLISHED WITHIN THE PROJECT SCOPE BY ANOTHER MECHANICAL CREW. PRIOR TO STOPPING FLOW OF SEGMENTS TO BE JOINED, THE CREW LEAD FOLLOWED STEPS OF THE SOP AND INFORMED GSO OF GAUGE READINGS PRIOR TO AND AFTER MONITORING FOR ~30 MINUTES. NOTE, ON 11.03.2015 THERE WAS NO EVIDENCE OF CUSTOMER DEMAND ON THE SYSTEM AS THE TEMPERATURE WAS 70 DEGREES. AFTER THE PIPE JOINING WAS STARTED, APPROXIMATELY 50 MINUTES LATER, PRESSURE DROPPED AND CUSTOMERS NOTIFIED CREW OF AN INTERRUPTION OF SERVICE.
2025-03-31 10:13 | YES | NO | NO | 20150107 | 16346 | 2015-12-09 19:10 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2015-11-09 12:15 |  |  | 2015 | 127 E. GROVE STREET | STOCKTON | SAN JOAQUIN | CA | 95204 | 37.983 | -121.2997 | [9 empty] | 2015-11-09 14:15 | 1132993 |  | NATURAL GAS |  | 300 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2015-11-09 12:15 |  |  |  | 2015-11-09 12:35 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | METER SET MELTED FROM THE FIRE | CLASS 3 LOCATION | 100000 | 121125.8215068102 | 4000 | 4845.032860272408 | 1000 | 1211.258215068102 | 0 | 0 |  |  | 1500 | 1503.521126760563380281690140845070422535 |  | 0 | 106500 | 54065.8617386766552112676056338028169014 | 128685.6337089112733802816901408450704225 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON NOVEMBER 9, 2015, 1215 HOURS, PG&E WAS NOTIFIED OF A STRUCTURE FIRE AT 127 E. GROVE STREET IN STOCKTON. PG&E'S GAS SERVICE REPRESENTATIVE (GSR) WAS ONSITE AT 1235 HOURS AND GAS HAD ALREADY BEEN SHUT-IN AT THE SERVICE VALVE BY THE FIRE DEPARTMENT. THE GSR PLUGGED THE RISER AT 1326 HOURS. THE FIRE DEPARTMENT CONFIRMED THAT THE METER HAD BEEN MELTED AND GAS WAS BEING RELEASED PRIOR TO THEIR ARRIVAL. THE FIRE REPORT FROM THE STOCKTON FIRE DEPARTMENT INDICATED THAT THE ORIGIN OF THE FIRE WAS THE VEHICLE STORAGE AREA, HEAT SOURCE UNDETERMINED, AND ITEM FIRST IGNITED AS UNDETERMINED. THE NEIGHBORING STRUCTURE AT 139 E. GROVE STREET IN STOCKTON WAS ALSO DAMAGED BY THE FIRE. THE INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO ONE FATALITY AND THE CPUC DUE TO GAS RELEASE FROM PG&E'S FACILITIES, SUBSEQUENT IGNITION AND MEDIA COVERAGE. UNIVISION MEDIA WAS CONFIRMED ON-SITE AT 1326 HOURS. AN INITIAL SPECIAL LEAK SURVEY WAS CONDUCTED FOR THE AREA ON 11/9/15 AND NO LEAKS WERE FOUND. A FOLLOW-UP SPECIAL LEAK SURVEY WAS CONDUCTED WHEN CONDITIONS WERE DRY, AND NO LEAKS WERE FOUND.
2025-03-31 10:13 | NO | YES | NO | 20150108 | 16463 | 2015-12-27 21:28 | SUPPLEMENTAL FINAL | 20050 | AMERENUE | 1901 CHOUTEAU | SAINT LOUIS | MO | 63103 | 2015-11-27 14:45 |  |  | 2015 | 3404 GEORGIA ST | LOUISIANA | PIKE | MO | 63353 | 39.4306 | -91.0731 | [9 empty] | 2015-11-27 21:55 | 1134407 |  | NATURAL GAS |  | 11.83 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 5 | 2015-11-27 14:45 |  |  |  | 2015-11-27 13:19 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 0.5 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 7 |  |  | 3408 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 200000 | 242251.6430136204 | 500 | 605.629107534051 | 4500 | 5450.661967806459 | 0 | 0 |  |  | 60 | 60.14084507042253521126760563380281690141 |  | 0 | 205060 | 102897.3330122654214084507042253521126761 | 248368.0749340313325352112676056338028169 | 1 | 0 | 0 |  |  |  |  | 30 | 30 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA-BASED INFORMATION ASSISTED WITH INDICATION OF INCIDENT. | [12 empty] | YES | 1 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | NUT FOLLOWER |  |  |  | CONTINENTAL |  | OTHER | MATERIALS JOINED: 1ST PLASTIC, 2ND PLASTIC | [22 empty] | YES | NO ADDITIONAL FACTORS WERE FOUND TO CONTRIBUTE. |  | YES |  |  |  | OTHER | COULD NOT DETERMINE SUBCAUSE FOR THE COUPLING FAILURE. | YES | 2003 | 100 | [84 empty] | JIM DIEMER | SUPERINTENDENT GAS OPERATIONS AND ENGINEERING | jdiemer@ameren.com | 636-639-8208 |  |  |  |  | PAM HARRISON | SUPERINTENDENT GAS OPERATIONS AND ENGINEERING | 573-619-3124 | pschaefer@ameren.com | ON 11/27/15 AT 13:09, AMEREN RECEIVED A REPORT OF AN OUTSIDE GAS ODOR AT 3404 GEORGIA ST, LOUISIANA, MO FROM THE BUSINESS OWNER. AN AMEREN GAS SERVICE WORKER WAS DISPATCHED TO THE LOCATION AND ARRIVED AT 13:19. THE SERVICE WORKER TALKED WITH THE BUSINESS OWNER AND CONDUCTED A LEAK INVESTIGATION. SMALL LEAKS WERE FOUND ON THE ABOVE GROUND PIPING ON EACH SIDE OF THE SERVICE REGULATOR. THE SERVICE WORKER SHUT OFF THE SERVICE AT THE RISER VALVE, REPAIRED THE LEAKS AND THEN TURNED THE SERVICE ON AND TESTED HIS REPAIRS WITH LEAK SOAP SOLUTION. HE FOUND NO LEAKS AND WAS PREPARING TO GO INSIDE TO RELIGHT CUSTOMER'S EQUIPMENT AND A FIRE BROKE OUT OUTSIDE AT THE METERSET LOCATION AT APPROXIMATELY 14:45. THE BUSINESS OWNER AND SERVICE WORKER ATTEMPTED TO EXTINGUISH THE FIRE BUT WERE UNABLE TO DO SO AND 911 WAS CALLED. THE FIRE SPREAD QUICKLY AND THE FIRE DEPARTMENTS WERE UNABLE TO EXTINGUISH THE FIRE BEFORE THE BUILDING WAS A TOTAL LOSS. THE IGNITION SOURCES HAS NOT BEEN DETERMINED. AT 16:10 AMEREN GAS PERSONNEL ARRIVED, LOCATED EMERGENCY VALVES, AND CONDUCTED BAR-HOLE TESTING AROUND THE PERIMETER OF 3404 GEORGIA AND THE ADJACENT STRIP MALL NEXT DOOR. NO INDICATIONS OF GAS WERE FOUND. EMERGENCY VALVES WERE NOT UTILIZED DUE TO THE BUILDING ALREADY WAS ENGULFED IN FIRE AND NATURAL GAS WAS NO LONGER FUELING THE FIRE. ONCE THE FIRE WAS CONTROLLED, THE RISER WAS EXCAVATED. DURING EXCAVATION OF THE RISER, BUBBLES BEGAN TO APPEAR IN WATER WITHIN THE EXCAVATION APPROXIMATELY 24"-30" FROM WHERE THE RISER WENT INTO THE GROUND. NO GAS READINGS COULD BE OBTAINED DUE TO EXCESSIVE WATER IN THE EXCAVATION. AMEREN CREW PERSONNEL CONTINUED TO EXCAVATE IN ORDER TO EXPOSE THE RISER AND SERVICE PIPE AND DISCOVERED A 1/2" COMPRESSION COUPLING LEAKING ON THE 1/2" CTS PE SERVICE. THE SERVICE WAS SQUEEZED OFF AT APPROXIMATELY 21:15. THIS SUPPLEMENTAL REPORT WAS SUBMITTED TO CORRECT INFORMATION ON PART B, PART C, PART D AND PART G FROM PREVIOUSLY SUBMITTED REPORTS. ALTHOUGH THE SOURCE OF THE GAS RELEASE CANNOT BE CONCLUSIVELY DETERMINED, THE LEAKING COUPLING COULD NOT BE DISCOUNTED AS A POSSIBLE SOURCE AND IS THEREFORE IDENTIFIED AS THE SOURCE IN THIS SUPPLEMENTAL REPORT.
2025-03-31 10:13 | NO | YES | NO | 20150109 | 16212 | 2015-12-31 11:00 | ORIGINAL FINAL | 30769 | MISSOURI GAS ENERGY | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2015-12-01 14:44 |  |  | 2015 | 2038 WHEELING | KANSAS CITY | JACKSON | MO | 64126 | 39.0869 | -94.5112 | [9 empty] | 2015-12-01 15:54 | 1134701 |  | NATURAL GAS |  | 13.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 10 | 2015-12-01 14:44 |  |  |  | 2015-12-01 14:54 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2000 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | A VEHICLE COLLIDED WITH THE OUTSIDE METER AND SEVERED THE SERVICE RISER. | CLASS 3 LOCATION | 300000 | 363377.4645204306 | 896 | 1085.287360701019392 | 500 | 605.629107534051 | 0 | 0 |  |  | 71 | 71.16666666666666666666666666666666666667 |  | 0 | 301467 | 151266.2078451916071573333333333333333333 | 365139.5476553323370586666666666666666667 | 0 | 0 | 6 |  |  |  |  | 15 | 15 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS CAUSED BY A THIRD PARTY VEHICULAR COLLISION | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MARK LAUBER | MANAGER OF PIPELINE SAFETY COMPLIANCE | mark.lauber@thelacledegroup.com | (314) 658-5413 |  |  |  |  | CRAIG R. HOEFERLIN | VICE PRESIDENT OF OPERATIONS SERVICES | 3143492972 | craig.hoeferlin@thelacledegroup.com | THE OPERATOR OF STOLEN VEHICLE STRUCK AN OUTSIDE METER SET WHILE ATTEMPTING TO EVADE LAW ENFORCEMENT. THE VEHICLE WENT OFF THE ROAD, LOST CONTROL AND STRUCK THE METER. THE GAS SUPPLYING THE METER IGNITED AND CAUSED DAMAGE TO THE ADJACENT APARTMENT BUILDING. GAS WAS MADE SAFE APPROXIMATELY 1.5 HOURS AFTER THE INCIDENT OCCURED.
2025-03-31 10:13 | NO | YES | NO | 20160001 | 34477 | 2016-01-07 14:10 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2015-12-09 09:30 |  |  | 2015 | INTERSECTION RHODE ISLAND RD AND HASKEL CIRCLE | LAKEVILLE | PLYMOUTH | MA | 02347 | 41.8798 | -70.931 | [9 empty] | 2015-12-09 12:27 | 1135352 |  | NATURAL GAS |  | 1743.64 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 6 | 2015-12-09 09:30 |  |  |  | 2015-12-09 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1990 | [5 empty] | 4 | ASTM D2513 | DRISCOPIPE M8000 | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 1 | 4 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 91087 | 110329.877035908206874 | 0 | 0 | 0 | 0 | COST ASSOCIATED WITH EMERGENCY RESPONSE IS ROLLED INTO DAMAGE AND REPAIR COSTS |  | 5493 | 5505.894366197183098591549295774647887324 |  | 0 | 96580 | 50788.600774185067071661971830985915493 | 115835.7714021053899725915492957746478873 | 0 | 0 | 403 |  |  |  |  | 74 | 74 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 20154901133 |  |  | UTILITY OWNER | YES | YES | 13 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | MEGGAN BIRMINGHAM | MANAGER COMPLIANCE GAS OPERATIONS | meggan.pena@eversource.com | 508.468.9956 |  |  |  |  | MEGGAN BIRMINGHAM | MANAGER COMPLIANCE GAS OPERATIONS | 508.468.9956 | meggan.pena@eversource.com | 3RD PARTY CONTRACTOR WORKING ON A WATER MAIN INSTALLATION HIT THE GAS LINE SEVERING THE 4 IN LINE. 403 CUSTOMERS WERE IMPACTED. A BREAKDOWN BETWEEN COMMERCIAL AND RESIDENTIAL WAS NOT OBTAINED.
2025-03-31 10:13 | NO | YES | NO | 20160002 | 16221 | 2016-01-13 18:09 | ORIGINAL FINAL | 11032 | LACLEDE GAS CO | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2015-12-14 06:26 |  |  | 2015 | 5730 MANGO DRIVE | MEHLVILLE | SAINT LOUIS | MO | 63129 | 38.4693 | -90.3483 | [9 empty] | 2015-12-14 10:16 | 1135749 |  | NATURAL GAS |  | 251 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2015-12-14 06:30 |  |  |  | 2015-12-14 06:58 |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 50 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1978 | [5 empty] | 3 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.304 |  | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 300000 | 363377.4645204306 | 20000 | 24225.16430136204 | 500 | 605.629107534051 | 0 | 0 |  |  | 1319 | 1322.096244131455399061032863849765258216 |  | 0 | 321819 | 162007.2339764529346291079812206572769953 | 389530.3541734581463990610328638497652582 | 0 | 0 | 0 |  |  |  |  | 18 | 18 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE MAOP WAS NOT EXCEEDED. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 1978 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [5 empty] | YES | STRESS FROM TREE. | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | MARK LAUBER | DIR OF HEALTH SAFETY ENVIRONMENTAL AND CRISIS MGMT | mark.lauber@thelacledegroup.com | (314) 658-5413 |  |  |  |  | CRAIG R. HOEFERLIN | VICE PRESIDENT OF OPERATIONS SERVICES | (314) 349-2972 | craig.hoeferlin@thelacledegroup.com | A BUTT FUSION JOINT ON A 3 INCH PE PLASTIC MAIN FAILED RESULTING IN A LEAK. THE NATURAL GAS MIGRATED INTO A NEARBY RESIDENTIAL BASEMENT AND IGNITED. THE LEAK WAS LOCATED UNDER A TREE WHICH WAS DETERMINED TO BE PLACING STRESS ON THE PIPE AND WAS A CONTRIBUTING FACTOR TO THE JOINT FAILURE. THE MAIN WAS PERMANENTLY REPAIRED.
2025-03-31 10:13 | NO | YES | NO | 20160003 | 16299 | 2016-01-15 11:21 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2015-12-16 10:36 |  |  | 2015 | 28800 NORTHLINE ROAD | ROMULUS | WAYNE | MI | 48174 | 42.2101 | -83.3215 | [9 empty] | 2015-12-16 17:45 | 1135991 |  | NATURAL GAS |  | 7991.85 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-12-16 10:36 |  |  |  | 2015-12-16 10:52 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 120 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2000 | [5 empty] | 6 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 6 | 10 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 25746 | 31185.054005143354092 | 57344 | 69458.391084865241088 | 2326 | 2817.386608248405252 | TRAFFIC CONTROL |  | 32526 | 32602.3521126760563380281690140845070423 |  | 0 | 117942 | 73009.4580664288622251267605633802816901 | 136063.1838109330567700281690140845070423 | 0 | 0 | 0 |  |  |  |  | 45 | 45 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | BORING | WATER | YES | 53430367 |  |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ROBERT FRECKELTON | MANAGER | freckeltonr@dteenergy.com | [5 empty] | FRENAE SMITH | SUPERVISOR | 313-389-7762 | smithff@dteenergy.com | A CONTRACTOR CREW PERFORMING DIRECTIONAL BORING FOR WATER MAIN WORK STRUCK A 6-INCH PLASTIC GAS DISTRIBUTION MAIN DURING PULL-BACK OF A REAMING TOOL. THE LOCATION OF THE GAS MAIN HAD NOT BEEN VERIFIED PRIOR TO THE WORK. DTE GAS EMERGENCY RESPONSE PERSONNEL STOPPED THE LEAKING GAS FROM THE EAST BY INSTALLING A LINE STOPPER PRESSURE CONTROL FITTING ON A 12-INCH SECTION OF MAIN, AND FROM THE WEST BY PINCHING THE 6-INCH PLASTIC MAIN. LEAKING GAS WAS STOPPED AT 23:23, SOME 13 HOURS AFTER THE DAMAGE. REPAIRS WERE COMPLETED AT 04:30 ON DECEMBER 17, 2015, USING 3 FEET OF NEW 6-INCH PLASTIC PIPE AND TWO ELECTROFUSION COUPLINGS.
2025-03-31 10:13 | NO | NO | NO | 20160004 | 16223 | 2016-01-15 11:48 | ORIGINAL FINAL | 31265 | NEW HAMPSHIRE GAS CORP | 15 BUTTRICK ROAD | LONDONDERRY | NH | 03053 | 2015-12-19 08:51 |  |  | 2015 | 207 EMERALD ST. 03431 | KEENE | CHESHIRE | NH | 03431 | 42.9336 | -72.2781 | [9 empty] | 2015-12-19 19:54 | 1136250 |  |  |  | 3.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-12-19 08:51 |  |  |  | 2015-12-19 09:03 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | BLOWERS | 2003 | [8 empty] | OTHER | MECHANICAL AIR SUPPLY BLOWER | [9 empty] | OTHER | [8 empty] | LIBERTY UTILITIES TECHNICIANS PURGED HIGH CONCENTRATION BTU PROPANE FROM SYSTEM AT 10 DESIGNATED LOCATIONS. | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 41986 | 50855.887417849330572 | 50000 | 60562.9107534051 | LOCAL CITY AND TOWNS EMERGENCY RESPONSES REIMBURSEMENT IS YET TO BE DETERMINED. |  | 76 | 76.17840375586854460093896713615023474178 |  | 0 | 92062 | 46216.794085911155901370892018779342723 | 111494.9765750102991166009389671361502347 | 35 | 0 | 54 |  |  |  |  | 3.5 | 3.5 | 5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PROPANE SCADA ONLY MONITORS SYSTEM ALARMS, THERE ARE NO OTHER CONTROLLER ADJUSTMENTS OR ACTIVITIES. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [10 empty] | YES | ELECTRICAL POWER FLUCTUATIONS CAUSED THE ADJUSTABLE SPEED DRIVES TO TRIP, SHUTTING DOWN CONTROL SUPPLY AIR BLOWERS TO SYSTEM. | [71 empty] | RUSSELL MCINTYRE | PROGRAM MANAGER- COMPLIANCE | russell.mcintyre@libertyutilities.com | 603-216-3664 | 603-421-1768 |  |  |  | LEO CODY | MANAGER-COMPLIANCE | 603-216-3528 | leo.cody@libertyutilities.com | LIBERTY UTILITIES AND A THIRD PARTY MONITORING COMPANY REPORTED THAT THEIR MONITORING HAD DETECTED A PROBLEM WITH THE BLOWERS THAT PROVIDE AIR TO THE PROPANE/AIR MIXING SYSTEM AT THE PLANT. THIS MECHANICAL FAILURE RESULTED IN INCORRECT AIR TO PROPANE MIXTURE VOLUMES BEING SENT INTO THE DISTRIBUTION SYSTEM. LIBERTY UTILITIES RESOURCES RESPONDED AND CORRECTED THE MALFUNCTION, MITIGATED ADDITIONAL HAZARDS AND COMMENCED CUSTOMER AWARENESS AND NOTIFICATIONS.
2025-03-31 10:13 | NO | YES | NO | 20160005 | 16230 | 2016-01-17 12:14 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2015-12-19 14:02 |  |  | 2015 | 42-22 ORCHARD STREET | NEW YORK | QUEENS | NY | 11101-2906 | 40.7479 | -73.9389 | [9 empty] | 2015-12-19 14:55 | 1136234 |  | NATURAL GAS |  | 2419 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2015-12-19 14:14 |  |  |  | 2015-12-19 14:14 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1968 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.322 | [6 empty] | MECHANICAL PUNCTURE | 12 | 8 | [7 empty] | CLASS 4 LOCATION | 100000 | 121125.8215068102 | 54810 | 66389.06276788267062 | 2821 | 3416.959424707115742 | 6546 | 7928.896275835795692 | MATERIALS |  | 30455 | 30526.4906103286384976525821596244131455 |  | 0 | 194632 | 110600.9454754689366607699530516431924883 | 229387.2305855644205516525821596244131455 | 2 | 0 | 0 |  |  |  |  | 58 | 60 | 80 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | DRILLING | SITE DEVELOPMENT | YES | 153310385 | NY 811 |  | CONTRACT LOCATOR | YES | YES | 47 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | (718) 319-2310 | (718) 904-4607 |  |  |  | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | (718) 319-2310 | fagank@coned.com | ON DECEMBER 19, 2015 AT 14:02, THE FIRE DEPARTMENT OF NEW YORK (FDNY) REPORTED A CONTRACTOR DAMAGE AT A CONSTRUCTION SITE AT THIS LOCATION TO CON EDISON'S GAS EMERGENCY RESPONSE CENTER. A CODE MURRE (MULTIPLE RESOURCE RESPONSE EVENT) WAS INITIATED AND GAS DISTRIBUTION SERVICES (GDS), GAS CONSTRUCTION AND SUPERVISION WERE DISPATCHED. GDS SUPERVISION ARRIVED AT 14:14 AND REPORTED A SUSPECTED GAS FED FIRE IN THE STREET WITH A THIRD PARTY'S DRILLING MACHINE ENGULFED IN FLAMES. AN 8" HIGH PRESSURE RADIAL MAIN VALVE WAS IDENTIFIED TO ISOLATE THE GAS SUPPLY TO THE AREA, THE VALVE WAS LOCATED AND AT 14:33, VALVE #17788 WAS CLOSED AND THE GAS IGNITION WAS EXTINGUISHED. GDS INVESTIGATED AND REPORTED A POSCILLICO CONSTRUCTION CO. DRILLING RIG DAMAGED AN 8" HIGH PRESSURE STEEL MAIN WHILE DRILLING FOR I-BEAM SUPPORTS FOR NEW ELECTRIC VAULTS ASSOCIATED WITH NEW BUILDING CONSTRUCTION. THE DAMAGED 8" MAIN SUPPLIES 42-43 ORCHARD STREET WHICH IS THE METERING BUILDING TO THE SUNNYSIDE RAILROAD YARD AT THE SOUTHERN END OF ORCHARD STREET. NO BUILDINGS WERE DAMAGED BY THE FIRE AND THERE WERE TWO COMMERCIAL SERVICES INTERRUPTED AS A RESULT OF THE MAIN VALVE CLOSURE, 42-22 AND 42-43 ORCHARD ST. NYC EMERGENCY MANAGEMENT (NYCEM) REPORTED THIS INCIDENT, AS WELL AS THE LOSS OF SUPPLY TO THE METERING HOUSE, DID NOT IMPACT RAILROAD OPERATIONS. ONE CONSTRUCTION WORKER (AN UNNAMED THIRD PARTY LABORER) WAS TRANSPORTED VIA EMS TO AN AREA HOSPITAL DUE TO A REPORTED MINOR RESPIRATORY CONDITION. FDNY BATTALION 45, NYCEM AND NYC DEPARTMENT OF ENVIRONMENTAL PROTECTION-HAZMAT RESPONDED AND MULTIPLE MEDIA SOURCES WERE ON LOCATION AND/OR INQUIRED. MULTIPLE INTERNAL COMPANY DEPARTMENTS RESPONDED TO SUPPORT THE RESPONSE AND MITIGATION OF THIS INCIDENT. ON DECEMBER 21, 2015 AT 14:17, GAS CONSTRUCTION COMPLETED REPAIRS AND THE MAIN WAS PLACED IN SERVICE. THERE WERE NO REPORTED EVACUATIONS. THE US DOT, NYS DPS AND NYC DEP WERE NOTIFIED. THIS WAS AN UPGRADED INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20160007 | 16405 | 2016-01-26 16:00 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2015-12-29 11:15 |  |  | 2015 | INTERSECTION OF EAST 188 STREET AND PARK AVENUE | NEW YORK | NEW YORK | NY | 10458 | 40.865 | -73.9034 | [9 empty] | 2015-12-29 17:42 | 1136912 |  | NATURAL GAS |  | 9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2015-12-29 11:15 |  |  |  | 2015-12-29 11:23 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 33 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1907 | [5 empty] | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | OTHER | [8 empty] | CIRCUMFERENTIAL CRACK (2) | CLASS 4 LOCATION | 0 | 0 | 7262 | 8796.157157824556724 | 1126 | 1363.876750166682852 | 0 | 0 |  |  | 108 | 108.253521126760563380281690140845070423 |  | 0 | 8496 | 4308.122176625808807211267605633802816901 | 10268.2874291180001393802816901408450704 | 0 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 4 | 0 | YES | 2 | 0 | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | WATER MAIN BREAK CAUSED SOIL EROSION AND UNDERMINING CAST IRON MAIN RESULTING IN (2) CIRCUMFERENTIAL CRACKS. | [154 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | (718) 319-2310 | (718) 904-4607 |  |  |  | NICKOLAS HELLEN | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | (718) 319-2310 | hellenn@coned.com | ON DECEMBER 29, 2015 AT 11:15, A CON EDISON METER READER REPORTED AN INSIDE AND OUTSIDE GAS LEAK AT 4662 PARK AVE., BRONX, NEW YORK TO THE COMPANY'S GAS EMERGENCY RESPONSE CENTER (GERC). GAS DISTRIBUTION SERVICES (GDS) AND THE FIRE DEPARTMENT OF NEW YORK (FDNY) WERE DISPATCHED, ARRIVED AT 11:23 AND INVESTIGATED. AT 11:39, GDS DETECTED 3% NATURAL GAS IN A SEWER MANHOLE AND OBSERVED GAS BUBBLING IN RAIN WATER ON THE ROAD SURFACE. SUPERVISION WAS NOTIFIED AND GAS CONSTRUCTION WAS DISPATCHED. THE INVESTIGATION CONTINUED AND AT 12:45, SUPERVISION REPORTED DETECTING 62% IN ELECTRIC MANHOLE M26008. THE COVER WAS PULLED TO VENT THE TYPE 1 READINGS. THE FDNY REMAINED ON LOCATION AND ASSISTED GDS INVESTIGATE BUILDINGS AND SUBSURFACE STRUCTURES IN THE AREA TO ENSURE NO GAS MIGRATED INTO THESE LOCATIONS. AT 13:36, SUPERVISION REPORTED A PROBABLE WATER MAIN BREAK IN THE AREA DUE TO WATER INFILTRATION INTO THE REPAIR EXCAVATION AT THE SOUTHEAST CORNER OF EAST 188 STREET AND PARK AVENUE AND N.Y.C. DEPARTMENT OF ENVIRONMENTAL PROTECTION (DEP) WAS NOTIFIED TO RESPOND. AT 13:48, GDS REPORTED A GAS FIRE IN THE EXCAVATION WHICH WAS QUICKLY EXTINGUISHED WITH A PORTABLE FIRE EXTINGUISHER. FDNY WAS ON LOCATION AND NO INJURIES WERE REPORTED AT THAT TIME. SUPERVISION REPORTED FROM LOCATION AN UNIDENTIFIED ELECTRIC FACILITY MAY HAVE BEEN DAMAGED WITH A DIGGING BAR AS A SUSPECTED SOURCE OF THE IGNITION. AT 14:09, TWO GAS CONSTRUCTION EMPLOYEES AND ONE COMPANY CONTRACTOR (PETMAR CO.) EMPLOYEE WERE TRANSPORTED VIA EMS TO JACOBI MEDICAL CENTER WITH SUSPECTED 1ST DEGREE BURNS TO THEIR FACES, AND ONE GAS CONSTRUCTION EMPLOYEE WAS TRANSPORTED BY HIS SUPERVISOR TO THE SAME HOSPITAL DUE TO SUSPECTED BURNS TO THE FACE AS WELL. MULTIPLE INTERNAL COMPANY DEPARTMENTS WERE NOTIFIED. FIRE BANK LOCATIONS ON THE NORTHEAST AND SOUTHEAST CORNERS OF EAST 188 STREET WERE IDENTIFIED TO CUT AND CAP THE GAS MAIN AND GAS DISTRIBUTION ENGINEERING DETERMINED THERE WOULD BE NO NEGATIVE SYSTEM IMPACT OR CUSTOMER OUTAGES AS A RESULT OF THE 6" LOW PRESSURE MAIN ISOLATION. ELECTRIC OPERATIONS DE-ENERGIZED THE ELECTRIC FEEDER SUSPECTED TO HAVE BEEN DAMAGED (FEEDER 3X71) AND FIRE BANKS WERE EXCAVATED, THE MAIN WAS TAPPED AND AT 18:17 STOPPERS WERE INSTALLED ISOLATING THE AFFECTED SEGMENT OF MAIN. AT 19:03, THE MAIN WAS CUT AND CAPPED AND BOTH END CAPS WERE INSTALLED AND AT 19:16, GDS REPORTED THAT ALL GAS READINGS DISSIPATED. IT WAS REPORTED AT 17:04, THAT ALL FOUR INJURED PERSONNEL WERE RELEASED FROM THE HOSPITAL WITH FIRST AID TREATMENT ONLY. THE INITIAL EXCAVATION, MADE IN THE ROADWAY OFF THE SOUTHEAST CORNER OF THE INTERSECTION, WAS FOUND TO CONTAIN A LARGE PIECE OF CONCRETE WHICH HAD APPARENTLY BECOME DISLODGED FROM THE ROADWAY PAVEMENT. THAT EXCAVATION, AND OTHERS MADE TO LOCATE THE SOURCE OF THE LEAK, ALSO CONTAINED VISIBLE VOIDS IN THE SUBSURFACE SOIL CAUSED BY THE LEAKING WATER MAIN. BEFORE THE DEP MADE REPAIRS TO THE WATER MAIN THE LEAKING WATER WAS HEARD FLOWING IN A CATCH BASIN LOCATED AT THE NORTHERLY CURB OF E 188TH STREET. THE STREET VOIDS UNDER THE PAVEMENT CAUSED THE LOW PRESSURE CAST IRON MAIN TO CRACK AND RELEASE NATURAL GAS. SIGNIFICANT MEDIA COVERAGE WAS REPORTED ON LOCATION INCLUDING CHANNEL 4, CHANNEL 7, CHANNEL 11 AND NEWS12. THE U.S. DEPARTMENT OF TRANSPORTATION, N.Y.S. DEPARTMENT OF PUBLIC SERVICE (PSC) AND N.Y.C. DEPARTMENT OF ENVIRONMENTAL PROTECTION WERE NOTIFIED AND UPDATED; PSC STAFF AND OSHA RESPONDED TO THE LOCATION. NTSB SENIOR PIPELINE INVESTIGATOR ROGER EVANS CALLED THE GERC, WAS UPDATED AND REPORTED THIS INCIDENT DOES NOT MEET THE REQUIREMENT FOR NTSB RESPONSE AND INVESTIGATION. MR. EVANS REPORTED HE WAS SATISFIED WITH THE INFORMATION PROVIDED.
2025-03-31 10:13 | NO | NO | NO | 20160008 | 16232 | 2016-02-01 13:49 | ORIGINAL FINAL | 6484 | GRAHAM COUNTY UTIL INC | 9 WEST CENTER | PIMA | AZ | 85543 | 2015-12-16 06:30 |  |  | 2015 | THATCHER | THATCHER | GRAHAM | AZ | 85552 | 32.8302 | -109.7515 | [9 empty] | 2015-12-16 08:23 | 1135942 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-12-16 07:30 |  |  |  | 2015-12-16 08:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | COOPERATIVE |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | OTHER | 2" AXIAL FLOW REGULATOR | [9 empty] | OTHER | [8 empty] | NOT A RELEASE, REGULATOR FROZE UP | CLASS 3 LOCATION | 0 | 0 | 4000 | 4845.032860272408 | 68880 | 83431.46585389086576 | 7485 | 9066.26773978474347 | WAGES ETC. FROM OTHER LOCAL GAS COMPANIES |  | 0 | 0 |  | 0 | 80365 | 40316.45442423087956 | 97342.76645394801723 | 110 | 0 | 1832 |  |  |  |  | 0 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | WES REIDHEAD | GAS SUPERINTENDENT | wesr@gce.coop | (928)485-2451 | (928)485-9491 |  |  |  | JASON HUGHES | GAS SUPERINTENDANT | (928) 651-6034 | jasonhughes@gce.coop | IT WAS DETERMINED THAT A 2" AXIAL FLOW REGULATOR AT THATCHER TAP # 14-2 HAD FROZEN IN THE UNSEASONABLY COLD WEATHER, CAUSING LOSS OF LINE PACK AND EVENTUAL OUTAGE TO 1972 CONSUMERS IN THE THATCHER AREA.
2025-03-31 10:13 | NO | YES | YES | 20160009 | 16348 | 2016-02-01 16:19 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2016-01-02 03:19 |  |  | 2016 | 12505 WHISPERING HOLLOW DRIVE | OKLAHOMA CITY | OKLAHOMA | OK | 73142 | 35.5964 | -97.6469 | [9 empty] | 2016-01-02 04:39 | 1137106 |  | NATURAL GAS |  | 75.4 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 10 | 2016-01-02 03:19 |  |  |  | 2016-01-02 03:19 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1983 | [5 empty] | 4 | ASTM D2513 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 500000 | 600651.8042697905 | 5000 | 6006.518042697905 | 4200 | 5045.4751558662402 | 0 | 0 |  |  | 243 | 279.67924528301886792452830188679245283 |  | 0 | 509443 | 253608.0867651576384291105121293800539084 | 611983.4767136376640679245283018867924528 | 0 | 0 | 5 |  |  |  |  | 49 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 5 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 1983 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [6 empty] | YES | YES | [7 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | RICHARD LAMIRAND | MANAGER - REGULATORY COMPLIANCE | richard.lamirand@onegas.com | 918-947-7037 |  |  |  |  | RICHARD LAMIRAND | MANAGER - REGULATORY COMPLIANCE | 918-947-7037 | richard.lamirand@onegas.com | THE SOURCE OF THE LEAK WAS A CRACK IN A BUTT FUSION WELD IN A FOUR INCH POLYETHYLENE MAIN. THE CRACK EXTENDS 3.4 INCHES AROUND THE OUTER CIRCUMFERENCE AND 1.8 INCHES ALONG THE INTERIOR CIRCUMFERENCE. THERE WAS A LACK OF FUSION IN THE INTERIOR MID-PORTION OF THE WELD IN THE SEGMENT OF THE WELD WHERE THE CRACK WAS LOCATED. THREE ONG EMPLOYEES WERE AT THE RESIDENCE NEXT DOOR INVESTIGATING A REPORT OF AN ODOR AT THE TIME OF THE INCIDENT. SUPPLEMENTAL TO ORIGINAL REPORT SENT 2/1/16: CORRECTED PART G5 FROM BUTT WELD TO FUSION JOINT AND PROVIDED THE ASSOCIATED INFORMATION. SUPPLEMENTAL/FINAL SUBMITTED 7/29/16: NO CHANGES TO THE INFORMATION ALREADY REPORTED ARE FORTHCOMING.
2025-03-31 10:13 | NO | YES | NO | 20160010 | 16455 | 2016-02-08 10:19 | SUPPLEMENTAL FINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2016-01-09 14:45 |  |  | 2016 | 422 SOUTH 11TH STREET | OMAHA | DOUGLAS | NE | 68102 | 41.2558 | -95.9308 | [9 empty] | 2016-01-09 17:00 | 1137694 |  | NATURAL GAS |  | 50 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 100 | 2016-01-09 14:52 |  |  |  | 2016-01-09 15:16 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 42 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 2009 | [5 empty] | 2 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.229 |  | 2406 | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 3 LOCATION | 5000000 | 6006518.042697905 | 1500 | 1801.9554128093715 | 6000 | 7207.821651237486 | 0 | 0 |  |  | 127 | 146.169811320754716981132075471698113208 |  | 0 | 5007627 | 2491586.42477757758809299191374663072776 | 6015673.98957327261221698113207547169811 | 2 | 0 | 18 |  |  |  |  | 8.7 | 8.7 | 10 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 160090027 |  |  | UTILITY OWNER | YES | YES | 528 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | MICHAEL CONRAD | CLAIMS REPRESENTATIVE AND INVESTIGATOR | mike_conrad@mudnebr.com | 402-504-7165 | 402-504-5165 |  |  |  | MICHAEL CONRAD | CLAIMS REPRESENTATIVE AND INVESTIGATOR | 402-504-7165 | mike_conrad@mudnebr.com | ON 01/09/16 AT APPROXIMATELY 14:45 THE GAS SERVICE THAT PROVIDED NATURAL GAS TO 422 SOUTH 11TH STREET IN OMAHA NE WAS DAMAGED BY A PRIVATE BORING CONTRACTOR, NORTH CENTRAL SERVICES INC., AS THE CONTRACTOR WAS INSTALLING FIBER OPTICS IN AND AROUND THE AREA OF THIS SERVICE ADDRESS. AS A RESULT OF THE DAMAGED GAS SERVICE THERE WAS AN EXPLOSION AND A FIRE AT THIS LOCATION THAT RESULTED IN A LOSS. OUR INVESTIGATION REVEALED THAT ALTHOUGH THE GAS SERVICE HAD BEEN PROPERLY LOCATED, NORTH CENTRAL SERVICES INC. DID NOT ATTEMPT TO VERIFY OR POTHOLE THE EXACT DEPTH/LOCATION OF THIS GAS SERVICE AND OTHER UTILITIES THAT WERE LOCATED IN THE SAME AREA AS THE GAS SERVICE. BY NOT VERIFYING OR POTHOLING THE LOCATION AND DEPTH OF THE GAS SERVICE NORTH CENTRAL SERVICE INC. DAMAGED THE GAS SERVICE AND INITIATED THE LOSS.
2025-03-31 10:13 | NO | YES | NO | 20160011 | 16320 | 2016-02-09 15:50 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2016-01-10 07:00 |  |  | 2016 | 12755 ALLISONVILLE ROAD | FISHERS | HAMILTON | IN | 46038 | 39.9733 | -86.0329 | [9 empty] | 2016-01-11 16:47 | 1137816 |  | NATURAL GAS |  | 15.79 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2016-01-10 07:36 |  |  |  | 2016-01-10 07:36 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 23 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1987 | [5 empty] | 1 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | 350000 | 420456.26298885335 | 1000 | 1201.303608539581 | 800 | 961.0428868316648 | 0 | 0 |  |  | 69 | 79.41509433962264150943396226415094339623 |  | 0 | 351869 | 175109.41675752404607493261455525606469 | 422698.0245785642184415094339622641509434 | 0 | 0 | 1 |  |  |  |  | 54 | 54 | 90 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | JOHN SPINKS | MANAGER GAS COMPLIANCE AND QMP | jaspinks@vectren.com | 937-440-1844 | 937-440-1818 |  |  |  | JIM FRANCIS | VICE PRESIDENT SAFETY AND SYSTEM INTEGRITY | 812-491-4369 | jmfrancis@vectren.com | AN ELECTRIC COMPANY REPRESENTATIVE INDICATED A POWER LINE WAS DOWNED WHEN A TREE LIMB FELL DUE TO THE WEIGHT OF THE SNOW THAT HAD ACCUMULATED. UPON FURTHER INVESTIGATION IT WAS DETERMINED A RETIRED STEEL FUEL LINE WAS ENERGIZED BY THE DOWNED POWER LINE. THE RISER SERVING THE HOUSE WAS SITTING DIRECTLY ON TOP OF THE RETIRED STEEL FUEL LINE AND THE RETIRED FUEL LINE TERMINATED IN THE BASEMENT AND WAS UNCAPPED. WHEN THE RETIRED STEEL FUEL LINE BECAME ENERGIZED WITH THE APPROXIMATELY 7000 VOLTS, THE ACTIVE GAS RISER AND RETIRED FUEL LINE STARTED ARCING AT THE POINT OF CONTACT AND CAUSED A BURN HOLE IN BOTH PIPES APPROXIMATELY 1/4 BY 1/2. THIS CAUSED THE 58 PSIG GAS TO TRAVEL FROM THE HOLE IN THE RISER INTO THE HOLE OF THE RETIRED FUEL LINE AND DIRECTLY INTO THE BASEMENT AND IGNITION OF THE GAS HAPPENED NEAR THE FURNACE INSIDE THE BASEMENT. THE SERVICE TO THE HOUSE IS SCHEDULED TO BE PERMANENTLY RETIRED AT THE MAIN THE WEEK OF JUNE 12, 2016. .
2025-03-31 10:13 | NO | NO | NO | 20160012 | 30817 | 2016-02-10 18:22 | SUPPLEMENTAL FINAL | 15462 | PECO ENERGY CO | 2301 MARKET STREET, S9-1 | PHILADELPHIA | PA | 19103 | 2016-01-11 08:45 |  |  | 2016 | 2520 YORK ROAD | JAMISON | BUCKS | PA | 18929 | 40.2619 | -75.0863 | [9 empty] | 2016-01-13 10:06 | 1137930 |  | NATURAL GAS |  | 8560 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-01-11 08:45 |  |  |  | 2016-01-11 09:10 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2015 | [5 empty] | 6 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | MECHANICAL PUNCTURE | 6 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 512 | 615.067447572265472 | 5600 | 6727.3002078216536 | 0 | 0 |  |  | 20094 | 23127.0566037735849056603773584905660377 |  | 0 | 26206 | 24434.8698769620478258544474393530997305 | 30469.4242591675039776603773584905660377 | 4 | 0 | 0 |  |  |  |  | 60 | 60 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE INCIDENT WAS A DAMAGE CASE AND THE LOSS OF GAS APPEARS AS NORMAL GAS USAGE. SYSTEM WAS OPERATING BELOW MAOP OF DISTRIBUTION SYSTEM. SCADA SYSTEM DID NOT ALARM TO ANY UNUSUAL FLOW CONDITIONS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | STORM DRAIN/CULVERT | YES | 20153580320 |  |  | CONTRACT LOCATOR | YES | YES | 7 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | DAVID BONNER | PRINCIPAL ENGINEER | david.bonner@exeloncorp.com | 215-841-6476 |  |  |  |  | DAVID BONNER | PRINCIPAL ENGINEER | 215-841-6476 | david.bonner@exeloncorp.com | ON JANUARY 11, 2016, A THIRD-PARTY CONTRACTOR WAS EXCAVATING TO INSTALL A STORM SEWER AND STRUCK A 6" HIGH PRESSURE GAS MAIN. THE DAMAGED MAIN WAS INSTALLED ON DECEMBER 9, 2015 AND COMPANY GAS MAPS WERE IN THE PROCESS OF BEING UPDATED. THE NEWLY INSTALLED MAIN WAS RELOCATED AS PART OF A PENNSYLVANIA DEPARTMENT OF TRANSPORTATION PROJECT TO INSTALL A NEW STORM DRAIN. THE MAIN WAS OPERATING AT 60 PSIG AND HAD AN MAOP OF 99 PSIG. THE COMPANY STOPPED THE FLOW OF GAS BY PERFORMING SQUEEZE OFFS AWAY FROM THE BLOWING GAS. A BYPASS WAS INSTALLED AND FINAL REPAIRS WERE MADE BY REPLACING THE DAMAGED SECTION OF MAIN. THE IMPACTED CUSTOMERS WERE RESTORED THE DAY OF THE INCIDENT. A VALVE WAS NOT USED TO STOP THE FLOW OF GAS SINCE THE SITUATION WAS SAFE AND CONTROLLED TO APPROPRIATELY LIMIT THE INTERRUPTION TO CUSTOMERS.
2025-03-31 10:13 | NO | YES | NO | 20160013 | 16322 | 2016-02-13 20:25 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2016-01-14 07:22 |  |  | 2016 | 4489 W. JEFFERSON | ECORSE | WAYNE COUNTY | MI | 48229 | 42.2407 | -83.145 | [9 empty] | 2016-01-14 09:23 | 1138010 |  | NATURAL GAS |  | 107.76 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2016-01-14 07:22 |  |  |  | 2016-01-14 07:41 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1931 | [5 empty] | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 175000 | 210228.131494426675 | 13000 | 15616.946911014553 | 45000 | 54058.662384281145 | 0 | 0 |  |  | 398 | 458.075471698113207547169811320754716981 |  | 0 | 233398 | 116351.4813747293558032345013477088948787 | 280361.816261420486207547169811320754717 | 0 | 0 | 0 |  |  |  |  | 5 | 5 | 5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [9 empty] | YES |  |  |  | OTHER | CAST IRON MAIN CRACK | NO | [86 empty] | FRENAE F. SMITH | MANAGER | smithff@dteenergy.com | 313-389-7762 | 313-389-7757 |  |  |  | FRENAE SMITH | MANAGER | 313-389-7762 | smithff@dteenergy.com | ON JANUARY 14, 2016 AT 05:01 DTE GAS WAS NOTIFIED OF A LEAK COMPLAINT FROM THE ECORSE FIRE DEPARTMENT AT THE INTERSECTION OF W. JEFFERSON AND SOUTHFIELD ROAD IN ECORSE, MI. THE DTE GAS SERVICE TECHNICIAN TEAM ARRIVED AT 05:19 AND WAS INFORMED THAT THERE WAS AN ODOR IN THE AIR. THE TECHNICIAN BEGAN TO PERFORM HIS OUTSIDE LEAK INVESTIGATION AND FOUND NO COMBUSTIBLE READS. THE SERVICE TECHNICIAN INFORMED THE ECORSE FIRE DEPARTMENT AND LEFT THE SCENE. LATER THAT MORNING AT 07:22, DTE GAS WAS NOTIFIED OF AN EXPLOSION AT 4489 W. JEFFERSON WHICH IS A RESTROOM IN DINGELL PARK IN ECORSE, MI. THE DTE GAS SERVICE TECHNICIAN TEAM ARRIVED AT 07:41. THE SERVICE TECHNICIAN DID IDENTIFY COMBUSTIBLE GAS READS NEAR THE RESTROOM. AFTER FURTHER INVESTIGATION, THE DISTRIBUTION CREW DISCOVERED COMBUSTIBLE READS IN THE SEWER NEAR 255 WHITE STREET IN ECORSE, MI AND A CIRCUMFERENTIAL CRACK IN THE 6-INCH CAST IRON MAIN NEARBY. THE DISTRIBUTION CREW REPAIRED THE LEAK WITH A REPAIR CLAMP. THIS LEAK MIGRATED TO THE LOCATION OF THE EXPLOSION AT 4489 W. JEFFERSON VIA THE SEWER.
2025-03-31 10:13 | NO | NO | NO | 20160014 | 16793 | 2016-02-17 14:13 | SUPPLEMENTAL FINAL | 8160 | INTERMOUNTAIN GAS CO | 555 SOUTH COLE ROAD | BOISE | ID | 83709 | 2016-02-07 08:00 |  |  | 2016 | 51 S. THOMPSON RD | BLACKFOOT | BINGHAM | ID | 83221 | 43.1864 | -112.2963 | [9 empty] | 2016-02-11 14:32 | 1140286 |  | NATURAL GAS |  | 3065.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-02-07 08:15 |  |  |  | 2016-02-07 09:30 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1972 | [8 empty] | OTHER | REGULATOR - DEBRIS FAILURE IN REG | [9 empty] | OTHER | [8 empty] | REGULATOR HAD DEBRIS DAMAGE THE DIAPHRAGM WHICH CAUSED IT TO FAIL WIDE OPEN. THIS CAUSED THE RELIEF TO OPEN. THE SIZE OF REGULATOR, RELIEF AND PRESSURE CONDITIONS CAUSED THE EXCESSIVE GAS LOSS. | CLASS 3 LOCATION | 0 | 0 | 250 | 300.32590213489525 | 546 | 655.911770262611226 | 0 | 0 |  |  | 17869 | 20566.2075471698113207547169811320754717 |  | 0 | 18665 | 19420.9910566923819677520215633423180593 | 21522.4452195673177967547169811320754717 | 0 | 0 | 0 |  |  |  |  | 280 | 245 | 250 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA WORKED AS INTENDED, ALARM DUE TO HIGH PRESSURE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | TYLER MUZZANA | ENGINEER III | tyler.muzzana@intgas.com | 208-377-6044 |  |  |  |  | LANCE ELROY | DIRECTOR - OPERATIONS SERVICES | 208-377-6122 | lance.elroy@intgas.com | SMALL DEBRIS IN THE REGULATOR PUNCTURED THE DIAPHRAGM WHICH CAUSED THE REGULATOR TO FAIL WIDE OPEN. NORMAL CONTROL PRESSURE IS 245 PSIG AND UPSTREAM PRESSURE WAS APPROXIMATELY 650 PSIG. THIS RESULTED IN THE RELIEF TO OPEN AND BLOW TO ATMOSPHERE. THE RELIEF IS SET TO START OPENING AT 265 PSIG AND IT BUILT TO 272 PSIG DURING FULL RELIEF. DUE TO PIPING CONFIGURATION THIS RESULTED IN APPROXIMATELY 280 PSIG OUT OF THE REGULATOR AND PRESSURE LOSSES IN THE PIPE UP TO THE RELIEF. ALL PIPING DOWNSTREAM OF THE RELIEF DID NOT SEE MORE THAN 272 PSIG. ONLY 30' PIPING WAS SUBJECTED TO THE 110% MAOP PRESSURE. OPERATOR PERSONNEL ARRIVED ON SITE AND PROMPTLY SHUT IN THE REGULATOR THAT FAILED BY USING AN UPSTREAM ISOLATION VALVE. THE STATION HAS A REDUNDANT REGULATOR THAT MAINTAINED FEED INTO THE SYSTEM. THE RELIEF WAS REBUILT AND PUT BACK INTO SERVICE. IGC REQUESTED THIS INCIDENT BE RETRACTED, AND WAS DENIED BY BRIAN PIERZINA, PHMSA ACCIDENT INVESTIGATOR. IGC DISAGREES WITH THIS DECISION AND IS WORKING WITH INGAA, WHO IS SEEKING CLARIFICATION FROM PHMSA LEADERSHIP ON THE DEFINITION OF AN INCIDENT, SINCE THE RULEMAKING LANGUAGE IN 2010 SUPPORTS THAT REGULATOR STATION RELIEF'S IN EXCESS OF 3M CUBIC FEET SHOULD NOT BE REPORTED AS INCIDENTS. -LANCE ELROY, IGC DIRECTOR OF OPERATIONS. 2-8-18.
2025-03-31 10:13 | YES | NO | NO | 20160015 | 16347 | 2016-02-17 20:21 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2016-01-17 16:59 |  |  | 2016 | 61 MARR AVE | OAKLAND | ALAMEDA COUNTY | CA | 94611 | 37.8297 | -122.2217 | [9 empty] | 2016-01-17 20:11 | 1138311 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 1 | 2016-01-17 16:59 |  |  |  | 2016-01-17 17:34 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | 2008 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | OTHER | FIRE RELATED RELEASE | [5 empty] | CLASS 3 LOCATION | 150000 | 180195.54128093715 | 5000 | 6006.518042697905 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 155000 | 77119.308520687755 | 186202.059323635055 | 0 | 0 | 1 |  |  |  |  | 15 | 15 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER OF REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON JANUARY 17, 2016 AT 1659 HOURS, PG&E WAS NOTIFIED OF A POTENTIAL GAS-RELATED EXPLOSION AND FIRE ASSOCIATED WITH AN INSIDE METER SET AT 61 MARR AVENUE IN OAKLAND. PG&ES GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON-SITE AT 1734 HOURS. UPON THE GSRS ARRIVAL, THE FIRE DEPARTMENT SHUT OFF THE GAS AT THE METER AND HAD THE FIRE UNDER CONTROL. PER THE FIRE REPORT FROM THE OAKLAND FIRE DEPARTMENT, THE AREA OF ORIGIN IS THE VEHICLE STORAGE AREA AND HEAT SOURCE UNDETERMINED. PER THE EXPONENT REPORT, THE AREA OF ORIGIN IS THE CARPORT, POINT OF ORIGIN IS UNDETERMINED, CAUSE OF THE FIRE IS UNDETERMINED, AND THE FIRST FUEL IGNITED IS UNDETERMINED. THE EXPONENT REPORT STATES THAT THERE WAS NO INDICATION OF AN IGNITION OF A NATURAL GAS LEAK THAT COULD HAVE CAUSED AN EXPLOSION IN THE CARPORT OR THE HOUSE. IN ADDITION, THE LOUD BOOMS WERE LIKELY CAUSED BY THE RUPTURE OF PRESSURIZED CONTAINERS, BATTERIES RUPTURING, AUTOMOBILE TIRES EXPLODING, OR OTHER MATERIALS FALLING DUE TO THE FIRE. PG&E'S REPAIR CREW SHUT IN THE SERVICE BY 2100 HOURS, BY CUTTING AND CAPPING THE SERVICE LINE 3 FEET FROM THE BUILDING. THERE ARE NO REPORTED INJURIES OR FATALITIES. POLICE AND FIRE DEPARTMENT WERE REPORTED ON-SITE. AN INITIAL SPECIAL LEAK SURVEY WAS CONDUCTED IN RAINY AND WET CONDITIONS AND NO LEAKS WERE IDENTIFIED. A FOLLOW-UP SPECIAL LEAK SURVEY WAS CONDUCTED ONCE CONDITIONS WERE DRY AND NO LEAKS WERE IDENTIFIED. THE CPUC & DOT WERE INITIALLY NOTIFIED BASED ON THE INFORMATION AVAILABLE AT THE TIME AND THE CAUSE WAS NOT YET DETERMINED, AND ESTIMATED DAMAGES EXCEEDING $50K.
2025-03-31 10:13 | NO | YES | YES | 20160016 | 16608 | 2016-02-19 14:11 | SUPPLEMENTAL FINAL | 11713 | KEYSPAN ENERGY DELIVERY - LONG ISLAND | 175 EAST OLD COUNTRY ROAD | HICKSVILLE | NY | 11801 | 2015-02-11 14:00 |  |  | 2015 | 21 OLD COUNTRY ROAD | WATER MILL | SUFFOLK | NY | 11976 | 40.907 | -72.3618 | [9 empty] | 2015-02-11 16:20 | 1107916 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | NO | 0 | 2015-02-11 14:28 |  |  |  | 2015-02-11 14:28 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | RESIDENTIAL BUILDING (ONE STORY HOME) |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | INSIDE METER AND REGULATOR SET AND INTERNAL PIPING | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | THIRD PARTY WORK CAUSED DAMAGE | [5 empty] | CLASS 4 LOCATION | 500000 | 605629.107534051 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 50 | 50.11737089201877934272300469483568075117 |  | 0 | 500050 | 250879.7742083194178403755868544600938967 | 605679.2249049430187793427230046948356808 | 0 | 0 | 1 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT THE RESULT OF ANY OPERATION THAT THE CONTROL ROOM CAN DETECT UNDER PRESENT OPERATING CONDITIONS AND ALARMS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | RENOVATION WORK WAS ONGOING AND THE WORKERS REPORTED TO THE POLICE THAT THEY HAD CUT THROUGH INTERNAL PIPING IMMEDIATELY PRIOR TO THE INCIDENT. | [154 empty] | CORINNE BYRNES | PRIN PROG MGR FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE BYRNES | PRIN PROG MGR- FEDERAL PROGRAMS | 6317703549 | corinne.byrnes@nationalgrid.com | BASED ON THE PRELIMINARY INVESTIGATION IT APPEARS THE GAS LEAK ON PIPING LOCATED IN THE BASEMENT OF THE PREMISES, RENOVATION WORK WAS ONGOING AND THE WORKERS REPORTED TO THE POLICE THAT THEY HAD CUT THROUGH INTERNAL PIPING IMMEDIATELY PRIOR TO THE INCIDENT. THE COMPANY CONDUCTED A PRESSURE TEST ON THE GAS SERVICE LINE TO THE PREMISES FOLLOWING THE INCIDENT; NO LEAKS WERE DETECTED ON THE SERVICE LINE. THERE IS NO RELEVANT LEAK HISTORY IN THE AREA OR OTHER INDICATION OF ISSUES WITH THE COMPANY'S GAS FACILITIES. THE ACCOUNT WAS INACTIVE AT THE TIME OF THE INCIDENT
2025-03-31 10:13 | NO | YES | YES | 20160017 | 16622 | 2016-02-19 15:17 | SUPPLEMENTAL | 5230 | FLEMINGSBURG UTILITIES SYSTEM | 140 NEWMAN PARK WAY | FLEMINGSBURG | KY | 41041 | 2016-01-28 12:42 |  |  | 2016 | 5040 MAIN STREET | MAYSLICK | MASON | KY | 41055-0000 | 38.5188 | -83.8414 | [9 empty] | 2016-01-28 14:43 | 1139171 |  | NATURAL GAS |  | 5 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2016-01-28 03:00 |  |  |  | 2016-01-28 08:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1996 | [5 empty] | 4 | ASTM D2513 | AMERIFLOW | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.438 |  | 2406 | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 2 LOCATION | 0 | 0 | 0 | 0 | 500 | 600.6518042697905 | 0 | 0 |  |  | 20 | 23.01886792452830188679245283018867924528 |  | 0 | 520 | 270.065763509044057951482479784366576819 | 623.670672194318801886792452830188679245 | 0 | 0 | 0 |  |  |  |  | 28 | 28 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | ELECTRICAL ARCING CAUSED BY OPERATOR WHILE USING A ELECTRICAL POWERED TOOL TO TIGHTEN UP THE BOLTS WHILE GAS WAS LEAKING TO THE ATMOSPHERE. |  |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | JOE EDWARD DUNAWAY JR. | UTILITIES SUPERINTENDENT | joedunaway@altiusbb.com | 606-748-8778 | 606-845-0712 |  |  |  | JOE EDWARD DUNAWAY JR. | UTILITIES SUPERINTENDENT | 606-748-8778 | joedunaway@altiusbb.com | RECEIVED AN ODOR COMPLAINT ON JANUARY 28TH 2016 AT 3AM FROM MASON COUNTY KENTUCKY EMERGENCY DISPATCH THAT A CUSTOMER HAD REPORTED THE SMELL OF NATURAL GAS AT OR NEAR 5040 MAIN STREET MAYSLICK KENTUCKY. AFTER TWO CITY OF FLEMINGSBURG NATURAL GAS EMPLOYEES DANNY SHROUT AND COLBY MCCLOUD RESPONDED THEY MADE THE DETERMINATION THAT THE LEAK WAS NOT AN EMERGENCY AND NO THREAT TO LOSS OF LIFE OR ANY STRUCTURE WOULD OCCUR AND IT SHOULD BE FIXED WHEN IT BECAME DAYLIGHT THAT SAME DAY. AT APPROXIMATELY 8AM ON JANUARY 28TH 2016 THREE DIFFERENT CITY OF FLEMINGSBURG NATURAL GAS EMPLOYEES COTY HUNT, MIKE BROWN AND SCOTTY MASTERS WAS ASSIGNED TO DIG OUT AND REPAIR THE LEAK AT OR NEAR 5040 MAIN STREET MAYSLICK KENTUCKY, THE SAID THREE EMPLOYEES ARRIVED ON THE JOB SITE OF THE LEAK AT APPROXIMATELY 9AM. THE LEAK WAS PINPOINTED BY A NATURAL GAS LEAK DETECTOR ABOVE GROUND AND THEN EXCAVATING WAS STARTED, ONCE THE FOUR INCH MAIN WAS LOCATED AND HAD BEEN EXPOSED IT WAS DISCOVERED THAT A ONE INCH SERVICE LINE SADDLE ATTACHED TO THE FOUR INCH MAIN WAS LEAKING AROUND A SEAL APPARENTLY. ONE EMPLOYEE MIKE BROWN TIGHTENED THE FOUR BOLTS ON THE SADDLE TO TRY TO STOP THE ESCAPING NATURAL GAS BUT IT DID NOT STOP THE LEAK. AFTER THIS ATTEMPT EMPLOYEE COTY HUNT CALLED FROM HIS CELL PHONE TO SUPERINTENDENT JOE DUNAWAY TO EXPLAIN TO HIM WHAT THEY HAD DISCOVERED AND WANTED TO KNOW WHAT STEPS SHOULD BE TAKEN NOW, THE SUPERINTENDENT INSTRUCTED TO LOOSEN THE BOLTS UP ON THE SADDLE AND THEN ATTEMPT TO TIGHTEN THE BOLTS ONCE AGAIN AS TIGHT AS THEY COULD GET THEM, COTY HUNT AGREED TO DO SO AND SAID HE WOULD CALL BACK IF IT DIDN'T WORK. COTY HUNT RELAYED TO MIKE BROWN WHAT THE SUPERINTENDENT HAD EXPLAINED TO HIM TO DO AND THEN MIKE BROWN ATTEMPTED TO STOP THE ESCAPING NATURAL GAS BUT THIS TO FAILED TO STOP THE LEAK. COTY HUNT AGAIN CALLED FROM HIS CELL PHONE TO SUPERINTENDENT JOE DUNAWAY TO EXPLAIN TO HIM WHAT THEY TRIED BUT HAD FAILED TO STOP THE LEAK, THE SUPERINTENDENT EXPLAINED TO COTY HUNT REMOVE THE SADDLE WHICH WOULD EXPOSE A HOLE IN THE FOUR INCH MAIN, PLACE A TEMPORARY FULL CIRCLE REPAIR CLAMP OVER THE HOLE TO STOP THE ESCAPING NATURAL GAS, GO EITHER UPSTREAM OR DOWNSTREAM OF THE CLAMP AND INSTALL A NEW SADDLE TO INSTALL THE ONE INCH SERVICE LINE BACK UP AND THEN WE WOULD CALL A SUB-CONTRACTOR TO COME IN AND REPAIR THE HOLE THAT WE PLACED THE TEMPORARY FULL CIRCLE CLAMP OVER. COTY HUNT THEN EXPLAINED TO EMPLOYEES MIKE BROWN AND SCOTTY MASTERS. COTY HUNT TOLD SCOTTY MASTERS TO GO BACK TO THE FLEMINGSBURG DISTRIBUTION CENTER AND GET EVERYTHING THAT WAS NEEDED TO INSTALL THE FULL CIRCLE REPAIR CLAMP AND THE SADDLE ALSO TO GET ALL THE TOOLS AND PARTS NEEDED WHILE MIKE BROWN AND HIMSELF STAY AT THE LEAK. SCOTTY MASTERS THEN RETURNED WITH WHAT HE THOUGHT WAS EVERYTHING THAT WAS NEEDED TO REPAIR THE LEAK, COTY HUNT AND SCOTTY MASTERS UNLOADED THE TOOLS AND PARTS AND THEN BEGAN HANDING MIKE BROWN THE TOOLS AND PARTS, SCOTTY MASTERS HAD BROUGHT BACK A COMBUSTIBLE GAS POWERED GENERATOR WITH AN ELECTRIC IMPACT WRENCH TO HELP WITH THE INSTALLATION OF THE FULL CIRCLE REPAIR CLAMP. EMPLOYEE MIKE BROWN REMOVED THE SADDLE FROM THE FOUR INCH MAIN WHILE NATURAL GAS WAS ESCAPING AND PLACED THE FOUR INCH REPAIR CLAMP OVER THE HOLE, THE GENERATOR WAS RUNNING BY THIS TIME AND THE ELECTRIC IMPACT WRENCH WAS PLUGGED IN AND HANDED TO MIKE BROWN TO TIGHTEN UP THE BOLTS ON THE CLAMP, HE TIGHTENED THE BOLTS BUT NATURAL GAS WAS STILL ESCAPING. COTY HUNT CALLED FROM HIS CELL PHONE TO SUPERINTENDENT JOE DUNAWAY TO EXPLAIN TO HIM WHAT HAD HAPPENED TO THIS POINT AND THE GAS WAS STILL LEAKING, THE SUPERINTENDENT INSTRUCTED TO REMOVE THE FULL CIRCLE REPAIR CLAMP AND TO SPRAY WITH SOAPY WATER AND RUN A RASP/FILE OVER THE HOLE TO MAKE SURE THAT THERE WASN'T ANY ROUGH EDGES AND THE REPLACE THE FULL CIRCLE REPAIR CLAMP BACK OVER THE HOLE AND TIGHTEN THE BOLTS AS TIGHT AS YOU COULD GET THEM. COTY HUNT RELAYED TO MIKE BROWN WHAT THE SUPERINTENDENT HAD EXPLAINED TO HIM TO DO AND THEN MIKE BROWN REMOVED
2025-03-31 10:13 | NO | YES | NO | 20160018 | 16774 | 2016-02-22 11:44 | SUPPLEMENTAL FINAL | 4483 | ENSTAR NATURAL GAS CO | 3000 SPENARD ROAD | ANCHORAGE | AK | 99503 | 2016-01-24 02:25 |  |  | 2016 | 1213 LILAC LANE | KENAI | KENAI CITY BOROUGH | AK | 99611 | 60.5763 | -151.3206 | [9 empty] | 2016-01-24 08:00 | 1138799 |  | NATURAL GAS |  | 406 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 80 | 2016-01-24 02:25 |  |  |  | 2016-01-24 02:38 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 96 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.14 | [6 empty] | LEAK |  |  | OTHER | WELD JOINT | [5 empty] | CLASS 3 LOCATION | 550000 | 660716.98469676955 | 25000 | 30032.590213489525 | 100000 | 120130.3608539581 | 0 | 0 |  |  | 2749 | 3163.943396226415094339622641509433962264 |  | 0 | 677749 | 338768.9828935437100404312668463611859838 | 814043.8791604435900943396226415094339623 | 0 | 0 | 24 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [56 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | EARTHQUAKE |  |  |  |  | NO | [218 empty] | RUSTY ALLEN | ENGINEER | rusty.allen@enstarnaturalgas.com | 907-334-7765 |  |  |  |  | STEVEN COOPER | DIRECTOR OF OPERATIONS | 907-334-7730 | steve.cooper@enstarnaturalgas.com | ON JANUARY 24, 2016, AT APPROXIMATELY 0130, A MAGNITUDE 7.1 EARTHQUAKE OCCURRED IN SOUTHCENTRAL ALASKA. THE EPICENTER WAS IN COOK INLET, 162 MILES SOUTHWEST OF THE CITY OF ANCHORAGE. AT APPROXIMATELY 0225, ENSTAR NATURAL GAS COMPANY RECEIVED A CALL TO ITS CALL CENTER FROM EMERGENCY RESPONDERS NOTIFYING IT OF AN IGNITION AND FIRE AT A RESIDENCE LOCATED AT 1213 LILAC LANE IN KENAI, ALASKA. ENSTAR'S FIRST RESPONDING EMPLOYEE ARRIVED ON SCENE AT 0238. SHORTLY THEREAFTER, FIRE CREWS EXTINGUISHED THE INITIAL FIRE. OVER THE COURSE OF THE NEXT THREE HOURS, CREWS WORKED WITH EMERGENCY RESPONDERS TO EVACUATE THE STREET, SHUT DOWN ELECTRICITY TO STRUCTURES ON THE STREET, AND LOCATE THE GAS LEAK. CREWS DETERMINED THAT THERE WAS AN UNDERGROUND GAS LEAK IN FRONT OF 1213 LILAC LANE. AT APPROXIMATELY 4 A.M., CREWS BEGAN EXCAVATING AT THE SITE OF THE SUSPECTED GAS LEAK. THE GROUND WAS FROZEN, WITH FROST EXTENDING 2-4 FEET BELOW THE SURFACE, AND THE MAIN WAS APPROXIMATELY 8 FEET DEEP AT THIS LOCATION. DURING THE EXCAVATION, AT APPROXIMATELY 0554, A SECONDARY IGNITION OCCURRED AT 1215 LILAC LANE. THE ENSUING FIRE DAMAGED THE HOMES AT 1211, 1213, 1215, AND 1217 LILAC LANE. CREWS SHUT DOWN THE MAIN ON LILAC LANE BY STOPPING GAS FLOW TO THE THREE TIE-IN POINTS THAT FED THE STREET. CREWS DETERMINED THE SOURCE OF THE LEAK WAS A 1 1/4 INCH STEEL MAIN THAT HAD SEPARATED AT A WELD JOINT. CREWS REPAIRED THE BROKEN MAIN AND RESTORED SERVICE TO NON-AFFECTED HOMES AT APPROXIMATELY 1800. THROUGHOUT THE DAY, ADDITIONAL ENSTAR CREWS WERE CALLED IN FROM THE KENAI AND ANCHORAGE AREAS TO SUPPORT THE RESPONSE. FOR THE FOLLOWING TWO AND A HALF WEEKS, ENSTAR CREWS WORKED TO EXTRACT TRAPPED GAS IN THE GROUND. NO INJURIES WERE REPORTED AS A RESULT OF THIS INCIDENT; ONLY PROPERTY DAMAGE WAS REPORTED.
2025-03-31 10:13 | NO | YES | NO | 20160020 | 30395 | 2016-02-29 11:43 | SUPPLEMENTAL FINAL | 17570 | ROCHESTER GAS & ELECTRIC CORP | 180 SOUTH CLINTON AVENUE | ROCHESTER | NY | 14607 | 2016-02-02 08:15 |  |  | 2016 | 134 BUCKLEY PL | HENRIETTA | MONROE | NY | 14467 | 43.0567 | -77.6298 | [9 empty] | 2016-02-02 08:55 | 1139554 |  | NATURAL GAS |  | 15.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2016-02-02 08:20 |  |  |  | 2016-02-02 08:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1967 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | MOTOR VEHICLE DAMAGE | [5 empty] | CLASS 3 LOCATION | 114225 | 137218.904685433639725 | 175 | 210.228131494426675 | 2340 | 2811.05044398261954 | 0 | 0 |  |  | 103 | 118.547169811320754716981132075471698113 |  | 0 | 116843 | 58192.9409870026578634501347708894878706 | 140358.7304307220066947169811320754716981 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 42 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | 911 DISPATCHER CALLED OPERATOR |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS THE DIRECT RESULT OF HOMEOWNER/CUSTOMER DAMAGE TO THE SERVICE LINE WITH THEIR MOTOR VEHICLE. THE ONLY PART OF THE SYSTEM SHUT DOWN DUE TO THIS INCIDENT WAS THE SERVICE TO THE HOUSE DAMAGED BY THE HOMEOWNER | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DANIEL C. BLANCE | ENGINEER | dcblance@nyseg.com | (607) 762-4710 |  |  |  |  | MICHAEL D. EASTMAN | VICE PRESIDENT - GAS OPERATIONS | (585) 724-8253 | mdeastman@nyseg.com | THE INCIDENT WAS THE DIRECT RESULT OF HOMEOWNER/CUSTOMER DAMAGE TO THE SERVICE LINE WITH THEIR MOTOR VEHICLE. THE ONLY PART OF THE SYSTEM SHUT DOWN DUE TO THIS INCIDENT WAS THE SERVICE TO THE HOUSE DAMAGED BY THE HOMEOWNER. THAT SERVICE WILL NOT BE RESTARTED UNTIL A FORMAL REQUEST IS MADE BY THE CUSTOMER. AS OF 5/24/2018, THE CUSTOMER HAS NOT REQUESTED THAT RG&E RESTORE SERVICE.
2025-03-31 10:13 | NO | YES | NO | 20160022 | 16259 | 2016-03-03 15:56 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2016-02-05 08:41 |  |  | 2016 | 40 WORTH STREET | NEW YORK | NEW YORK | NY | 10013-2904 | 40.7174 | -74.0069 | [9 empty] | 2016-02-05 13:34 | 1139859 |  | NATURAL GAS |  | 108 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 20 | 2016-02-05 08:41 |  |  |  | 2016-02-05 09:02 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1900 | [5 empty] | 12 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 128000 | 153766.861893066368 | 1000 | 1201.303608539581 | 0 | 0 |  |  | 1335 | 1536.509433962264150943396226415094339623 |  | 0 | 130335 | 65604.5276322336364932614555256064690027 | 156504.6749355682131509433962264150943396 | 8 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | (718) 319-2310 | (718) 904-4607 |  |  |  | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | (718) 319-2310 | fagank@coned.com | ON FEBRUARY 5, 2016 AT 08:41, NEW YORK CITY EMERGENCY MANAGEMENT (NYCEM) REPORTED A MAJOR CRANE COLLAPSE AT 40 WORTH STREET, MANHATTAN, N.Y. TO THE GAS EMERGENCY RESPONSE CENTER. A CODE MURRE (MULTIPLE RESOURCE RESPONSE EVENT) WAS INITIATED AND NUMEROUS GAS DISTRIBUTION SERVICES (GDS) AND CONSTRUCTION CREWS AND SUPERVISORS WERE DISPATCHED. LEAK SURVEY, BRONX GDS AND QUEENS GDS CREWS WERE MOVED TO MANHATTAN TO ASSIST AT THE SITE AND WITH INCOMING LEAK VOLUME. WORTH STREET, BETWEEN WEST BROADWAY AND CHURCH STREET, IS SUPPLIED BY A RADIAL 6" LOW PRESSURE STEEL MAIN CONNECTED TO A 12" LOW PRESSURE (LP) CAST IRON MAIN ON THE EAST SIDE OF WEST BROADWAY. THE 6" MAIN ON WORTH STREET SUPPLIES FOUR SERVICES ONLY AND ENDS IN FRONT OF 53 WORTH STREET. ELECTRIC OPERATIONS AND STEAM OPERATIONS WERE NOTIFIED AND RESPONDED; GAS DISTRIBUTION ENGINEERING WAS NOTIFIED TO IDENTIFY AN ISOLATION PLAN FOR THE 12" LP CAST IRON MAIN SUPPLYING THE MAIN ON WORTH STREET AND ASSESS THE OUTAGE IMPACT RELATED TO SAME. AT 08:46, THE FIRE DEPARTMENT OF NEW YORK (FDNY) REPORTED AN OUTSIDE GAS ODOR AT 57 WORTH ST. WHICH WAS IN THE IMMEDIATE AREA OF THE COLLAPSE. GDS ARRIVED AT 08:50, INVESTIGATED AND REPORTED THAT A LARGE CRANE FELL ON WORTH STREET FROM HUDSON ST. TO CHURCH ST. GDS REPORTED NO GAS OR CO READINGS OR GAS ODORS WERE DETECTED DURING THE INITIAL INVESTIGATION. THE FDNY REQUESTED THE GAS MAIN ON WORTH STREET BE ISOLATED FROM WEST BROADWAY TO CHURCH STREET. AT 10:23, NYCEM REPORTED THE FDNY HAD EVACUATED APPROXIMATELY TWENTY OCCUPANTS OR MORE FROM THE NY STATE COURT BUILDING AT 71 THOMAS STREET DUE TO AN INSIDE GAS ODOR. GDS INVESTIGATED AND DID NOT DETECT ANY GAS ODORS OR READINGS AND NO CO READINGS WERE DETECTED. AN NEW YORK POLICE DEPARTMENT (NYPD) OFFICER INFORMED GDS THE BUILDING WAS NOT EVACUATED DUE TO A GAS ODOR BUT WAS EVACUATED FOR SAFETY DUE TO THE CRANE COLLAPSE NEARBY. AT 11:12, GDS REPORTED THE FOUR SERVICES ON WORTH STREET AND #171 WEST BROADWAY (USED FOR A FIRE BANK STOPPER LOCATION) WERE VERIFIED OFF AT THE SERVICE HEAD VALVES AND AT 11:48, THE STOPPERS WERE INSTALLED IN THE NORTH AND SOUTH FIRE BANKS ISOLATING THE GAS MAIN ON WORTH STREET. AT 14:40, THE CUT AND CAP OF THE 12" LP CAST IRON MAIN WAS COMPLETED. FIVE SERVICES WERE ISOLATED INTERRUPTING SERVICE TO EIGHT GAS METER ACCOUNTS (ALL COMMERCIAL). THERE WAS NO NEGATIVE SYSTEM IMPACT AS A RESULT OF THIS MAIN ISOLATION. A TOTAL OF TWENTY-TWO GAS ODOR COMPLAINTS WERE RECEIVED IN THE AREA OF THE CRANE COLLAPSE. ALL READINGS WERE VENTED TO 0% GAS READINGS. THERE WAS SIGNIFICANT MEDIA COVERAGE OF THIS EVENT AND REPORTING INCLUDED THE PRESENCE OF GAS ODORS IN THE AREA. CON EDISON'S SENIOR EXECUTIVES WERE ON LOCATION AND NYC ELECTED OFFICIALS RESPONDED TO LOCATION INCLUDING MAYOR DIBLASIO. ON FEBRUARY 10, 2016 AT 07:11, GAS RESTORATION WAS COMPLETED TO ALL AVAILABLE CUSTOMERS, EXCAVATIONS BACKFILLED AND RESTORATION WORK COMPLETED. OSHA RESPONDED TO LOCATION AND NYS PUBLIC SERVICE COMMISSION, NYC DEPARTMENT OF ENVIRONMENTAL PROTECTION AND US DEPARTMENT OF TRANSPORTATION WERE NOTIFIED.
2025-03-31 10:13 | NO | NO | NO | 20160023 | 30553 | 2016-03-08 14:57 | SUPPLEMENTAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2016-02-07 15:18 |  |  | 2016 | 14100 FRANKLIN ST | WOODBRIDGE | PRINCE WILLIAM COUNTY | VA | 22191 | 38.6465 | -77.2775 | [9 empty] | 2016-02-07 16:41 | 1139990 |  | NATURAL GAS |  | 1.68 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 12 | 2016-02-07 15:31 |  |  |  | 2016-02-07 15:31 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1963 | [5 empty] | 0.5 | TYPE K | READING TUBE CORP. OR REVERE TUBING | COPPER | [10 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 48600 | 58383.3553750236366 | 0 | 0 | 30000 | 36039.10825618743 | 0 | 0 |  |  | 5 | 5.75471698113207547169811320754716981132 |  | 0 | 78605 | 39112.2760290125614894878706199460916442 | 94428.2183481921986754716981132075471698 | 0 | 0 | 0 |  |  |  |  | 20 | 20 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [6 empty] | YES | CORROSIVE SOIL |  |  |  | YES |  |  | YES | NO |  | NO | NO | [8 empty] | NO | OTHER | SEE NARRATIVE | [20 empty] | 2015-05-19 | NO | [227 empty] | RICHARD FITZPATRICK | SUPERVISOR - PIPELINE SAFETY | richardfitzpatrick@washgas.com | 703-750-5921 |  |  |  |  | STEVE PRICE | AVP - PIPELINE SAFETY | 703-750-4341 | sprice@washgas.com | ON SUNDAY, FEBRUARY 7, 2016, AT APPROXIMATELY 15:18, WASHINGTON GAS RECEIVED A CALL FROM THE PRINCE WILLIAM COUNTY FIRE DEPARTMENT RELATIVE TO AN OUTSIDE GAS ODOR LOCATED AT 14100 FRANKLIN ST. IN WOODBRIDGE, VA. WASHINGTON GAS PERSONNEL ARRIVED ON SCENE AT 15:31. UPON ARRIVAL, THE WASHINGTON GAS TECHNICIAN HAD EXITED HIS VEHICLE AND WAS APPLYING THE APPROPRIATE PPE WHEN A POSSIBLE LOW ORDER EXPLOSION OCCURRED. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THE INCIDENT. AN ODORANT SAMPLE WAS TAKEN AND THE LEVEL OF ODORANT WAS DETERMINED TO BE ACCEPTABLE. RELATIVE TO PART A #13 OF THIS FORM. SELECTING YES WOULD NOT ALLOW THE DATE & TIME TO BE INPUTTED BEFORE THE CURRENT DATE. WG RESPONSE TO PART A #13 IS YES. #13A. 2/8/2016 2100HRS. #13B. CUSTOMER HAS NOT ELECTED TO HAVE NATURAL GAS RESTORED THAT WAS PREVIOUSLY INACTIVE. PART C #3C. READING TUBE CORP. & REVERE TUBING WERE BRANDS USED FOR BARE COPPER SERVICE. WG IS UNABLE TO IDENTIFY WHICH WAS USED FOR THIS SPECIFIC SERVICE. PART D #2F. THE LEAK SIZE (SIZE OF OPENING ON PIPE) WAS UNKNOWN. KNOWN FACTS INCLUDED THAT GAS WAS MIGRATING INTO 14100 FRANKLIN ST, AND THERE WAS A SUFFICIENT CONCENTRATION OF GAS TO RESULT IN AN IGNITION. IN ORDER TO ARRIVE AT AN ESTIMATED AMOUNT OF GAS LOST, THE HOME SIZE WAS FIGURED AT 2,100 SQ. FT., WITH AN ESTIMATED CEILING HEIGHT OF 8 FT. THIS RESULTS IN AN ESTIMATED HOME VOLUME OF 2,100 SQ. FT. * 8 FT = 16,800 CU. FT. AN EXPLOSIVE MIXTURE WOULD EXIST WHEN APPROXIMATELY 5 - 15% OF A VOLUME OF SPACE IS OCCUPIED BY GAS. USING A CONSERVATIVE VOLUME OF 16,800 CU. FT., 10% (MID-RANGE BETWEEN THE LEL AND UEL) OF THE HOME VOLUME WOULD EQUAL 1,680 CU. FT. AT A HEATING VALUE OF APPROXIMATELY 1,040 BTU/CU. FT., THIS WOULD TRANSLATE TO 1,747,200 BTU. AT $3/MMBTU, THIS AMOUNT OF GAS WOULD COST $5.24. IT IS UNLIKELY THAT THE ENTIRE STRUCTURE FILLED WITH 10% OF GAS DUE TO THE LOCALIZED NATURE OF THE INCIDENT. HOWEVER, USING THE ENTIRE HOME VOLUME PROVIDES A CONSERVATIVE ESTIMATE THAT TAKES INTO ACCOUNT SOME CONTINGENCIES SUCH AS GAS THAT MAY HAVE MIGRATED ELSEWHERE (UNDERGROUND, OR ESCAPED THE HOME BEFORE THE IGNITION). PART G # 5. BARE COPPER SERVICE LINE IS NOT COATED.
2025-03-31 10:13 | NO | YES | NO | 20160024 | 16263 | 2016-03-10 08:39 | ORIGINAL FINAL | 603 | CENTERPOINT ENERGY RESOURCES CORP. | 10825 E GEDDES AVE SUITE 410 | CENTENNIAL | CO | 80112 | 2016-02-19 12:15 |  |  | 2016 | 4119 HWY 8 & TRACELWOOD | ARKADELPHIA | CLARK | AR | 71923 | 34.1252 | -94.1192 | [9 empty] | 2016-02-19 17:58 | 1140886 |  | NATURAL GAS |  | 134 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-03-19 12:15 |  |  |  | 2016-03-19 12:25 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1985 | [5 empty] | 3 | ASTM D2513 | DUPONT ALDYL | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 36000 | 43246.929907424916 | 826 | 992.276780653693906 | 200000 | 240260.7217079162 | ROW EQUIPMENT DAMAGED |  | 597 | 687.113207547169811320754716981132075472 |  | 0 | 237423 | 118466.9577507393749508517520215633423181 | 285187.0416035419797173207547169811320755 | 0 | 0 | 0 |  |  |  |  | 38 | 38 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | PHILLIP GILES | AREA MANAGER | phillip.giles@centerpointenergy.com | 501-623-7074 | 501-623-2140 |  |  |  | KEITH A. KITTINGER | REGIONAL OPERATIONS DIRECTOR | 501-377-4669 | keith.kittinger@centerpointenergy.com | ON FEBRUARY 19TH, AT APPROXIMATELY 12:15 PM, CNP RECEIVED A CALL FROM A LOCAL WATER DEPARTMENT EMPLOYEE STATING THAT A TRACK HOE WAS BURIED IN A CREEK AT THE INTERSECTION OF HWY 8 & TRACELWOOD AND THAT A GAS LINE HAD IGNITED CATCHING THE TRACK HOE ON FIRE. UPON ARRIVAL, IT WAS DETERMINED THAT THE TRACK HOE WAS CLEARING RIGHT OF WAY UNDER THE POWER LINES PARALLELING HWY 8, HAD GONE OVER A CONCRETE WING WALL OF A CULVERT, SLID INTO THE CREEK AND BURIED ITSELF IN THE CREEK IN WHICH CNP HAD A BURIED 3" PLASTIC GAS LINE. THE GAS LINE UNDER THE CREEK WAS BROKEN BY THE WEIGHT OF THE TRACK HOE TRACK AND IGNITED CAUSING THE TRACK HOE TO CATCH FIRE IN THE ENGINE COMPARTMENT. CNP WORKED TO EXCAVATE BELLHOLES AT A SAFE DISTANCE ON BOTH SIDE OF THE MAIN BREAK. GAS WAS SHUT OFF AT 2:15 PM. REPAIRS WILL REQUIRE A 300' BORE OF THE CREEK.
2025-03-31 10:13 | NO | YES | NO | 20160025 | 16343 | 2016-03-14 12:42 | SUPPLEMENTAL FINAL | 6720 | ATMOS ENERGY CORPORATION - COLORADO/KANSAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2016-02-16 19:28 |  |  | 2016 | 467 CHERRY DR | STEAMBOAT SPRINGS | ROUTT | CO | 80487 | 40.4823 | -106.8241 | [9 empty] | 2016-02-16 21:15 | 1140636 |  | NATURAL GAS |  | 30 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2016-02-16 19:28 |  |  |  | 2016-02-16 20:08 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 435000 | 522567.069714717735 | 5000 | 6006.518042697905 | 5000 | 6006.518042697905 | 0 | 0 |  |  | 300 | 345.283018867924528301886792452830188679 |  | 0 | 445300 | 221726.4540513510983692722371967654986523 | 534925.3888189814695283018867924528301887 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | SNOW FALLING FROM ADJACENT ROOF ONTO METER | NO | [218 empty] | DOUGLAS SHATAS |  | doug.shatas@atmosenergy.com | 8168630951 |  |  |  |  | DOUGLAS SHATAS |  | 8168630951 | doug.shatas@atmosenergy.com | SNOW LOAD FELL FROM THE ROOF OF A CONDOMINIUM ONTO THE ADJACENT NEIGHBORS METER SETTING. GAS ESCAPED, AND IGNITED FROM AN UNKNOWN SOURCE.
2025-03-31 10:13 | NO | NO | NO | 20160026 | 16409 | 2016-03-14 14:23 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2016-02-14 |  |  | 2016 | 40 CLINTON STREET | BROOKLYN | KINGS | NY | 11201 | 40.6956 | -73.992 | [9 empty] | 2016-02-14 11:10 | 1140432 |  |  |  | 1.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-02-14 03:06 |  |  |  | 2016-02-14 03:28 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | 1996 | [8 empty] | OTHER | PRESUMED - DEFECTIVE REGULATOR | [9 empty] | OTHER | [8 empty] | A CALL WAS RECEIVED FROM FDNY TO REPORT A FIRE AT AN APARTMENT AT 40 CLINTON ST CUSTOMER RANGE WAS THE SOURCE OF THE FIRE AND IT IS SUSPECTED THAT RANGE WAS OVERPRESSURIZED DUE TO A DEFECTIVE GAS SERVICE REGULATOR SUPPLYING 152 APARTMENT UNITS. | CLASS 4 LOCATION | 50000 | 60065.18042697905 | 5000 | 6006.518042697905 | 20000 | 24026.07217079162 | 0 | 0 | ALL COSTS ARE ESTIMATED AT THIS POINT IN TIME |  | 0 | 0 |  | 0 | 75000 | 37315.794445494075 | 90097.770640468575 | 0 | 0 | 152 |  |  |  |  | 10.5 | 10.5 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT THE RESULT OF ANY OPERATION THAT THE CONTROL ROOM CAN DETECT UNDER PRESENT OPERATING CONDITIONS AND ALARMS | [12 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | CONSTRUCTION | NO | [50 empty] | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAM | 6317703549 | corinne.byrnes@nationalgrid.com | INCIDENT OCCURRED BY IGNITION OF A CUSTOMER RANGE IN APARTMENT BUILDING AT 40 CLINTON STREET, BROOKLYN, NY. THE ROOT CAUSE WAS OVERPRESSURIZATION OF THE GAS SERVICE REGULATOR SUPPLYING COOKING LOADS TO 152 APARTMENTS, DUE TO IMPROPER INSTALLATION OF THE VENT LINES AT THE TIME OF THE INITIAL INSTALLATION. THIS WAS A PARALLEL GAS SERVICE REGULATOR INSTALLATION. PART OF THE VENT LINES WERE INSTALLED BELOW GRADE, PASSING THROUGH TWO CONCRETE BARRIERS: ONE AT FOUNDATION WALL, AND ONE AT SIDEWALK. THESE VENT LINES WERE BOTH UNSLEEVED, AND CORRODED OVER TIME. WATER FROM THE SURROUNDING SOIL INFILTRATED THE VENT LINE AND COLLECTED ON TOP OF THE PRIMARY REGULATOR DIAPHRAGM AND FROZE. IN ADDITION, THE VENT LINE WAS PARTIALLY FROZEN AND BLOCKED. THE SECONDARY REGULATOR SERVED TO VENT EXCESS GAS DUE TO ELEVATED PRESSURE. A SERVICE PERSON RESPONDING TO A CALL AT THIS LOCATION FOUND THE COUPLING ON THE SECONDARY VENT LINE DISCONNECTED, AND OUT OF AN ABUNDANCE OF CAUTION, "VALVED OUT" THE SECONDARY REGULATOR TO STOP THE FLOW OF BLOWING GAS. THIS PREVENTED THE INTERNAL RELIEF OF THE SECONDARY GAS SERVICE REGULATOR TO VENT THE EXCESS PRESSURE FROM THE FAILED REGULATOR; THEREFORE BOTH RELIEF VALVES WERE RENDERED INEFFECTIVE, ALLOWING DOWNSTREAM PRESSURE TO BUILD UP TO LEVELS BEYOND RECOMMENDED LIMITS FOR THE CUSTOMERS' EQUIPMENT AND A FIRE RESULTED IN ONE OF THE APARTMENTS. COOKING LOADS FOR ALL 152 APARTMENTS REMAIN TURNED OFF UNTIL THE ASSIGNED PLUMBER OBTAINS THE PERMIT FROM THE DEPARTMENT OF BUILDINGS. IN PART G ABOVE, THE TASK WHICH LED TO THE INCIDENT WAS NOT A COVERED TASK FOR OUR OQ PROGRAM AT THE TIME OF THE SERVICE AND EQUIPMENT INSTALLATION; HOWEVER, IT IS A COVERED TASK AT THIS POINT IN TIME. LAST SERVICE WAS RESTORED ON 9/1/2016
2025-03-31 10:13 | NO | NO | NO | 20160027 | 16300 | 2016-03-20 13:34 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2016-02-18 21:21 |  |  | 2016 | 371 INDUSTRIAL PARK DRIVE | BELLEVILLE | WAYNE COUNTY | MI | 48111 | 42.2004 | -83.4833 | [9 empty] | 2016-02-19 13:18 | 1140855 |  | NATURAL GAS |  | 69.23 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-02-18 21:21 |  |  |  | 2016-02-18 21:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 1 | 6 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 45806 | 55026.913092764047286 | 131 | 157.370772718685111 | 2326 | 2794.232193463065406 | TRAFFIC CONTROL |  | 256 | 294.64150943396226415094339622641509434 |  | 0 | 48519 | 24285.5231445386767647789757412398921833 | 58273.1575683797600671509433962264150943 | 1 | 69 | 167 |  |  |  |  | 10 | 10 | 10 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | WATER | YES | 60490792 |  |  | UTILITY OWNER | YES | YES | 8 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | FRENAE F. SMITH | MANAGER | smithff@dteenergy.com | 313-389-7762 | 313-389-7757 |  |  |  | FRENAE SMITH | MANAGER | 313-389-7762 | smithff@dteenergy.com | MAINTENANCE CREW WORKING FOR THE CITY OF BELLEVILLE WATER DEPARTMENT STRUCK AND MECHANICAL PUNCTURED A 4-INCH 10PSIG PLASTIC MAIN WHILE PERFORMING WATER MAIN WORK. THIS INCIDENT LEAD TO ROAD CLOSURES (SUMPTER ROAD AND INDUSTRIAL PARK DRIVE IN BELLEVILLE, MICHIGAN) AND 237 INDUSTRIAL, COMMERCIAL, AND RESIDENTIAL CUSTOMERS TO BE WITHOUT NATURAL GAS SERVICE FOR APPROXIMATELY FOURTEEN HOURS. DTE GAS EMERGENCY RESPONSE CREWS PINCHED THE 4-INCH PLASTIC MAIN TO STOP THE RELEASE OF GAS. THE REPAIR WAS MADE BY INSTALLING A 5-FOOT SEGMENT OF 4-INCH MEDIUM DENSITY PLASTIC; JOINTS WERE MADE USING TWO ELECTROFUSION COUPLINGS. REPAIR WAS COMPLETED 13:25. AT THAT TIME RE-LIGHTS WERE STARTED AND THE ROAD WAS RE-OPENED.
2025-03-31 10:13 | NO | YES | NO | 20160028 | 16267 | 2016-03-24 15:02 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2016-02-25 12:47 |  |  | 2016 | 4946 TILBURY | HOUSTON | HARRIS | TX | 77056 | 29.7553 | -95.4602 | [9 empty] | 2016-02-25 14:18 | 1141368 |  | NATURAL GAS |  | 459 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-02-25 12:47 |  |  |  | 2016-02-25 13:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1994 | [5 empty] | 2 | ASTM D2513 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 750000 | 900977.70640468575 | 5000 | 6006.518042697905 | 3179 | 3818.944171547327999 | 0 | 0 |  |  | 2294 | 2640.264150943396226415094339622641509434 |  | 0 | 760473 | 379669.7551470362479560350404312668463612 | 913443.4327698743792254150943396226415094 | 0 | 0 | 2 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | [9 empty] | YES |  |  |  |  | MUNICIPALITY | BACKHOE/TRACKHOE | WATER | YES | 560402263 | LONE STAR 811 |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | LESLIE J. DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVEN YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steve.yarbrough@centerpointenergy.com | THE CITY OF HOUSTON WAS EXCAVATING WITH A LARGE BACKHOE TO REPAIR A WATER LEAK AND DAMAGED A 2" PLASTIC GAS MAIN IN FRONT OF 4946 TILBURY DRIVE HOUSTON, TEXAS ON FEBRUARY 25, 2016. THE ESCAPING GAS IGNITED AND PARTIALLY BURNED THE HOUSE AT 4946 TILBURY DRIVE.
2025-03-31 10:13 | NO | YES | NO | 20160029 | 16338 | 2016-03-25 11:19 | SUPPLEMENTAL FINAL | 11032 | LACLEDE GAS CO | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2016-02-24 07:52 |  |  | 2016 | 1010 SAINT CHARLES ST | SAINT LOUIS | SAINT LOUIS | MO | 63101 | 38.6299 | -90.1942 | [9 empty] | 2016-02-27 09:45 | 1141503 |  | NATURAL GAS |  | 1420 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-02-24 08:20 |  |  |  | 2016-02-24 08:43 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 84 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1903 | [5 empty] | 24 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 114000 | 136948.611373512234 | 500 | 600.6518042697905 | 0 | 0 |  |  | 6093 | 7012.698113207547169811320754716981132075 |  | 0 | 120593 | 63455.935854352760429919137466307277628 | 144561.9612909895716698113207547169811321 | 0 | 0 | 0 |  |  |  |  | 12 | 12 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | SYSTEM PRESSURE WAS NOT A CONTRIBUTING FACTOR TO THE LEAK | YES | YES | [7 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [6 empty] | YES | OUTSIDE FORCES FROM THE TRAFFIC ABOVE THE PIPE AND SUBSIDANCE NEAR CONCRETE AND BRICK MAY HAVE BEEN CONTRIBUTING FACTORS TO THE FAILURE. |  | YES |  |  |  | OTHER | CAST IRON | NO | [86 empty] | PATRICK SEAMANDS | MANAGER OF PIPELINE SAFETY AND COMPLIANCE | patrick.seamands@thelacledegroup.com | (314) 349-2936 |  |  |  |  | CRAIG R. HOEFERLIN | VICE PRESIDENT OF OPERATIONS SERVICES | (314) 349-2972 | craig.hoeferlin@thelacledegroup.com | AFTER COMPLETING A LEAK INVESTIGATION FROM A CUSTOMER REPORTED CALL OF A SLIGHT INSIDE ODOR, IT WAS DETERMINED A NEARBY 24 INCH CAST IRON MAIN WAS LEAKING. EXCAVATION CREWS HAD DIFFICULTY REACHING THE MAIN DUE ITS DEPTH OF 84 INCHES ALONG WITH THE CONCRETE AND BRICK FOUND BELOW THE PIPE. TWO LONGITUDINAL CRACKS TOTALING 32 INCHES IN LENGTH WERE FOUND ON THE BOTTOM SECTION OF THE PIPE. INSTALLATION OF A STAINLESS STEEL CLAMP WAS ATTEMPTED TO REPAIR THE LEAK; HOWEVER IT WAS UNSUCCESSFUL. THE INCIDENT WAS DEEMED TO BE REPORTABLE ON FEBRUARY 27, 2016, WHEN IT WAS DETERMINED THAT THE REPAIR COSTS WOULD PROBABLY EXCEED $50,000. THE COMPANY ORDERED A 44 INCH LONG STEEL, SPLIT SLEEVE ENCAPSULATION FITTING AS AN ALTERNATE REPAIR. THE ENCAPSULATION FITTING REQUIRED ADDITIONAL EXCAVATION OF THE PIPE WHICH UNCOVERED A THIRD CRACK 16 INCHES LONG. THE ENCAPSULATION FITTING WAS SUCCESSFULLY INSTALLED AROUND THE ORIGINAL TWO CRACKS. THE THIRD CRACK WAS SOAP TAPED AS A TEMPORARY REPAIR. SERVICE TECHNICIANS REMAINED ONSITE TO MONITOR THE LEAK WHILE THE REPAIRS WERE MADE. IT IS UNCLEAR IF THE PIPE WAS CONSTRUCTED RESTING ON CONCRETE AND BRICK OR IF SUBSIDENCE OVER THE PAST 113 YEARS MOVED THE PIPE TO ITS CURRENT POSITION. THE COMPANY IS ALSO UNABLE TO DETERMINE IF OUTSIDE FORCES FROM THE TRAFFIC ABOVE THE PIPE WAS A CONTRIBUTING FACTOR TO THE FAILURE. THE UNCERTAINTY OF THE ROOT CAUSE OF FAILURE HAS PROMPTED THE COMPANY TO ACCELERATE ITS PLANS FOR FULL REPLACEMENT OF THIS PIPE SEGMENT AND ADJOINING MAIN. THE COMPANY HAS PROPOSED REPLACING OR ABANDONING APPROXIMATELY 2,800 FEET OF THE 24 INCH CAST IRON MAIN INVOLVED AND APPROXIMATELY 900 FEET OF 12 INCH CAST IRON MAIN.
2025-03-31 10:13 | NO | YES | NO | 20160030 | 16272 | 2016-03-25 19:52 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2016-02-25 11:23 |  |  | 2016 | 44275 DIVISION ST | LANCASTER | LOS ANGELES | CA | 93535 | 34.6874 | -118.1307 | [9 empty] | 2016-02-25 13:29 | 1141377 |  | NATURAL GAS |  | 20 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 6 | 2016-02-25 11:52 |  |  |  | 2016-02-25 12:04 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1965 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | MECHANICAL PUNCTURE | 0.8 | 0.8 | [7 empty] | CLASS 3 LOCATION | 140000 | 168182.50519554134 | 2819 | 3386.474872473078839 | 200 | 240.2607217079162 | 0 | 0 |  |  | 119 | 136.962264150943396226415094339622641509 |  | 0 | 143138 | 71284.9328572091086688113207547169811321 | 171946.2030538732784352264150943396226415 | 1 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 626-893-4536 | kle2@semprautilities.com | ON FEBRUARY 25, 2016, AT 11:52, LOS ANGELES FIRE DEPARTMENT REPORTED A MULTIVEHICLE INCIDENT AT 44275 DIVISION ST, LANCASTER. ONE OF THE VEHICLES JUMPED THE CURB AND IMPACTED THE GAS SERVICE RISER AT THE ADDRESS. THIS RESULTED IN A RELEASE OF GAS AND IGNITION. CREW RESPONDED AND CONTROLLED THE GAS. ALL REPAIRS TO THE DAMAGED SERVICE WERE COMPLETED. AT 13:29, IT WAS DETERMINED THAT THE ASSOCIATED DAMAGES COULD POSSIBLY EXCEED $50,000. THIS INCIDENT WAS REPORTED TO CPUC AND DOT (#1141377) DUE TO A GAS RELEASE AND THE ASSOCIATED DAMAGES EXCEEDING $50,000 AND MEDIA COVERAGE. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2025-03-31 10:13 | NO | NO | NO | 20160031 | 16273 | 2016-03-31 16:00 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2016-03-10 16:00 |  |  | 2016 | 1400 WALNUT AVE | ROSENBERG | FT. BEND | TX | 77471 | 29.5608 | -95.8133 | [9 empty] | 2016-03-10 16:19 | 1142486 |  | NATURAL GAS |  | 967.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2016-03-10 14:40 |  |  |  | 2016-03-10 15:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1987 | [5 empty] | 4 | AA | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 2614 | 3140.207632722464734 | 118 | 141.753825807670558 | 0 | 0 | N/A |  | 4841 | 5571.716981132075471698113207547169811321 |  | 0 | 7573 | 6513.454426153039374156334231805929919137 | 8853.678439662210763698113207547169811321 | 0 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET |  |  |  | YES | YES | [7 empty] | RAILROAD | TRENCHER | ELECTRIC | YES | 560387171 | TEXAS 811 |  | CONTRACT LOCATOR | YES |  |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO UNLOCATABLE FACILITY | [170 empty] | LESLIE J. DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steve.yarbrough@centerpointenergy.com | RAILROAD CONTROLS CONTRACTOR FOR BNSF RR, CUT 4" PLASTIC MAIN WITH TRENCHER WHILE INSTALLING CONTROL BOX WIRES. EMERGENCY RESPONDERS SHUT DOWN RAILWAY AT 1440 HOURS. RAILWAY WAS REOPENED AT 1641 HOURS WHEN GAS HAD BEEN SECURED.
2025-03-31 10:13 | NO | YES | NO | 20160032 | 16453 | 2016-04-04 08:38 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2016-03-12 15:20 |  |  | 2016 | 371 GLENCOE CHURCH LOOP | SUMMERFIELD | ROCKINGHAM | NC | 27358 | 36.2619 | -79.8553 | [9 empty] | 2016-03-12 17:24 | 1142665 |  | NATURAL GAS |  | 7.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-03-12 15:24 |  |  |  | 2016-03-12 16:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1974 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | SERVICE RISER CUT WITH SAW. | CLASS 1 LOCATION | 171990 | 206612.20763272253619 | 500 | 600.6518042697905 | 500 | 600.6518042697905 | 0 | 0 |  |  | 40 | 46.03773584905660377358490566037735849057 |  | 0 | 173030 | 86112.7113494251009059029649595687331536 | 207859.5489771111737937735849056603773585 | 0 | 0 | 1 |  |  |  |  | 58 | 60 | 75 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | FARRIS BERRY | MANAGER - PIPELINE SAFETY | farris.berry@piedmontng.com | 704-731-4618 |  |  |  |  | MINH TRAN | MANAGING DIRECTOR - CONSTRUCTION | 704-587-6865 | minh.tran@piedmontng.com | A CONTRACTOR WORKING FOR PIEDMONT WAS RETIRING A DISTRIBUTION MAIN LINE. AFTER RETIRING THE LINE, THEY WERE CUTTING THE SERVICE LINES WITH RECIPROCATING SAWS. THE SERVICE LINE INVOLVED IN THE INCIDENT WAS FED FROM A DIFFERENT MAIN THAN EXPECTED. WHEN THE CONTRACTOR CUT THE SERVICE LINE, THE GAS IGNITED. CREWS WERE UNABLE TO TURN OFF GAS UNTIL APPROXIMATELY 6:00 PM. THE HOME WAS UNOCCUPIED AT THE TIME, AND THERE WERE NO INJURIES. THE RESULTING FIRE CAUSED EXTENSIVE DAMAGE TO THE RESIDENCE.
2025-03-31 10:13 | NO | YES | YES | 20160033 | 16444 | 2016-04-04 10:09 | SUPPLEMENTAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY | CANONSBURG | PA | 15317 | 2016-03-04 10:55 |  |  | 2016 | 372 LEXINGTON WAY | LITTLESTOWN | ADAMS | PA | 17340-1565 | 39.7383 | -77.0919 | [9 empty] | 2016-03-04 12:49 | 1141981 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 2 | 0 | 0 | 2 | YES |  |  |  |  | YES | 0 | 2016-03-04 10:55 |  |  |  | 2016-03-04 10:26 |  | NO | PRIVATE PROPERTY | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1999 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.99 |  | UNKNOWN | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | 199000 | 239059.418099376619 | 0 | 0 | 4500 | 5405.8662384281145 | 0 | 0 |  |  | 0 | 0 |  | 0 | 203500 | 101250.1889287739235 | 244465.2843378047335 | 0 | 0 | 1 |  |  |  |  | 42 | 44 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | NUT FOLLOWER |  | RISER |  | NORMAC |  | OTHER | MATERIALS JOINED: 1ST PLASTIC, 2ND STEEL | [22 empty] | YES | ALTHOUGH THIS IS JURISDICTIONAL PIPING, IT IS CUSTOMER OWNED. THE TRUE CAUSE WILL NOT BE KNOW UNTIL THE FINAL TESTING IS COMPLETED | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | RICK BURKE | OPERATIONS COMPLIANCE MANAGER | rburke@nisource.com | 724-416-6332 | 724-416-6385 |  |  |  | MIKE DAVIDSON | VP GENERAL MANAGER | 724-416-6308 | mdavids@nisource.com | ON MARCH 4, 2016 AT APPROXIMATELY 9:03 AM, A BYSTANDER CALLED IN AN ODOR OF GAS IN THE AIR IN THE VICINITY OF 244 SOUTH COLUMBUS AVE, LITTLESTOWN, PA. COLUMBIA'S EMPLOYEE ARRIVED ONSITE AT 9:49 AM. THERE WAS NO INDICATION OF LEAKAGE AT THAT ADDRESS AND THE EMPLOYEE STARTED TO ASSESS AND ESTABLISH THE PERIMETER. THE EMPLOYEE CONTINUED TO INVESTIGATE THE ENTIRE BLOCK AND DISCOVERED 30 % LEL READINGS IN THE VICINITY OF THE SERVICE RISER AT 372 LEXINGTON WAY, LITTLESTOWN, PA AT APPROXIMATELY 10:26 AM. HE THEN WENT TO THE FRONT DOOR TO EVACUATE THE PREMISE, KNOCKED ON THE DOOR, AND NO ONE ANSWERED. AT 10:30 AM HE SHUT OFF GAS TO THE METER VALVE. AT 10:31 AM HE CALLED INTEGRATION CENTER TO HAVE GAS COMPANY CREWS AND EMERGENCY SERVICES RESPOND TO THE SCENE. HE ALSO REQUESTED THE INTEGRATION CENTER TO CONTACT ELECTRIC COMPANY TO SHUT OFF THE ELECTRICITY TO THE HOME. AT 10:35 AM HE TERMINATED SERVICE TO THE CUSTOMER SERVICE LINE BY ENGAGING THE EXCESS FLOW VALVE. AT 10:35 AM THE LITTLESTOWN FIRE DEPARTMENT ARRIVED. THE FIRE FIGHTERS DISCOVERED A CAR IN THE GARAGE THROUGH A WINDOW THEY WERE ABLE TO OPEN AND WERE CONCERNED THAT SOMEONE WAS HOME. THE EMPLOYEE AND FIRE FIGHTERS GOT 20% LEL READINGS INSIDE THE GARAGE AND THE FIREFIGHTERS DECIDED TO ENTER THE HOME TO LOOK FOR ANYONE INSIDE. AT APPROXIMATELY 10:55 AM THE RESIDENCE AT 372 LEXINGTON WAY EXPLODED SEVERELY DAMAGING THE HOME. TWO FIRE FIGHTERS FROM THE LITTLESTOWN FIRE DEPARTMENT IN THE BASEMENT OF THE HOME AT THE TIME OF THE INCIDENT SUFFERED THIRD DEGREE BURNS TO THEIR HANDS AND WERE ADMITTED TO THE BAYVIEW BURN CENTER IN BALTIMORE, MD. BOTH FIREFIGHTERS WERE RELEASED ON MARCH 8, 2016.
2025-03-31 10:13 | NO | NO | NO | 20160034 | 16277 | 2016-04-04 16:01 | ORIGINAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2015-05-22 12:48 |  |  | 2015 | 2729 HARRISON AVE | EVERETT | SNOHOMISH | WA | 98201 | 47.9805 | -122.1822 | [9 empty] | 2016-02-25 16:15 | 1141375 |  | NATURAL GAS |  | 62.67 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-05-22 12:26 |  |  |  | 2015-05-22 12:48 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1969 | [5 empty] | 4 | API 5L | UNKNOWN | STEEL |  | OTHER | ERW | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 56131 | 67989.134869987633362 | 3108 | 3764.590532431661016 | 0 | 0 |  |  | 626 | 627.469483568075117370892018779342723005 |  | 0 | 59865 | 30298.6870799678219775023474178403755869 | 72381.194885987369495370892018779342723 | 0 | 0 | 0 |  |  |  |  | 30 | 30 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS CAUSED B Y A THIRD PARTY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | AUGER | SEWER (SANITARY/STORM) | NO |  |  |  |  | NO |  |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | DARRYL HONG | SR. REGULATORY COMPLIANCE ANALYST | darryl.hong@pse.com | 425-462-3911 |  |  |  |  | DARRYL HONG | SR. REGULATORY COMPLIANCE ANALYST | 425-462-3911 | darryl.hong@pse.com | PSE RESPONDED TO A BROKEN GAS LINE AT 2729 HARRISON AVE. UPON ARRIVAL, PSE EMERGENCY RESPONDERS FOUND A DAMAGED 4" STW MAIN BLOWING GAS. PSE FIRST RESPONDERS WERE ABLE TO STOP THE FLOW OF GAS BY INSTALLING THREE LEAK CLAMPS. THE EVERETT FIRE DEPARTMENT EVACUATED AN UNKNOWN AMOUNT OF PEOPLE FROM FIVE STRUCTURES. THIRD PARTY CONTRACTOR (HOLOCENE DRILLING) WAS CONDUCTING SEWER/ SANITARY STORM DRAIN WORK WITH AN AUGER WHEN THE 4" STW MAIN WAS DAMAGED. HOLOCENE DRILLING DID NOT CALL FOR LOCATES PRIOR TO WORK COMMENCING. WHEN OUR FIRST RESPONDERS WERE ON SITE DURING THE INCIDENT THEY NOTICED LOCATES MARKED IN THE CONSTRUCTION SITE AND THOUGHT THESE WERE CALLED IN BY HOLOCENE DRILLING AS PART OF THE CONSTRUCTION WORK BEING CONDUCTED. AFTER RESEARCHING THE INCIDENT FURTHER IT WAS DETERMINED THAT ANOTHER CONTRACTOR HAD CALLED IN LOCATES EARLIER IN THE MONTH AND THE LOCATES WERE MARKED FOR A SPECIFIC CONSTRUCTION JOB, NOT THE ONE HOLOCENE DRILLING WAS WORKING ON. THE ONLY LOCATES CALLED IN BY HOLOCENE DRILLING WAS ABOUT A MILE AWAY FROM THE DAMAGE SITE. BY NOT CALLING IN LOCATES FOR THE SPECIFIC WORK BEING CONDUCTED AND NOT USING HAND TOOLS TO LOCATE THE MAIN HOLOCENE DRILLING DRILLED AN AUGER RIGHT INTO THE TOP OF THE PSE 4" STW MAIN CAUSING AN UNCONTROLLED RELEASE OF GAS. .
2025-03-31 10:13 | NO | NO | NO | 20160035 | 16279 | 2016-04-08 14:29 | ORIGINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2016-03-11 20:50 |  |  | 2016 | 1511 W 13TH AVE. | CORSICANA | NAVARRO | TX | 75110 | 32.0796 | -96.4752 | [9 empty] | 2016-03-11 22:57 | 1142608 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 6 | 2016-03-11 20:55 |  |  |  | 2016-03-11 21:45 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1969 | [5 empty] | 0.75 | DUPONT | DUPONT | PLASTIC |  |  |  |  | OTHER | DUPONT |  | 0.648 |  |  | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 |  |  |  |  | 32 | 32 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | SOCKET, ELECTROFUSION |  | 2008 |  | OTHER | DUPONT | POLYETHYLENE (PE) | [11 empty] | YES |  |  |  | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | ROY MOSS | OPERATIONS MANAGER | roy.moss@atmosenergy.com | 972-485-6260 | 972-485-6267 |  |  |  | ANDY TREADWAY | COMPLIANCE DIRECTOR | 214-206-2044 | andy.treadway@atmosenergy.com | A LEAK WAS FOUND AT 918 COTTONWOOD, CORSICANA, TX. ONCE ELIMINATED, THE GAS READINGS IN THE DAMAGED STRUCTURE RETURNED TO ZERO.
2025-03-31 10:13 | NO | NO | NO | 20160036 | 16295 | 2016-04-08 14:30 | SUPPLEMENTAL FINAL | 12878 | MOUNTAINEER GAS CO | 501 56TH ST. SE | CHARLESTON | WV | 25304 | 2016-03-09 06:45 |  |  | 2016 | BELLE HOLLOW | BELLE | KANAWHA | WV | 25015 | 38.2423 | -81.5295 | [9 empty] | 2016-03-09 08:29 | 1142311 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-03-09 07:00 |  |  |  | 2016-03-09 07:30 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1993 | [8 empty] | OTHER | SEE NARRATIVE SECTION H | [9 empty] | OTHER | [8 empty] | SEE NARRATIVE SECTION H | CLASS 1 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SEE NARRATIVE SECTION H |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 680 | 680 | 930 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS SITE WAS NOT CONTROLLED. IT WAS MONITORED. DATA WAS PROVIDED AFTER NOTIFICATION. SEE NARRATIVE SECTION H. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | SEE NARRATIVE SECTION H. | [47 empty] | PHILIP KINGREY | ENGINEER | philipkingrey@mgcwv.com | 888-420-4427 | 304-925-9605 |  |  |  | THOMAS WESTFALL | DIRECTOR OF GAS SUPPLY AND TECHNICAL SERVICES | 888-420-4427 | thomaswestfall@mgcwv.com | ON 3/9/2016 A FIRE WAS REPORTED AT THE BELLE HOLLOW STATION. MOUNTAINEER ARRIVED AT APPROXIMATELY 07:30 AND TURNED OFF GAS STATION AT APPROXIMATELY 07:35. COLUMBIA GAS TRANSMISSION AND ENERGY CORP. OF AMERICA ALSO RESPONDED TO SHUT OFF THEIR FACILITIES. THE STATION WAS COMPLETELY DESTROYED BY FIRE. INVESTIGATION OF CAUSE IS STILL UNDERWAY. MOUNTAINEER CONTINUES TO SHARE INFORMATION AND COOPERATE WITH THE WV PUBLIC SERVICE COMMISSION OFFICE OF PIPELINE SAFETY TO COMPLETE THE INVESTIGATION. ADDED 5/9/2016: MOUNTAINEER HAS COMPLETED ITS INVESTIGATION OF THE INCIDENT. MOUNTAINEER CONTINUES TO WORK WITH THE WV PUBLIC SERVICE COMMISSION-PIPELINE SAFETY TO DO FURTHER EVALUATION ON SOME EQUIPMENT BUT THOSE EVALUATIONS ARE NOT EXPECTED TO BE RELATED TO THE INCIDENT. IT IS MOUNTAINEER'S FINDING THAT THE CAUSE OF THE INCIDENT WAS A LEAK ON THE INLET/SUPPLY PIPING OF THE POINT OF DELIVERY STATION. THIS PORTION OF THE STATION WAS NOT OWNED OR OPERATED BY MOUNTAINEER. MOUNTAINEER HAS EVALUATED THE CONDITION OF ITS REMAINING PIPING AND EQUIPMENT AND DETERMINED THAT THERE WAS NO FAILURE OF ITS PIPING OR EQUIPMENT OTHER THAN SECONDARY DAMAGE AS A RESULT OF THE FIRE.
2025-03-31 10:13 | NO | YES | NO | 20160037 | 16319 | 2016-04-13 18:18 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2016-03-13 17:16 |  |  | 2016 | RHEEM BLVD & CENTER ST | MORAGA | CONTRA COSTA | CA | 94556 | 37.8603 | -122.125 | [9 empty] | 2016-03-14 16:03 | 1142804 |  | NATURAL GAS |  | 5200 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 19 | 2016-03-13 17:16 |  |  |  | 2016-03-13 18:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1954 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | TRAFFIC LIGHT FELL INTO A SINKHOLE AND SEVERED THE 4" GAS LINE. | CLASS 3 LOCATION | 0 | 0 | 10000 | 12013.03608539581 | 0 | 0 | 100000 | 120130.3608539581 | COSTS ASSOCIATED WITH RELIGHT |  | 14000 | 16113.2075471698113207547169811320754717 |  | 0 | 124000 | 69635.4922307498005660377358490566037736 | 148256.6044865237213207547169811320754717 | 19 | 0 | 2584 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM PERFORMED AS INTENDED. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | WINTER RAINS SATURATED LOCAL SOILS, RESULTING IN SUBSIDENCE. AS RAIN CONTINUED, A TRAFFIC SIGNAL POLE AND A PORTION OF THE SIDEWALK FELL INTO THE EXPANDING SINKHOLE. THE COLLAPSE RUPTURED THE 4" DISTRIBUTION GAS MAIN. | NO | [218 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-328-6107 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON MARCH 13, 2016 AT 1716 HOURS, PG&E'S GAS CONTROL WAS NOTIFIED OF A SINKHOLE AT RHEEM BLVD AND CENTER ST, IN MORAGA. THE SINKHOLE CAUSED A TRAFFIC LIGHT TO FALL, WHICH SEVERED THE 4" STEEL DISTRIBUTION MAIN AND RESULTED IN AN UNINTENTIONAL RELEASE OF GAS. PG&E'S GAS SERVICE REPRESENTATIVE ARRIVED ON SITE AT 1835 HOURS. PG&E CREWS STOPPED THE FLOW OF GAS ON 3/14/16 AT 0105 HOURS BY SHUTTING OFF 7 VALVES. APPROXIMATELY 2603 CUSTOMERS WERE SHUT-IN IN ORDER TO MAKE THE SITUATION SAFE. PG&E CREWS CUT AND CAPPED THE DAMAGED MAIN BY 0930 ON 3/14/16. THE AREA IS A DUAL FEED ALLOWING CREWS TO BEGIN PREPARATION TO RE-LIGHT CUSTOMERS. WITHIN 36 HOURS OF THE INCIDENT, 90% OF THE SERVICES WERE RESTORED. ADDITIONALLY, PG&E BROUGHT IN CNG TRAILERS TO RESTORE SERVICE TO LOCAL BUSINESSES. A BYPASS WAS INSTALLED TO REMOVE THE CNG TRAILER AND CONTINUOUSLY PROVIDE SERVICE TO THE LOCAL BUSINESSES. REPAIRS TO THE MAIN ARE ON-GOING AND WILL BE COMPLETE ONCE THE TOWN OF MORAGA PERFORMS THEIR STORM DRAIN WORK WITHIN THE SINK HOLE. THERE WERE NO INJURIES, FATALITIES OR IGNITION ASSOCIATED WITH THIS INCIDENT. POLICE, FIRE DEPARTMENT AND MEDIA (ABC, KRON, CBS) WERE REPORTED ON SITE. THIS INCIDENT WAS REPORTED TO THE CPUC DUE TO THE UNINTENTIONAL RELEASE OF GAS AND MEDIA PRESENCE. THIS INCIDENT WAS REPORTED TO THE DOT ON 3/14/16 ONCE IT WAS DETERMINED THAT COSTS WOULD EXCEED $50,000.
2025-03-31 10:13 | NO | YES | NO | 20160038 | 16303 | 2016-04-19 11:47 | SUPPLEMENTAL FINAL | 2364 | DUKE ENERGY OHIO | 139 EAST FOURTH STREET PO BOX 960 - ROOM 460-ANNEX | CINCINNATI | OH | 45202 | 2016-03-21 10:22 |  |  | 2016 | 46 WOODSTOCK DRIVE | FAIRFIELD | BUTLER | OH | 45014 | 39.317 | -84.5052 | [9 empty] | 2016-03-21 11:28 | 1143355 |  | NATURAL GAS |  | 1274.26 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 20 | 2016-03-21 10:27 |  |  |  | 2016-03-21 10:41 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1973 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 4 LOCATION | 600000 | 720782.1651237486 | 10250 | 12313.36198753070525 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 610250 | 303626.18080483679025 | 733095.52711127930525 | 0 | 0 | 20 |  |  |  |  | 41 | 41 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY | 2014-01-01 | NO |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 607601201 | OHIO UTILITIES PROTECTION SERVICE |  | CONTRACT LOCATOR | YES | YES | 8 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | LOCATING AND EXCAVATION PRACTICES NOT SUFFICIENT. | [169 empty] | RANDY SUTTLES | SENIOR REGULATORY COMPLIANCE SPECIALIST | randall.suttles@duke-energy.com | 513-287-3346 |  |  |  |  | CHRISTIE TITMUS | MANAGER GAS COMPLIANCE | 513-287-3781 | christie.titmus@duke-energy.com | DUKE ENERGY'S INVESTIGATION REVEALED A COUPLE OF FACTORS CONTRIBUTED TO THE CAUSE OF THE INCIDENT. FIRST, THE CONTRACTOR HIRED BY DUKE ENERGY (USIC LOCATING SERVICES, INC.) TO LOCATE THE FACILITIES DID NOT FOLLOW THE PROCEDURE WHEN DEALING WITH AN UNTONEABLE SERVICE. DUKE ENERGY HAS A PROCEDURE THAT REQUIRES THE LOCATING COMPANY TO TAKE ADDITIONAL STEPS WHEN LOCATING UNTONEABLE SERVICES. SECOND, THE PLUMBER PERFORMING THE WORK USED A TRACK HOE TO EXCAVATE INSIDE THE TOLERANCE ZONE INSTEAD OF HAND DIGGING TO LOCATE THE SERVICE.
2025-03-31 10:13 | NO | YES | NO | 20160039 | 16801 | 2016-04-20 08:32 | SUPPLEMENTAL FINAL | 18440 | SOUTH JERSEY GAS CO | 101 SOUTH LINCOLN PLACE | ATLANTIC CITY | NJ | 08401 | 2016-03-17 04:51 |  |  | 2016 | 321 N. HOOK ROAD | PENNSVILLE | SALEM | NJ | 08070-1151 | 39.6668 | -75.4887 | [9 empty] | 2016-03-17 09:25 | 1143067 |  | NATURAL GAS |  | 19.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2016-03-17 04:51 |  |  |  | 2016-03-17 05:44 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1968 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | VEHICLE STRUCK METER BUILDUP | CLASS 4 LOCATION | 110000 | 132143.39693935391 | 5000 | 6006.518042697905 | 1000 | 1201.303608539581 | 0 | 0 |  |  | 50 | 57.54716981132075471698113207547169811321 |  | 0 | 116050 | 57768.329910378544894878706199460916442 | 139408.7657604027167547169811320754716981 | 0 | 0 | 1 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OBVIOUS NATURE OF ACCIDENT, A PICKUP TRUCK STRUCK A METER AT A RESIDENCE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DAVID NEWMAN | MANAGER COMPLIANCE | dnewman@sjindustires.com | 609-561-9000 | 609-704-1802 |  |  |  | DAVID NEWMAN | MANAGER COMPLIANCE | 609-561-9000 | dnewman@sjindustries.com | A PICKUP TRUCK WAS TRAVELLING NORTH ON N. HOOK RD AND LEFT THE ROAD DUE TO DRIVER ERROR. THE TRUCK THEN STRUCK THE FRONT RIGHT SIDE OF THE HOME AT 321 N. HOOK RD. DIRECTLY HITTING THE GAS METER BUILDUP AT THAT LOCATION OF THE HOUSE. THE BUILDUP WAS SEVERED FROM THE RISER CAUSING A RELEASE OF NATURAL GAS. THE NATURAL GAS IGNITED CAUSING A FIRE AT THE HOME.
2025-03-31 10:13 | NO | NO | NO | 20160040 | 16284 | 2016-04-20 10:50 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2016-03-21 08:15 |  |  | 2016 | MT. GILLIAD & HWY 377 | KELLER | TARRANT | TX | 76248 | 32.9606 | -97.2478 | [9 empty] | 2016-03-21 10:50 | 1143358 |  | NATURAL GAS |  | 20000 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-03-21 08:30 |  |  |  | 2016-03-21 09:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1971 | [5 empty] | 6 | X42 | UNKNOWN | STEEL |  | SEAMLESS | SEAMLESS | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 50000 | 60065.18042697905 | 0 | 0 | 0 | 0 |  |  | 2000 | 2301.886792452830188679245283018867924528 |  | 0 | 52000 | 27006.5763509044057951482479784366576819 | 62367.0672194318801886792452830188679245 | 0 | 0 | 0 |  |  |  |  | 410 | 410 | 500 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS DUE TO 3RD PARTY, NO CONTROLLER ISSUES WERE PRESENT | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | BRANDON WALTON | OPERATIONS SUPERVISOR | brandon.walton@atmosenergy.com | 214-491-0443 | 940-433-8911 |  |  |  | PETE PEDERSEN | COMPLIANCE MANAGER | 214-206-2791 | peter.pedersen@atmosenergy.com | 3RD PARTY CONTRACTOR WAS DRIVING A FORK LIFT ON OUR ROW AND GOT STUCK. FORK LIFT OPERATOR REQUESTED ASSISTANCE FROM ANOTHER CONTRACTOR WORKING ON SITE FOR USE OF A TRACK LOADER IN ORDER TO REMOVE THE PIECE OF EQUIPMENT. THE TRACK LOADER ALSO SANK IN THE WET AREA AND PUNCTURED THE PIPE WITH A TRACK ON THE LOADER.
2025-03-31 10:13 | NO | NO | NO | 20160041 | 16305 | 2016-04-25 16:24 | SUPPLEMENTAL | 603 | CENTERPOINT ENERGY RESOURCES CORP. | 10825 E GEDDES AVE SUITE 410 | CENTENNIAL | CO | 80112 | 2016-04-05 12:50 |  |  | 2016 | I-430 N OF ARKANSAS RIVER | NORTH LITTLE ROCK | PULASKI | AR | 72118 | 34.8036 | -92.3688 | [9 empty] | 2016-04-05 14:45 | 1144548 |  | NATURAL GAS |  | 1000 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-04-05 12:50 |  |  |  | 2016-04-05 13:15 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | OVERHEAD CROSSING |  |  |  | YES | YES | UNCASED | [9 empty] | OTHER | PUBLICLY TRADED LDC | MAIN |  | UNKNOWN | [5 empty] | 10 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | 0 | 0 | 35000 | 42045.626298885335 | 300 | 360.3910825618743 | 0 | 0 |  |  | 3850 | 4431.132075471698113207547169811320754717 |  | 0 | 39150 | 21662.3571894527962056603773584905660377 | 46837.1494569189074132075471698113207547 | 0 | 0 | 0 |  |  |  |  | 200 | 200 | 280 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 2 | 0 | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | INCORRECT OPERATION | INCORRECT EQUIPMENT | [222 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED |  |  |  |  | YES | WRONG EQUIPMENT SPECIFIED | COMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | JAY REBER | DISTRICT OPERATIONS MANAGER | jay.reber@centerpointenergy.com | 501-377-4980 | 501-377-4721 |  |  |  | KEITH KITTINGER | REGIONAL OPERATIONS DIRECTOR | 501-377-4669 | keith.kittinger@centerpointenergy.com | CNP'S INVESTIGATION DETERMINED THAT THE WRONG TYPE OF EQUIPMENT (FITTING) WAS SPECIFIED FOR INSTALLATION OF AN EXPANSION JOINT, CAUSING LINE SEPARATION FOR A BRIEF PERIOD OF TIME. CURRENTLY THE LINE IS SHUT-IN AND WILL REMAIN INACTIVE UNTIL OCTOBER 1, 2106 WHEN THE ORDERED PROPER EQUIPMENT ARRIVES FOR INSTALLATION. WE ANTICIPATE NO CHANGES UNTIL REPAIRS ARE COMPLETED WITH INSTALLATION OF THE NEW EQUIPMENT AND WILL SUBMIT THE FINAL REPORT AT THAT TIME.
2025-03-31 10:13 | NO | YES | YES | 20160043 | 16789 | 2016-04-29 23:48 | SUPPLEMENTAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2016-03-30 09:05 |  |  | 2016 | CHOSIN FEW WAY | BAYONNE | HUDSON | NJ | 07002 | 40.6742 | -74.1021 | [9 empty] | 2016-03-30 14:48 | 1144063 |  |  |  | 0 |  | NO | [5 empty] | 0 | YES | 0 | 2 | 0 | 0 | 0 | 2 | NO |  |  |  |  | NO | 0 | 2016-03-30 09:05 |  |  |  | 2016-03-30 09:05 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 35 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2015 | [5 empty] | 20 | API 5L | UNKNOWN | STEEL |  | OTHER | ERW | 0.375 | [6 empty] | OTHER | [8 empty] | PIPELINE WAS NOT IN SERVICE. THE INCIDENT OCCURRED DURING PRESSURE TESTING OF PIPE. | CLASS 1 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 82 | 7 | 15 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | YES | 9 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | THE INCIDENT OCCURRED DURING PRESSURE TESTING OF PIPE. AIR WAS INTRODUCED WHILE EXCAVATING THE END OF PIPE. |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | MICHAEL DONOHUE | PRINCIPLE REGULATORY SPECIALIST | michael.donohue@pseg.com | 908-608-4053 |  |  |  |  | MATTHEW WEISSMAN | GENERAL REGULATORY COUNSEL | 973-430-7052 | matthew.weissman@pseg.com | ON MARCH 30, 2016, AT APPROXIMATELY 9:00 A.M. A CREAMER-SANZARI JOINT VENTURE CREW WORKING FOR PSE&G GAS DISTRIBUTION WAS IN THE PROCESS OF PREPARING TO PRESSURE TEST APPROXIMATELY 1200-FOOT OF 20-INCH STEEL. ONE END OF THE MAIN WAS EXPOSED, AND A CREW WAS IN THE PROCESS OF EXCAVATING THE OTHER END WHEN A FAILURE OCCURRED. TWO CREAMER-SANZARI JOINT VENTURE WORKERS WERE THROWN FROM THE EXCAVATION BY THE FORCE OF THE SUDDEN RELEASE OF THE PRESSURE, AND SUSTAINED SERIOUS INJURIES, WERE TAKEN TO JERSEY CITY MEDICAL CENTER-BARNABAS HEALTH WHERE THEY RECEIVED TREATMENT, AND WERE SUBSEQUENTLY RELEASED. ADDITIONALLY, ONE CREAMER-SANZARI EMPLOYEE AND TWO BAYONNE POLICE OFFICERS SUSTAINED NON-LIFE THREATENING INJURIES WERE TREATED AND ALSO RELEASED.
2025-03-31 10:13 | NO | NO | NO | 20160044 | 16291 | 2016-05-04 09:01 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2016-04-05 08:00 |  |  | 2016 | 16400 GOLF CLUB DRIVE | CROSBY | HARRIS | TX | 77532 | 29.92 | -95.0898 | [9 empty] | 2016-04-05 09:55 | 1144518 |  | NATURAL GAS |  | 104 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 12 | 2016-04-05 08:51 |  |  |  | 2016-04-05 08:51 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1982 | [5 empty] | 2 | UNKNOWN | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | 2306 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 50000 | 60065.18042697905 | 391 | 469.709710938976171 | 1636 | 1965.332703570754516 | 0 | 0 |  |  | 521 | 599.64150943396226415094339622641509434 |  | 0 | 52548 | 26440.4213389193965516361185983827493261 | 63099.8643509227429511509433962264150943 | 0 | 0 | 0 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED DETECTION THRESHOLDS OF THE SYSTEM | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | [7 empty] | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 560703906 | TEXAS 811 |  | CONTRACT LOCATOR | NO |  |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | LESLIE DAVENPORT | COMPLIANCE COORDIANTOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steven.yarbrough@centerpointenergy.com | CONTRACTOR INSTALLING SEWER SYSTEM WAS EXCAVATING WITH A TRACKHOE AND DAMAGED 2" PLASTIC GAS MAIN. ESCAPING GAS IGNITED AND DAMAGED THE TRACKHOE.
2025-03-31 10:13 | NO | YES | NO | 20160045 | 16339 | 2016-05-04 17:06 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 10885 NE 4TH ST 98004 | BELLEVUE | WA | 98004 | 2016-03-09 02:00 |  |  | 2016 | 8411 GREENWOOD AVE N | SEATTLE | KING | WA | 98103 | 47.6902 | -122.3557 | [9 empty] | 2016-03-09 04:12 | 1142307 |  | NATURAL GAS |  | 46.52 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2016-03-09 02:00 |  |  |  | 2016-03-09 02:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1969 | [5 empty] | 0.75 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | LEAK |  |  | OTHER | OUTSIDE FORCE | [5 empty] | CLASS 3 LOCATION | 3000000 | 3603910.825618743 | 0 | 0 | 17650 | 21203.00869072360465 | 0 | 0 | THE THREE MILLION DOLLAR PROPERTY DAMAGE COST IS BASED OFF A MEDIA REPORT. |  | 522 | 600.792452830188679245283018867924528302 |  | 0 | 3018172 | 1501969.19630667268651253369272237196765 | 3625714.62676229679332924528301886792453 | 15 | 0 | 1 |  |  |  |  | 39.2 | 42 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  | YES | THE GAS CONTROL ROOM COULD NOT SEE ANY PRESSURE DROP OR ALARMS IN SCADA WHEN REVIEWING MONITORING POINTS CLOSE TO THE INCIDENT. | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | SERVICE PIPE ACCIDENTALLY DAMAGED BY HOMELESS INDIVIDUAL WHEN MOVING BELONGINGS THAT HAD BECOME ENTANGLED ON PIPE. | [154 empty] | STEPHANIE SILVA | GAS COMPLIANCE PROGRAM MANAGER | stephanie.silva@pse.com | 425-462-3923 |  |  |  |  | STEPHANIE SILVA | GAS COMPLIANCE PROGRAM MANAGER | 425-462-3923 | stephanie.silva@pse.com | PSE WAS NOTIFIED BY THE SEATTLE FIRE DEPARTMENT OF AN ODOR CALL AT THE ADDRESS OF 213 N 85TH ST. WHEN PSE FIRST RESPONDERS ARRIVED ON SITE THEY FOUND SEVERAL BUILDINGS DESTROYED BY AN EXPLOSION. LAB ANALYSIS OF THE FAILED PART INDICATES THAT OUTSIDE FORCE CAUSED THE FAILURE OF THE ABOVEGROUND PIPE AT THIS LOCATION. THIS IS CONSISTENT WITH THE SEATTLE FIRE DEPARTMENT'S ASSESSMENT OF INCIDENT CAUSE.
2025-03-31 10:13 | NO | NO | NO | 20160046 | 16298 | 2016-05-16 19:33 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2016-03-04 00:15 |  |  | 2016 | 900 SW HOLDEN ST | SEATTLE | KING | WA | 98126 | 47.5344 | -122.3477 | [9 empty] | 2016-03-28 15:29 | 1143926 |  | NATURAL GAS |  | 13.72 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 60 | 2016-03-04 00:15 |  |  |  | 2016-03-04 00:19 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1967 | [8 empty] | OTHER | STAINLESS STEEL SENSE LINE TUBING | [9 empty] | LEAK |  |  | OTHER | SEVERED FROM A CAR ACCIDENT | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 87000 | 104513.413942943547 | 6586 | 7911.785565841680466 | 0 | 0 |  |  | 153 | 176.094339622641509433962264150943396226 |  | 0 | 93739 | 46726.0434271374359243288409703504043127 | 112601.2938484078689754339622641509433962 | 0 | 0 | 0 |  |  |  |  | 40.6 | 40 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VEHICLE STRUCK THE RTU AND REGULATOR STATION AT THE INTERSECTION OF HIGHLAND AND HOLDEN. CONTROL ROOM LOST COMMUNICATION WITH THE RTU AND RECEIVED A COMMUNICATION ALARM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DARRYL HONG | SR. REGULATORY COMPLIANCE ANALYST | darryl.hong@pse.com | 425-462-3911 |  |  |  |  | CHERYL MCGRATH | MANAGER OF COMPLIANCE PROGRAMS | 425-462-3207 | cheryl.mcgrath@pse.com | PSE RESPONDED TO A REPORT OF DAMAGE TO PSE FACILITY AT 900 SW HOLDEN ST. UPON ARRIVAL PSE FIRST RESPONDERS FOUND A DAMAGED ABOVEGROUND REGULATOR STATION AND AN EXISTING RTU. THE DAMAGE WAS CAUSED BY A CAR ACCIDENT THAT RESULTED IN AN UNCONTROLLED RELEASE OF GAS. FIRST RESPONDERS WERE ABLE TO STOP THE FLOW OF GAS BY SHUTTING OFF THE HEADER VALVE TO REGULATOR RUN THAT WAS DAMAGED. FIRST RESPONDERS USED AN EXISTING BYPASS TO SERVE CUSTOMERS DOWN STREAM. THE CITY OF SEATTLE FIRE DEPARTMENT EVACUATED 60 PEOPLE FROM AN APARTMENT BUILDING AND NEIGHBORING HOMES AS A PRECAUTION. A CAR TRAVELING DOWN 9TH AVE SW AT A HIGH RATE OF SPEED SMASHED THROUGH THE FENCE OF A PSE DISTRICT REGULATOR DAMAGING THE OUTLET INTERMEDIATE PRESSURE REGULATOR RUN OF THE STATION. PSE IS IN THE PROCESS OF REPLACING THE DAMAGED REGULATOR RUN AND RTU. PSE PRESSURE CONTROL TECHNICIANS ALSO REPLACED CONTROL LINE TUBING TO TWO REGULATOR RUNS AS THESE WERE DAMAGED AS WELL.
2025-03-31 10:13 | NO | NO | NO | 20160047 | 16788 | 2016-05-19 12:00 | SUPPLEMENTAL FINAL | 12876 | QUESTAR GAS COMPANY | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2016-04-21 16:21 |  |  | 2016 | HARRISION BLVD AND DOUGLAS ST | OGDEN | WEBER | UT | 84404 | 41.257 | -111.9479 | [9 empty] | 2016-04-22 08:08 | 1145920 |  | NATURAL GAS |  | 4453.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 20 | 2016-04-21 16:21 |  |  |  | 2016-04-21 16:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1983 | [5 empty] | 4 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 5.5 | 4.2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 68 | 81.688645380691508 | 7389 | 8876.432363498964009 | 0 | 0 |  |  | 19301 | 22214.3584905660377358490566037735849057 |  | 0 | 26758 | 24259.7672659765784980781671159029649596 | 31172.4794994456932528490566037735849057 | 0 | 0 | 0 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 60990168 |  |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | REID HESS | MANAGER GAS OPERATIONS | reid.hess@dominionenergy.com | 8013243374 |  |  |  |  | VAUGHN SHOSTED | VP OPERATIONS | 8013243384 | vaughn.shosted@questar.com | 3RD PARTY DAMAGE TO 4" INCH PLASTIC MAIN CAUSING RELEASE OF GAS. SAFETY CONSIDERATIONS WERE EMPLOYED TO DETERMINE IT WAS BEST TO SHUT THE GAS SUPPLY TO THE DAMAGED AREA BY USE OF VALVES INSTEAD OF REMOTE HOLE SQUEEZE LOCATION. INTENDED ORIGINAL TO BE ORIGINAL/FINAL. FINAL BUTTON WAS NOT CLICKED. NO SUPPLEMENTAL INFORMATION.
2025-03-31 10:13 | NO | NO | NO | 20160048 | 30339 | 2016-05-19 15:03 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 255 NORTH SHORE DRIVE | PITTSBURGH | PA | 15212 | 2016-04-17 13:47 |  |  | 2016 | 324 AVENUE A | FOREST HILLS | ALLEGHENY | PA | 15221-4210 | 40.413 | -79.8434 | [9 empty] | 2016-04-17 14:58 | 1145497 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2016-04-16 13:25 |  |  |  | 2016-04-16 13:48 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | INCIDENT OCCURRED ON HOUSE LINE PIPING OWNED BY THE CUSTOMER | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | LEAK ON INTERIOR HOUSE LINE | [5 empty] | CLASS 3 LOCATION | 71000 | 85292.556206310251 | 0 | 0 | 8000 | 9610.428868316648 | 0 | 0 |  |  | 8 | 9.20754716981132075471698113207547169811 |  | 0 | 79008 | 39314.4876694693924231805929919137466307 | 94912.1926217967103207547169811320754717 | 0 | 0 | 8 |  |  |  |  | 0.4 | 0.4 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | WAYNE DADIG | MANAGER PROCESS WORK MANAGEMENT | wayne.dadig@peoples-gas.com | 412 258-4604 | 412 258-4641 |  |  |  | PAUL BECKER | VICE PRESIDENT OPERATIONS AND ENGINEERING | 412-258-4406 | paul.becker@peoples-gas.com | THERE WAS A FIRE/EXPLOSION AT 322 - 324 AVENUE A IN FOREST HILLS AT APPROXIMATELY 1:50 PM ON SUNDAY, APRIL 17TH, 2016. NO RESIDENTS WERE PRESENT AT THE TIME OF THE EXPLOSION. THE DUPLEX WAS DESTROYED AND PLANS ARE BEING MADE FOR ITS DEMOLITION. THE REPORT FILED BY THE ALLEGHENY COUNTY FIRE MARSHAL STATES THE CAUSE OF THE INCIDENT HAS BEEN CLASSIFIED AS UNDETERMINED.
2025-03-31 10:13 | NO | YES | NO | 20160049 | 16307 | 2016-05-27 11:49 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2016-05-15 17:37 |  |  | 2016 | 1120 MCCONNELL DRIVE | DECATUR | DEKALB | GA | 30033 | 33.8116 | -84.3124 | [9 empty] | 2016-05-16 18:01 | 1147911 |  | NATURAL GAS |  | 560.04 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-05-15 17:37 |  |  |  | 2016-05-15 18:17 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 5 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1989 | [5 empty] | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1.9 | 1.9 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 136044 | 163430.148120158757564 | 2601 | 3124.590685811450181 | 0 | 0 |  |  | 1074 | 1236.113207547169811320754716981132075472 |  | 0 | 139719 | 70125.4547008891341069946091644204851752 | 167790.8520135173775563207547169811320755 | 0 | 0 | 24 |  |  |  |  | 40 | 40 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | CITY STREET | [12 empty] | COUNTY | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | NO | [5 empty] | YES | 50 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@aglresources.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@aglresources.com | A 2-INCH PLASTIC MAIN WITH ONE-WAY FEED WAS RUPTURED BY A COUNTY WATER & SEWER CREW WHILE PERFORMING MAINTENANCE WORK. ONCE THE INCIDENT WAS MADE SAFE IT WAS IDENTIFIED THAT MUD, WATER AND DEBRIS HAD ENTERED THE DOWNSTREAM GAS PIPELINE WHERE CREWS BEGAN RUNNING A CLEANING PIG TO CLEAN THE PIPELINE WHERE IT WAS DETERMINED THAT SATISFACTORY RESULTS WERE NOT BEING OBTAINED. AT THIS POINT DURING EVALUATIONS IT WAS DETERMINED THAT THE AFFECTED PIPELINE SHOULD BE REPLACED WHERE COST OF REPLACEMENT WAS THE DIRECT RESULTS OF THE INCIDENT AND NOT IMPROVEMENTS TO THE EXISTING SYSTEM WHERE THE ADDITIONAL COST RESULTED IN THE INCIDENT EXCEEDING THE $50,000 THRESHOLD FOR REPORTING. NOTIFICATION OF EXCAVATION BY THE EXCAVATOR WAS NOT MADE TO THE ONE-CALL CENTER BEFORE DAMAGE OCCURRED.
2025-03-31 10:13 | YES | NO | NO | 20160051 | 16310 | 2016-05-27 19:18 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2016-04-29 12:38 |  |  | 2016 | 173 S ARDMORE AVE | LOS ANGELES | LOS ANGELES | CA | 90004 | 34.0717 | -118.3019 | [9 empty] | 2016-04-29 13:54 | 1146542 |  | NATURAL GAS |  | 48 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 16 | 2016-04-29 12:38 |  |  |  | 2016-04-29 12:57 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1974 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | MSA WAS MELTED DUE TO THE FIRE. | CLASS 3 LOCATION | 755000 | 906984.224447383655 | 2206 | 2650.075760438315686 | 200 | 240.2607217079162 | 0 | 0 |  |  | 288 | 331.471698113207547169811320754716981132 |  | 0 | 757694 | 377149.3854982146081605013477088948787062 | 910206.0326276430944331698113207547169811 | 0 | 0 | 3 |  |  |  |  | 34 | 34 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 626-893-4536 | kle2@semprautilities.com | ON APRIL 29, 2016 AT 12:38 PM, LOS ANGELES CITY FIRE DEPARTMENT REPORTED A STRUCTURE FIRE AT 173 S ARDMORE AVE, LOS ANGELES. CREW RESPONDED AND CONTROLLED THE GAS. THERE WERE NO INJURIES THAT RESULTED FROM THIS INCIDENT. INVESTIGATION OF THE INCIDENT SHOWED THAT THE FIRE LIKELY STARTED FROM INSIDE THE HOME OF THE ADDRESS, SPREAD TO THE TWO ADJACENT HOMES (169 AND 179 S. ARDMORE AVE), AND AT SOME TIME ENGULFED THE MSA OF 173 S. ARDMORE AVE. THE METER EVENTUALLY MELTED CAUSING A RELEASE OF GAS WHILE FUELING THE FIRE. ORIGINAL CAUSE OF THE FIRE IS STILL UNDER INVESTIGATION. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO A GAS RELEASE AND THE ASSOCIATED DAMAGE EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2025-03-31 10:13 | NO | YES | NO | 20160052 | 16381 | 2016-06-02 15:25 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2016-05-03 03:28 |  |  | 2016 | 342 EAST MAIN ST. | ASHLAND | ASHLAND | OH | 44805 | 40.8684 | -82.308 | [9 empty] | 2016-05-03 09:00 | 1146803 |  |  |  | 0.02 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 1 | 2016-05-03 07:56 |  |  |  | 2016-05-03 08:15 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 27 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 0.099 |  |  | UNKNOWN | MECHANICAL PUNCTURE | 0.2 | 0.2 | [7 empty] | CLASS 3 LOCATION | 400000 | 480521.4434158324 | 0 | 0 | 1500 | 1801.9554128093715 | 0 | 0 |  |  | 0 | 0 |  | 0 | 401500 | 199763.8862648782815 | 482323.3988286417715 | 0 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | ROB SMITH | OPERATIONS COMPLIANCE MANAGER | rrsmith@nisource.com | 6148182110 | 6148182151 |  |  |  | ROB SMITH | OPERATIONS COMPLIANCE MANAGER | 6148182110 | rrsmith@nisource.com | ON MAY 3, 2016, AN EXPLOSION OCCURRED IN THE EARLY-MORNING HOURS AT THE GASOLINE STATION AT THE ABOVE-REFERENCED ADDRESS. THE GAS STATION HAS BEEN UNDER REMEDIATION FOR A LARGE PETROLEUM RELEASE FROM UNDERGROUND STORAGE TANKS FOR NEARLY TWO YEARS. ACCORDING TO INTERVIEWS CONDUCTED BY THE ASHLAND FIRE DEPARTMENT OF EMPLOYEES AT THE PROPERTY, AS WELL AS PATRONS OF THE STORE PRIOR TO THE INCIDENT, A CHEMICAL ODOR, NOT NATURAL GAS, WAS SMELLED ON SITE. A COLUMBIA SERVICE TECHNICIAN WAS ON SITE TO SET A GAS METER AT THE GAS STATION THE DAY PRIOR TO THE EXPLOSION, MAY 2, 2016. COLUMBIA'S TECHNICIAN FOUND THE SERVICE LINE CURB VALVE IN THE "OFF" POSITION WHEN HE ARRIVED ON SITE. THE TECHNICIAN TURNED THE CURB VALVE TO THE "ON" POSITION BRIEFLY TO DETERMINE IF THE GAS SERVICE WAS ACTIVE, AND PROMPTLY TURNED THE CURB VALVE BACK TO THE "OFF" POSITION WHEN NO GAS WAS FOUND AT THE METER SETTING. THE CURB VALVE'S "OFF" POSITION WAS VERIFIED WHEN EXCAVATED FOLLOWING THE INCIDENT. FOLLOWING THE INCIDENT, ON MAY 3, 2016, THE CURB VALVE AND THE CUSTOMER-OWNED SERVICE LINE WERE EXPOSED AND IT WAS DISCOVERED THAT THE SERVICE LINE DOWNSTREAM OF THE CURB VALVE HAD BEEN SEVERED PRIOR TO THE MAY 2, 2016 SITE VISIT BY COLUMBIA. COLUMBIA TESTED THE CURB VALVE AND THE SERVICE LINE FROM THE MAIN UP TO THE CURB VALVE AND FOUND NO GAS LEAKAGE. ON WEDNESDAY, JUNE 8, 2016, COLUMBIA, ALONG WITH OTHER INTERESTED PARTIES, TOOK SAMPLES FROM SIX (6) LOCATIONS UNDER THE CONCRETE PAD OF THE STRUCTURE. THE RESULTS OF THE LABORATORY ANALYSIS INDICATED THAT VERY LOW LEVELS OF DEGRADED PETROLEUM PRODUCTS AND VERY LOW LEVELS OF NATURAL GAS WERE PRESENT AT THE TIME THE SAMPLES WERE TAKEN. COLUMBIA HAS DETERMINED THAT THE CAUSE OF THIS INCIDENT CANNOT BE ASCERTAINED TO ANY REASONABLE DEGREE OF CERTAINTY. PLEASE CONSIDER THIS REPORT A FINAL REPORT.
2025-03-31 10:13 | NO | YES | YES | 20160053 | 16467 | 2016-06-10 14:13 | SUPPLEMENTAL FINAL | 32513 | AMEREN ILLINOIS COMPANY | 10 EXECUTIVE DR. | COLLINSVILLE | IL | 62234 | 2016-05-11 10:42 |  |  | 2016 | 430 N WEST STREET | CARLINVILLE | MACOUPIN | IL | 62626 | 39.2847 | -89.8832 | [9 empty] | 2016-05-11 11:37 | 1147479 |  | NATURAL GAS |  | 5.4 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 14 | 2016-05-11 10:42 |  |  |  | 2016-05-11 09:22 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1982 | [5 empty] | 0.625 | ALDYL A | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 2306 | MECHANICAL PUNCTURE | 0.5 | 2 | [7 empty] | CLASS 3 LOCATION | 125000 | 150162.951067447625 | 3689 | 4431.609011902514309 | 155668 | 187004.530134139495108 | 0 | 0 |  |  | 21 | 24.16981132075471698113207547169811320755 |  | 0 | 284378 | 141502.4566390641535328490566037735849057 | 341623.2600248103891339811320754716981132 | 1 | 0 | 32 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 4 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 1111116 | ILLINOIS JULIE ONE CALL CENTER |  | CONTRACT LOCATOR | YES | YES | 36 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | JOHN BOZARTH | MANAGER GAS COMPLIANCE AND TRAINING | jbozarth@ameren.com | 217-625-6854 | 314-613-2640 |  |  |  | JOHN BOZARTH | MANAGER GAS COMPLIANCE AND TRAINING | 217-625-6854 | jbozarth@ameren.com | A 1/2" PLASTIC GAS SERVICE TO 419 N WEST STREET WAS CUT BY A THIRD PARTY CONTRACTOR, RESULTING IN GAS BLOWING TO ATMOSPHERE. THE AMEREN ILLINOIS FIRST RESPONDER STOPPED THE BLOWING GAS USING AN EXPANDABLE PLUG INTO THE CUT 1/2" SERVICE. APPROXIMATELY 80 MINUTES LATER, AFTER THE CUT GAS SERVICE HAD BEEN PLUGGED AND AN AMEREN ILLINOIS CREW WAS ON SITE TO MAKE REPAIRS, AN EXPLOSION OCCURRED AT THE STRUCTURE LOCATED AT 430 N WEST STREET. THE POST INVESTIGATION OF THE AREA REQUIRED A TEMPORARY OUTAGE TO 33 GAS CUSTOMERS. REVISION AS OF (12/20/2016): THE LIKELY CAUSE OF THE INCIDENT, GIVEN THE RELATIVELY SHORT TIMEFRAME BETWEEN THE DAMAGED GAS SERVICE AT 419 N WEST ST AND THE INCIDENT OCCURRING AT 430 N WEST ST, IS ATTRIBUTED TO THE THIRD PARTY DAMAGE OF THE GAS SERVICE. THE CONTRACTOR INSTALLING A WATER MAIN IN THE STREET HAD A VALID DIG TICKET, BUT THE SERVICE WAS INACCURATELY MARKED INACCURATELY MARKED IN THE FIELD BY THE LOCATOR. ADDITIONAL POST-INCIDENT INVESTIGATION AT THE 430 N WEST STREET LOCATION DETERMINED THAT THE SEWER TRAP FOR THE SEWER LATERAL INTO THE STRUCTURE WAS DRY. AMEREN ILLINOIS, HOWEVER, WAS NOT ABLE TO ESTABLISH THAT NATURAL GAS FROM THE HIT SERVICE LOCATION MIGRATED INTO THE HOME AT 430 N WEST ST. PART A, LINE 10 - LOST GAS ESTIMATE WAS UPDATED TO 5.4 MCF, WITH AN ASSOCIATED LOST GAS COST OF $21 UPDATED IN PART D. PART A, LINE 12 - THERE WERE TWO INJURIES REPORTED, HOWEVER AMEREN ILLINOIS COULD ONLY CONFIRM THAT ONE REQUIRED INPATIENT HOSPITALIZATION. PART A, LINE 13 - THE GAS MAIN WAS SHUT DOWN AFTER THE INCIDENT OCCURRED. THE AMEREN ILLINOIS FIRST RESPONDER HAD REMOVED THE PLUG STOPPER AFTER THE INCIDENT, AND THEN THE ADJACENT 1-1/4" PLASTIC GAS MAIN WAS EXCAVATED AND SQUEEZED OFF INTERRUPTING SERVICE TO THE 400 BLOCK OF N WEST ST. THE GAS MAIN SERVING THE 200 AND 300 BLOCK OF N WEST ST WAS ALSO TAKEN OUT OF SERVICE AS A PRECAUTIONARY MEASURE. THE GAS MAINS WERE REENERGIZED UPON COMPLETION OF AIR PRESSURE TESTING OF THE GAS FACILITIES IN THE 200 - 400 BLOCK OF N WEST ST. PART G - THE PRIMARY CAUSE OF THE INCIDENT WAS UPDATED TO G3, THIRD PARTY DAMAGE, WITH ADDITIONAL SUPPORTING INFORMATION PROVIDED. REVISION AS OF 12/31/2016 PART A, LINE 13B - CLARIFYING THE TIME RESTORATION TO GAS MAINS IS CORRECTLY STATED AS 5/13/2016 00:00, WHICH WAS RIGHT AT MIDNIGHT. PART A, LINE 14 - REVISED TO "YES" PART C, LINE 5 - REVISED TO "MECHANICAL", WITH DIMENSIONS INTENDED TO SHOW THE CIRCUMFERENCE OF THE CUT 1/2" SERVICE..
2025-03-31 10:13 | NO | NO | NO | 20160054 | 30431 | 2016-06-10 15:12 | SUPPLEMENTAL FINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2016-05-10 12:04 |  |  | 2016 | 7191 BETH-BATH PIKE | BATH | LEHIGH | PA | 18014 | 40.6986 | -75.3927 | [9 empty] | 2016-05-10 17:20 | 1147400 |  | NATURAL GAS |  | 10000 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-05-10 12:04 |  |  |  | 2016-05-10 12:44 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | OTHER | WATER CROSSING |  |  | YES | [6 empty] | YES | UNCASED | MONOCACY CREEK | 2 |  | PRIVATELY OWNED |  | MAIN |  | 1930 | [5 empty] | 4.026 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | 0 | 0 | 24000 | 28831.286604949944 | 28000 | 33636.501039108268 | 0 | 0 |  |  | 17000 | 19566.0377358490566037735849056603773585 |  | 0 | 69000 | 43972.0146070969162587601078167115902965 | 82033.8253799072686037735849056603773585 | 0 | 0 | 0 |  |  |  |  | 59 | 59 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS THE RESULT OF THIRD PARTY EXCAVATOR DAMAGE AND WAS NOT RELATED TO THE CONTROLLER OR CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | STATE HIGHWAY | [12 empty] | STATE | BACKHOE/TRACKHOE | ROAD WORK | NO |  |  |  | DATA NOT COLLECTED | DATA NOT COLLECTED |  |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JOHN TOUMEH | COMPLIANCE ENGINEER | jtoumeh@ugi.com | 717-675-4606 |  |  |  |  | FRANK BENNETT | DIRECTOR ENGINEERING AND TECHNICAL SERVICES | 610-796-3567 | fbennet@ugi.com | AT APPROXIMATELY 12:04 PM ON TUESDAY MAY 10, 2016 A STATE DOT MAINTENANCE CREW STRUCK A DISTRIBUTION MAIN LEADING TO A LEAK ON A MEDIUM PRESSURE MAIN. THE STATE HIGHWAY DEPARTMENT WAS CLEARING A LOG JAM ADJACENT TO A BRIDGE. UGI'S MAIN WAS LOCATED IN THE STREAM BED ABOUT 6 FEET UPSTREAM OF THE BRIDGE. AS THE HIGHWAY DEPARTMENT WAS REMOVING SUBMERGED DEBRIS, IT STRUCK THE 4" MAIN CAUSING A NEARBY COUPLING TO FAIL. NO ONE-CALL WAS MADE, THE STATE DOT CREW FAILED TO VERIFY THE PRECISE LOCATION OF THE GAS MAIN BEFORE THE DAMAGE OCCURRED. THE ROAD WHERE THE DAMAGE OCCURRED WAS SHUTDOWN FOR APPROXIMATELY 28 HOURS AND A DETOUR WAS SET UP. THE DAMAGED SECTION OF MAIN WAS ISOLATED FROM THE SYSTEM. A TEMPORARY REGULATOR STATION WAS INSTALLED DOWNSTREAM OF THE DAMAGED MAIN IN ORDER TO SUPPLY GAS TO 770 CUSTOMERS DOWNSTREAM OF THE DAMAGE UNTIL THE DAMAGED LINE CAN BE REPLACED. 6/1/2018 SUPPLEMENTAL REPORT SUBMITTED TO INDICATE "FINAL" REPORT.
2025-03-31 10:13 | NO | YES | NO | 20160055 | 16522 | 2016-06-17 16:31 | SUPPLEMENTAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2016-05-19 09:24 |  |  | 2016 | 9955 LINDA LANE | DES PLAINES | COOK | IL | 60016-1301 | 42.0584 | -87.8661 | [9 empty] | 2016-05-19 10:41 | 1148179 |  | NATURAL GAS |  | 22.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 8 | 2016-05-19 09:18 |  |  |  | 2016-05-19 09:35 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1987 | [5 empty] | 0.625 | UNKNOWN | SAMUEL MOORE AND COMP - DEKORON DIVISION | OTHER | TRIPL-DEK (PLASTIC ALUMINUM COMPOSITE) | [9 empty] | MECHANICAL PUNCTURE | 0.4 | 0.4 | [7 empty] | CLASS 3 LOCATION | 1130000 | 1357473.07764972653 | 500 | 600.6518042697905 | 4500 | 5405.8662384281145 | 0 | 0 |  |  | 58 | 66.75471698113207547169811320754716981132 |  | 0 | 1135058 | 564774.1079633736773180592991913746630728 | 1363546.35040940556707547169811320754717 | 0 | 0 | 6 |  |  |  |  | 58 | 59 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | GROUND ROD INSERTED INTO THE SOIL BY HAND WHILE ATTEMPTING TO LOCATE TELECOMMUNICATIONS FACILITIES. | [154 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | lquezad@aglresources.com | (630) 388-2316 | (630) 388-3992 |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | (630) 388-2316 | lquezad@aglresources.com | WHILE LOCATING UNDERGROUND TELECOMMUNICATIONS UTILITY LINES FOR ANOTHER COMPANY, A THIRD-PARTY CONTRACTOR INSERTED A 3/8" GROUNDING ROD INTO THE SOIL AND PUNCTURED A 5/8" SERVICE LINE. AT 9:18A.M., THE LOCATING COMPANY NOTIFIED NICOR GAS OF THE DAMAGE TO THE SERVICE LINE. A COMPANY EMERGENCY RESPONDER WAS IMMEDIATELY DISPATCHED TO THE SCENE. WHILE THE EMERGENCY RESPONDER WAS EN ROUTE, THE FIRE DEPARTMENT NOTIFIED NICOR GAS OF AN EXPLOSION AT THE SAME APARTMENT COMPLEX WHERE THE LOCATING COMPANY CALLED TO REPORT DAMAGE TO THE SERVICE LINE. NATURAL GAS FROM THE DAMAGED SERVICE LINE MIGRATED INTO THE STRUCTURE WHICH LED TO THE SUBSEQUENT EXPLOSION.
2025-03-31 10:13 | NO | YES | NO | 20160056 | 16328 | 2016-06-27 20:45 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2016-05-25 15:04 |  |  | 2016 | 8915 GERBER ROAD | SACRAMENTO | SACRAMENTO | CA | 95829 | 38.4818 | -121.3688 | [9 empty] | 2016-05-25 19:20 | 1148802 |  | NATURAL GAS |  | 330.16 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-05-25 15:04 |  |  |  | 2016-05-25 15:22 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2008 | [5 empty] | 8 | PE2406 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 45663 | 54855.126676742887203 | 514778 | 618404.668996788428018 | 0 | 0 |  |  | 1419 | 1633.188679245283018867924528301886792453 |  | 0 | 561860 | 280354.8105459432435976576819407008086253 | 674892.9843527765982398679245283018867925 | 1 | 0 | 1307 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 173288 | 811 |  | UTILITY OWNER | YES | YES | 24 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-328-6107 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON MAY 25, 2016 AT 1504 HOURS, PGE WAS NOTIFIED OF A THIRD-PARTY DIG-IN (CROSSBORE) AT 8915 GERBER ROAD IN SACRAMENTO. IRISH CONSTRUCTION STRUCK AN 8' PLASTIC MAIN DURING HORIZONTAL BORING ACTIVITIES THAT RESULTED IN AN UNINTENTIONAL RELEASE OF GAS. THE CONTRACTOR HAD A VALID USA (W000173288). PG&E FACILITIES WERE LOCATED & MARKED; HOWEVER, THE OFFSET WITHIN THE SIDEWALK WAS NOT MARKED. PG&E'S GAS SERVICE REPRESENTATIVE (GSR) WAS ON-SITE AT 1522 HOURS. PG&E CREWS ARRIVED AT 1535 HOURS AND SHUT IN THE FLOW OF GAS AT 1639 HOURS BY SQUEEZING THE MAIN. AT 1900 HOURS, IT WAS DETERMINED THAT A TOTAL OF 1308 CUSTOMER'S GAS SERVICE WOULD BE IMPACTED. AN OPERATING EMERGENCY CENTER WAS OPENED TO ADDRESS THE INCIDENT. REPAIRS TO THE MAIN WERE COMPLETED BY 2332 HOURS. GSRS COMPLETED MAJORITY OF THE SERVICE RESTORATION BY 5/26/16 AT 1700 HOURS. THE REMAINING CUSTOMERS WERE RESTORED AT THE REQUEST OF THE CUSTOMER. THERE WERE NO INJURIES, FATALITIES, OR IGNITION ASSOCIATED WITH THIS INCIDENT. THIS WAS REPORTED TO THE CPUC AND DOT DUE TO AN UNINTENTIONAL RELEASE OF GAS THAT RESULTED IN A SIGNIFICANT CUSTOMER OUTAGE WITH AN ESTIMATED DAMAGE COST OF GREATER THAN $50,000.
2025-03-31 10:13 | NO | YES | YES | 20160058 | 16334 | 2016-07-02 07:41 | ORIGINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2016-06-03 08:44 |  |  | 2016 | JOSEPH E LOWERY BLVD | ATLANTA | FULTON | GA | 30318 | 33.7622 | -84.417 | [9 empty] | 2016-06-03 19:59 | 1149649 |  | NATURAL GAS |  | 608.42 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | NO |  |  |  |  | NO | 0 | 2016-06-03 08:44 |  |  |  | 2016-06-03 09:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 4 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2001 | [5 empty] | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1.9 | 1.9 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 100 | 120.1303608539581 | 10262 | 12327.777630833180222 | 0 | 0 |  |  | 513 | 590.433962264150943396226415094339622642 |  | 0 | 10875 | 5701.736144416954663455525606469002695418 | 13038.3419539512892653962264150943396226 | 0 | 0 | 62 |  |  |  |  | 45 | 45 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 5256300884000 |  |  | CONTRACT LOCATOR | YES | YES | 7 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@aglresources.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@aglresources.com | A 2-INCH PLASTIC MAIN WITH ONE-WAY FEED WAS RUPTURED BY A CONTRACT CREW WHILE INSTALLING SEWER. ONE EMPLOYEE FOR THE CONTRACT CREW WAS IN THE EXCAVATION WHEN THE PLASTIC MAIN WAS STRUCK BY ANOTHER EMPLOYEE OPERATING A BACKHOE WHERE THE EMPLOYEE IN THE EXCAVATION WAS TAKEN TO THE HOSPITAL AS A PRECAUTION FOR CHEST PAINS. THE COMPANY WAS ABLE TO LATER DETERMINE THAT THE EMPLOYEE WAS BEING HELD OVERNIGHT FOR OBSERVATION. AT THIS POINT IT WAS DETERMINED THAT THE INCIDENT RESULTED IN AN INPATIENT HOSPITALIZATION MEETING THE THRESHOLD FOR REPORTING. NOTIFICATION TO THE ONE-CALL CENTER WAS MADE WHERE THE MAIN WAS ACCURATELY LOCATED AND MARKED BEFORE DAMAGE OCCURRED.
2025-03-31 10:13 | NO | YES | NO | 20160060 | 16341 | 2016-07-12 16:54 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY, SUITE 1800 | DALLAS | TX | 75240 | 2016-06-13 11:23 |  |  | 2016 | SHELL ROAD & SEQUOIA SPUR | GEORGETOWN | WILLIAMSON | TX | 78628 | 30.6855 | -97.7161 | [9 empty] | 2016-06-13 11:55 | 1150511 |  | NATURAL GAS |  | 1578 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-06-13 11:23 |  |  |  | 2016-06-13 11:30 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 72 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1997 | [5 empty] | 8 | PE2406 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 24 | 8 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 500 | 600.6518042697905 | 167000 | 200617.702626110027 | 0 | 0 |  |  | 500 | 575.471698113207547169811320754716981132 |  | 0 | 168000 | 83870.9526084138564487870619946091644205 | 201793.8261284930250471698113207547169811 | 2 | 0 | 1424 |  |  |  |  | 19 | 20 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | DEVELOPER | TRENCHER | SITE DEVELOPMENT | YES | 1665287819 | TEXAS811 |  | CONTRACT LOCATOR | YES | YES | 24 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | MIKE LABAY | OPERATIONS SUPERVISOR | michael.labay@atmosenergy.com | 512-310-3820 | 512-310-3880 |  |  |  | MARLO SUTTON | COMPLIANCE DIRECTOR | 214-206-2033 | marlo.sutton@atmosenergy.com | A THIRD-PARTY EXCAVATOR WAS WORKING IN AN AREA OF CLEARLY-MARKED GAS FACILITIES. WHILE PERFORMING TRENCHING WORK, THE EXCAVATOR STRUCK AN 8" PE MAIN OWNED BY ATMOS ENERGY OPERATING AT 19 PSIG. THE GAS ULTIMATELY IGNITED REQUIRING ATMOS ENERGY TO ISOLATE THE DAMAGED SECTION. THIS RESULTED IN THE INTERRUPTION OF GAS SERVICE TO 1,424 CUSTOMERS.
2025-03-31 10:13 | NO | YES | YES | 20160061 | 16452 | 2016-07-13 10:28 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2016-06-13 22:09 |  |  | 2016 | 13400 DENVER DRIVE | HARTLAND | LIVINGSTON COUNTY | MI | 48353 | 42.6281 | -83.69 | [9 empty] | 2016-06-14 01:10 | 1150568 |  | NATURAL GAS |  | 154 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2016-06-13 22:31 |  |  |  | 2016-06-13 23:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1998 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | OTHER | [8 empty] | METER AND RISER DAMAGE DUE TO VEHICLE IMPACT | CLASS 3 LOCATION | 15000 | 18019.554128093715 | 3971 | 4770.376629510676151 | 330 | 396.43019081806173 | 0 | 0 |  |  | 1148 | 1321.283018867924528301886792452830188679 |  | 0 | 20449 | 10825.3594655098114474150943396226415094 | 24507.6439672903774093018867924528301887 | 0 | 0 | 1 |  |  |  |  | 46 | 46 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS CAUSED BY EXTERNAL FORCE, NOT DUE TO ANY OPERATOR ACTIONS | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | KARLI MAYER | GENERAL ENGINEER I | karli.mayer@cmsenergy.com | 9892954218 |  |  |  |  | AMANDA WARD | GAS REGULATORY SERVICES LEAD | 248-431-0888 | amanda.ward@cmsenergy.com | ON JUNE 13, 2016, AT APPROXIMATELY 22:09 HOURS, A VEHICLE EXITED THE ROAD AND STRUCK A PEDESTAL CONTAINING BOTH GAS AND ELECTRIC METERS, RESULTING IN DAMAGE TO BOTH METERS AND THE 5/8" SERVICE RISER. THE ESCAPING GAS IGNITED, CAUSING DAMAGE TO THE HOME AT 13400 DENVER DR, HARTLAND TWP, MICHIGAN (LIVINGSTON COUNTY). THE MOTORIST WAS TAKEN TO THE HOSPITAL BY AMBULANCE, IT IS UNKNOWN IF INJURIES REQUIRED AN OVERNIGHT STAY OR IF INJURIES WERE CAUSED BY IMPACT OR IGNITION. CONSUMERS ENERGY PERSONNEL ARRIVED ON SITE AT 23:20, AND CALLED FOR A FULL CREW AT 23:27. THE CREW ARRIVED AT 00:02, AND SQUEEZED OFF THE MAIN AT 02:08, RESTRICTING GAS FEED TO THE HOME. SURROUNDING HOMES WERE BAR TESTED AT ALL FOUR CORNERS, AND NO GAS WAS PRESENT. THE SERVICE RISER WAS CUT AND CAPPED THAT NIGHT, AND REPLACED ON 7/6/2016.
2025-03-31 10:13 | NO | NO | NO | 20160062 | 16454 | 2016-07-30 19:25 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2016-06-30 07:39 |  |  | 2016 | NORTHEAST CORNER OF E 4TH ST AND N ALMONT AVE | IMLAY CITY | LAPEER | MI | 48444 | 43.0257 | -83.0774 | [9 empty] | 2016-06-30 16:00 | 1152125 |  | NATURAL GAS |  | 736 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 34 | 2016-06-30 07:39 |  |  |  | 2016-06-30 08:38 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2014 | [5 empty] | 4 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 3 | 5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 4265 | 5123.559890421312965 | 56 | 67.273002078216536 | 0 | 0 |  |  | 5490 | 6318.67924528301886792452830188679245283 |  | 0 | 9811 | 7995.035551964835298681940700808625336927 | 11509.5121377825483689245283018867924528 | 4 | 0 | 6 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT OCCURRED AS A RESULT OF A THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 61671615 | MISS DIG - TICKET NUMBER A61671615 |  | CONTRACT LOCATOR | UNKNOWN/OTHER | YES | 3 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | KARLI MCNEILL | G ENGINEER I | karli.mcneill@cmsenergy.com | 734-524-6350 |  |  |  |  | AMANDA WARD | GAS REGULATORY SERVICES LEAD | 517-545-8746 | amanda.ward@cmsenergy | ON JUNE 30, 2016 AT APPROXIMATELY 07:39 A FOUR INCH PLASTIC NATURAL GAS PIPELINE WAS STRUCK BY A CONTRACTOR AT THE NORTHEAST CORNER OF N. ALMONT AVENUE AND E 4TH ST, IMLAY CITY, MICHIGAN (LAPEER COUNTY) RESULTING IN BLOWING GAS. POLICE AND FIRE PERSONNEL BLOCKED TRAFFIC AND EVACUATED APPROXIMATELY 10 RESIDENCES AND 7 COMMERCIAL BUSINESSES AS A SAFETY PRECAUTION. CONSUMERS ENERGY PERSONNEL PERFORMED A SQUEEZE-OFF PROCEDURE STOPPING THE FLOW OF GAS AT APPROXIMATELY 12:45. NATURAL GAS SERVICE WAS INTERRUPTED TO TEN CUSTOMERS WHILE THE DAMAGE SECTION WAS REPAIRED. SERVICE WAS RESTORED TO THE IMPACTED CUSTOMERS AT 21:00. ORIGINAL PRELIMINARY GAS LOSS CALCULATION INDICATED 5,000 MCF WAS RELEASED. AFTER FURTHER INVESTIGATION, ACTUAL GAS LOSS IS 736 MCF AND IS UPDATED ACCORDINGLY IN THIS SUPPLEMENTAL REPORT, ALONG WITH COST OF GAS RELEASED. THE ORIGINAL STAKING TICKET WAS COMPLETED ON JUNE 22, 2016. THERE IS PHOTOGRAPHIC EVIDENCE THAT STAKING WAS COMPLETED CORRECTLY AT THAT TIME. AFTER AN INVESTIGATION DONE BY CONSUMERS ENERGY DAMAGE PREVENTION, IT WAS FOUND THAT THE MISS DIG RESTAKING REQUEST WAS SUBMITTED ON JUNE 29TH AND WAS DUE ON JUNE 30TH BY 12:58 PM. THE CONTRACTOR DAMAGED THE FACILITY AROUND 7:40 AM ON JUNE 30TH, BEFORE RESTAKING WAS DUE OR COMPLETED.
2025-03-31 10:13 | YES | NO | NO | 20160063 | 31633 | 2016-08-07 21:25 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2016-07-08 08:08 |  |  | 2016 | 4649 FARMDALE AVE | LOS ANGELES | LOS ANGELES | CA | 91602 | 34.1553 | -118.3814 | [9 empty] | 2016-07-08 09:33 | 1152764 |  | NATURAL GAS |  | 24 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-07-08 07:08 |  |  |  | 2016-07-08 07:08 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1988 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | MSA MELTED BY THE FIRE. CAUSE IS UNDER INVESTIGATION AND NOT DETERMINED AT THIS TIME. | CLASS 3 LOCATION | 0 | 0 | 1646 | 1977.345739656150326 | 200 | 240.2607217079162 | 0 | 0 |  |  | 144 | 165.735849056603773584905660377358490566 |  | 0 | 1990 | 1071.7814511664957832506738544474393531 | 2383.342310420670299584905660377358490566 | 0 | 0 | 1 |  |  |  |  | 35 | 35 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 626-893-4536 | kle2@semprautilities.com | ON JULY 8, 2016, LOS ANGELES FIRE DEPARTMENT REPORTED A STRUCTURE FIRE AT 4649 FARMDALE AVE IN LOS ANGELES. CREW RESPONDED AND CONTROLLED THE GAS. ONE FATALITY WAS REPORTED FROM THIS INCIDENT. INVESTIGATION INTO THE CAUSE OF DEATH AND THE CAUSE OF FIRE ARE ONGOING. ADDITIONALLY, IT HAS NOT BEEN DETERMINED WHETHER THE INCIDENT RESULTED FROM THE RELEASE OF GAS OR THAT THE GAS WAS CAUSED BY THE INCIDENT. THIS INCIDENT WAS REPORTED TO CPUC AND DOT DUE TO THE ASSOCIATED DAMAGE EXCEEDING $50,000. A SUPPLEMENTAL REPORT WILL BE SUBMITTED ONCE THE INVESTIGATION HAS BEEN COMPLETED. UPDATED INFORMATION 6-16-17: INVESTIGATION SHOWED THAT GAS WAS THE NOT THE PRIMARY CAUSE OF THE STRUCTURE FIRE. UPDATED INFORMATION 9-19-17: REMOVED FATALITY AND PUBLIC'S PROPERTY DAMAGE SINCE GAS WAS NOT THE PRIMARY CAUSE OF THE STRUCTURE FIRE. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2025-03-31 10:13 | NO | YES | YES | 20160064 | 16482 | 2016-08-11 08:50 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2016-07-02 03:03 |  |  | 2016 | 3900 GREENFIELD | MELVINDALE | WAYNE COUNTY | MI | 48122 | 42.2931 | -83.1753 | [9 empty] | 2016-07-02 03:31 | 1152248 |  | NATURAL GAS |  | 24010 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 1000 | 2016-07-02 03:03 |  |  |  | 2016-07-02 03:13 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | PIPE 3" NIPPLE ON A BLOW-OFF & 30-INCH PIPELINE | 2010 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.7 | 12 | [7 empty] | CLASS 3 LOCATION | 706000 | 848120.347628944186 | 4723666 | 5674557.011335728423946 | 0 | 0 | 0 | 0 |  |  | 82595 | 95062.1698113207547169811320754716981132 |  | 0 | 5512261 | 2789435.41095878741983613477088948787062 | 6617739.52877599336466298113207547169811 | 2 | 0 | 1 |  |  |  |  | 540 | 540 | 540 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VEHICLE CRASHED INTO AN ABOVE GROUND PIPING CAUSING THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | FRENAE F. SMITH | MANAGER | smithff@dteenergy.com | 313-389-7762 | 313-389-7757 |  |  |  | FRENAE F. SMITH | MANAGER | 313-389-7762 | smithff@dteeenergy.com | ON JULY 2, 2016 AT 02:59 DTE GAS WAS NOTIFIED OF A FIRE FROM THE MELVINDALE FIRE DEPARTMENT AT 3900 GREENFIELD IN MELVINDALE, MI. THE DTE GAS SERVICE TECHNICIAN TEAM ARRIVED ONSITE AT 03:10 AND IT WAS CONFIRMED THAT A VEHICLE HAD HIT ABOVE GROUND PIPING OF A 3" NIPPLE ON A BLOW-OFF WHICH LEAD TO A RUPTURE OF A 30-INCH PIPELINE OPERATING AT 540 PSIG AT THE DTE GAS RIVER ROUGE FACILITY. DTE GAS COORDINATED WITH FIRST RESPONDERS TO CONTAIN THE INCIDENT. IT WAS DETERMINED THAT THE VEHICLE CROSSED THROUGH THE STATION YARD AND STRUCK THE 3" NIPPLE ON A BLOW-OFF, THE LEAKING GAS DID IGNITE WHICH CAUSE THE 30-INCH PIPELINE RUPTURE. THERE WAS ONE INJURY TO THE DRIVER. THE DRIVER APPEARS TO HAVE BEEN INTOXICATED PRIOR TO THE VEHICLE STRIKING THE 3" NIPPLE ON A BLOW-OFF. DTE GAS CONTROL WAS ABLE TO CLOSE THE REMOTE VALVE AND THE LEAKING GAS WAS STOPPED. AS A RESULT OF THE INCIDENT, OAKWOOD HOSPITAL, DEARBORN INDUSTRIAL GENERATION AND MARATHON DETROIT REFINERY WERE WITHOUT HIGH PRESSURE GAS. OAKWOOD HOSPITAL WAS RETURN TO SERVICE ON AFTERNOON OF JULY 2, 2016. DEARBORN INDUSTRIAL GENERATION AND MARATHON DETROIT REFINERY WERE RETURNED TO SERVICE AT 12 NOON ON JULY 12, 2016. REMEDIATION OF THE RIVER ROUGE GAS FACILITY WAS COMPLETED IN SEPTEMBER OF 2016 .
2025-03-31 10:13 | NO | YES | YES | 20160066 | 16446 | 2016-08-11 10:11 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2016-06-10 17:01 |  |  | 2016 | 6800 GRATIOT | DETROIT | WAYNE COUNTY | MI | 48207 | 42.3696 | -83.0205 | [9 empty] | 2016-06-10 20:01 | 1150277 |  | NATURAL GAS |  | 160 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 1 | 2016-06-10 17:01 |  |  |  | 2016-06-10 17:36 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 78000 | 93701.681466087318 | 1648 | 1979.748346873229488 | 0 | 0 | 0 | 0 |  |  | 6 | 6.90566037735849056603773584905660377358 |  | 0 | 79654 | 39634.766753424552875385444743935309973 | 95688.3354733379059785660377358490566038 | 1 | 0 | 0 |  |  |  |  | 10 | 10 | 10 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | FRENAE F. SMITH | MANAGER | smithff@dteenergy.com | 313-389-7762 | 313-389-7755 |  |  |  | FRENAE F. SMITH | MANAGER | 313-389-7762 | smithff@dteeenergy.com | ON JUNE 10, 2016 AT 17:01 DTE GAS WAS NOTIFIED FROM 911 THAT A VEHICLE HIT A COMMERCIAL BUILDING AT 6800 GRATIOT IN DETROIT, MI. THE DTE GAS SERVICE TECHNICIAN ARRIVED ONSITE AT 17:36 AND IT WAS CONFIRMED THAT A VEHICLE HAD HIT THE VACANT COMMERCIAL BUILDING DAMAGING THE OUTSIDE GAS METER. THIS RESULTED IN A RELEASE OF NATURAL GAS. DTE GAS COORDINATED WITH FIRST RESPONDERS TO CONTAIN THE INCIDENT. LEAKING GAS DID IGNITE, AND THERE WAS ONE INJURY TO THE DRIVER. THE SERVICE LINE TO THIS BUILDING WAS DISCONNECTED FROM THE MAIN AND IS NOT IN SERVICE.
2025-03-31 10:13 | NO | YES | YES | 20160068 | 16492 | 2016-08-11 11:53 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2016-07-06 18:11 |  |  | 2016 | 101 W. MARGARET | DETROIT | WAYNE COUNTY | MI | 48203 | 42.4259 | -83.1041 | [9 empty] | 2016-07-06 19:12 | 1152596 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 1 | 2016-07-06 18:11 |  |  |  | 2016-07-06 18:32 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | UNKNOWN | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | THE CAUSE OF THIS INCIDENT IS STILL UNKNOWN. | CLASS 3 LOCATION | 57127 | 68626.871245040643787 | 4570 | 5489.95749102588517 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 61697 | 30696.967598715305937 | 74116.828736066528957 | 0 | 0 | 2 |  |  |  |  | 2 | 2 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | FRENAE F. SMITH | MANAGER | smithff@dteenergy.com | 313-389-7762 | 313-389-7755 |  |  |  | FRENAE F. SMITH | MANAGER | 313-389-7762 | smithff@dteenergy.com | ON JULY 6, 2016 AT 18:11 DTE GAS WAS NOTIFIED FROM 911 OF AN EXPLOSION AT 101 W. MARGARET IN DETROIT, MI. THE DTE GAS SERVICE TECHNICIAN ARRIVED ONSITE AT 18:32. WHEN THE SERVICES TECHNICIAN ARRIVED, HE REPORTED THAT THE FIRE HAD SPREAD AN ADJACENT HOMES. DTE GAS COORDINATED WITH FIRST RESPONDERS TO CONTAIN THE INCIDENT BY DISCONNECTING THE GAS SERVICES AT THE GAS MAIN. A NATURAL GAS LEAK INVESTIGATION WAS CONDUCTED AND NO NATURAL GAS LEAKS WERE DETECTED. THERE WAS ONE INJURY TO THE OCCUPANT AT 101 W. MARGARET. DTE GAS WAS UNABLE TO RETRIEVE THE GAS METER ASSEMBLY BECAUSE THE DEMOLITION CONTRACTOR PERFORMED THE DEMOLITION WITHOUT CONTACTING DTE GAS AS REQUESTED. DTE GAS HAS COMPLETED ITS INVESTIGATION AND HAVE DETERMINED THE CAUSE AS "UNKNOWN". ACCORDING TO DETROIT FIRE DEPARTMENT ARSON UNIT, THE CAUSE OF THE EXPLOSION IS UNKNOWN. SEVERAL ATTEMPTS BY DETROIT FIRE DEPARTMENT ARSON UNIT WERE MADE TO TALK TO THE CUSTOMER WHO WAS HOME AT THE TIME OF THE EXPLOSION, HOWEVER, HE WAS UNRESPONSIVE WHILE IN THE HOSPITAL. I AM TOLD THE CUSTOMER WAS RELEASED AFTER SEVERAL WEEKS IN THE HOSPITAL AND INVESTIGATORS HAVE NOT BEEN ABLE TO LOCATE HIM TO CONDUCT THEIR FOLLOW UP.
2025-03-31 10:13 | NO | YES | NO | 20160070 | 16359 | 2016-08-15 20:16 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2016-07-14 12:32 |  |  | 2016 | 2510 ALUM ROCK AVENUE | SAN JOSE | SANTA CLARA | CA | 95116 | 37.3605 | -121.8394 | [9 empty] | 2016-07-14 15:07 | 1153381 |  | NATURAL GAS |  | 1500 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 1 | 2016-07-14 12:32 |  |  |  | 2016-07-14 12:32 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 84 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | SENSING LINE TEE | UNKNOWN | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | SENSING LINE TEE KNOCKED OFF | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 193073 | 231939.291611562522413 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 193073 | 96062.298412998367233 | 231939.291611562522413 | 0 | 0 | 0 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 4 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | YES | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 618900370 | N/A |  | UTILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON JULY 14, 2016 AT 1232 HOURS, A PG&E M&C CREW STRUCK A 1 1/4' SENSING LINE TEE WHICH REDUCES TO 3/4' PIPING FROM THE 10' STEEL MAIN WITH A BACKHOE NEAR 2510 ALUM ROCK AVENUE IN THE CITY OF SAN JOSE. PG&E HAD A VALID USA TICKET (W618900370) AND PG&E FACILITIES WERE PROPERLY LOCATED & MARKED. PG&E CREWS SHUT-IN GAS ON 7/15/16 AT 0319 HOURS BY TURNING OFF AN EXISTING VALVE AND INSTALLING A PRESSURE CONTROL FITTING DOWNSTREAM. REPAIRS WERE COMPLETED ON 7/15/16 AT 1340 HOURS. PG&E EMPLOYEES INVOLVED IN THE INCIDENT WERE PAT TESTED. THE POLICE DEPARTMENT, FIRE DEPARTMENT AND MEDIA WERE REPORTED ON-SITE. THERE WERE NO IGNITION, INJURIES, OR FATALITIES ASSOCIATED WITH THIS INCIDENT AND NO CUSTOMERS WERE IMPACTED. THIS INCIDENT IS BEING REPORTED TO THE DOT AND CPUC DUE TO THE UNINTENTIONAL RELEASE OF GAS, REPAIR COSTS EXCEEDING $50,000 AND MEDIA PRESENCE.
2025-03-31 10:13 | NO | YES | NO | 20160071 | 16685 | 2016-08-16 20:03 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2016-07-16 16:45 |  |  | 2016 | 333 JOHNSON RD | LOS BANOS | MERCED | CA | 93635 | 37.0727 | -120.862 | [9 empty] | 2016-07-16 20:33 | 1153599 |  | NATURAL GAS |  | 1500 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-07-16 13:20 |  |  |  | 2016-07-16 13:20 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1989 | [5 empty] | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 6 | 3 |  | CLASS 3 LOCATION | 0 | 0 | 216602 | 260204.764216890323762 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 216602 | 107769.009446438768442 | 260204.764216890323762 | 0 | 1 | 0 |  |  |  |  | 370 | 40 | 60 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | STEPHEN RAMOS | COMPLIANCE ENGINEER | s3rc@pge.com | 9254137311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 9253285776 | gsr8@pge.com | ON JULY 16TH 2016 AT 1320 HRS, GSR RESPONDED TO ODOR CALL AT 333 JOHNSON ROAD, LOS BANOS (ADJACENT TO KAGOME FOODS). PG&E SHUT-IN THE FLOW OF GAS AT 1400 HOURS BY SHUTTING THE INLET & OUTLET VALVES AT THE PRIMARY REG STATION. IT WAS DETERMINED THAT AN OVER-PRESSURE EVENT OCCURRED AT 1045 HOURS, RESULTING IN A 4-INCH PLASTIC LINE FAILURE AND AN UNINTENTIONAL RELEASE OF GAS. AFTER THE PIPE RUPTURE, AN INSPECTION OF THE PRIMARY REGULATOR SET REVEALED THE REGULATOR BOOT HAD FAILED. BASED ON THE EVENT REVIEW, THERE IS A POSSIBILITY THAT THE MONITOR FAILED TO CONTROL OR DID NOT LOCK UP WITH CAUSED THE OVERPRESSURE EVENT. AN ANALYSIS OF THE 4 INCH PLASTIC SERVICE PIPE REVEALED A DUCTILE FAILURE ON THE PIPE. THE MAOP OF THE PLASTIC LINE IS 60 PSI, AND THE SYSTEM WAS OVERPRESSURED TO 370 PSIG. THE SERVICE SUPPLIED A SINGLE CUSTOMER (KAGOME FOODS) AND THE CUSTOMER WAS SUPPLIED WITH CNG BY 2100 HOURS WHILE PG&E CREWS REPAIRED THE LINE. REPLACEMENT OF THE 4-INCH PLASTIC LINE, LARGE METER SET, BOTH REGULATOR AND MONITOR WERE COMPLETED ON 7/18/16 AT 2000 HOURS; CNG WAS REMOVED AND THE SERVICE WAS RESTORED BY 2100 HOURS. THERE WERE NO INJURIES, NO FATALITIES, NO IGNITION ASSOCIATED WITH THIS INCIDENT. FIRE DEPARTMENT AND POLICE DEPARTMENT WERE REPORTED ON-SITE. THIS INCIDENT IS BEING REPORTED TO CPUC AND DOT DUE TO THE UNINTENTIONAL RELEASE OF GAS AND ESTIMATED DAMAGES EXCEEDING $50,000. PLEASE NOTE THAT AFTER FURTHER REVIEW, THIS INCIDENT SHOULD BE CLASSIFIED AS A TRANSMISSION BECAUSE THE LINE IS SERVING A TRANSMISSION LARGE VOLUME CUSTOMER (NOT DOWNSTREAM OF A DISTRIBUTION CENTER).
2025-03-31 10:13 | NO | NO | NO | 20160072 | 16523 | 2016-08-19 11:25 | SUPPLEMENTAL FINAL | 19740 | TRUSSVILLE, UTILITIES BOARD, CITY OF | 127 MAIN STREET | TRUSSVILLE | AL | 35173 | 2016-08-04 13:42 |  |  | 2016 | 7550 COMMERCE CIRCLE | TRUSSVILLE | JEFFERSON | AL | 35173 | 33.639 | -86.5687 | [9 empty] | 2016-08-04 14:46 | 1155350 |  | NATURAL GAS |  | 5.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-08-04 13:42 |  |  |  | 2016-08-04 13:51 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 15 |  | NO | [11 empty] | OTHER | PUBLIC UTILITY | SERVICE |  | 2002 | [5 empty] | 1.05 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | OTHER | [8 empty] | COMPLETELY SEVERED BY EXCAVATOR | CLASS 2 LOCATION | 65817 | 79066.199603249602677 | 128 | 153.766861893066368 | 2783 | 3343.227942565653923 | 0 | 0 |  |  | 73 | 84.01886792452830188679245283018867924528 |  | 0 | 68801 | 34272.9213139665454745229110512129380054 | 82647.2132756328512698867924528301886792 | 1 | 0 | 0 |  |  |  |  | 41 | 41 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | TELECOMMUNICATIONS | YES | 162142492 |  |  | UTILITY OWNER | YES | YES | 24 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | BRYAN SMITH | CHIEF ENGINEER | bsmith@trussville.com | 2056553211 | 2056616051 |  |  |  | BRYAN SMITH | CHIEF ENGINEER | 2056553211 | bsmith@trussville.com | ON AUGUST 1, 2016 AT 1621, WE, UTILITIES BOARD CITY OF TRUSSVILLE, WERE NOTIFIED BY 811 TO LOCATE OUR FACILITIES AT 7550 COMMERCE CIRCLE, TRUSSVILLE, AL 35173 FOR STAR CONSTRUCTION, A CONTRACTOR FOR CENTURYLINK, IN ORDER FOR THEM TO EXCAVATE A TELECOMMUNICATION LINE. WE LOCATED OUR FACILITIES FOR THE CONTRACTOR ON AUGUST 3, 2016. WE WERE NOTIFIED BY THE CONTRACTOR ON AUGUST 4, 2016 AT 1342 THAT THEY HAD HIT ONE OF OUR GAS LINES AT THIS LOCATION AND IT WAS ON FIRE. THE FIRE DEPARTMENT ARRIVED ON THE SCENE AT 1347. WE ARRIVED ON THE SCENE AT 1351 TO FIND A GAS SERVICE LINE HAD BEEN HIT AND WAS ON FIRE ALONG WITH THE CONTRACTOR'S MINI EXCAVATOR. THE FIRE DEPARTMENT PROTECTED EXPOSURES IN THE AREA OF THE FIRE WHILE WE BEGAN TO SHUT DOWN THE SERVICE LINE. WE PINCHED THE SERVICE LINE OFF APPROXIMATELY 56 FEET FROM THE DAMAGED AREA TO EXTINGUISH THE FIRE AT 1417. WE NOTIFIED THIS INCIDENT TO THE ALABAMA PUBLIC SERVICE COMMISSION AT 1423 AND TO THE NATIONAL RESPONSE CENTER AT 1446 ON AUGUST 4, 2016. WE TALKED WITH THE CONTRACTOR'S OPERATOR WHO WAS EXCAVATING THE HOLE AND HE REPORTED THAT THE GAS IGNITED AS SOON AS THE LINE WAS HIT. HE STATED THAT IT SINGED HIS ARM HAIR, BUT HE WAS NOT INJURED. WITH THE CONTRACTOR'S ASSISTANCE, WE REMOVED THE MINI EXCAVATOR'S BUCKET THAT WAS STILL IN THE APPROXIMATELY 6 1/2 FOOT LONG BY 3 FOOT WIDE EXCAVATION TO SEE THE EXTENT OF THE DAMAGE. WE OBSERVED THAT THE BUCKET HAD COMPLETELY SEVERED THE 3/4 INCH PE GAS SERVICE LINE AND THE 3/4 INCH CONDUIT CONTAINING ELECTRICAL WIRES TO THE PARKING LOT LIGHTS. ALSO LOCATED IN THE HOLE WERE TWO 3/4 INCH PVC SPRINKLER LINE WITH CONTROL WIRES, A 3/4 INCH CONDUIT CONTAINING ELECTRICAL WIRES, AND A 2 INCH CONDUIT CONTAINING TELECOMMUNICATION WIRES WHICH WERE NOT DAMAGED. WE MEASURED THE DISTANCE OF THE GAS SERVICE LINE FROM LOCATE MARKS IN TWO LOCATIONS TO DETERMINE IF THE LINE WAS LOCATED WITHIN THE TOLERANCE ZONE OF THE LOCATE MARKS. THE METHOD WE USED TO DETERMINE THIS WAS WE PULLED A TAPE MEASURE FROM THE LOCATE MARK ON THE PARKING LOT CURB NEXT TO THE EXCAVATION AND LOCATE MARK BETWEEN THE EXCAVATION AND THE ROAD. WE PULLED ANOTHER TAPE 90° OFF THAT TAPE AND MEASURED TO THE CENTER LINE OF THE GAS SERVICE LINE IN TWO LOCATIONS. THE SERVICE LINE DISTANCE AT THE FIRST LOCATION, CLOSEST TO THE PARKING LOT CURB, WAS 23 3/8 INCHES AND THE DISTANCE AT THE OPPOSITE END OF THE DITCH WAS 21 INCHES FROM THE LOCATE MARK. FROM THESE MEASUREMENTS IT WAS DETERMINED THAT THE SERVICE LINE LOCATION WAS NOT IN THE TOLERANCE ZONE OF THE LOCATE MARKS. THE SERVICE LINE WAS BURIED 15 1/2 INCHES FROM THE TOP OF GROUND TO THE TOP OF THE SERVICE LINE. AFTER FINAL INVESTIGATION, IT WAS DETERMINED THAT SEVERAL FURTHER STEPS IN LOCATING AND EXCAVATION COULD HAVE BEEN PERFORMED TO HELP MITIGATE THE RISK OF DAMAGE TO THE GAS SERVICE LINE: 1. DURING THE LOCATING PROCESS INSTEAD OF INDUCING A SIGNAL TO LOCATE THE SERVICE, A DIRECT CONNECTION COULD HAVE BEEN PERFORMED TO INDUCE A LOWER FREQUENCY, POSSIBLY REDUCING THE CHANCES OF INTERFERENCE BY THE OTHER UTILITIES IN THE AREA. 2. THE SIGNAL COULD HAVE BEEN " BALANCED" TO VERIFY THERE WAS A SYMMETRICAL MAGNETIC FIELD FOR THE SERVICE LINE. 3. THE CONTRACTOR COULD HAVE UTILIZED A NON-INVASIVE EXCAVATION METHOD TO DETERMINE THE PRECISE LOCATION OF THE GAS SERVICE LINE BECAUSE MECHANIZED EQUIPMENT WAS BEING UTILIZED WITHIN THE TOLERANCE ZONE OF THE LOCATE MARKS.
2025-03-31 10:13 | NO | YES | YES | 20160073 | 16587 | 2016-08-19 18:03 | SUPPLEMENTAL FINAL | 31159 | KANSAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2016-06-02 14:00 |  |  | 2016 | 918 W. 5TH STREET | NEWTON | HARVEY COUNTY | KS | 67114 | 38.0475 | -97.3612 | [9 empty] | 2016-08-19 16:45 | 1156778 |  | NATURAL GAS |  | 0.01 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2016-06-02 14:25 |  |  |  | 2016-06-02 15:30 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1943 | [5 empty] | 1.25 | ASTM D2513 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 240.2607217079162 | OVERTIME PAID TO KANSAS GAS SERVICE FIELD INSPECTOR. |  | 2 | 2.30188679245283018867924528301886792453 |  | 0 | 202 | 101.638165241892555795148247978436657682 | 242.562608500369030188679245283018867925 | 0 | 0 | 0 |  |  |  |  | 12 | 12 | 13 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NOT APPLICABLE BECAUSE WE WERE NOTIFIED BY THE CONTRACTOR OF THE INCIDENT. | [12 empty] | NO |  |  | YES | 2 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | CONTRACTOR WAS REMOVING A 4 BOLT SERVICE LINE SADDLE AND ESCAPING GAS IGNITED. |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | RANDY SPECTOR | DIRECTOR OF ENGINEERING | randy.spector@onegas.com | 913-599-8931 |  |  |  |  | RANDY SPECTOR | DIRECTOR OF ENGINEERING | 913-599-8931 | randy.spector@onegas.com | NPL, A CONTRACTOR PERFORMING WORK FOR KANSAS GAS SERVICE, HAD A TWO MAN CREW REPLACING A FOUR BOLT SERVICE LINE SADDLE. THE CONTRACTOR EMPLOYEE HAD REMOVED THREE OF THE FOUR BOLTS, WHEN GAS ESCAPING AROUND THE SADDLE FITTING IGNITED AND BURNED THE EMPLOYEE. THE EMPLOYEE WAS TRANSPORTED TO THE HOSPITAL, AND THEN ADMITTED FOR BURNS. AFTER RESOLVING THE IMMEDIATE CONCERNS, THE CONTRACTOR NOTIFIED THE LOCAL KANSAS GAS SERVICE SUPERVISOR BY PHONE. IF GAS HAD STILL BEEN BLOWING, THE CONTRACTOR WOULD HAVE NOTIFIED THE KANSAS GAS SERVICE DISPATCH CENTER. NOTIFICATION WAS ADEQUATE UNDER THESE CIRCUMSTANCES, AND THE CONTRACTOR EMPLOYEES ARE OQ QUALIFIED ON MEASURES TO PREVENT ACCIDENTAL IGNITION. THE INCIDENT OCCURRED ON JUNE 2ND, BUT DUE TO A MISUNDERSTANDING, LOCAL COMPANY PERSONNEL ASSUMED THAT ALL REPORTING RESPONSIBILITIES WOULD BE COMPLETED BY THE CONTRACTOR. AS A RESULT, THE REPORT IS JUST NOW BEING SUBMITTED. TO ADDRESS THIS SITUATION, THE COMPANY HAS REVIEWED THE PHMSA REQUIREMENTS WITH THE APPROPRIATE PERSONNEL, AND WILL REVIEW THIS SUBJECT MATTER IN FUTURE TRAININGS.
2025-03-31 10:13 | YES | NO | NO | 20160074 | 16367 | 2016-08-24 16:38 | ORIGINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2016-07-25 12:38 |  |  | 2016 | 1660 S TAMIAMI TRAIL | OSPREY | SARASOTA | FL | 34229 | 27.1723 | -82.48 | [9 empty] | 2016-07-25 19:40 | 1154430 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 32 | 2016-07-25 12:38 |  |  |  | 2016-07-25 13:10 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2011 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | METER AND RISER COMPROMISED BY OUTSIDE FORCE / DAMAGE (FIRE / HEAT) | CLASS 3 LOCATION | 60000 | 72078.21651237486 | 6000 | 7207.821651237486 | 100 | 120.1303608539581 | 0 | 0 |  |  | 100 | 115.094339622641509433962264150943396226 |  | 0 | 66200 | 32994.1225073241958897574123989218328841 | 79521.2628640889456094339622641509433962 | 1 | 0 | 0 |  |  |  |  | 42 | 42 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LOCALIZED EVENT AT A METER SET THAT DID NOT /WOULD NOT AFFECT THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MARK WITECKI | GAS COMPLIANCE MANAGER | mgwitecki@tecoenergy.com | 813-228-4465 | 813-228-1770 |  |  |  | LUKE BUZARD | DIRECTOR-PIPELINE SAFETY AND OPERATIONAL SERVICES | 813-228-4733 | labuzard@tecoenergy.com | GREG WARNER (PROPERTY WORKER) STATED THE FIRE ALARM SOUNDED, AND KITCHEN PERSONNEL STATED THAT GAS TO THE KITCHEN EQUIPMENT HAD STOPPED. MR. WARNER THEN WENT TO LOOK AT THE GAS METER, AND DISCOVERED A FIRE IN THE IMMEDIATE VICINITY OF THE METER. HE IMMEDIATELY CALLED THE FIRE DEPARTMENT UPON DISCOVERY OF THE FIRE. PGS CUSTOMER CONTACT CENTER WAS THEN NOTIFIED BY THE FIRE DEPARTMENT OF THE FIRE AT THE BUILDING AND METER, AND OF A GAS LEAK. UPON ARRIVAL, THE FIRE DEPARTMENT EXTINGUISHED MOST OF FLAMES AT THE BUILDING AND METER. A SMALL FIRE REMAINED AT THE BASE OF THE RISER TRANSITION DUE TO ESCAPING GAS. THE SERVICE LINE THAT WAS SUPPLYING THE RISER WAS THEN EXCAVATED BY HAND, AND SQUEEZED OFF TO PREVENT ADDITIONAL GAS FROM ESCAPING AND FUELING THE REMAINING FIRE. IT IS BELIEVED THAT MULCH UNDER AND AROUND THE METER SET CAUGHT FIRE DUE TO A PROPERTY EMPLOYEE DISPOSING AN UNEXTINGUISHED CIGARETTE INTO THE MULCH. AFTER THE MULCH IGNITED, THE FIRE THEN COMPROMISED THE BOTTOM OF THE GAS METER, WHICH BREACHED THE METER CASING, THEN ALLOWED GAS TO ESCAPE AND FUEL THE FIRE. EXCESSIVE HEAT GENERATED BY THE FIRE THEN COMPROMISED THE INTEGRITY OF THE RISER. THAT RESULTED IN A BREACH OF THE SYSTEM AT THE TRANSITION RISER, WHICH FUELED THE SMALLER FIRE THAT WAS DISCOVERED AFTER THE BUILDING AND METER FIRE WAS EXTINGUISHED. THE SMALLER FIRE WAS EXTINGUISHED AFTER GAS FLOW WAS STOPPED TO THE TRANSITION RISER.
2025-03-31 10:13 | NO | YES | NO | 20160075 | 16368 | 2016-08-24 19:46 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2016-07-26 11:30 |  |  | 2016 | ON ACACIA TREE DR., 150-FEET WEST OF ANASAZI DRIVE | LAS VEGAS | CLARK COUNTY | NV | 89144 | 36.181 | -115.328 | [9 empty] | 2016-07-26 13:28 | 1154508 |  | NATURAL GAS |  | 1425 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 30 | 2016-07-26 11:30 |  |  |  | 2016-07-26 11:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1996 | [5 empty] | 4 | ASTM D2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | OTHER | [8 empty] | MECHANICAL PUNCTURE - FOR EXPLANATION REFER TO NARRATIVE PART C, 5 | CLASS 3 LOCATION | 25499 | 30632.040714150775919 | 82668 | 99309.366710750082108 | 221494 | 266081.541469865954014 | 1624 | 1950.917060268279544 | PLUMBER FEES AND VEHICLE TOWING. |  | 2903 | 3341.188679245283018867924528301886792453 |  | 0 | 334188 | 167919.6346532547069216576819407008086253 | 401315.0546342803746038679245283018867925 | 44 | 0 | 3476 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LINE WAS DAMAGED DURING EXCAVATION ACTIVITY. | [12 empty] | YES | 8 | 0 | YES | 3 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 620800166 |  |  | UTILITY OWNER | NO | YES | 27 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | RENEE CRONISTER | COMPLIANCE SPECIALIST | renee.cronister@swgas.com | 702-365-2080 | 702-369-0542 |  |  |  | THOMAS CARDIN | DIRECTOR OF GAS OPERATIONS | 702-365-2028 | thomas.cardin@swgas.com | SOUTHWEST GAS (COMPANY) CONSTRUCTION CREWS WERE PERFORMING MAINTENANCE TO REPLACE A 4-INCH PE VALVE, THAT HAD A PREVIOUSLY DISCOVERED NON-HAZARDOUS GRADE 2 LEAK, AND HIT A 4-INCH PE GAS LINE WITH A BACKHOE DURING EXCAVATION. PART A, 16: FIRE DEPARTMENT CONDUCTED A PRECAUTIONARY EVACUATION OF 30 OCCUPANTS AS A RESULT OF THE FIRE. PART C, 5: THE DAMAGE TO THE 4-INCH PE MAIN WAS EXTENSIVE AS A RESULT OF THE IGNITION AND SUBSEQUENT FIRE; THEREFORE, THE SIZE OF THE PUNCTURE COULD NOT BE DETERMINED. THE ESTIMATED VOLUME OF GAS RELEASED WAS CALCULATED ASSUMING A FULL 4-INCH CIRCUMFRENTIAL BREAK. PART G3, 11: SEVERAL NON-GAS UTILITIY LINE MARKINGS WERE VISIBLE IN THE AREA THE COMPANY DELINEATED FOR EXCAVATION, INCLUDING WATER, POWER AND STREET LIGHTING. COMPANY PERSONNEL DID NOT SUFFICIENTLY LOCATE AND MARK ALL OF THE GAS FACILITIES WITHIN THE DELINEATED AREA IN ACCORDANCE WITH ITS LINE LOCATING PROCEDURES. AS A RESULT OF THE COMPANY'S INVESTIGATION TO DATE, THE COMPANY BELIEVES THAT IF ITS LINE LOCATING PROCEDURES WERE FOLLOWED A DISCREPANCY IN THE ALIGNMENT OF THE FACILITY WOULD HAVE BEEN IDENTIFIED BETWEEN THE MAP, ASBUILT AND THE ACTUAL FIELD FACILITY LOCATION. PART G3, 14: IN ADDITION TO THE PRIMARY CAUSE OF INSUFFICIENT LOCATING PRACTICES THE COMPANY IDENTIFIED AN ADDITIONAL CONTRIBUTING CAUSE. THE EXCAVATION DAMAGE OCCURRED AT OR NEAR AN UNMAPPED AND NON-LOCATED 4-INCH 45 DEGREE ELBOW THAT DID NOT APPEAR ON AS-BUILT DOCUMENTATION. THE EXCAVATION DAMAGE IS BELIEVED TO HAVE OCCURRED ON A PORTION OF THE PIPE THAT CHANGED DIRECTION BECAUSE THE 4" PE MAIN AND VALVE WERE EXPOSED AND BEING SPOTTED BY COMPANY EMPLOYEES WHILE THE BACKHOE OPERATOR WAS REMOVING DIRT ADJACENT TO THE PIPELINE FACILITY.
2025-03-31 10:13 | NO | YES | YES | 20160076 | 16426 | 2016-08-29 09:37 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2016-08-16 01:30 |  |  | 2016 | 2410 PRAIRIETON AVENUE | TERRE HAUTE | VIGO | IN | 47802 | 39.4406 | -87.4231 | [9 empty] | 2016-08-16 12:55 | 1156405 |  | NATURAL GAS |  | 124 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2016-08-16 02:23 |  |  |  | 2016-08-16 02:23 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1969 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 1 |  | CLASS 2 LOCATION | 200000 | 240260.7217079162 | 900 | 1081.1732476856229 | 100 | 120.1303608539581 | 0 | 0 |  |  | 427 | 491.452830188679245283018867924528301887 |  | 0 | 201427 | 100460.9517554335549622641509433962264151 | 241953.4781466444602452830188679245283019 | 0 | 0 | 0 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JOHN SPINKS | MANAGER GAS COMPLIANCE AND QMP | jaspinks@vectren.com | 937-440-1844 | 937-440-1818 |  |  |  | JAMES FRANCIS | VICE PRESIDENT SAFETY AND SYSYTEM INTEGRITY | 812-491-4369 | jmfrancis@vectren.com | ON AUGUST 16, 2016, A DRIVER HEADING SOUTH ON PRAIRIETON ROAD IN TERRE HAUTE INDIANA, LOST CONTROL OF HIS VEHICLE VEERING OFF THE ROADWAY INITIALLY STRIKING A UTILITY POLE AND CONTINUING THROUGH A FOUR INCH STEEL PROTECTIVE BARRICADE INTO THE METER SETTING AT 2410 PRAIRETON ROAD. THIS WAS AN INACTIVE SERVICE LOCKED-OFF AT THE RISER VALVE WITH NO METER ATTACHED. THE IMPACT RESULTED IN BREAKING A ONE INCH STEEL SERVICE RISER BELOWGROUND ALLOWING A RELEASE OF NATURAL GAS THAT SUBSEQUENTLY IGNITED. THE FIRE DESTROYING THE VEHICLE, THE BUILDING AND BUILDING CONTENTS. THE DRIVER WAS ADMITTED TO A HOSPITAL BURN UNIT.
2025-03-31 10:13 | NO | YES | YES | 20160077 | 31541 | 2016-08-29 16:56 | SUPPLEMENTAL FINAL | 603 | CENTERPOINT ENERGY RESOURCES CORP. | 10825 E GEDDES AVE SUITE 410 | CENTENNIAL | CO | 80112 | 2016-07-31 16:18 |  |  | 2016 | 2437 FAIRFIELD AVE. | SHREVEPORT | CADDO | LA | 71103 | 32.4883 | -93.7495 | [9 empty] | 2016-07-31 20:30 | 1154972 |  | NATURAL GAS |  | 0.27 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2016-07-31 17:00 |  |  |  | 2016-07-31 16:53 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1911 | [5 empty] | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 50000 | 60065.18042697905 | 11046 | 13269.599659928211726 | 1360 | 1633.77290761383016 | 0 | 0 |  |  | 0 | 0 |  | 0 | 62406 | 31049.726242206709926 | 74968.552994521091886 | 0 | 0 | 1 |  |  |  |  | 0.5 | 0.5 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE METALLURGICAL ANALYSIS AND SUBSEQUENT GEOTECHNICAL INVESTIGATION INDICATED THAT THE PIPE FRACTURED DUE TO A RECENT OVERLOAD EVENT OCCURRING AFTER A LOSS OF SUPPORT, MOST LIKELY CAUSED BY LOSS OF SOIL BY WATER INFILTRATION AND EROSION THROUGH THE VOIDS, CRACKS AND OPENINGS AROUND THE VARIOUS SEWER LINE CONNECTIONS IN THE SEWER MANHOLE AND ON THE MANHOLE WALL ITSELF. | [154 empty] | JAMES TODD HEBERT | OPERATIONS SPECIALIST | james.hebert@centerpointenergy.com | 337-256-2161 |  |  |  |  | BOBBY R. BURNS | REGIONAL OPERATIONS DIRECTOR | 318-429-4495 | bobby.r.burns@centerpointenergy.com | THE INITIAL POST-INCIDENT INVESTIGATION REVEALED EROSION OF SOIL AND CAVE IN OF SURFACE PAVEMENT AROUND A SEWER MANHOLE DISCOVERED ON MAY 6, 2016, WHICH CAUSED DAMAGE TO THE CONNECTION OF A SERVICE LINE PROVIDING SERVICE TO 2437 FAIRFIELD AVE. THIS SERVICE LINE CONNECTION WAS REPAIRED WITH THE INSTALLATION OF A NEW SERVICE LINE AND TAP ON MAY 6, 2016. THIS NEW SERVICE LINE AND CONNECTION DID NOT LEAK AFTER MAY 6. THERE WAS NO CRACK IN THE CAST IRON MAIN AT THE TIME THAT THE MAY 6 SERVICE LINE REPLACEMENT WAS COMPLETED; THE INSPECTION AT THAT TIME DID NOT REVEAL A LOSS OF SUPPORT UNDER THE CAST IRON MAIN. SERVICE TO 2437 FAIRFIELD WAS LEFT OFF AT THE TIME OF THIS REPAIR DUE TO CUSTOMER NOT BEING HOME. ON MAY 23, 2016 A CENTERPOINT ENERGY EMPLOYEE RETURNED TO RESTORE SERVICE TO THIS RESIDENCE AT THE CUSTOMER'S REQUEST. DURING THIS RESTORATION A BAR HOLE INSPECTION WAS MADE IN WHICH THERE WAS NO EVIDENCE OF A LEAK. ON MAY 26, 2016 A CENTERPOINT ENERGY CONTRACT SERVICES INSPECTOR WENT BACK TO SITE OF THE SERVICE LINE REPAIR AND PERFORMED A VISUAL INSPECTION, AND AT THAT TIME THERE WAS NO INDICATION OF A LEAK. ON JULY 31, 2016 AT APP. 16:18, CENTERPOINT ENERGY WAS NOTIFIED AND RESPONDED TO TWO EMERGENCY CALLS REPORTED AT 2437 FAIRFIELD AVE. AN EMERGENCY LEAK INVESTIGATION ORDER AND AN EMERGENCY FIRE INVESTIGATION ORDER WERE CREATED. TECHNICIAN ARRIVED AT APP. 16:53 TO BEGIN AN INVESTIGATION. DURING THE INVESTIGATION OF JULY 31, GAS WAS DETECTED NEAR THE STRUCTURE, AFTER WHICH TELEPHONIC REPORTS WERE MADE TO NRC AND STATE REGULATORY OFFICIALS. DURING ONGOING INVESTIGATION OF THE INCIDENT, A FRACTURE WAS FOUND AUGUST 2, 2016, ON THE CAST IRON MAIN AT A LOCATION OF AN ADJACENT STEEL SERVICE LINE TAP, WHICH WAS 2.8' AWAY FROM THE NEWLY INSTALLED POLY SERVICE LINE TAP. METALLURGICAL INSPECTION OF JANUARY 18, 2017, SHOWED THAT THE PIPE WALL THICKNESS/STRENGTH WAS WELL PRESERVED WITHOUT ANY GRAPHITIC CORROSION BEYOND SHALLOW SURFACE CORROSION. THE METALLURGICAL ANALYSIS AND SUBSEQUENT GEOTECHNICAL INVESTIGATION INDICATED THAT THE PIPE FRACTURED DUE TO A RECENT OVERLOAD EVENT OCCURRING AFTER A LOSS OF SUPPORT, MOST LIKELY CAUSED BY LOSS OF SOIL BY WATER INFILTRATION AND EROSION THROUGH THE VOIDS, CRACKS AND OPENINGS AROUND THE VARIOUS SEWER LINE CONNECTIONS IN THE SEWER MANHOLE AND ON THE MANHOLE WALL ITSELF. THE FRACTURE OCCURRED SUBSEQUENT TO THE MAY 26, 2016 INSPECTION AND BEFORE THE JULY 31, 2016 INCIDENT. THE GEOTECHNICAL INVESTIGATION REVEALED THAT THE CAST-IRON MAIN LINE UNDERWENT DEFLECTIONS DUE TO THE OCCURRENCE OF THE LOSS OF SOIL SUPPORT FROM THE SOIL CAVING, RESULTING IN AN UNDETECTED INCREASE IN STRESSES IN THE MAIN PIPE AT THE LOCATION OF THE CONNECTION OF THE STEEL SERVICE LINE WHERE THE CRACK OCCURRED. THE ODOR OF NATURAL GAS WAS DETECTED BY PERSONS PRESENT AT THE SUBJECT PROPERTY ON JULY 29, JULY 30 AND THE MORNING OF JULY 31 WITHOUT ANYONE CONTACTING CENTERPOINT BEFORE THE FIRE OCCURRED.
2025-03-31 10:13 | NO | NO | NO | 20160078 | 16373 | 2016-09-02 19:08 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2016-08-03 13:07 |  |  | 2016 | 5858 SHOUP AVE | WOODLAND HILLS | LOS ANGELES | CA | 91367 | 34.1773 | -118.6145 | [9 empty] | 2016-08-03 18:29 | 1155265 |  | NATURAL GAS |  | 701 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-08-03 13:07 |  |  |  | 2016-08-03 13:16 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 45 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1982 | [5 empty] | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 11540 | 13863.04364254676474 | 200 | 240.2607217079162 | 75000 | 90097.770640468575 | ESTIMATE COST FOR THE DAMAGED BACKHOE |  | 4206 | 4840.867924528301886792452830188679245283 |  | 0 | 90946 | 47635.0463893980197771967654986522911051 | 109041.9429292515578267924528301886792453 | 0 | 0 | 0 |  |  |  |  | 40 | 40 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | WATER | YES | 62080196 | DIGALERT |  | UTILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 626-893-4536 | kle2@semprautilities.com | ON AUGUST 3RD AT 13:07, A THIRD PARTY CONTRACTOR WAS DIGGING WITH A BACKHOE TO INSTALL A FIRE SERVICE WHEN HE STRUCK A 4 INCH PLASTIC GAS MAIN CAUSING A RELEASE OF GAS AND IGNITION. ACTUAL INCIDENT LOCATION IS 5858 SHOUP AVE, WOODLAND HILLS. INITIAL REPORT SHOWED 5858 SHOUP AVE, LOS ANGELES. THE BACKHOE WAS EVENTUALLY ENGULFED BY THE FIRE AND SUFFERED EXTENSIVE DAMAGE. CREW RESPONDED AND CONTROLLED THE GAS. NO INJURIES OR OUTAGES RESULTED FROM THIS INCIDENT. ALL REPAIRS TO THE DAMAGED MAIN WERE COMPLETED. INVESTIGATION OF THE INCIDENT SHOWED THAT THERE WAS A VALID USA TICKET FOR THE CONTRACTOR AND THE 4 INCH GAS MAIN WAS PROPERLY MARKED. HOWEVER, THE CONTRACTOR FAILED TO USE HAND TOOLS WHERE REQUIRED. THIS INCIDENT WAS INITIALLY REPORTED TO THE CPUC WHEN SOCALGAS BECAME AWARE OF MEDIA COVERAGE. AT 15:19, IT WAS DETERMINED THAT THE ASSOCIATED DAMAGE COULD POTENTIALLY EXCEED $50,000. THIS INCIDENT WAS THEN REPORTED TO DOT DUE TO A RELEASE OF GAS AND THE ASSOCIATED DAMAGE EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2025-03-31 10:13 | NO | NO | NO | 20160079 | 16374 | 2016-09-04 19:12 | ORIGINAL FINAL | 1640 | BOSTON GAS CO | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2016-08-08 10:32 |  |  | 2016 | 107 LOW STREET | NEWBURYPORT | ESSEX | MA | 01950 | 42.8082 | -70.8897 | [9 empty] | 2016-08-11 16:57 | 1155977 |  | NATURAL GAS |  | 3824 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 3 | 2016-08-08 10:50 |  |  |  | 2016-08-08 10:56 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1982 | [5 empty] | 10 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.3 | 13 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 2500 | 3003.2590213489525 | 15000 | 18019.554128093715 | 0 | 0 |  |  | 5500 | 6330.188679245283018867924528301886792453 |  | 0 | 23000 | 14562.8138521965959366576819407008086253 | 27353.0018286879505188679245283018867925 | 30 | 0 | 5 |  |  |  |  | 55.03 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS DUE TO THIRD PARTY DAMAGE, AND WAS CONFIRMED BY FIRST RESPONDER. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY | 2015-01-01 |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | TRENCHER | DRAINAGE | YES | 20162900357 |  |  | UTILITY OWNER | YES | YES | 12 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | DATA NOT COLLECTED | [169 empty] | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAM | 6317703549 | corinne.byrnes@nationalgrid.com | AT 10:32 ON 8/8/2016, AN EMERGENCY RESPONSE UNIT WAS DISPATCHED TO 107 LOW ST FOLLOWING A REPORTED HIT LINE BY A 3RD PARTY CONTRACTOR, GRANESE CONSTRUCTION. ONE-CALL WAS NOTIFIED BUT MAPS/RECORDS WERE NOT AVAILABLE. BETWEEN 12:30 AND 13:30, PREPARATIONS WERE MADE TO SHUTDOWN THE MAIN AND ASSOCIATED SERVICES. THREE CUSTOMERS WERE EVACUATED; A TOTAL OF 35 CUSTOMERS WERE OUT OF SERVICE. MAIN AND SERVICES WERE ISOLATED USING SYSTEM ISOLATION VALVES, COMPLETED BY 17:00. AT 22:20, MUELLER STOP-OFF FITTING WAS INSTALLED TEMPORARILY TO SECURE LEAK AND ADDITIONAL REPAIRS WERE MADE TO MAIN. APPROX. AN 8 FOOT SECTION OF MAIN WAS REPLACED. REPAIRS WERE COMPLETED BY 3:48 ON 8/9/2016, AND AT 4:20, GAS WAS REINTRODUCED TO MAIN AND VALVES REOPENED. AT 6:00, RELIGHTS WERE STARTED.THERE CURRENTLY ARE 3 "CANNOT GET IN" CUSTOMERS WITH CARDS LEFT TO NOTIFY THEM TO SCHEDULE RELIGHTS.
2025-03-31 10:13 | NO | YES | YES | 20160080 | 30493 | 2016-09-07 10:32 | SUPPLEMENTAL FINAL | 2604 | COLUMBIA GAS OF VIRGINIA INC | 1809 COYOTE DRIVE | CHESTER | VA | 23836 | 2016-08-21 15:23 |  |  | 2016 | 6772 BURBAGE LAKE CR | SUFFOLK | Not Within a County or Parish | VA | 23435 | 36.884 | -76.4087 | [9 empty] | 2016-08-21 18:44 | 1156927 |  | NATURAL GAS |  | 12.1 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 5 | 2016-08-21 15:25 |  |  |  | 2016-08-21 15:56 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 26 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1994 | [5 empty] | 0.005 | ASTMD2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 2406 |  |  | 2406 | LEAK |  |  | OTHER | THIRD PARTY DAMAGE | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 110 | 132.14339693935391 | 16052 | 19283.325524277354212 | 0 | 0 |  |  | 29 | 33.37735849056603773584905660377358490566 |  | 0 | 16191 | 8072.180941822674361029649595687331536388 | 19448.8462797072741597358490566037735849 | 0 | 0 | 5 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NOT ENOUGH GAS LOST DURING THIS INCIDENT TO TRIGGER A CONTROL ALERT | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | SUSPECTED CAUSE OF DAMAGE IS DUE TO CHARTER COMMUNICATION CONTRACTOR USING A HAND HELD TORCH TO INSTALL HEAT SHRINK SLEEVES ON A COMMUNICATION LINE, WHICH COMPROMISED A 1/2" PLASTIC GAS SERVICE LINE; RESULTING IN A FIRE. | [154 empty] | PHILIP COLEMAN | COMPLIANCE SPECIALIST | pcoleman@nisource.com | 8047686439 | 8047686455 |  |  |  | GUY DAILEY | COMPLIANCE MANAGER | 8043149390 | gdailey@nisource.com | CONTRACTOR EMPLOYEE FOR CHARTER COMMUNICATIONS WAS PERFORMING MAINTENANCE ON A COMMUNICATION LINE AT 6772 BURBAGE LAKE CR IN SUFFOLK, VA ON SUNDAY AUG 21, 2016. INITIAL REPORT INDICATED WHILE USING A HAND HELD TORCH TO INSTALL HEAT SHRINK SLEEVES ON THE COMMUNICATION LINE, THE CONTRACTOR COMPROMISED THE HALF INCH SERVICE WHICH IMPACTED A 4" PLASTIC MP GAS MAIN. THIS RESULTED IN THE GAS PIPELINE DEVELOPING A LEAK WITH AN IGNITION SOURCE (THE TORCH) ERUPTING INTO FIRE. THE CONTRACTOR WAS INJURED WITH 2ND AND 3RD DEGREE BURNS ON HIS LOWER EXTREMITIES AND WAS HOSPITALIZED AS A RESULT OF HIS INJURIES. HE WAS ADMITTED TO THE HOSPITAL ON SUNDAY 08/21/16 AND RELEASED TUESDAY 8/23/2016.
2025-03-31 10:13 | NO | YES | YES | 20160081 | 16790 | 2016-09-07 11:18 | SUPPLEMENTAL FINAL | 13299 | NEW JERSEY NATURAL GAS CO | 1415 WYCKOFF ROAD | WALL | NJ | 07719 | 2016-08-09 13:42 |  |  | 2016 | 271 HARMONY RD | MIDDLETOWN | MONMOUTH | NJ | 07748 | 40.417 | -74.1231 | [9 empty] | 2016-08-09 17:13 | 1155755 |  | NATURAL GAS |  | 0.01 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2016-08-09 13:42 |  |  |  | 2016-08-09 13:42 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 44 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1957 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.237 | [6 empty] | LEAK |  |  | OTHER | CORROSION | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 10 | 11.50943396226415094339622641509433962264 |  | 0 | 10 | 10.6469002695417789757412398921832884097 | 11.50943396226415094339622641509433962264 | 0 | 0 | 0 |  |  |  |  | 35 | 35 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 5 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | IMPROPER EQUIPMENT WAS USED TO CUT OFF THE SERVICE TEE. |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | MOBEEN KHAN | DIRECTOR | mukhan@njng.com | 732 919 8035 | 732 919 0936 |  |  |  | MOBEEN KHAN | DIRECTOR | 732 919 8035 | mukhan@njng.com | THE INCIDENT OCCURRED AT THE SITE OF A CORRODED SERVICE TEE. THIS SERVICE HAD BEEN CLASSIFIED AS A BARE STEEL SERVICE. NJNG HAS A PROGRAM TO COMPLY WITH STATE REGULATIONS WHERE BARE STEEL SERVICE IN A DEFINED AREA IS REPLACE IF 20% OR MORE OF BARE STEEL SERVICES ARE EXHIBITING LEAKS. DURING THIS REPLACEMENT WORK CONTRACTOR CREW DISCOVERED THE LEAK AND NOTIFIED THE GAS COMPANY. OUR COMPANY CREW ARRIVED ON SITE AND PROCEEDED TO REPAIR/RETIRE THE SERVICE TEE. DURING THE REPAIR PROCESS, THE CREW MECHANIC UTILIZED A TOOL TO REMOVE THE DAMAGED SERVICE TEE THAT IS NOT RECOMMENDED FOR USE IN A GASEOUS ENVIRONMENT, THIS TOOL MAY HAVE BEEN THE CAUSE OF IGNITION. THE CREW MECHANIC WAS ADMITTED TO THE HOSPITAL WITH BURNS TO HIS ARMS. IN ITS INTERVIEWS WITH THE INJURED EMPLOYEE AND HIS CREW LEADER, NJNG HAS LEARNED THE RESPONDING EMPLOYEES FAILED TO FOLLOW THE GUIDELINES FOR WEARING PROPER FIRE PROTECTION ATTIRE BEFORE ENTRY INTO A GASEOUS ENVIRONMENT, INCLUDING FAILURE TO USE BREATHING APPARATUS. BOTH RESPONDING EMPLOYEES WERE FULLY TRAINED AND QUALIFIED IN CONFORMANCE WITH OUR OPERATOR QUALIFICATION ('OQ') PROGRAM AT THE TIME OF THE INCIDENT. IN ADDITION, THE COMPANY PROVIDES SAFETY TRAINING BEYOND OQ INCLUDING FIRE SAFETY, BURN PREVENTION, PERSONAL PROTECTIVE EQUIPMENT AND RESPIRATORY PROTECTION AND FIT TESTING. POST-INCIDENT, NJNG'S MANAGER TRAINING & FIELD SUPPORT DISQUALIFIED BOTH RESPONDING EMPLOYEES FROM OQ TASK #39 ' REMOVE SERVICE TEE OR FITTING FROM STEEL AND CAST IRON MAINS. THEREFORE, THE RESPONDING EMPLOYEES WILL NOT PERFORM THESE TASKS UNTIL THEY ARE RETRAINED/REQUALIFIED.
2025-03-31 10:13 | NO | NO | NO | 20160082 | 16414 | 2016-09-07 23:24 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD N.E. SUITE 20 | ALBUQUERQUE | NM | 87109 | 2016-08-09 14:03 |  |  | 2016 | 7900 WYOMING BLVD. NE | ALBUQUERQUE | BERNALILLO | NM | 87109 | 35.1725 | -106.5598 | [9 empty] | 2016-08-09 15:15 | 1155756 |  | NATURAL GAS |  | 385 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2016-08-09 14:03 |  |  |  | 2016-08-09 14:28 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 54 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2004 | [5 empty] | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | MECHANICAL PUNCTURE | 5 | 1 | [7 empty] | CLASS 3 LOCATION | 90000 | 108117.32476856229 | 5656 | 6794.573209899870136 | 1365 | 1639.779425656528065 | 0 | 0 |  |  | 1567 | 1803.528301886792452830188679245283018868 |  | 0 | 98588 | 49940.5785108542721064986522911051212938 | 118355.2057060054806538301886792452830189 | 12 | 0 | 0 |  |  |  |  | 58 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 16010345 |  |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | GARY G. ROYBAL | MANAGER DOT PIPELINE SAFETY COMPLIANCE | ggroybal@tecoenergy.com | 505-697-3636 | 505-697-4481 |  |  |  | EDWARD KACER | VP DELIVERY AND ENGINEERING SERVICES | 505-697-3303 | ejkacer@tecoenergy.com | DIRECTIONAL DRILLING CONTRACTOR HIT A 2 INCH PE MAIN WHILE CONDUCTING BORING EXCAVATION ACTIVITIES. THE CONTRACTOR/EXCAVATOR DEVIATED FROM THE ORIGINAL BORE PATH AND FAILED TO EXPOSE AND DETERMINE THE DEPTH OF THE PIPELINE AT THE POINT OF CONFLICT.
2025-03-31 10:13 | NO | NO | NO | 20160083 | 16379 | 2016-09-08 12:57 | ORIGINAL | 31597 | CITY OF HOOKER | 111 S BROADWAYS | HOOKER | OK | 73945 | 2016-08-10 09:06 |  |  | 2016 | 300 BLK W. CLARENCE STREET/ US HWY 54 | HOOKER | TEXAS | OK | 73945 | 36.8553 | -101.2148 | [9 empty] | 2016-08-10 16:00 | 1155868 |  | NATURAL GAS |  | 140 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-08-10 09:06 |  |  |  | 2016-08-10 09:06 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 63 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1975 | [5 empty] | 4 | API 5L | UNKNOWN | STEEL |  | SEAMLESS | SEAMLESS | 1.237 | [6 empty] | OTHER | [8 empty] | A 2 IN POLY BY-PASS LINE WAS BURNED SECONDARY FROM AN PRIMARY FIRE IN A DEMOLITION ACTIVITY | CLASS 3 LOCATION | 42000 | 50454.751558662402 | 0 | 0 | 0 | 0 | 26000 | 31233.893822029106 | TREATMENT AND EMERGENCY TRANSPORT TO EMPLOYEE |  | 58 | 66.75471698113207547169811320754716981132 |  | 0 | 68058 | 33894.7389854779703180592991913746630728 | 81755.4000976726400754716981132075471698 | 0 | 0 | 0 |  |  |  |  | 60 | 60 | 200 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 6 | 0 | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | DURING REMOVAL OF A VESSEL A MINOR FIRE IGNITED RESULTED FROM RESIDUE IN THE PIPE WHICH MELTED A 2 IN POLY BY-PASS TO SUPPLY THE DISTRIBUTION SYSTEM. | [47 empty] | RAYMOND E. HOLBERT | SUPERINDENANT | publicworks@hookeroklahoma.net | 580-652-2885 | 580-652-2488 |  |  |  | RAYMOND E. HOLBERT | SUPERENTIDENT | 580-652-2885 | publicworks@hookeroklahoma.net
2025-03-31 10:13 | YES | NO | NO | 20160084 | 16818 | 2016-09-09 19:26 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2016-08-10 15:15 |  |  | 2016 | 1041 W CAMBRIDGE AVE | VISALIA | TULARE | CA | 93277 | 36.3145 | -119.3028 | [9 empty] | 2016-08-10 05:40 | 1155896 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-08-10 15:15 |  |  |  | 2016-08-10 15:21 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2007 | [8 empty] | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | THE METER SET ASSEMBLY WAS MELTED DURING THE FIRE | CLASS 3 LOCATION | 184000 | 221039.863971282904 | 2749 | 3302.383619875308169 | 200 | 240.2607217079162 | 6000 | 7207.821651237486 | CONTENTS VALUE |  | 0 | 0 |  | 0 | 192949 | 96000.602966181817029 | 231790.329964103614369 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 626-893-4536 | kle2@semprautilities.com | ON AUGUST 10, 2016 AT 15:15, VISALIA POLICE DEPARTMENT REPORTED A HOUSE FIRE AT 1041 W CAMBRIDGE AVE IN VISALIA. CREW RESPONDED AND WAS INFORMED BY THE VISALIA FIRE DEPARTMENT THAT THEY HAD ALREADY SHUT OFF THE GAS AT THE STOPCOCK. THE METER SUFFERED DAMAGE FROM THE FIRE AND WAS MELTED. IT IS UNKNOWN TO SOCALGAS AS TO WHEN THE FIRE STARTED OR WHEN THE FIRE WAS CONTROLLED BY THE FIRE DEPARTMENT. NO INJURIES RESULTED FROM THIS INCIDENT. INVESTIGATION INTO THE INCIDENT SHOWED THAT THE CAUSE OF THE FIRE IS UNDETERMINED. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO A GAS RELEASE AND ESTIMATED DAMAGES EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2025-03-31 10:13 | NO | YES | NO | 20160085 | 16721 | 2016-09-09 20:33 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2016-08-10 13:11 |  |  | 2016 | 950 CHAMPION LANE | DEER PARK | NAPA | CA | 94576 | 38.5483 | -122.4737 | [9 empty] | 2016-08-10 14:20 | 1155870 |  | NATURAL GAS |  | 100 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-08-10 13:11 |  |  |  | 2016-08-10 13:11 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1949 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | NATURAL GAS RELEASED FROM THE RISER DURING A VALVE CHANGE, FOLLOWED BY IGNITION | CLASS 1 LOCATION | 150000 | 180195.54128093715 | 31600 | 37961.1940298507596 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 181600 | 90353.9769506896536 | 218156.7353107879096 | 0 | 0 | 1 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 9254137311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLAINCE | 9253285776 | gsr8@pge.com | ON AUGUST 10, 2016 AT 1311 HOURS, PG&E WAS NOTIFIED OF A STRUCTURE FIRE AT 950 CHAMPION LANE IN THE CITY OF DEER PARK. PG&E'S CONSTRUCTION CREW WAS PERFORMING A SERVICE VALVE CHANGE ON A RISER; THERE WAS AN UNINTENTIONAL RELEASE AND IGNITION OF GAS CAUSING THE HOME TO CATCH ON FIRE. THE CAUSE OF INCIDENT IS INCORRECT OPERATIONS. PG&E CREWS STOPPED THE FLOW OF GAS AT 1400 HOURS BY SQUEEZING THE SERVICE LINE; THIS SERVICE LINE HAS BEEN ABANDONED AT THE MAIN. A SPECIAL LEAK SURVEY WAS COMPLETED, NO GAS LEAK WAS DETECTED. FIRE DEPARTMENT, AMBULANCE AND POLICE DEPARTMENT WERE REPORTED ON-SITE. THERE WERE 2 EMPLOYEE INJURIES- ONE WAS TREATED ON SITE FOR A 1ST DEGREE BURN, THE OTHER WAS TREATED AT THE HOSPITAL AND WAS RELEASED THE SAME DAY FOR A 2ND DEGREE BURN. BOTH EMPLOYEES WERE PAT TESTED WITH NEGATIVE RESULTS. NO KNOWN MEDIA ON SITE OR DEATH REPORTED. THIS INCIDENT IS BEING REPORTED TO THE DOT AND CPUC DUE TO THE UNINTENTIONAL RELEASE OF GAS AND REPAIR COSTS ESTIMATED TO EXCEED $50,000. PLEASE NOTE THAT PART A, 13B WAS RESPONDED WITH THE TIME THAT THE SERVICE WAS DEACTIVATED AND THE STUB WAS INSTALLED.
2025-03-31 10:13 | NO | YES | YES | 20160086 | 38837 | 2016-09-09 20:40 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2016-08-11 00:10 | EASTERN | NO | 2016 | 8701 ARLISS ST | SILVER SPRING | MONTGOMERY COUNTY | MD | 20901-3981 | 38.9984 | -77.0011 |  |  | YES | [6 empty] | 2016-08-11 01:31 | 1155909 |  | NATURAL GAS |  | 38 | 0 | YES | 0 | 0 | 0 | 0 | 7 | 7 | YES | 0 | 0 | 1 | 0 | 32 | 33 | YES | 2016-08-11 00:05 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 38 | NO | 200 | 2016-08-11 00:36 |  |  |  | 2016-08-11 00:36 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNDETERMINED | UNKNOWN | [8 empty] | OTHER | UNDETERMINED | [9 empty] | OTHER | [8 empty] | UNDETERMINED | CLASS 4 LOCATION | 1650000 | 1982150.95409030865 | 0 | 0 | 52336 | 62871.425656527511216 | 0 | 0 |  | 3.83 | 146 | 168.037735849056603773584905660377358491 | 0 | 0 | 1702482 | 847142.3814527966654290458221024258760108 | 2045190.41748268521781977358490566037736 | 0 | 0 | 30 | 0 | 0 | 3 | 0 | 20 | 20 | 25 | 192.619(A)(4) | 1955-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | CAUSE OF INCIDENT IS UNDETERMINED. | [45 empty] | SHANNON B. MALONEY | MANAGER PIPELINE SAFETY COMPLIANCE AND QUALITY | smaloney@washgas.com | 7037505558 |  | RICHARD FITZPATRICK | richardfitzpatrick@washgas.com | 7036397825 | STEPHEN PRICE | AVP SAFETY QUALITY SYSTEM PROTECTION | 703-750-4586 | sprice@washgas.com | ON AUGUST 10, 2016 AN EXPLOSION AND FIRE OCCURRED AT 8701 ARLISS STREET IN SILVER SPRING, MARYLAND. THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB) CONCLUDED THAT THE PROBABLE CAUSE OF THE EXPLOSION IN BUILDING 8701 WAS THE FAILURE OF AN INDOOR MERCURY SERVICE REGULATOR. WASHINGTON GAS BELIEVES THE EVIDENCE, INCLUDING MULTIPLE SOURCES OF NATURAL GAS ONSITE THAT COULD HAVE CONTRIBUTED TO THE INCIDENT, DOES NOT PERMIT A CONCLUSIVE DETERMINATION OF PROBABLE CAUSE. THUS, FOR THE PURPOSES OF THIS REPORT, WASHINGTON GAS AVERS THAT THE ACTUAL CAUSE REMAINS UNDETERMINED. NONETHELESS, WASHINGTON GAS HAS IMPLEMENTED ALL SAFETY RECOMMENDATIONS PROMULGATED BY THE NTSB WITH RESPECT TO THE INCIDENT, INCLUDING EXPEDITED REMOVAL OF MERCURY SERVICE REGULATORS REMAINING ON THE COMPANY'S SYSTEM. THE MARYLAND PUBLIC SERVICE COMMISSION APPROVED WASHINGTON GAS' EXPEDITED REMOVAL PROGRAM ON DECEMBER 18, 2020. OPERATOR NOTE: REFERENCE PART A, QUESTION 21.D, "NO" IS SELECTED BECAUSE OPTION OF "UNKNOWN" IS NOT PROVIDED.
2025-03-31 10:13 | NO | YES | YES | 20160087 | 30154 | 2016-09-10 01:38 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2016-01-07 15:05 |  |  | 2016 | 10753 SANTA ROSA RD | CAMARILLO | VENTURA | CA | 93012 | 34.2373 | -118.9173 | [9 empty] | 2016-08-12 08:35 | 1156034 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2016-01-07 15:05 |  |  |  | 2016-01-07 15:17 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1977 | [5 empty] | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 100000 | 120130.3608539581 | 320521 | 385043.033912715041701 | 200 | 240.2607217079162 | 0 | 0 |  |  | 0 | 0 |  | 0 | 420721 | 209327.178065369503041 | 505413.655488381057901 | 0 | 0 | 1 |  |  |  |  | 45 | 45 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [6 empty] | YES | ROCK IMPINGMENT | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | KHOA LE | SR PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | KHOA LE | SR PIPELINE SAFETY AND COMPLIANCE ADVISOR | 626-893-4536 | kle2@semprautilities.com | ON JANUARY 7/2016 AT 15:05, SOCALGAS WAS NOTIFIED OF A FIRE AT 10753 SANTA ROSA RD IN CAMARILLO. METER WAS SECURED BY VENTURA COUNTY FIRE DEPARTMENT. CUSTOMER SERVICE PERFORMED A CLOCK TEST THAT SHOWED A 1.5 CFH HOUSELINE LEAK; THE METER WAS BLANKED TO CONFIRM. AN 1813 NOTICE WAS ISSUED AND THE METER WAS LEFT OFF. THERE WAS NO DAMAGE TO THE MSA. PER THE VENTURA COUNTY FIRE DEPARTMENT ARSON INVESTIGATOR, THE FUEL FOR THE FIRE WAS PROPANE STORED IN THE GARAGE; THE IGNITION SOURCE SUSPECTED TO BE THE GARAGE TENANT LIGHTING INCENSE. ONE PERSON, THE GARAGE TENANT, SUFFERED INJURIES. THE INDIVIDUAL WAS TRANSPORTED TO THE HOSPITAL AND ADMITTED. SAMPLING USING A SENSIT G2 WAS NEGATIVE EXCEPT NEAR RISER. MSA WAS SOAPED; NO LEAKS FOUND. CUSTOMER SERVICE REQUESTED DISTRIBUTION TO FOLLOW UP THE NEXT DAY. THE CUSTOMER HAD THE HOUSELINE LEAK REPAIRED ON OR ABOUT JANUARY 15/2016 AND SERVICE WAS RESTORED JANUARY 16/2016 ON JANUARY 8/2016, DISTRIBUTION FOLLOWED UP WITH A BAR PER POLICY AND OBTAINED POSITIVE READINGS BOTH AT THE PROPERTY AND IN SANTA ROSA RD THAT COULD POTENTIALLY RELATED TO A MAIN LEAK. ADDITIONALLY, THE SERVICE LINE TO 10753 SANTA ROSA RD. WAS CUT AND TESTED; NO LEAKS FOUND. THERE IS NO EVIDENCE THE MAIN LEAK WAS RELATED TO THE SUBJECT INCIDENT. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO AN INDIVIDUAL THAT WAS ADMITTED TO THE HOSPITAL AND THE DISCOVERY OF A GAS LEAK ON THE MAIN. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536. UPDATED INFORMATION: THE FIRE DEPARTMENT RULED OUT PROPANE INVOLVEMENT. UPDATED 3/3/18: LEAK LOCATION: PIPE WALL, LONGITUDINAL CRACK LEAK CAUSE: EXTERNAL POINT LOAD FROM ROCK IMPINGEMENT, INSTALLATION DEFECT
2025-03-31 10:13 | NO | NO | NO | 20160088 | 16388 | 2016-09-12 14:34 | ORIGINAL FINAL | 2604 | COLUMBIA GAS OF VIRGINIA INC | 1809 COYOTE DRIVE | CHESTER | VA | 23836 | 2016-08-29 16:00 |  |  | 2016 | SIGNAL HILL RD | MANASSAS | PRINCE WILLIAM | VA | 20110 | 38.7488 | -77.4483 | [9 empty] | 2016-08-30 16:24 | 1157709 |  | NATURAL GAS |  | 46.33 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 40 | 2016-08-29 16:33 |  |  |  | 2016-08-29 16:50 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 67 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1994 | [5 empty] | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | OTHER | ADYLA |  |  | UNKNOWN |  | MECHANICAL PUNCTURE | 3 | 5 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 4000 | 4805.214434158324 | 0 | 0 | 0 | 0 |  |  | 11675 | 13437.2641509433962264150943396226415094 |  | 0 | 15675 | 14420.4317684497109541778975741239892183 | 18242.4785851017202264150943396226415094 | 0 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | GAS CONTROL IDENTIFIED LOW PRESSURE BY ALARM WHICH WAS INVESTIGATED WHICH REVEALED DAMAGE TO OUR FACILITY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 623601311 |  |  | CONTRACT LOCATOR | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | GUY DAILEY |  | gdailey@nisource.com | 804-314-9390 |  |  |  |  | GUY DAILEY |  | 804-314-9390 | No Email Address | THIRD PARTY CONTRACTOR (ALWAYS PREPARED) WAS BORING IN FIBER CONDUIT. DURING BACK REAMING OPERATIONS, HEAD IMPACTED 4" PLASTIC MAIN AND TORE 3 X 5 HOLE IN TOP. THIS SECTION OF MAIN WAS NOT LOCATED AND THUS NOT SPOTTED PRIOR TO BORE. WGL 8" MAIN HAD TO BE BY PASSED IN ORDER TO SAFELY MAKE REPAIRS. WGL MADE SAFE. CGV MADE REPAIRS TO 4" MAIN DAMAGED AFTER DEMARK VALVE. NO OUTAGES OR OTHER DAMAGES.
2025-03-31 10:13 | NO | NO | NO | 20160089 | 16449 | 2016-09-16 15:06 | SUPPLEMENTAL FINAL | 11032 | LACLEDE GAS CO | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2016-08-17 08:06 |  |  | 2016 | 3401 HARRY S TRUMAN BLVD | SAINT CHARLES | SAINT CHARLES | MO | 63301-4050 | 38.8043 | -90.5549 | [9 empty] | 2016-08-17 13:58 | 1156548 |  | NATURAL GAS |  | 170.82 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-08-17 08:06 |  |  |  | 2016-08-17 08:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1986 | [5 empty] | 4 | ASTM D2513 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.5 |  | 2306 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 3977 | 4777.584451161913637 | 52271 | 62793.340921972438451 | 0 | 0 |  |  | 733 | 843.64150943396226415094339622641509434 |  | 0 | 56981 | 28766.2685360260888069218328840970350404 | 68414.5668825683143521509433962264150943 | 3 | 0 | 581 |  |  |  |  | 19.1 | 19.1 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CAUSED BY A THIRD PARTY EXCAVATION DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER |  |  |  | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 162300442 |  |  | CONTRACT LOCATOR | YES | YES | 7 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | PATRICK SEAMANDS | MANAGER OF PIPELINE SAFETY AND COMPLIANCE | patrick.seamands@spireenergy.com | 314-349-2936 |  |  |  |  | CRAIG HOEFERLIN | VICE PRESIDENT OF OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | A CONTRACTOR WAS INSTALLING WATER MAIN AND STRUCK A 4" PLASTIC GAS DISTRIBUTION MAIN WHILE EXCAVATING WITH A BACKHOE. LOCATES WERE MADE BY THE CONTRACT LOCATOR BUT THE GAS MAIN WAS MIS-LOCATED. ADEQUATE GAS PRESSURE COULD NOT BE MAINTAINED TO MAKE REPAIRS TO THE GAS DISTRIBUTION MAIN WHICH RESULTED IN THE LOSS OF GAS SERVICE TO 584 CUSTOMERS.
2025-03-31 10:13 | NO | YES | YES | 20160090 | 16458 | 2016-09-19 15:30 | SUPPLEMENTAL FINAL | 13360 | ENTERGY NEW ORLEANS, INC | 3700 TULANE AVENUE L-TUL-111 | NEW ORLEANS | LA | 70119 | 2016-08-18 13:10 |  |  | 2016 | 12425 OLD GENTILLY ROAD | NEW ORLEANS | ORLEANS | LA | 70129 | 30.0074 | -89.9389 | [9 empty] | 2016-08-18 18:26 | 1156669 |  | NATURAL GAS |  | 1795 |  | NO | [5 empty] | 0 | YES | 2 | 0 | 0 | 0 | 0 | 2 | NO |  |  |  |  | NO | 0 | 2016-08-18 13:10 |  |  |  | 2016-08-18 13:10 |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 72 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1964 | [5 empty] | 20 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.375 | [6 empty] | OTHER | [8 empty] | SUDDEN HIGH PRESSURE GAS RELEASE DUE TO PIPE BLOWING OUT OF A MECHANICAL COUPLING AFTER SERVICE LINE WAS CUT AND CAPPED TO ISOLATE FEED TO A DECOMMISSIONED POWER PLANT. THERE WAS NO IGNITION AND NO EXPLOSION. | CLASS 3 LOCATION | 0 | 0 | 26000 | 31233.893822029106 | 0 | 0 | 0 | 0 | ALL ESTIMATES INCLUDED IN 2B. THE ORIGINAL ESTIMATE OF 75,000 WAS OVERSTATED. |  | 6565 | 7555.943396226415094339622641509433962264 |  | 0 | 32565 | 19925.832101392123897574123989218328841 | 38789.8372182555210943396226415094339623 | 0 | 0 | 0 |  |  |  |  | 123 | 125 | 149 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | EMPLOYEES ON SITE WORKING ON THE SERVICE LINE WHEN THE INCIDENT OCCURED. |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSE IS UNDER INVESTIGATION BUT THE C&M PERSONNEL ON THE SCENE PERFORMING THE WORK WERE THE CAUSE OF OR A CONTRIBUTING FACTOR TO THE INCIDENT | [12 empty] | YES | 11 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | BOLTED |  | COUPLING |  | DRESSER |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | 20 INCH DIAMETER PIPE SEGMENT BLEW OUT OF A COUPLING AFTER THE PIPE WAS GAPPED DOWNSTREAM OF THE COUPLING. COUPLING WAS CONSTRAINED AND ANCHORED PRIOR TO BEING GAPPED. ONCE GAP SEGMENT WAS REMOVED THE PIPE WAS NO LONGER CONSTRAINED AND THE EXISTING ANCHORING WAS NOT SUBSTANTIAL ENOUGH TO RESIST THE BLOW OUT. |  |  | YES |  |  |  |  | NO | [86 empty] | LEON T HINSON | SENIOR ENGINEER - REGULATORY COMPLIANCE | lhinson@entergy.com | 504-595-3722 | 504-593-3440 |  |  |  | DAVID B PETERSON | MANAGER - ENGINEERING AND COMPLIANCE | 504-595-3725 | dpeter4@entergy.com | OVER THE PAST SEVERAL YEARS, ENTERGY FOSSIL GROUP HAD DEACTIVATED ITS THREE EXISTING ELECTRIC GENERATION UNITS AT THE MICHOUD POWER PLANT IN EASTERN NEW ORLEANS. IN EARLY 2016, ENTERGY FOSSIL GROUP REQUESTED ENOI GAS OPERATIONS TO PHYSICALLY SEPARATE THE TWO GAS SERVICES THAT DELIVERED GAS FROM THE ENOI DISTRIBUTION MAIN ON PARIS RD TO THE GENERATING UNITS FROM THE POWER PLANT. ALL GAS WORK WAS PERFORMED BY ENOI GAS OPERATION PERSONNEL. THE SCOPE OF WORK WAS TO CLOSE THE SERVICE VALVES SERVING THE PLANT, PURGE THE SERVICE LINES, CUT AND WELD A STEEL CAP ON BOTH THE UPSTREAM AND DOWNSTREAM ENDS TO PROVIDE PHYSICAL SEPARATION. INITIAL WORK WAS ON THE 20 INCH LINE FEEDING MICHOUD UNITS 1 AND 2. PRIMARY WORK ONSITE WAS: 1. EXCAVATING THE SERVICE TO GAIN ACCESS TO THE LINE. EXCAVATION DIMENSIONS WERE APPROXIMATELY 8 FEET WIDE BY 15 FEET LONG BY 8 FEET DEEP TO ALLOW FOR COMPLETE 360° ACCESS TO SERVICE. 2. PURGING THE SERVICE LINE WITH INERT GAS, AND THEN GAPPING THE SERVICE TO ISOLATE THE DOWNSTREAM SEGMENT INTO THE PLANT. 3. WELDING STEEL CAPS ON BOTH SIDES OF THE NEW GAP. 4. OPENING THE SERVICE VALVE TO RE-PRESSURIZE THE SERVICE LINE UPSTREAM OF THE GAP. WITHIN 3 MINUTES OF HAVING THE UPSTREAM VALVE FULLY OPEN, THE PRESSURE RELEASE OCCURRED (13:10 CST). APPROXIMATELY 10 FEET UPSTREAM OF THE EXCAVATION, THE GAPPED SERVICE SEGMENT WAS BLOWN OUT OF A STRAPPED STYLE 40 DRESSER COUPLING. THE SERVICE VALVE WAS CLOSED WITHIN 7 MINUTES. THE RESULT OF THE BLOWOUT BUCKLED AND CRACKED CONCRETE ROADWAY, BLEW ALL THE DIRT UNDERNEATH ROADWAY AND DOWNSTREAM OF THE COUPLING INTO AND OUT OF THE EXCAVATION. SEVEN EMPLOYEES RECEIVED MINOR INJURIES AND WERE TREATED AND RELEASED. TWO EMPLOYEES RECEIVED INJURIES SEVERE ENOUGH TO REQUIRE HOSPITALIZATION FOR AN EXTENDED PERIOD. PHMSA STATE PARTNER, LA DNR, OFFICE OF CONSERVATION, PIPELINE DIVISION WAS NOTIFIED AT 14:05 CST THAT THE INCIDENT HAD OCCURRED, WHICH WAS WITHIN ONE HOUR OF FIRST KNOWLEDGE OF THE GAS RELEASE. ENTERGY NOTIFIED PHMSA VIA THE NATIONAL RESPONSE CENTER AT 18:26 CST WHEN IT BECAME APPARENT THE EVENT MET THE REQUIREMENTS OF AN 'INCIDENT'. ENTERGY SUBMITTED THE REQUIRED INCIDENT REPORT AND ORIGINALLY CLASSIFIED THE EVENT AS 'OTHER' BUT UPON FURTHER INVESTIGATION AND GATHERING MORE FACTS, RE-CLASSIFIED THE CAUSE AS PIPE, WELD, OR JOINT FAILURE (MECHANICAL FITTING FAILURE).
2025-03-31 10:13 | NO | YES | NO | 20160091 | 16439 | 2016-09-21 09:20 | SUPPLEMENTAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY | CANONSBURG | PA | 15317 | 2016-08-25 17:58 |  |  | 2016 | 3316 CARLISLE PIKE | NEW OXFORD | ADAMS | PA | 17350 | 39.8715 | -77.0278 | [9 empty] | 2016-08-25 21:05 | 1157352 |  | NATURAL GAS |  | 12750 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 150 | 2016-08-25 17:56 |  |  |  | 2016-08-25 18:30 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1994 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | VEHICLE STRUCK VALVE ASSEMBLY | [5 empty] | CLASS 2 LOCATION | 8000 | 9610.428868316648 | 6 | 7.207821651237486 | 15732 | 18898.908369544688292 | 1758 | 2111.891743812583398 | XRAYS OF ALL THE WELDS IN THE VICINITY OF THE DAMAGE. |  | 36847 | 42408.8113207547169811320754716981132075 |  | 0 | 62343 | 51916.0133589448188079137466307277628032 | 73037.2481240798741571320754716981132075 | 0 | 0 | 0 |  |  |  |  | 830 | 830 | 936 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OPERATOR'S CONTRACTOR | [167 empty] | RICK BURKE | OPERATIONS COMPLIANCE MANAGER | rburke@nisource.com | 724-416-6332 | 724-416-6385 |  |  |  | MIKE DAVIDSON | VP AND GENERAL MANAGER OF COLUMBIA GAS OF PA | 724-416-6308 | mdavids@nisource.com | ON 8/25/2016 AT 17:56 AN EMPLOYEE OF BOBZILLA LANDSCAPING, A CONTRACTOR FOR COLUMBIA GAS OF PENNSYLVANIA, WAS LEAVING COLUMBIA'S REGULATOR SITE AT 3316 CARLISLE PIKE, NEW OXFORD, PENNSYLVANIA WHEN HIS VEHICLE STRUCK AND SHEARED OFF A 2 INCH FITTING ON AN ABOVE GROUND VALVE ASSEMBLY, RESULTING IN THE RELEASE OF GAS AT 830 PSIG. 12,750 MCF NATURAL GAS WAS LOST. FURTHER, THERE WAS NO IGNITION, NO INJURIES, OR FATALITIES AS A RESULT OF THIS INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20160093 | 16394 | 2016-09-21 20:48 | ORIGINAL FINAL | 18112 | SAN DIEGO GAS & ELECTRIC CO | 8326 CENTURY PARK COURT | SAN DIEGO | CA | 92123 | 2016-08-22 14:42 |  |  | 2016 | 1703 BACON ST | SAN DIEGO | SAN DIEGO | CA | 92107 | 32.7438 | -117.2535 | [9 empty] | 2016-08-22 20:58 | 115704 |  | NATURAL GAS |  | 210 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 100 | 2016-08-22 14:42 |  |  |  | 2016-08-22 16:47 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1942 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | LEAK - CAUSE UNDETERMINED | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 85000 | 102110.806725864385 | 0 | 0 | 0 | 0 |  |  | 1260 | 1450.188679245283018867924528301886792453 |  | 0 | 86260 | 43632.7431388555491509433962264150943396 | 103560.9954051096680188679245283018867925 | 0 | 0 | 180 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 626-893-4536 | kle2@semprautilities.com | ON AUGUST 22, 2016 AT 14:42, SDG&E WAS NOTIFIED OF A GAS LEAK AT 1703 BACON ST IN SAN DIEGO. CREWS RESPONDED AND CONTROLLED THE GAS BY SHUTTING OFF THE MAIN. FURTHER LEAK INVESTIGATION SHOWED THAT THE LEAK WAS LOCATED ON A 0.75 INCH STEEL SERVICE. THE CAUSE OF THE LEAK IS UNDETERMINED. NO INJURIES RESULTED FROM THIS INCIDENT. ALL REPAIRS TO THE DAMAGED SERVICE WERE COMPLETED AND THE AFFECTED CUSTOMERS WERE RESTORED. THIS INCIDENT WAS REPORTED TO CPUC AND DOT DUE TO A GAS RELEASE OF UNDETERMINED CAUSE AND DAMAGES THAT EXCEED $50,000. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2025-03-31 10:13 | NO | NO | NO | 20160094 | 16395 | 2016-09-23 09:32 | ORIGINAL FINAL | 13061 | NATIONAL FUEL GAS DISTRIBUTION CORP | 6363 MAIN ST. | WILLIAMSVILLE | NY | 14221 | 2016-08-24 18:22 |  |  | 2016 | 11466 STATE HWY 618 | CONNEAUT LAKE | CRAWFORD | PA | 16316-2828 | 41.6215 | -80.3256 | [9 empty] | 2016-08-24 18:22 | 1157237 |  | NATURAL GAS |  | 68.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 5 | 2016-08-24 10:38 |  |  |  | 2016-08-24 11:07 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1982 | [5 empty] | 4 | ASTM D2513 | UPONOR DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | MECHANICAL PUNCTURE | 5 | 3.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 83962 | 100863.853580200299922 | 1000 | 1201.303608539581 | 0 | 0 |  |  | 534 | 614.603773584905660377358490566037735849 |  | 0 | 85496 | 42840.8715101010989993045822102425876011 | 102679.7609623247865823773584905660377358 | 18 | 2 | 433 |  |  |  |  | 35 | 35 | 41 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | AUGER | POLE | YES | 20162211567 |  |  | CONTRACT LOCATOR | YES | YES | 35 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | STEVEN MONNIE | ENGINEER I | monnies@natfuel.com | 814-871-8204 | 814-871-4623 |  |  |  | KURT W MEIGHEN | SUPERINTENDENT | 814-371-5870 | meighenk@natfuel.com | AT APPROXIMATELY 10:40 AM ON WEDNESDAY, AUGUST 24, 2016, A CONTRACTOR USING AN AUGER TO INSTALL A UTILITY POLE STRUCK A 4" NATURAL GAS MAIN RESULTING IN AN UNINTENTIONAL RELEASE OF NATURAL GAS. THERE WERE NO INJURIES OR FATALITIES. A ONE-CALL REQUEST TO MARK UNDERGROUND FACILITIES WAS MADE PRIOR TO THE EXCAVATION ACTIVITY. INVESTIGATION INTO THE INCIDENT REVEALED THAT THE LOCATING SIGNAL HAD DRIFTED TO AN ADJACENT ABANDONED STEEL GAS MAIN LOCATED APPROXIMATELY 2' - 3' AWAY FROM THE ACTIVE 4" PLASTIC GAS MAIN.
2025-03-31 10:13 | NO | YES | NO | 20160096 | 16519 | 2016-09-26 17:26 | SUPPLEMENTAL FINAL | 6720 | ATMOS ENERGY CORPORATION - COLORADO/KANSAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2016-08-20 12:30 |  |  | 2016 | APPROXIMATE INTERSECTION OF ROAD 30 AND ROAD I | Not Within a Municipality | HAMILTON | KS | 67878 | 37.8515 | -101.8998 | [9 empty] | 2016-09-09 14:51 | 1158594 |  | NATURAL GAS |  | 45420 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-08-31 12:15 |  |  |  | 2016-08-31 12:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 3 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.6 | 1.3 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 5000 | 6006.518042697905 | 1000 | 1201.303608539581 | 0 | 0 |  |  | 136260 | 156827.5471698113207547169811320754716981 |  | 0 | 142260 | 148059.9266284158063234501347708894878706 | 164035.3688210488067547169811320754716981 | 0 | 0 | 0 |  |  |  |  | 218 | 257 | 285 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE MONITORING POINT DID NOT REACH THE LOW ALARM LIMIT | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | [14 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | NO |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | NO ONE-CALL NOTIFICATION COUPLED WITH SHALLOW MAIN | [169 empty] | DOUGLAS SHATAS | COMPLIANCE MANAGER | doug.shatas@atmosenergy.com | 8168630951 |  |  |  |  | DOUGLAS SHATAS | MANAGER OF COMPLIANCE | 816-863-0951 | doug.shatas@atmosenergy.com | FARMER DAMAGED MAIN WITH A ROOT CUTTING IMPLEMENT IN A REMOTE AREA WHERE WATER RUNOFF CAUSED MAIN TO BECOME SHALLOW. THE FARMER WAS NOT AWARE OF THE DAMAGE, THEREFORE DID NOT REPORT TO THE UTILITY. SEVERAL DAYS LATER, COMPANY CREWS WERE IN PROCESS OF REPAIRING A LEAK ON THE SAME LINE WHEN THE PRESSURE WAS DISCOVERED TO BE LOWER THAN NORMAL, BUT HIGHER THAN THE LOW ALARM LIMIT OF THE REMOTE PRESSURE MONITORS. THE OPERATOR PERSONNEL THEN BEGAN INVESTIGATING AND FOUND THE LOCATION OF THE DAMAGE. VALVES WERE UTILIZED TO SHUT DOWN A SHORT SECTION OF MAIN BEING FED FROM 2 DIRECTIONS, WHICH ALLOWED THE DAMAGE TO BE REPAIRED.
2025-03-31 10:13 | NO | YES | YES | 20160097 | 16398 | 2016-09-27 16:17 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2016-08-28 21:07 |  |  | 2016 | CAREY RD AND STATE ROUTE 9 | SALEM | COLUMBIANA | OH | 44460 | 40.8713 | -80.8853 | [9 empty] | 2016-08-28 22:55 | 115559 |  | NATURAL GAS |  | 121 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2016-08-28 21:30 |  |  |  | 2016-08-28 22:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | DAMAGE BY CAR SHEARING OFF A ONE INCH RELIEF VALVE ON STATION PIPING. | CLASS 3 LOCATION | 4000 | 4805.214434158324 | 438205 | 526417.247780087092105 | 43608 | 52386.447761194048248 | 0 | 0 |  |  | 385 | 443.113207547169811320754716981132075472 |  | 0 | 486198 | 242123.2129530281992635660377358490566038 | 584052.0231829866341643207547169811320755 | 0 | 0 | 74 |  |  |  |  | 17 | 17 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ROB SMITH | OPERATIONS COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB SMITH | OPERATIONS COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | A DRIVER HEADED NORTHBOUND ON STATE ROUTE 9 LOST CONTROL OF HER VEHICLE ON WET PAVEMENT AND STRUCK A TELEPHONE POLE, A TREE, AND THE CAREY ROAD AND STATE ROUTE 9 REGULATOR STATION BUILDING. THE VEHICLE IMPACT SHEARED OFF A ONE-INCH PRESSURE RELIEF VALVE RESULTING IN THE IGNITION OF THE ESCAPING GAS AND CAUSING FIRE DAMAGE TO THE REGULATOR BUILDING, THE REGULATOR STATION AND THE VEHICLE. THE STATION'S MONITOR AND CONTROL REGULATORS FAILED OPEN DUE TO HEAT DAMAGE. AT THE TIME OF THE INCIDENT COLUMBIA'S PIPELINE WAS OPERATING AT A PRESSURE OF 17 PSIG, AND COLUMBIA'S ENGINEERS CALCULATED THAT THE PRESSURE SUBSEQUENTLY REACHED APPROXIMATELY 120 PSIG. THE DRIVER OF THE CAR SUSTAINED BURNS AND WAS LIFE-FLIGHTED TO A NEARBY HOSPITAL. COLUMBIA LEAK SURVEYED THE ENTIRE SYSTEM AND REPLACED APPROXIMATELY 1300 FEET OF FIRST GENERATION PLASTIC MAIN LINE ALONG WITH NUMEROUS SERVICE LINES AND ALL OF THE SERVICE REGULATORS IN THE SYSTEM. PLEASE CONSIDER THIS A FINAL REPORT.
2025-03-31 10:13 | NO | YES | NO | 20160098 | 16399 | 2016-09-27 16:23 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2015-12-03 15:30 |  |  | 2015 | 7147 GERMANO RD. SE | CARROLTON | CARROLL | OH | 44615 | 40.4636 | -81.0021 | [9 empty] | 2016-08-22 12:05 | 1156976 |  | NATURAL GAS |  | 9.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2015-12-03 15:30 |  |  |  | 2015-12-03 15:48 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 18 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1967 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 3 LOCATION | 129490 | 156845.82626916852798 | 15694 | 19009.486427278792788 | 1700 | 2059.1389656157734 | 0 | 0 |  |  | 37 | 37.08685446009389671361502347417840375587 |  | 0 | 146921 | 73721.1374955450716978779342723004694836 | 177951.5385165231880647136150234741784038 | 0 | 0 | 34 |  |  |  |  | 2.7 | 2.7 | 4 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | HOMEOWNER |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | MILLING EQUIPMENT | ROAD WORK | NO | [5 empty] | YES | 24 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | ROB SMITH | OPERATIONS COMPLIANCE MANAGER | rrsmith@nisource.com | 6148182110 | 6148182151 |  |  |  | ROB SMITH | OPERATIONS COMPLIANCE MANAGER | 6148182110 | rrsmith@nisource.com | ON DECEMBER 03, 2015 A CONTRACTOR WAS GRINDING ROADWAY PAVEMENT WITHOUT A VALID ONE CALL TICKET AND STRUCK A 2 INCH BARE STEEL MAIN LINE. A SMALL GAS FED FIRE IGNITED UNDER THE GRINDING MACHINE THAT WAS PROMPTLY EXTINGUISHED. AT THE TIME OF THE INCIDENT COLUMBIA GAS OF OHIO INC. (COLUMBIA) BELIEVED THAT THE GRINDING EQUIPMENT SUSTAINED ONLY MINOR DAMAGE. SINCE THE TIME OF THE EXCAVATION DAMAGE COLUMBIA HAS LEARNED THAT DAMAGE TOTALS HAVE EXCEEDED THE ESTIMATED PROPERTY DAMAGE REPORTING REQUIREMENTS IN 191.3. PLEASE CONSIDER THIS A FINAL REPORT.
2025-03-31 10:13 | NO | YES | YES | 20160100 | 16777 | 2016-09-29 13:53 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2016-09-01 15:10 |  |  | 2016 | 98 FIR DRIVE | WINTER PARK | GRAND | CO | 80482 | 39.8919 | -105.7664 | [9 empty] | 2016-09-01 16:15 | 1157922 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 3 | 2016-09-01 15:10 |  |  |  | 2016-09-01 15:10 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | 250000 | 300325.90213489525 | 69000 | 82889.948989231089 | 14000 | 16818.250519554134 | 0 | 0 |  |  | 5 | 5.75471698113207547169811320754716981132 |  | 0 | 333005 | 165687.4507881284638894878706199460916442 | 400039.8563606616050754716981132075471698 | 0 | 0 | 14 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA MONITORED PRESSURE ONLY, AND PRESSURE DID NOT VARY BEYOND NORMAL RANGE. | [12 empty] | YES | 1 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1990 | NO | YES | YES |  |  | 2016 |  |  |  |  | NO | COAL TAR | [21 empty] | 2011-08-24 | NO | [227 empty] | KELLI BRADLEY | ENGINEER | kelli.s.bradley@xcelenergy.com | 303-571-3341 |  |  |  |  | MARK NOLAN | PRINCIPAL ENGINEER | 303-571-3931 | mark.nolan@xcelenergy.com | ON SEPTEMBER 1, 2016, AN EXPLOSION OCCURRED AT 98 FIR DRIVE IN WINTER PARK, CO. ONE PERSON WAS INJURED AND REQUIRED HOSPITALIZATION. THE LEAK ORIGIN AND CAUSE ARE STILL UNDER INVESTIGATION AS NOTED IN PART G RESPONSE. PLEASE NOTE THAT PORTAL REQUIRES ANSWERS TO PART B AND C IN ORDER TO SUBMIT THE REPORT. THE ANSWERS ARE NOT KNOWN AT THIS TIME. PLACEHOLDER RESPONSES WILL BE REPLACED WITH TRUE VALUES WHEN FINAL REPORT IS SUBMITTED. SUPPLEMENTAL: THE CAUSE OF THE PINHOLE LEAK IS EXTERNAL CORROSION. THE MAIN WAS FOUND TO BE IN CONTACT WITH ROCKS WHICH IN TURN HAD CAUSED THE PIPE TO CORRODE. NO DISBANDING OR OTHER PIPE DAMAGE WAS FOUND DURING THE INVESTIGATION. SECOND SUPPLEMENTAL: IN PART A INDICATED IGNITION = YES. THERE WAS A FLASH EXPLOSION THAT DID NOT RESULT IN SUSTAINED FIRE, SO ORIGINAL REPORT INDICATED NO IGNITION.
2025-03-31 10:13 | NO | YES | NO | 20160101 | 31686 | 2016-10-05 14:20 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2016-09-02 20:58 |  |  | 2016 | 2113 FRIENDSHIP ROAD | BUFORD | HALL | GA | 30519 | 34.1075 | -83.8784 | [9 empty] | 2016-09-03 20:14 | 1158091 |  | NATURAL GAS |  | 7300 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2016-09-02 20:58 |  |  |  | 2016-09-02 21:39 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 108 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | 6-INCH POSI-HOLD COUPLING | 2011 | [8 empty] | OTHER | 6-INCH POSI-HOLD COUPLING | [9 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 34000 | 40844.322690345754 | 82730 | 99383.84753447953613 | 0 | 0 |  |  | 19856 | 22853.1320754716981132075471698113207547 |  | 0 | 136586 | 79218.7876501691346642318059299191374663 | 163081.3023002969882432075471698113207547 | 9 | 5 | 438 |  |  |  |  | 343 | 280 | 300 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRELIMINARY INVESTIGATION DETERMINED THAT THE CONTROLLER(S) AND/OR CONTROL ROOM DID NOT CONTRIBUTE TO THE INCIDENT | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 585-3552 | rlonn@southernco.com | A 6-INCH HP STEEL MAIN WITH A BULL PLUG END CONNECTED BY A STYLE 700 POSI-HOLD COMPRESSION COUPLING (MARKED WITH A 300 PSI PRESSURE RATING AND TESTED TO 2X WORKING PRESSURE (600 PSI) IN THE FACTORY DURING PRODUCTION) SEPARATED FROM THE MAIN. AS A RESULT OF THE SEPARATION, GAS SERVICE TO 452 CUSTOMERS WAS INTERRUPTED TO MAKE REPAIRS TO THE MAIN. AT THIS POINT IT WAS DETERMINED THAT THE INCIDENT RESULTED IN A COST MEETING THE THRESHOLD FOR REPORTING. PRIOR TO THE SEPARATION, THE MAIN ASSOCIATED WITH THE POSI-HOLD COMPRESSION COUPLING EXPERIENCED AN INCREASE IN PRESSURE APPROXIMATELY 10 PSIG ABOVE 110% OF MAOP. THE OVER-PRESSURE ABOVE THE ALLOWED 10% BUILD-UP WAS THE RESULT OF UNDERSIZED PIPING BETWEEN THE REGULATOR AND RELIEF VALVE WHICH LIMITED THE AMOUNT OF FLOW THE RELIEF VALVE COULD PASS TO STAY WITHIN THE NECESSARY TOLERANCE FOR BUILD-UP. THE REGULATOR STATION IN QUESTION HAS SINCE BEEN REBUILT WHERE THE PIPING AND FITTINGS ARE ADEQUATE FOR THE REQUIRED OVER-PRESSURE PROTECTION.
2025-03-31 10:13 | NO | YES | YES | 20160102 | 16659 | 2016-10-12 15:12 | SUPPLEMENTAL FINAL | 10060 | KAPLAN GAS DEPT, CITY OF | 701 NORTH CUSHING AVE | KAPLAN | LA | 70548 | 2016-08-28 02:15 |  |  | 2016 | 500 BLOCK OF EAST VETERANS MEMORIAL DRIVE | KAPLAN | VERMILION | LA | 70548 | 29.997 | -92.2801 | [10 empty] | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 1200 |  | NO | [5 empty] | 0 | YES | 2 | 0 | 0 | 0 | 1 | 3 | NO |  |  |  |  | NO | 0 | 2016-08-28 02:15 |  |  |  | 2016-08-28 03:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | AUTO ACCIDENT CAUSING THE DAMAGE OF VALVES TO RELEASE GAS IN AIR UNTIL SHUT OFF. | CLASS 3 LOCATION | 0 | 0 | 261000 | 313540.241828830641 | 10000 | 12013.03608539581 | 0 | 0 | NONE |  | 5276 | 6072.377358490566037735849056603773584906 |  | 0 | 276276 | 140451.708511928833587601078167115902965 | 331625.6552727170170377358490566037735849 | 96 | 6 | 1538 |  |  |  |  | 90 | 90 | 135 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | CHRISTINE L TRAHAN | CITY CLERK | clerk@cityofkaplan.com | 337 643 8811 | 337 643 8861 |  |  |  | CHRISTINE L TRAHAN | CITY CLERK | 337 643 8811 | clerk@cityofkaplan.com | RESIDENT HIT THE REGULATOR STATION BY AUTOMOBILE. GAS SYSTEM WAS SHUT DOWN AT THE MAIN HUB WHICH FED TO THE HIGH PRESSURE REGULATOR STATION. THE SYSTEM SHALL BE REBUILT WITH A BY-PASS REGULATOR STATION TO RESTORE DOWNSTREAM LOW PRESSURE TO HOSPITAL, NURSING HOMES, SCHOOLS, COMMERCIAL AND RESIDENTIAL CUSTOMERS.
2025-03-31 10:13 | NO | NO | NO | 20160103 | 16461 | 2016-10-12 23:34 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2016-09-13 09:45 |  |  | 2016 | 2711 W 35TH AVE | GARY | LAKE | IN | 46408 | 41.5556 | -87.3703 | [9 empty] | 2016-09-13 14:34 | 1158888 |  | NATURAL GAS |  | 2940 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 6 | 2016-09-13 09:17 |  |  |  | 2016-09-13 09:43 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1979 | [5 empty] | 3 | D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | MECHANICAL PUNCTURE | 3.5 | 1 | [7 empty] | CLASS 3 LOCATION | 80000 | 96104.28868316648 | 15512 | 18634.621575665980472 | 1000 | 1201.303608539581 | 0 | 0 |  |  | 1400 | 1611.32075471698113207547169811320754717 |  | 0 | 97912 | 49509.5254180495046086037735849056603774 | 117551.5346220890226040754716981132075472 | 35 | 0 | 0 |  |  |  |  | 28 | 28 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | AUGER | ELECTRIC | NO |  |  |  | CONTRACT LOCATOR |  | YES | 16 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | LUKE E. SELKING | MANAGER PIPELINE SAFETY AND COMPLIANCE | leselking@nisource.com | 260-433-6115 |  |  |  |  | LUKE E. SELKING | MANAGER PIPELINE SAFETY AND COMPLIANCE | 260-433-6115 | leselking@nisource.com | DAMAGE OCCURRED TO A 3" PLASTIC GAS MAIN BY A TRUCK MOUNTED AUGER PERFORMING AN ELECTRIC POLE INSTALLATION. THE GAS WAS BLOWING FOR APPROXIMATELY 1 HOUR WHEN IT IGNITED WITHOUT WARNING. NO CAUSE FOR IGNITION HAS BEEN DETERMINED. ALL PERSONNEL WERE CLEAR, NO ONE WAS INJURED.
2025-03-31 10:13 | NO | YES | NO | 20160104 | 16515 | 2016-10-14 15:59 | SUPPLEMENTAL FINAL | 31159 | KANSAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2016-09-26 11:35 |  |  | 2016 | 9TH STREET AND MAGNOLIA | SALINA | SALINE | KS | 67401 | 38.7981 | -97.6129 | [9 empty] | 2016-10-14 14:50 | 1161573 |  | NATURAL GAS |  | 512 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 50 | 2016-09-26 11:35 |  |  |  | 2016-09-26 11:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 144 |  | YES |  |  |  |  | YES | CASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1971 | [5 empty] | 4 | ASTM D2513 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 82103 | 98630.630171925218843 | 19692 | 23656.070659361429052 | 0 | 0 |  |  | 2111 | 2429.64150943396226415094339622641509434 |  | 0 | 103906 | 52895.0445879545277367789757412398921833 | 124716.3423407206101591509433962264150943 | 5 | 0 | 0 |  |  |  |  | 25 | 25 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS SECTION OF PIPE NOT REGULATED BY A CONTROL ROOM | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | NO | [7 empty] | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | RANDY SPECTOR | DIRECTOR OF ENGINEERING | randy.spector@onegas.com | (913)530-3219 |  |  |  |  | RANDY SPECTOR | DIRECTOR OF ENGINEERING | (913) 530-3219 | randy.spector@onegas.com | ON 9/26/16 KEMP CONSTRUCTION, A CONTRACTOR FOR AT&T WAS PERFORMING A 2 INCH BORE FOR FIBER OPTIC WHEN THEY STRUCK A 4 INCH STEEL KANSAS GAS DISTRIBUTION MAIN PIPELINE. KEMP DID NOT HAVE VALID LOCATES FOR THIS AREA AT THE TIME OF THE INCIDENT. ON 10/13/16, KGS RECEIVED AN INVOICE FROM THE CONTRACTOR THAT PERFORMED THE REPAIR WORK IN EXCESS OF THE $50,000 THRESHOLD.
2025-03-31 10:13 | NO | YES | NO | 20160105 | 16412 | 2016-10-14 16:18 | ORIGINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2016-09-15 21:00 |  |  | 2016 | IMPERIAL PARKWAY & MEADOWS LANE | BONITA SPRINGS | LEE COUNTY | FL | 34135 | 26.3254 | -81.7625 | [9 empty] | 2016-09-16 09:27 | 1159133 |  | NATURAL GAS |  | 310.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2016-09-15 21:07 |  |  |  | 2016-09-15 21:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 120 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2000 | [5 empty] | 6 | ASTM D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | MECHANICAL PUNCTURE | 1.3 | 1.3 | [7 empty] | CLASS 3 LOCATION | 60000 | 72078.21651237486 | 24000 | 28831.286604949944 | 30000 | 36039.10825618743 | 0 | 0 |  |  | 2528 | 2909.584905660377358490566037735849056604 |  | 0 | 116528 | 59411.54394529115572506738544474393531 | 139858.1962791726113584905660377358490566 | 0 | 0 | 0 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS CAUSED BY A THIRD PARTY EXCAVATOR | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | AUGER | POLE | YES | 256603621 |  |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | MARK WITECKI | GAS COMPLIANCE MANAGER - REGULATORY AFFAIRS | mgwitecki@tecoenergy.com | 813-228-4465 | 813-228-1770 |  |  |  | LUKE BUZARD | DIRECTOR OF PIPELINE SAFETY AND OPERATIONAL SVCS. | 813-228-4733 | labuzard@tecoenergy.com | AT 21:07 ON SEPTEMBER 15, 2016, THE PEOPLES GAS SYSTEM (PGS) CALL CENTER RECEIVED A REPORT OF A DAMAGED PIPELINE NEAR IMPERIAL PARKWAY AND MEADOWS LANE IN BONITA SPRINGS, FLORIDA. PGS CONTACTED THE THIRD-PARTY CONTRACTOR WORKING IN THE AREA - PIKE ELECTRIC - AND CONFIRMED BOTH THAT PIKE ELECTRIC EXCAVATED INTO THE PIPELINE, AND THAT THE PIPELINE WAS LEAKING. A PGS TECHNICIAN WAS DISPATCHED TO THE SCENE AND WHILE IN ROUTE, HE RECEIVED A FOLLOW-UP TELEPHONE CALL FROM PIKE ELECTRIC, WHICH INFORMED HIM THAT ESCAPING NATURAL GAS FROM THE PIPELINE HAD IGNITED. PGS DISPATCHED THE REPAIR CONTRACTOR. THE DAMAGED LINE WAS A 6-INCH NATURAL GAS PLASTIC MAIN THAT PROVIDED SERVICE TO APPROXIMATELY 1000 HOMES. THE GAS PIPELINE WAS VERIFIED TO HAVE SUFFICIENT PRESSURE TO PREVENT AN INTERRUPTION TO THE DOWNSTREAM CUSTOMERS DURING THE LEAK. THE BONITA SPRINGS FIRE DEPARTMENT WAS ABLE TO CONTAIN THE FIRE FROM SPREADING, AND PREVENT FURTHER DAMAGE. THE ASSISTANT FIRE CHIEF CONFIRMED THAT THE FIRE DEPARTMENT COULD CONTROL THE FIRE WHILE PGS WORKED TO INSTALL A BYPASS LINE (A BYPASS LINE WAS INSTALLED TO PREVENT AN INTERRUPTION OF SERVICE TO THE DOWNSTREAM CUSTOMERS WHEN THE GAS MAIN WAS SQUEEZED OFF). THE BYPASS LINE WAS PLACED IN SERVICE AT APPROXIMATELY 03:00 ON SEPTEMBER 16, 2016. AFTER THIS INSTALLATION, GAS SERVICE TO THE DOWNSTREAM CUSTOMERS WAS THEN BEING SUPPLIED VIA A COMPRESSED NATURAL GAS TRAILER. THE DAMAGED GAS MAIN WAS SQUEEZED OFF, THE FIRE WAS EXTINGUISHED, AND THE SITE WAS "MADE SAFE" AT APPROXIMATELY 03:30 ON SEPTEMBER 16, 2016. PIKE ELECTRIC WAS CONTRACTED BY FLORIDA POWER & LIGHT COMPANY TO EXCAVATE HOLES USING AN AUGER, IN ORDER TO INSTALL NEW POWER POLES. PIKE ELECTRIC NOTIFIED SUNSHINE 811 OF THE PLANNED EXCAVATIONS. PGS RECEIVED THE SUNSHINE 811 NOTIFICATIONS, AND MARKED THE PIPELINE VIA A SPRAY PAINT OFFSET INDICATION AND YELLOW FLAGS, AS REQUIRED. THE PIPELINE WAS UNDETECTABLE USING THE TRACER WIRE, SO PGS USED MAPS TO DETERMINE THE LOCATION OF THE PIPELINE. THE PIPELINE MARKINGS WERE VERIFIED AS ACCURATE. THE MAJORITY OF THE PROPERTY DAMAGE WAS TO PIKE ELECTRIC'S TRUCK-MOUNTED AUGER EQUIPMENT. THE ESTIMATED COST OF THE PROPERTY DAMAGE, CONTAINED IN PART D 2A OF THIS REPORT, REFLECTS THE PUBLICLY-AVAILABLE COST OF SIMILAR AUGER EQUIPMENT THAT IS CURRENTLY FOR SALE.
2025-03-31 10:13 | NO | YES | NO | 20160106 | 16538 | 2016-10-24 17:20 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2016-09-26 15:30 |  |  | 2016 | 840 FULTON STREET | BROOKLYN | KINGS | NY | 11238 | 40.6835 | -73.9677 | [9 empty] | 2016-09-26 15:50 | 1160030 |  | NATURAL GAS |  | 364.4 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-09-26 12:21 |  |  |  | 2016-09-26 12:28 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1991 | [5 empty] | 8.625 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 6 | 6 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 4857 | 5834.731626676744917 | 93471 | 112287.049593803175651 | 785 | 943.023332703571085 | PERMIT FEES |  | 2395 | 2756.509433962264150943396226415094339623 |  | 0 | 101508 | 51863.0037462386461376900269541778975741 | 121821.3139871457558039433962264150943396 | 16 | 8 | 0 |  |  |  |  | 0.27 | 0.25 | 0.43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT THE RESULT OF ANY OPERATION THAT THE CONTROL ROOM CAN DETECT UNDER PRESENT OPERATING CONDITIONS OR ALARMS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DRILLING | BUILDING CONSTRUCTION | NO | [5 empty] | YES | 180 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CORINNE BYRNES | PRIN PROG MGR FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAMS | 6317703549 | corinne.byrnes@nationalgrid.com | THIRD PARTY CONTRACTOR (TITAN REALTY AND CONSTRUCTION) DRILLED A 6" ROUND BORE HOLE THROUGH AN 8" LOW PRESSURE STEEL MAIN INFILTRATING THE MAIN WITH COOLANT WATER AND RESULTING IN POOR PRESSURES IN THE AREA. NO NOTIFICATION TO ONE-CALL CENTER HAD BEEN MADE BY EXCAVATOR. NATIONAL GRID BECAME AWARE OF THE DAMAGE THROUGH NO OR LOW PRESSURE CALLS. BOTH CUSTOMER METER SERVICES AND FIELD OPERATIONS ARRIVED ON SITE. THE AFFECTED SECTION OF MAIN WAS ISOLATED AND SECURED. NO INJURIES REPORTED. A TOTAL OF 24 COMMERCIAL/INDUSTRIAL SERVICES (63 METERS) WERE IMPACTED BY THIS EVENT. ALL WERE RESTORED NO LATER THAN OCTOBER 4 AT 11:30 AM. **SUPPLEMENTAL REPORT ISSUED ON 2/28/2017 TO REVISE APPARENT CAUSE FROM G4 OTHER OUTSIDE FORCE DAMAGE TO G3 EXCAVATION DAMAGE DUE TO THIRD PARTY DRILLING ACTIVITY. **SUPPLEMENTAL REPORT ISSUED ON 4/18/2017 TO REMOVE ERRONEOUS DATE ENTERED FROM PART G3, "PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY" "DATE OF LAST LEAK SURVEY". THAT FIELD SHOULD BE BLANK.
2025-03-31 10:13 | NO | YES | YES | 20160107 | 39288 | 2016-10-25 15:51 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2016-09-27 07:32 | EASTERN | YES | 2016 | 300 WEST 234 STREET | NEW YORK | BRONX | NY | 10463-3703 | 40.8832 | -73.906 |  | YES | YES | [6 empty] | 2016-09-27 07:46 | 1160072 |  | NATURAL GAS |  | 1 | 0 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES | 2016-09-27 07:32 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 30 | 2016-09-27 07:32 | YES | OPERATOR | 2016-09-27 07:46 | 2016-09-27 07:14 | 2016-09-27 07:32 | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | INVESTIGATED BY NYPD/OTHER LAW ENFORCEMENT AGENCIES | UNKNOWN | UNKNOWN | [7 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | INVESTIGATED BY NYPD AND OTHER LAW ENFORCEMENT AGENCIES | CLASS 4 LOCATION | 1000000 | 1201303.608539581 | 651 | 782.048649159267231 | 14868 | 17860.982051766490308 | 0 | 0 |  | 4 | 4 | 4.60377358490566037735849056603773584906 | 0 | 0 | 1015523 | 505269.5688866904507105902964959568733154 | 1219951.24301409166319937735849056603774 | 0 | 0 | 9 | 4 | 31 | 9 | 0 | 58 | 58 | 91 | 192.619(A)(1) | 2015-03-26 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 5 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 7 | 0 | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | THE FIRE MARSHAL INVESTIGATION CONCLUDED THAT THE EXPLOSION WAS CAUSED BY AN ACCIDENTAL IGNITION OF NATURAL GAS TRAPPED IN THE SECOND-FLOOR BEDROOMS. INVESTIGATORS FOUND THAT THE TENANTS IN CONTROL OF THE HOUSE HAD SEALED SECOND-FLOOR BEDROOM WINDOWS WITH FOAM BOARDS TO CONCEAL A MARIJUANA GROW OPERATION. ALTHOUGH THE GAS LEAK WAS ISOLATED WITH SERVICE TURNED OFF, THE FOAM BOARDS ON THE SECOND FLOOR PREVENTED EMERGENCY RESPONDERS FROM VENTING ACCUMULATED GAS, WHICH SUBSEQUENTLY EXPLODED. | [47 empty] | KEVIN FAGAN | OPERATIONS MANAGER - GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | (718) 319-2310 | (718) 904-4607 |  |  |  | NICKOLAS HELLEN | DEPARTMENT MANAGER - GAS EMERGENCY RESPONSE CENTER | (718) 319-2310 | hellenn@coned.com | ON SEPTEMBER 27, 2016, AT 06:36, CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A REPORT FROM ITS CUSTOMER OPERATIONS CALL CENTER THAT A MEMBER OF THE PUBLIC HAD CALLED IN A STRONG OUTSIDE GAS ODOR ON TIBBETT AVENUE BETWEEN WEST 234TH AND WEST 236TH STREETS IN THE BRONX. AT 06:37, A DISPATCHER WITH THE FIRE DEPARTMENT OF THE CITY OF NEW YORK (FDNY) CALLED CON EDISON'S GERC AND REPORTED THAT THE FDNY WAS ON LOCATION FOR AN OUTSIDE GAS ODOR IN THE AREA OF A PRIVATE HOUSE LOCATED AT 300 WEST 234TH STREET. CON EDISON'S GERC DISPATCHED A LEAK SURVEY MECHANIC TO THE LOCATION AT 06:39. AT 06:45, THE FDNY REPORTED EVACUATING THE PRIVATE HOUSE AT 300 WEST 234TH STREET BECAUSE OF THE GAS ODOR. A MULTIPLE RESOURCE RESPONSE EVENT (CODE MURRE) WAS THEN INITIATED BY CON EDISON AND ADDITIONAL PERSONNEL - A SUPERVISOR AND MECHANIC FROM CON EDISON'S GAS DISTRIBUTION SERVICES (GDS) DEPARTMENT - WERE DISPATCHED TO THE LOCATION BY THE GERC. THE GERC THEN CALLED THE FDNY TO PROVIDE INFORMATION CONCERNING THE LOCATION OF THE CURB VALVE, AT WHICH TIME THE FDNY REPORTED THAT IT HAD ALREADY CLOSED THE CURB VALVE ON THE GAS SERVICE LINE SUPPLYING 300 WEST 234TH STREET. A FIELD OPERATIONS PLANNER WITH CON EDISON'S GAS EMERGENCY RESPONSE GROUP (ERG) WAS DISPATCHED AT 07:05. AT 07:08, THE FDNY REPORTED THAT IT HAD REQUESTED ASSISTANCE FROM THE NEW YORK CITY POLICE DEPARTMENT (NYPD) BECAUSE OF A POSSIBLE DRUG LAB AT THE LOCATION. CON EDISON'S LEAK SURVEY MECHANIC ARRIVED AT 07:14. HE ENTERED THE BASEMENT OF 304 WEST 234TH STREET AND, USING A GAS MEASUREMENT INSTRUMENT, DETECTED NO GAS-IN-AIR IN THE AREA OF THE GAS SERVICE POINT OF ENTRY. THE LEAK SURVEY MECHANIC THEN ENTERED THE BASEMENT OF 300 WEST 234TH STREET AND, USING A GAS MEASUREMENT INSTRUMENT, DETECTED NO GAS-IN-AIR IN THE AREA OF THE GAS SERVICE POINT OF ENTRY. THE GDS MECHANIC AND GDS SUPERVISOR ARRIVED AT 07:26 AND 07:28, RESPECTIVELY. TOGETHER WITH THE LEAK SURVEY MECHANIC, THEY ENTERED THE BASEMENT OF 300 WEST 234TH STREET TO INVESTIGATE AND VERIFY SHUTDOWN OF THE GAS SERVICE. WHEN THE CON EDISON ERG FIELD OPERATIONS PLANNER ARRIVED AT 07:31, HE JOINED THE OTHER CON EDISON RESPONDERS IN THE BASEMENT OF THE BUILDING. MOMENTS LATER, AT 07:32, THE GDS SUPERVISOR AND ERG FIELD OPERATIONS PLANNER REPORTED THAT AN EXPLOSION OCCURRED ON THE SECOND FLOOR OF THE BUILDING AND THAT ALL CON EDISON EMPLOYEES WERE ACCOUNTED FOR. TWO OF THE FOUR CON EDISON EMPLOYEES IN THE BASEMENT AT THE TIME OF THE EXPLOSION SUSTAINED MINOR INJURIES. ALL FOUR CON EDISON EMPLOYEES WERE TRANSPORTED TO MONTEFIORE MEDICAL CENTER FOR EVALUATION. THE AREA IS SUPPLIED BY A 4-INCH HIGH-PRESSURE POLYETHYLENE (HPPE) GAS MAIN, WITH A 1-INCH HPPE BRANCH SERVICE SUPPLYING 300 AND 304 WEST 234TH STREET. FOUR MAIN VALVES WERE CLOSED TO ISOLATE GAS SUPPLY TO THE AREA, WHICH INTERRUPTED GAS SERVICE TO NINE RESIDENTIAL CUSTOMERS. A RECENT LEAK SURVEY OF THE AREA, CONDUCTED A WEEK PRIOR TO THIS INCIDENT ON SEPTEMBER 20, 2016, FOUND NO LEAKS. ODORANT LEVELS AND DISTRIBUTION SYSTEM PRESSURE SUPPLYING THE AREA WERE CHECKED AFTER THE INCIDENT AND FOUND TO BE WITHIN ACCEPTABLE RANGES. MULTIPLE MEDIA OUTLETS WERE ON LOCATION. A FDNY BATTALION CHIEF WAS STRUCK AND KILLED BY DEBRIS PROPELLED BY THE EXPLOSION. OTHER INJURIES WERE REPORTED. THE NYPD ISOLATED THE AREA AS A CRIME SCENE. MULTIPLE MUNICIPAL AGENCIES WERE ON LOCATION. NYSDPS, NYCDEP, AND USDOT WERE NOTIFIED. NYSDPS SURESH THOMAS WAS NOTIFIED AND RESPONDED TO LOCATION. THE FIRE MARSHAL INVESTIGATION CONCLUDED THAT THE EXPLOSION WAS CAUSED BY AN ACCIDENTAL IGNITION OF NATURAL GAS TRAPPED IN THE SECOND-FLOOR BEDROOMS. INVESTIGATORS FOUND THAT THE TENANTS IN CONTROL OF THE HOUSE HAD SEALED SECOND-FLOOR BEDROOM WINDOWS WITH FOAM BOARDS TO CONCEAL A MARIJUANA GROW OPERATION. ALTHOUGH THE GAS LEAK WAS ISOLATED WITH SERVICE TURNED OFF, THE FOAM BOARDS ON THE SECOND FLOOR PREVENTED EMERGENCY RESPONDERS FROM VENTING ACCUMULATED GAS, WHICH SUBSEQUENTLY EXPLODED.
2025-03-31 10:13 | NO | NO | NO | 20160108 | 16551 | 2016-10-26 16:33 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2016-09-27 23:09 |  |  | 2016 | ON CHEYENNE AVE (NV-574) NEAR REVERE ST | NORTH LAS VEGAS | CLARK COUNTY | NV | 89030 | 36.2179 | -115.1542 | [9 empty] | 2016-09-28 02:24 | 1160185 |  | NATURAL GAS |  | 219 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-09-27 23:09 |  |  |  | 2016-09-27 23:09 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 108 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2010 | [5 empty] | 6 | API 5L | UNKNOWN | STEEL |  | OTHER | ELECTRIC RESISTANCE WELDED (ERW) | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1668 | 2003.774419044021108 | 35939 | 43173.650387304001559 | 19000 | 22824.768562252039 | PAVING COSTS |  | 548 | 630.716981132075471698113207547169811321 |  | 0 | 57155 | 28747.9191504519975348706199460916442049 | 68632.9103497321371386981132075471698113 | 4 | 2 | 0 |  |  |  |  | 268 | 268 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS LINE WAS DAMAGED BY A THIRD PARTY CONTRACTOR PERFORMING DRILLING ACTIVITY. DAMAGE WAS REPORTED BY A SOUTHWEST GAS CONTRACT EMPLOYEE THAT WAS ONSITE PERFORMING HIGH PRESSURE STANDBY ACTIVITY. | [12 empty] | YES | 1 | 0 | YES | 5 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DRILLING | ROAD WORK | YES | 625301508 |  |  | CONTRACT LOCATOR | YES | YES | 36 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO ABANDONED FACILITY | [170 empty] | YVONNE BRODEUR | COMPLIANCE SPECIALIST | yvonne.brodeur@swgas.com | 702-365-2149 | 702-369-0542 |  |  |  | THOMAS CARDIN | DIRECTOR GAS OPERATIONS | 702-365-2028 | thomas.cardin@swgas.com | EXCAVATOR CREWS WERE DRILLING TO INJECT A SOIL STABILIZATION POLYMER WHEN THEY HIT A 6-INCH STEEL HIGH PRESSURE DISTRIBUTION GAS PIPE. STATE LAW REQUIRES THE EXCAVATOR TO USE SPECIAL CARE WITHIN A TOLERANCE ZONE OF 24 INCHES ON EITHER SIDE OF A MARKED PIPE. THE EXCAVATOR WAS DRILLING OUTSIDE THE TOLERANCE ZONE AND SO WAS NOT REQUIRED TO USE SPECIAL CARE. THE ELECTRONIC LINE LOCATE EQUIPMENT SIGNAL CORRESPONDED WITH AN ABANDONED 6-INCH STEEL PIPE, WHICH WAS LOCATED AND MARKED INSTEAD OF THE ACTIVE PIPE. THE DIMENSIONS SHOWN ON THE COMPANY'S AS-BUILT DOCUMENTATION AND MAPPING RECORDS CONTAINED THE SAME INACCURATE, AND INTERNALLY CONTRADICTORY, DEPICTIONS OF THE LOCATION OF THE ACTIVE 6-INCH STEEL PIPE. THE ELECTRONIC LINE LOCATE EQUIPMENT SIGNAL CORRESPONDED WITH PORTIONS OF THOSE RECORDS AND CONFLICTED WITH OTHER PORTIONS OF THOSE RECORDS. THE COMPANY'S LINE LOCATE PERSONNEL FAILED TO FOLLOW ESTABLISHED PROCEDURES TO POTHOLE WHEN ENCOUNTERING SUCH DISCREPANCIES. CORRECTION TO PART G3, 14: A NEARBY ABANDONED FACILITY WAS LOCATED INSTEAD OF THE ACTIVE FACILITY.
2025-03-31 10:13 | NO | YES | YES | 20160109 | 16429 | 2016-10-27 15:42 | SUPPLEMENTAL FINAL | 18736 | SUNRAY UTILITIES SYSTEM | PO BOX 250 / 415 MAIN ST. | SUNRAY | TX | 79086 | 2016-10-06 14:53 |  |  | 2016 | 6TH STREET AND AVENUE K ALLEYWAY | SUNRAY | MOORE | TX | 79086 | 36.0188 | -101.8276 | [9 empty] | 2016-10-06 15:10 | 1160949 |  | NATURAL GAS |  | 7 |  | NO | [5 empty] | 0 | YES | 3 | 0 | 0 | 0 | 0 | 3 | YES |  |  |  |  | NO | 12 | 2016-10-06 14:45 |  |  |  | 2016-10-06 14:45 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1937 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | OPERATORS WERE REPAIRING GRADE 3 LEAK DETECTED IN ANNUAL GAS LOSS AUDIT. | CLASS 3 LOCATION | 0 | 0 | 200 | 240.2607217079162 | 10000 | 12013.03608539581 | 0 | 0 |  |  | 20 | 23.01886792452830188679245283018867924528 |  | 0 | 10220 | 5096.241845126277757951482479784366576819 | 12276.3156750282545018867924528301886792 | 66 | 0 | 668 |  |  |  |  | 24 | 24 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | EMPLOYEE OPERATORS WERE REPAIRING A GRADE 3 LEAK LOCATED ON A 2 INCH NATURAL GAS STEEL LINE THAT WAS UNDER APPROXIMATELY 24 PSIG OF PRESSURE. THIS REPAIR WAS AN APPROXIMATE 8 FOOT SECTION WHERE POLYETHYLENE REPLACEMENT PIPE WAS BEING JOINED WITH COMPRESSION FITTINGS. THE LINE FLASH FIRED WHEN THE POLY PIPE WAS IN PLACE BUT NOT YET JOINED TO THE STEEL PIPE. | [47 empty] | ROBLEY D. ROACH | CITY MANAGER | rob.roach@cityofsunray.com | 806-948-4111 | 806-948-4485 |  |  |  | ROBLEY D. ROACH | CITY MANAGER | 806-948-4111 | rob.roach@cityofsunray.com | EMPLOYEE OPERATORS WERE REPAIRING A GRADE 3 LEAK LOCATED ON A 2 INCH NATURAL GAS STEEL LINE THAT WAS UNDER APPROXIMATELY 24 PSIG OF PRESSURE. THIS REPAIR WAS AN APPROXIMATE 8 FOOT SECTION WHERE POLYETHYLENE REPLACEMENT PIPE WAS BEING JOINED WITH COMPRESSION FITTINGS. THE LINE FLASH FIRED WHEN THE POLY PIPE WAS IN PLACE BUT NOT YET JOINED TO THE STEEL PIPE. WHEN THE FLASH FIRE OCCURRED THERE WERE THREE EMPLOYEE OPERATORS IN THE EXPOSED EXCAVATION THAT WERE BURNED. ALL THREE WORKERS WERE TRANSPORTED FOR INPATIENT HOSPITALIZATION TREATMENT AT A REGIONAL BURN CENTER VIA AIR AMBULANCES. THE TEXAS STATE FIRE MARSHALL AND REGIONAL REPRESENTATIVE FROM THE TEXAS RAILROAD COMMISSION WERE CALLED TO THE SCENE. PRELIMINARY INVESTIGATION INDICATES THE POSSIBLE IGNITION SOURCE OF THE NATURAL GAS TO BE STATIC ELECTRICITY. MOVING FORWARD THE OPERATOR PLANS TO REDUCE THE RISKS OF THIS TYPE OF EVENT FROM HAPPENING IN THE FUTURE BY: 1) PURCHASING AND UTILIZING LINE STOPPING EQUIPMENT. 2) PURCHASING AND UTILIZING FIRE RESISTANT CLOTHING DURING REPAIRS. 3) HAVING A SAFETY OFFICER PRESENT AT GAS LINE REPAIRS TO ENSURE THE SCENE, OPERATIONS, AND PROCEDURES ARE BEING FOLLOWED IN AN EFFORT TO MITIGATE RISKS FOR BOTH WORKERS AND CUSTOMERS.
2025-03-31 10:13 | NO | YES | NO | 20160110 | 16419 | 2016-10-28 10:12 | ORIGINAL FINAL | 12878 | MOUNTAINEER GAS CO | 501 56TH ST. SE | CHARLESTON | WV | 25304 | 2016-06-23 21:00 |  |  | 2016 | PATTERSON ST & BIG DRAFT RD | WHITE SULPHUR SPRINGS | GREENBRIER | WV | 25986 | 37.7948 | -80.3013 | [9 empty] | 2016-06-24 08:35 | 1151498 |  |  |  | 50 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-06-23 21:00 |  |  |  | 2016-06-23 21:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | SEE NARRATIVE. |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | SEE NARRATIVE. | UNKNOWN | [8 empty] | OTHER | SEE NARRATIVE. | [9 empty] | OTHER | [8 empty] | SEE NARRATIVE. | CLASS 2 LOCATION | 0 | 0 | 567000 | 681139.146041942427 | 201000 | 241462.025316455781 | 0 | 0 | SEE NARRATIVE. |  | 200 | 230.188679245283018867924528301886792453 |  | 0 | 768200 | 382326.6731272501635795148247978436657682 | 922831.3600376434910188679245283018867925 | 169 | 0 | 1308 |  |  |  |  | 32 | 32 | 36 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SEE NARRATIVE. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | SEE NARRATIVE. | YES |  |  |  | YES | SEE NARRATIVE. | [213 empty] | PHILIP KINGREY | ENGINEER | philipkingrey@mgcwv.com | 888-420-4427 |  |  |  |  | THOMAS WESTFALL | DIRECTOR OF GAS SUPPLY AND TECHNICAL SERVICES | 888-420-4427 | thomaswestfall@mgcwv.com | A CATASTROPHIC RAINFALL EVENT IN THE EASTERN REGION OF WEST VIRGINIA CREATED A FLASH FLOOD THAT INUNDATED THE TOWN OF WHITE SULPHUR SPRINGS AND CAUSED DAMAGE TO LOCAL BUSINESSES AND RESIDENCES. A STATE OF EMERGENCY WAS DECLARED BY THE GOVERNOR. THE PIPELINE SEGMENTS THAT WERE AFFECTED BY THE FLOODWATERS WERE SHUT DOWN BY LOCAL OPERATIONS PERSONNEL, REPAIRED OR REPLACED AS NECESSARY, AND RESTORED TO SERVICE WHERE CUSTOMERS WERE ABLE TO RECEIVE GAS SERVICE. RESPONDING TO THE EMERGENCY COST APPROXIMATELY $201,000 AND DAMAGE TO COMPANY PROPERTY COST APPROXIMATELY $567,000. GIVEN THE SCOPE OF THE DAMAGE, IT IS DIFFICULT TO QUANTIFY THE TOTAL COST OF PUBLIC PROPERTY DAMAGE. THE PROPERTY DAMAGES THAT OCCURRED DID NOT OCCUR AT THE MOMENT OF THE RELEASE OF GAS, AND WERE NOT CAUSED BY OR THE RESULT OF THE RELEASE OF GAS.
2025-03-31 10:13 | NO | NO | NO | 20160111 | 16420 | 2016-10-28 12:07 | ORIGINAL FINAL | 12878 | MOUNTAINEER GAS CO | 501 56TH ST. SE | CHARLESTON | WV | 25304 | 2016-06-23 21:00 |  |  | 2016 | ELKVIEW CROSSINGS MALL RD | ELKVIEW | KANAWHA | WV | 25071 | 38.4569 | -81.4981 | [9 empty] | 2016-06-24 09:00 | 1151499 |  |  |  | 74 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-06-23 21:00 |  |  |  | 2016-06-23 21:00 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | YES | [6 empty] | YES | UNCASED | LITTLE SANDY CREEK | UNKNOWN |  | PRIVATELY OWNED |  | MAIN |  | 1989 | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | SEE NARRATIVE. | CLASS 2 LOCATION | 0 | 0 | 47000 | 56461.269601360307 | 500 | 600.6518042697905 | 0 | 0 | SEE NARRATIVE. |  | 300 | 345.283018867924528301886792452830188679 |  | 0 | 47800 | 23952.7434902325008692722371967654986523 | 57407.2044244980220283018867924528301887 | 27 | 0 | 0 |  |  |  |  | 15 | 15 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SEE NARRATIVE. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | CATASTROPHIC RAINFALL EVENT | [213 empty] | PHILIP KINGREY | ENGINEER | philipkingrey@mgcwv.com | 888-420-4427 |  |  |  |  | THOMAS WESTFALL | DIRECTOR OF GAS SUPPLY AND TECHNICAL SERVICES | 888-420-4427 | thomaswestfall@mgcwv.com | A CATASTROPHIC RAINFALL EVENT IN THE CENTRAL REGION OF WEST VIRGINIA CREATED A FLASH FLOOD THAT WASHED OUT THE LARGE CULVERT UNDER THE ELKVIEW CROSSINGS MALL ROAD. A STATE OF EMERGENCY WAS DECLARED BY THE GOVERNOR. MOUNTAINEER GAS COMPANY'S PIPELINE THAT PROVIDED GAS TO THE BUSINESSES AT THE MALL WAS DAMAGED AND SHUT DOWN BY LOCAL OPERATIONS PERSONNEL. MOUNTAINEER GAS HAS RELOCATED ITS PIPELINE AND RESTORED SERVICE TO OUR CUSTOMERS. SINCE THE EVENT, THE ROAD TO THE MALL HAS NOT BEEN RECONSTRUCTED. THE PROPERTY DAMAGES THAT OCCURRED WERE NOT CAUSED BY OR THE RESULT OF THE RELEASE OF GAS.
2025-03-31 10:13 | NO | NO | NO | 20160112 | 31260 | 2016-11-03 11:45 | SUPPLEMENTAL FINAL | 2568 | COLORADO SPRINGS, CITY OF | PO BOX 1103 | COLORADO SPRINGS | CO | 80947 | 2016-10-03 09:48 |  |  | 2016 | 207 W ROCKRIMMON BLVD | COLORADO SPRINGS | EL PASO | CO | 80919 | 38.9277 | -104.8308 | [9 empty] | 2016-10-03 21:34 | 1160670 |  | NATURAL GAS |  | 42.17 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 36 | 2016-10-03 10:05 |  |  |  | 2016-10-03 10:38 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 32 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1978 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | UNKNOWN |  |  |  | UNKNOWN |  | MECHANICAL PUNCTURE | 1.3 | 0.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 59252 | 71179.641413187253412 | 0 | 0 | 2B OPS PROPERTY DAMAGE COST INCLUDED IN 2C. 2A NO CLAIMS PAID. |  | 9 | 10.35849056603773584905660377358490566038 |  | 0 | 59261 | 29490.0549100347866930781671159029649596 | 71189.9999037532911478490566037735849057 | 8 | 0 | 0 |  |  |  |  | 33 | 33 | 34 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2016-04-21 | NO | [12 empty] | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | FENCING | NO | [5 empty] | UNKNOWN/OTHER |  | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | JESSICA NESVOLD | SR. REGULATORY COMPLIANCE ENGINEER | jnesvold@csu.org | 719-668-3582 |  |  |  |  | JOE AWAD | GENERAL MANAGER ENERGY CONSTRUCTION MAINTENANCE | 719-668-3504 | jawad@csu.org | THE INCIDENT APPEARS TO BE THE RESULT OF UNKNOWN THIRD PARTY DAMAGE FROM PREVIOUS EXCAVATION. DAMAGE APPEARS TO BE CAUSED BY A FENCE POST THAT WAS INSTALLED AT AN UNKNOWN DATE. IT IS UNKNOWN WHETHER THE FENCE POST WAS INSTALLED THROUGH THE PAVEMENT OR IF PAVEMENT WAS PREEXISTING. THE NUMBER OF EVACUEES CANNOT BE ESTIMATED BECAUSE WE DO NOT KNOW HOW MANY PEOPLE WERE IN THE BUILDINGS THAT WERE EVACUATED. WE DO KNOW THAT 36 BUSINESSES WERE EVACUATED FROM THE SCENE. EMERGENCY RESPONDERS DID NOT KEEP A RECORD OF THE NUMBER OF INDIVIDUALS EVACUATED. WE HAVE ESTIMATED 1 PERSON PER BUILDING.
2025-03-31 10:13 | NO | YES | YES | 20160114 | 16723 | 2016-11-11 17:25 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2016-10-11 19:33 |  |  | 2016 | 91 STRAWFLOWER CT | ROMEOVILLE | WILL | IL | 60446 | 41.62 | -88.1296 | [9 empty] | 2016-10-11 20:20 | 1161337 |  | NATURAL GAS |  | 566 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | YES | 20 | 2016-10-11 14:59 |  |  |  | 2016-10-11 15:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 43 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1998 | [5 empty] | 2 | ASTM D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | OTHER | [8 empty] | MULTIPLE MECHANICAL PUNCTURES EVERY COUPLE OF INCHES FOR SEVERAL FEET ALONG THE LENGTH OF THE MAIN. | CLASS 3 LOCATION | 1038000 | 1246953.145664085078 | 72450 | 87034.44643869264345 | 76067 | 91379.561590780307927 | 0 | 0 |  |  | 2296 | 2642.566037735849056603773584905660377358 |  | 0 | 1188813 | 592788.8546763440376098301886792452830189 | 1428009.71973129387843360377358490566038 | 0 | 0 | 8 |  |  |  |  | 56 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 12 | 0 | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2632375 | J.U.L.I.E. NOTE THAT JULIE TICKETS NUMBER ABOVE START WITH AN "A". SECOND AND THIRD TICKET IS A263335 AND A263391 |  | CONTRACT LOCATOR | NO | YES | 316 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | lquezad@southernco.com | 630-388-2316 |  |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | 630-388-2316 | lquezad@southernco.com | INCIDENT ORIGINALLY REPORTED TO THE NRC AS 77 STRAWFLOWER. ACTUAL ADDRESS OF EXPLOSION IS 91 STRAWFLOWER CT. A THIRD PARTY EXCAVATOR WAS INSTALLING CONDUIT VIA DIRECTIONAL DRILLING. A MAIN WAS STRUCK MULTIPLE TIMES DURING THE PULLBACK. THE RELEASE OF GAS WAS SECURED ABOUT 2 HOURS PRIOR TO THE INCIDENT. SUBSEQUENTLY, THE EXPLOSION OCCURRED. IN SECTION G3 QUESTION 14, ONLY ONE ROOT CAUSE CAN BE SELECTED; HOWEVER, OUR INVESTIGATION INDICATED 2 ROOT CAUSES; LOCATING PRACTICES INSUFFICIENT AND EXCAVATION PRACTICES INSUFFICIENT.
2025-03-31 10:13 | NO | YES | YES | 20160115 | 16597 | 2016-11-15 16:51 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2016-10-12 14:53 |  |  | 2016 | 2730 COLUMBUS AVE | SPRINGFIELD | CLARK | OH | 45503 | 39.9367 | -83.7669 | [9 empty] | 2016-10-12 16:28 | 1161404 |  | NATURAL GAS |  | 4147 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | NO |  |  |  |  | NO | 4 | 2016-10-12 14:53 |  |  |  | 2016-10-12 14:53 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 34 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | OTHER | [8 empty] | A METALLIC STRAP FAILED TO RESTRAIN A UNRESTRAINED MECHANICAL COUPLING | CLASS 3 LOCATION | 0 | 0 | 10000 | 12013.03608539581 | 27250 | 32735.52333270358225 | 0 | 0 |  |  | 13187 | 15177.4905660377358490566037735849056604 |  | 0 | 50437 | 32573.5786267068011853099730458221024259 | 59926.0499841371280990566037735849056604 | 8 | 0 | 0 |  |  |  |  | 111 | 111 | 125 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SEE NARRATIVE IN SECTION H FOR EXPLANATION. | [12 empty] | NO |  |  | YES | 1 | 0 | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | BOLTED |  | COUPLING |  | DRESSER STYLE 38 |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | THE MECHANICAL COUPLING WAS A SEAL ONLY DESIGN BUT HAD BEEN SECURED WITH STRAPS WELDED ACROSS THE JOINT THAT FAILED TO RESTRAIN THE PIPE. A LABORATORY ANALYSIS WAS CONDUCTED AND IT WAS DETERMINED THAT THE STRAPS FAILED DUE TO AN OVER LOAD CONDITION. |  | YES |  |  |  | OTHER | UNKNOWN | NO | [86 empty] | ROB SMITH | OPERATION COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB SMITH | OPERATION COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | NARRATIVE FOR PART E-7: THE GAS CONTROLLER FIRST BECAME AWARE OF THE INCIDENT THROUGH A LOW PRESSURE ALARM UPSTREAM OF THE EVENT AT 16:12 HOURS. IT WAS DETERMINED THAT GAS CONTROL PERSONNEL WERE NOT A CONTRIBUTING FACTOR IN CAUSING OR CONTRIBUTING TO THE INCIDENT. AS A RESULT OF INITIAL PHONE COMMUNICATION IT WAS DETERMINED THAT DISCOVERY FOR GAS CONTROL OCCURRED AFTER FIELD OPERATIONS PERSONNEL WERE AWARE AND RESPONDING. GAS CONTROL DOES NOT HAVE REMOTE CONTROL CAPABILITIES WITHIN THIS MARKET. NARRATIVE FOR PART H: IN THE PROCESS OF STOPPING OFF A DEAD END SECTION OF 8-INCH COATED STEEL HIGH PRESSURE PIPE AN UNEXCAVATED MECHANICAL COUPLING UPSTREAM OF THE WORK LOCATION PULLED APART. AS A RESULT OF THIS SEPARATION, TWO MEMBERS OF A CONTRACTOR CREW SUSTAINED INJURIES. THE MECHANICAL COUPLING WAS A SEAL ONLY DESIGN BUT HAD BEEN SECURED WITH STRAPS WELDED ACROSS THE JOINT THAT FAILED TO RESTRAIN THE PIPE. THE COMPONENTS IN QUESTION WERE SENT TO LABORATORY FOR FURTHER ANALYSIS. THE INVESTIGATION DETERMINED THAT THE STRAPS FAILED DUE TO AN OVER LOAD CONDITION AS A RESULT COLUMBIA HAS IMPLEMENTED PROTOCOLS TO PREVENT A RECURRENCE THAT INCLUDE AND ARE NOT LIMITED TO AN INVESTIGATION WHEN EXCAVATING AND WORKING ON METALLIC PIPE THAT MIGHT INCLUDE UNRESTRAINED FITTINGS. PLEASE CONSIDER THIS INCIDENT REPORT FINAL.
2025-03-31 10:13 | YES | NO | NO | 20160117 | 16779 | 2016-11-18 14:42 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2016-10-20 02:15 |  |  | 2016 | 605 WEST 141 STREET | NEW YORK | NEW YORK | NY | 10031-6905 | 40.8244 | -73.9528 | [9 empty] | 2016-10-20 03:56 | 1162007 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 30 | 2016-10-20 02:15 |  |  |  | 2016-10-20 02:27 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | 2003 | [8 empty] | OTHER | RUBBER GASKETS AND ALUMINUM METER | [9 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 4 LOCATION | 100000 | 120130.3608539581 | 50 | 60.06518042697905 | 312 | 374.806725864349272 | 0 | 0 |  |  | 4 | 4.60377358490566037735849056603773584906 |  | 0 | 100366 | 49938.7622552901681135902964959568733154 | 120569.8365338343339823773584905660377358 | 0 | 0 | 30 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | NICHOLAS HELLEN | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | hellenn@coned.com | ON OCTOBER 20, 2016 AT 02:15, NEW YORK CITY EMERGENCY MANAGEMENT REPORTED A FIRE ON THE TOP FLOOR OF THE SIX STORY BUILDING AT THIS LOCATION TO CON EDISON'S GAS EMERGENCY RESPONSE CENTER. CON EDISON GAS DISTRIBUTION SERVICES (GDS) AND ELECTRIC OPERATIONS PERSONNEL WERE DISPATCHED AT 02:17, ARRIVED AT 02:27 AND INVESTIGATED. THE BUILDING IS SUPPLIED BY A 3" LOW PRESSURE POLYETHYLENE GAS SERVICE. AT 02:59, GDS REPORTED THIRTY OCCUPANTS WERE EVACUATED PRIOR TO THEIR ARRIVAL. NEW YORK CITY FIRE DEPARTMENT FIRE MARSHAL WILSON REPORTED THAT A SECONDARY GAS IGNITION OCCURRED IN APARTMENT #64 AS A RESULT OF THE GAS METER GASKETS MELTING DUE TO THE PRIMARY FIRE, WHICH WAS NOT GAS-RELATED. GAS METER #3410522 WAS LOCATED IN THE APARTMENT. DAMAGE WAS GREATER THAN $50,000 AND TWO FIRE FIGHTERS WERE TRANSPORTED VIA AMBULANCE TO AN UNKNOWN HOSPITAL WITH WHAT WAS BELIEVED TO BE MINOR INJURIES. IT WAS UNKNOWN IF THE INJURIES WERE RELATED TO THE BUILDING FIRE OR THE SECONDARY GAS IGNITION. GAS SUPPLY WAS TURNED OFF AT THE METER CONTROL VALVE IN THE APARTMENT AS WELL AS AT A RISER VALVE, WHICH ISOLATED COOKING GAS TO THIRTY OF SIXTY-FOUR TOTAL APARTMENTS IN THE BUILDING AS WELL AS THE BOILER'S PILOT GAS SUPPLY. AT 05:00, THE EVACUATION WAS TERMINATED. PRESSURE AND ODORANT READINGS WERE TAKEN AND WERE WITHIN THE ACCEPTABLE RANGE. CON EDISON'S LAW AND PHOTOGRAPHIC DEPARTMENTS WERE NOTIFIED AND CHANNEL 4 NEWS AND OTHER MEDIA WERE ON LOCATION. THE NATIONAL RESPONSE CENTER, THE NEW YORK STATE DEPARTMENT OF PUBLIC SERVICE AND THE NEW YORK CITY DEPARTMENT OF ENVIRONMENTAL PROTECTION WERE NOTIFIED.
2025-03-31 10:13 | NO | YES | YES | 20160118 | 16728 | 2016-11-18 17:48 | SUPPLEMENTAL FINAL | 13840 | NORTHWEST NATURAL GAS CO | 250 SW TAYLOR ST | PORTLAND | OR | 97204 | 2016-10-19 09:38 |  |  | 2016 | 500 NW 23RD AVE | PORTLAND | MULTNOMAH | OR | 97210-3712 | 45.5264 | -122.6984 | [9 empty] | 2016-10-19 11:30 | 1161960 |  | NATURAL GAS |  | 52 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES |  |  |  |  | YES | 50 | 2016-10-19 08:51 |  |  |  | 2016-10-19 09:10 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1985 | [5 empty] | 1 | UNKNOWN | UNKNOWN | STEEL |  |  |  | 0.133 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 15000000 | 18019554.128093715 | 35000 | 42045.626298885335 | 85000 | 102110.806725864385 | 0 | 0 |  |  | 182 | 209.471698113207547169811320754716981132 |  | 0 | 15120182 | 7523057.93379651118037735849056603773585 | 18163920.03281657792754716981132075471698 | 15 | 0 | 111 |  |  |  |  | 50 | 50 | 57 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 5 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | CABLE TV | YES | 16229204 |  |  | CONTRACT LOCATOR | NO | YES | 32 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JOE KARNEY | SENIOR MANAGER CODE COMPLIANCE | jsk@nwnatural.com | 503-226-4211 |  |  |  |  | J. R. GONZALEZ | SENIOR MANAGER CODE COMPLIANCE | 503-226-4211 | j9g@nwnatural.com | AT APPROXIMATELY 8:51AM ON OCTOBER 19, 2016 NW NATURAL RECEIVED NOTIFICATION OF DAMAGE TO A 1" SERVICE LINE AT NW 23RD AVENUE AND GLISAN STREET IN PORTLAND. THE SERVICE WAS DAMAGED BY LOY CLARK DURING THE COURSE OF THEIR EXCAVATION FOR A THIRD PARTY. THE NATURAL GAS IGNITED AT 9:38AM RESULTING IN THE LOSS OF A STRUCTURE AT 500/510 NW 23RD AVENUE. A NW NATURAL FIRST RESPONDER ARRIVED ON SITE AT 9:10AM. GAS WAS CONTROLLED AT 9:52AM BY CLOSING A 2-INCH VALVE LOCATED AT THE INTERSECTION OF NW 22ND AVENUE AND NW GLISAN STREET. GAS SERVICE WAS INTERRUPTED TO 126 CUSTOMERS. ALL COSTS REPORTED IN PART D ARE PRELIMINARY ESTIMATES AND WILL BE UPDATED ON SUPPLEMENTAL REPORTS. HISTORICAL PERSPECTIVE: ON JULY 12TH 2016, A LOCATE REQUEST (TICKET 16173103) FOR INSTALLING ELECTRIC PRIMARY AND SERVICE WAS CALLED IN BY LOY CLARK AND, WAS ACCURATELY MARKED BY LOCATING INC. FOR THE AREA WHERE LOY CLARK WAS EXCAVATING ON OCTOBER 19TH, 2016. MARKS FROM THIS TICKET WERE STILL VISIBLE AND ACCURATE. ON SEPTEMBER 12TH, 2016, A LOCATE REQUEST FOR REPLACING TELEPHONE AND CABLE TV MAINLINE WAS CALLED IN BY LOY CLARK. THE LOCATE DESCRIPTION FOR THIS REQUEST WAS CLOSE TO, BUT DID NOT COVER, THE AREA WHERE LOY CLARK WAS EXCAVATING ON OCTOBER 19TH, 2016. LOCATE TICKET NUMBER 16229204. ON OCTOBER 19TH, 2016, DURING THE COURSE OF EXCAVATION ON PART OF THE SIDEWALK ON NW GLISAN WITHIN THE AREA COVERED BY THE JULY 12TH, 2016 LOCATE, AN EMPLOYEE WITH LOY CLARK PIPELINE HIT THE GAS SERVICE TO 500 NW 23RD WITH A BACK HOE CAUSING THE SERVICE LINE TO BE PULLED OUT OF AND SEPARATED FROM THE FITTING OF THE DRESSER VALVE. THE OPERATOR DID NOT EMPLOY HAND TOOLS OR OTHER NON-INVASIVE METHODS TO DETERMINE THE EXACT LOCATION OF THE UNDERGROUND SERVICE. LOY CLARK REPORTED THEY WERE PERFORMING COMMUNICATION WORK ON OCTOBER 19TH, 2016. THE LOY CLARK EMPLOYEES WERE DIGGING OUTSIDE OF THE LOCATE AREA THAT HAD BEEN CALLED IN BY LOY CLARK FOR COMMUNICATIONS WORK (LOCATE TICKET NUMBER 16229204).
2025-03-31 10:13 | NO | NO | NO | 20160119 | 16437 | 2016-11-21 10:20 | ORIGINAL FINAL | 2604 | COLUMBIA GAS OF VIRGINIA INC | 1809 COYOTE DRIVE | CHESTER | VA | 23836 | 2016-10-29 16:29 |  |  | 2016 | 639 DAVIS RD | CHATHAM | PITTSYLVANIA | VA | 24531 | 36.8051 | -79.3785 | [9 empty] | 2016-10-31 16:00 | 1162978 |  | NATURAL GAS |  | 227 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 12 | 2016-10-29 16:34 |  |  |  | 2016-10-29 17:34 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 37 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1987 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | LONGITUDINAL | 0.237 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 10 | 0.2 |  | CLASS 1 LOCATION | 0 | 0 | 0 | 0 | 59053 | 70940.581995087876793 | 5000 | 6006.518042697905 | MEALS AND HOTELS |  | 1350 | 1553.773584905660377358490566037735849057 |  | 0 | 65403 | 33306.5126246178999747250673854447439353 | 78500.8736226914421703584905660377358491 | 212 | 0 | 94 |  |  |  |  | 285 | 285 | 433 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO BECAUSE THIS WAS A DAMAGED LINE BY UNKNOWN 3RD PARTY | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2013-01-01 | NO | [12 empty] | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO | [5 empty] | YES | 25 | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | GUY DAILEY | OPERATIONS COMPLIANCE MANAGER | gdailey@nisource.com | (804)314-9390 |  |  |  |  | GUY DAILEY | OPERATIONS COMPLIANCE MANAGER | (804)314-9390 | gdailey@nisource.com | PREVIOUS UNKNOWN DAMAGE BY UNKNOWN 3RD PARTY CAUSED GAS MAIN TO LEAK . WHILE CREW WAS INVESTIGATING SOURCE OF GAS LEAK, THE PIPE RUPTURED. FLOW OF GAS WAS SHUT OFF AT UPSTREAM STATION.
2025-03-31 10:13 | NO | YES | NO | 20160120 | 16438 | 2016-11-21 10:58 | ORIGINAL FINAL | 1640 | BOSTON GAS CO | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2016-10-24 07:54 |  |  | 2016 | SQUIRE RD AND ROUTE 1 NORTH SIDE | REVERE | SUFFOLK | MA | 02151 | 42.4276 | -71.0235 | [9 empty] | 2016-10-25 15:34 | 1162502 |  | NATURAL GAS |  | 4672 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-10-23 23:07 |  |  |  | 2016-10-23 23:23 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 32 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1952 | [5 empty] | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.375 | [6 empty] | MECHANICAL PUNCTURE | 2.3 | 2.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 33538 | 40289.320423200467578 | 84786 | 101853.727753636914666 | 0 | 0 |  |  | 5716 | 6578.792452830188679245283018867924528302 |  | 0 | 124040 | 64957.155686985293266533692722371967655 | 148721.8406296675709232452830188679245283 | 20 | 0 | 3571 |  |  |  |  | 93 | 95 | 100 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | OTHER | LOCAL POLICE CALLED NATIONAL GRID CALL CENTER |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS NOT CAUSED BY ANY ACTIONS OF THE CONTROL ROOM OR CONTROLLER(S). IT WAS A THIRD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY | 2016-01-01 |  |  |  | NO | [9 empty] | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 20164103937 | NA |  | CONTRACT LOCATOR | NO | YES | 16 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | CORINNE BYRNES | PRIN PROG MGR OPERATIONS CODES AND POLICY | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAMS | 6317703549 | corinne.byrnes@nationalgrid.com | CMS DISPATCH WAS NOTIFIED BY REVERE POLICE ON 10/23 AT 23:07 THAT A PIPELINE DAMAGE OCCURRED. A CMS CREW WAS SENT OUT AND TO INVESTIGATE AT 23:23 AND CMS DISPATCH WAS NOTIFIED ON 10/23 AT 23:27 THAT A CONTRACTOR INSTALLING A GUARDRAIL STRUCK A 12" DIAMETER, 100 PSI NATURAL GAS DISTRIBUTION MAIN. MAIN WAS SHUT DOWN AT 16:09 ON 10/24 USING A MECHANICAL FITTING. A 60 PSI AND A 25 PSI REGULATOR STATION WERE SHUTDOWN AS WELL. PERMANENT REPAIRS TO 12" MAIN WERE COMPLETED ON 10/24 AT 21:37. IN TOTAL, 3000 HP AND 591 LP CUSTOMERS WERE OUT OF SERVICE (591 LP AND 23 HP SERVICES WERE OFFLINE.) THE LAST CUSTOMER IMPACTED BY THIS OUTAGE WAS RESTORED ON 11/1/2016 AT 11:30.
2025-03-31 10:13 | YES | NO | NO | 20160121 | 16787 | 2016-11-22 15:55 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2016-10-24 00:05 |  |  | 2016 | 2124 CHESHIRE BRIDGE ROAD | ATLANTA | FULTON | GA | 20324 | 33.8129 | -84.3543 | [9 empty] | 2016-10-24 10:23 | 1162352 |  | NATURAL GAS |  | 554.7 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2016-10-24 00:35 |  |  |  | 2016-10-24 01:34 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | OVERHEAD CROSSING |  |  |  | YES | YES | CASED | [9 empty] | PRIVATELY OWNED |  | MAIN |  | 2009 | [5 empty] | 4 | ASTM D2513 | DRISCO PLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | OTHER | [8 empty] | ENCASED 4-INCH PLASTIC MAIN MELTED DUE TO EXTERNALLY APPLIED HEAT FROM AN UNCONTROLLED FIRE. | CLASS 3 LOCATION | 0 | 0 | 41053 | 49317.117041375418793 | 12782 | 15355.062724352924342 | 0 | 0 |  |  | 1570 | 1806.981132075471698113207547169811320755 |  | 0 | 55405 | 28456.8405952937063341913746630727762803 | 66479.1608978038148331132075471698113208 | 27 | 1 | 0 |  |  |  |  | 41 | 45 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@southernco.com | A LEAK CALL WAS RECEIVED BY THE COMPANY'S 24/7 EMERGENCY CALL CENTER WHERE IT WAS IDENTIFIED THAT THE CITY OF ATLANTA'S FIRE DEPARTMENT HAD PREVIOUSLY RESPONDED AND EXTINGUISHED AN OUT OF CONTROL FIRE UNDERNEATH A BRIDGE ALONG CHESHIRE BRIDGE ROAD AT SOUTH FORK PEACHTREE CREEK. UPON INVESTIGATION, IT WAS DETERMINED THAT A 4-INCH PE PLASTIC MAIN ONE-WAY FEED INSERTED INTO A 16-INCH STEEL CASING FAILED DUE TO EXTERNALLY APPLIED HEAT FROM THE UNCONTROLLED FIRE. THE FIRE CONSISTED OF BURNING MATTRESSES AND OTHER TYPES OF FURNITURE ASSOCIATED WITH PEOPLE WHO WERE LIVING UNDERNEATH THE BRIDGE. IN ADDITION, APPROXIMATELY 2 1/2 HOURS AFTER GAS HAD BEEN SHUT OFF WHICH WAS AFTER THE FIRE DEPARTMENT'S EMERGENCY RESPONDERS HAD DETERMINED THAT THE INCIDENT WAS SAFE ENOUGH FOR THEM TO LEAVE, ONE PERSON WHO PREVIOUSLY WAS TOLD BY COMPANY CREWS TO STAY AWAY FROM THE INCIDENT SCENE, ENTERED UNDERNEATH THE BRIDGE ON THE OPPOSITE SIDE OF THE CREEK AND INITIATED A FLASH FIRE FROM AN UNKNOWN HEAT SOURCE WHERE THE INDIVIDUAL SUFFERED BURNS TO THE SKIN AND WAS TAKEN TO THE HOSPITAL AND ADMITTED. AN INVESTIGATION DETERMINED THAT THE FUEL SOURCE COULD NOT HAVE BEEN NATURAL GAS BASED ON THE LOCATION WHERE THE NATURAL GAS WAS BEING EMITTED OUTSIDE THE BRIDGE ABUTMENT THROUGH THE CASING. EVEN THOUGH THERE WERE NO REMAINING GASES TO DETERMINE THE EXACT SOURCE, IT WAS ORIGINALLY SUSPECTED AND REPORTED THAT THE GASES THAT IGNITED WERE DUE TO INCOMPLETELY COMBUSTIBLE GAS COMPOSITIONS, SUCH AS CARBON MONOXIDE OR OTHER TYPE OF GASEOUS COMPOUNDS TYPICAL OF THE TYPES OF MATERIALS BEING BURNED, GENERALLY FOUND IN SMOKE OR "SMOKE GAS". HOWEVER, THROUGH AN INVESTIGATION BY AN INDEPENDENT CONSULTANT IT WAS IDENTIFIED THAT THE FLASH FIRE WAS MORE LIKELY CAUSED BY THE INJURED PARTY'S IGNITION OF A FLAMMABLE SOURCE SUCH AS A BUG BOMB (MULTIPLE CANISTERS FOUND IN THE AREA) OR OTHER FLAMMABLE SUBSTANCE.
2025-03-31 10:13 | NO | YES | YES | 20160122 | 16653 | 2016-11-25 12:04 | SUPPLEMENTAL FINAL | 31432 | ALLIANT GAS | 600 E. LAS COLINAS BLVD SUITE 2000 IRVING | IRVING | TX | 75039 | 2016-11-05 20:11 |  |  | 2016 | 201 E ZURICH DR. | PAYSON | GILA | AZ | 85541 | 34.2469 | -111.3212 | [9 empty] | 2016-11-05 22:11 | 1163392 |  | PROPANE GAS |  | 32.2 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 10 | 2016-11-05 20:11 |  |  |  | 2016-11-05 17:50 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1974 | [5 empty] | 1.5 | ASTM D2513 | DUPONT - ALDYL-A PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 650000 | 780847.34555072765 | 20000 | 24026.07217079162 | 30000 | 36039.10825618743 | 0 | 0 |  |  | 1000 | 1150.943396226415094339622641509433962264 |  | 0 | 701000 | 349345.438184898877897574123989218328841 | 842063.4693739331150943396226415094339623 | 1 | 0 | 3 |  |  |  |  | 27 | 27.5 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | ,,,,,,,,,,,,TREE ROOT ENCROACHING ON ALDYL-A PIPE CAUSING IT TO FAIL | NO | [218 empty] | VINCE BEELER | SAFETY COMPLIANCE MANAGER | vbeeler@pinnpropane.com | 928-474-2294 | 928-474-0909 |  |  |  | VINCE BEELER | SAFETY COMPLIANCE MANAGER | 9289783182 | vbeeler@pinnpropane.com | ALLIANT GAS WAS NOTIFIED OF A LEAKING TANK OUTSIDE THE RESIDENCE OF 201 E ZURICH STREET IN PAYSON AZ, BY LOCAL EMERGENCY RESPONDERS AT AROUND 5:30 PM (MST) ON 11-5-16. UPON ARRIVAL OF ALLIANT'S ON-CALL PIPELINE TECH, IT WAS DETERMINED THERE WAS NOT A TANK LEAK, BUT A POTENTIAL PROPANE GAS PIPELINE LEAK. ALLIANT'S PIPELINE TECH CALLED OUT ADDITIONAL SUPPORT TO INVESTIGATE THE POTENTIAL LEAK. WHILE CONDUCTING THE INVESTIGATION OF THE LEAK, AN EXPLOSION OCCURRED CAUSING INJURIES OF VARYING DEGREES TO BOTH THE BUILDING OCCUPANTS AND THE ALLIANT EMPLOYEES. 911 WAS CALLED AND THE FIRE DEPARTMENT RESPONDED TO FIGHT THE FIRE. ALLIANT IMMEDIATELY BEGAN RESPONDING TO THE NEXT LEVEL OF THEIR EMERGENCY PLAN AND CALLING IN ADDITION RESOURCES. ALLIANT CREWS WORKED TO ISOLATE ALL OF THE COMPANY'S PIPELINES IN THE AREA OF 201 ZURICH DRIVE AND WAS ABLE TO HAVE THE LEAK ISOLATED BY 0130 ON NOVEMBER 6, 2017. AN INVESTIGATION WAS LAUNCHED AS SOON AS THE EMERGENCY RESPONSE WAS COMPLETED. THE INVESTIGATION REVEALED THAT THE LEAK OCCURRED AS A RESULT OF AN INTERNAL FRACTURE OF THE ADYL A PIPE. ALLIANT GAS HAS REVIEWED AND REVISED ITS EMERGENCY PLANS TO ENSURE THE SAFETY OF THE COMMUNITY. ALLIANT HAS CONTINUED TO FOLLOW ITS DIMP PLAN FOR THE REPAIR AND REPLACEMENT OF THE ADYL A PIPE. PART A #4 IS CONFIRMED AT 11/05/2016 20:11 AZ TIME. #7 IS CONFIRMED AT 11/05/2016 22:11 AZ TIME. #13A IS CONFIRMED ALL THREE PIPELINES LEADING TO THE INCIDENT WERE SHUT DOWN 11/06/2016 01:30 AZ TIME. #17A IS CONFIRMED AT 11/05/2016 20:11 AZ TIME WHEN INCIDENT MET ANY REPORTABLE CRITERIA. #17B IS CONFIRMED AT 11/05/2016 17:50 AZ TIME IS WHEN ALLIANT'S TECH FIRST ARRIVED ON SITE TO EVALUATE AND FIND IT NOT TO BE A SINGLE FAMILY PROPANE TANK BUT A UNDERGROUND PIPELINE CALL. PART F #1 IS CONFIRMED UNDER PART 199.2 APPLICABILITY (B)(2) DOES NOT APPLY.
2025-03-31 10:13 | NO | YES | NO | 20160123 | 30427 | 2016-12-02 10:03 | SUPPLEMENTAL FINAL | 20211 | ATMOS ENERGY CORPORATION - KY/MID-STATES (MID-STATES) | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2016-10-26 09:30 |  |  | 2016 | 1147 ECKERTON DR | NOLENSVILLE | WILLIAMSON | TN | 37135 | 35.9421 | -86.6597 | [9 empty] | 2016-10-26 10:45 | 1162559 |  | NATURAL GAS |  | 68 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-10-26 09:30 |  |  |  | 2016-10-26 09:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2016 | [5 empty] | 2 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 500000 | 600651.8042697905 | 10000 | 12013.03608539581 | 10000 | 12013.03608539581 | 0 | 0 |  |  | 250 | 287.735849056603773584905660377358490566 |  | 0 | 520250 | 258989.0139954974644743935309973045822102 | 624965.6122896387237735849056603773584906 | 0 | 0 | 74 |  |  |  |  | 87 | 90 | 100 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 3 | 0 | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | [197 empty] | OTHER EQUIPMENT FAILURE | [23 empty] | THE LEAK OCCURRED DURING THE ATTEMPTED INSTALLATION OF A 2' X 3/4' ELECTROFUSION TAP TEE ON TO A 2' HDPE MAIN. ALL OF THE MATERIALS AND EQUIPMENT USED DURING THE ATTEMPTED INSTALLATION WERE DESTROYED BY FIRE, LEAVING NO EVIDENCE TO EXAMINE. THE ELECTROFUSION PROCESS PROVIDED HEAT THAT APPARENTLY COMPROMISED THE PIPE. | [59 empty] | JACK M. SANDERS | MGR. COMPLIANCE | jack.sanders@atmosenergy.com | 615 771-8387 |  |  |  |  | JACK M. SANDERS | MGR. COMPLIANCE | 615 771-8387 | jack.sanders@atmosenergy.com | THE LEAK OCCURRED DURING THE ATTEMPTED INSTALLATION OF A 2' X 3/4' ELECTROFUSION TAP TEE ON TO A 2' HDPE MAIN. ALL OF THE MATERIALS AND EQUIPMENT USED DURING THE ATTEMPTED INSTALLATION WERE DESTROYED BY FIRE, LEAVING NO EVIDENCE TO EXAMINE. THE ELECTROFUSION PROCESS PROVIDED HEAT THAT APPARENTLY COMPROMISED THE PIPE.
2025-03-31 10:13 | NO | YES | NO | 20160124 | 16457 | 2016-12-02 16:46 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2016-11-10 16:50 |  |  | 2016 | FOSTER AVE BETWEEN NEW YORK AVE AND NOSTRAND AVE | BROOKLYN | KINGS | NY | 11210 | 40.6385 | -73.9472 | [9 empty] | 2016-11-10 16:10 | 1163761 |  | NATURAL GAS |  | 113.47 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-11-10 13:19 |  |  |  | 2016-11-10 13:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 30 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | MECHANICAL PUNCTURE | 1.3 | 1.3 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 85000 | 102110.806725864385 | 113000 | 135747.307764972653 | 0 | 0 |  |  | 411 | 473.037735849056603773584905660377358491 |  | 0 | 198411 | 98951.2849371825251159029649595687331536 | 238331.1522266860946037735849056603773585 | 20 | 0 | 819 |  |  |  |  | 10.5 | 10.5 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | NATIONAL GRID WAS NOTIFIED OF DAMAGE AND CUSTOMER OUTAGES BY LOCAL POLICE |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT THE RESULT OF ANY OPERATION THAT THE CONTROL ROOM CAN PERFORM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY | 2016-01-01 | NO |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | DRILLING | ENGINEERING/SURVEYING | YES | 163091923 | NEW YORK CITY ONE-CALL |  | CONTRACT LOCATOR | NO | YES | 20 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 5169030596 |  |  |  |  | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAMS | 5169030596 | corinne.byrnes@nationalgrid.com | DISPATCH AND SCHEDULE WAS NOTIFIED BY NY FIRE DEPT THAT A 30" HP 15LB MAIN WAS DAMAGED BY THIRD PARTY CONTRACTOR, SOILTESTING INC. PERFORMING TEST BORINGS FOR THE NY PARKS DEPT. CONTRACTOR BORED THROUGH THE TOP OF THE 30" CI MAIN WITH 1 1/2" PILOT DRILL SUBSEQUENTLY CREATING THE RELEASE. UNDER DIRECTION FROM GAS CONTROL, FIELD OPERATIONS AND I&R NEEDED TO CLOSE 3 VALVES TO SHUT DOWN THE DISTRIBUTION PIPELINE. A 30" STYLE 50A FULL ENCIRCLEMENT SLEEVE WAS INSTALLED TO REPAIR THE DAMAGED AREA OF MAIN. THE MAIN WAS INSTALLED UNDER EASEMENT ON PRIVATE PROPERTY AND THE MARK OUT CONTRACTOR NEGLECTED TO MARK OUT THE AREA INSIDE THE PRIVATE PROPERTY (BASKETBALL COURT). APPLICABLE INTERSECTION DRAWINGS WERE ACCURATE AND UP TO DATE. APPROX. 111 SERVICES SUPPLYING 839 CUSTOMERS HAVE BEEN AFFECTED. AS OF 11/30/2016 APPROX. 17 INDIVIDUAL CUSTOMER METERS ARE STILL OFFLINE; AND A BUILDING WITH MULTI-METER COOKING LOADS STILL OUT OF SERVICE.
2025-03-31 10:13 | NO | YES | NO | 20160125 | 16456 | 2016-12-13 16:13 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2016-11-14 10:50 |  |  | 2016 | 1154 PARK AVENUE | SAN JOSE | SANTA CLARA | CA | 95126 | 37.3257 | -121.913 | [9 empty] | 2016-12-12 11:26 | 1166201 |  | NATURAL GAS |  | 1330 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-11-14 10:50 |  |  |  | 2016-11-14 10:54 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 200000 | 240260.7217079162 | 28000 | 33636.501039108268 | 0 | 0 |  |  | 4230 | 4868.490566037735849056603773584905660377 |  | 0 | 232230 | 117943.6539283181605067385444743935309973 | 278765.7133130622038490566037735849056604 | 0 | 0 | 13 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS LOCATION IS NOT PART OF SCADA | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | ELECTRIC | YES | 630500538 | USA NORTH |  | UTILITY OWNER | YES | YES | 650 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CHERYL QUIJANO | SENIOR GAS COMPLIANCE ENGINEER | c1dz@pge.com | 925-328-5269 |  |  |  |  | SUSIE RICHMOND | REGULATORY COMPLIANCE MANAGER | 925-328-5776 | gsr8@pge.com | ON NOVEMBER 14, 2016 AT 1049 HOURS, PG&E WAS NOTIFIED OF A THIRD PARTY DIG IN AT 1154 PARKAVENUE, SAN JOSE. A THIRD PARTY CONTRACTOR, SIGNAL ELECTRIC, STRUCK A 6-INCH STEEL MAIN WITH AN AUGER. THERE WAS A VALID USA TICKET (W630500538) AND PG&E FACILITIES WERE PROPERLY LOCATED AND MARKED. THE DIG-IN WAS A RESULT OF THE CONTRACTOR NOT EXPOSING THE LINE IN THE AREA OF WHERE THE BORE WOULD BE CONDUCTED. PG&E'S GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SITE AT 1054 HOURS AND GAS WAS SHUT IN AT 1555 HOURS BY SQUEEZING THE 6-INCH STEEL MAIN AND CLOSING THE VALVE ON GRANT STREET, RESULTING IN THE LOSS OF GAS FOR 13 CUSTOMERS. THE REPAIR CREW COMPLETED REPAIRS BY REPLACING A SECTION OF MAIN AND SERVICES WERE READY TO BE RESTORED BY 11/16/16 AT 1730 HOURS. POLICE AND FIRE DEPARTMENTS WERE REPORTED ON SITE. THERE ARE NO KNOWN INJURIES, FATALITIES, AND NO IGNITION ASSOCIATED WITH THIS INCIDENT. THIS INCIDENT WAS INITIALLY ONLY REPORTED TO THE CPUC WHEN MEDIA WAS OBSERVED ONSITE AT APPROXIMATELY 1151 HOURS. AFTER FURTHER INVESTIGATION, PG&E DETERMINED THAT THE ESTIMATED REPAIR COSTS EXCEEDED THE $50,000 CRITERIA ON 12/12/16 AT 1120 HOURS. PG&E REPORTED THE INCIDENT TO THE DOT ON 12/12/16 AT 1126 HOURS.
2025-03-31 10:13 | NO | YES | YES | 20160126 | 31221 | 2016-12-16 16:48 | SUPPLEMENTAL FINAL | 32513 | AMEREN ILLINOIS COMPANY | 10 EXECUTIVE DR. | COLLINSVILLE | IL | 62234 | 2016-11-16 17:44 |  |  | 2016 | 50 N. 1ST AVENUE | CANTON | FULTON | IL | 61520 | 40.5566 | -90.0337 | [9 empty] | 2016-11-16 18:26 | 1164320 |  | NATURAL GAS |  | 33.29 |  | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2 | 1 | 0 | 0 | 1 | 4 | YES |  |  |  |  | YES | 50 | 2016-12-16 16:06 |  |  |  | 2016-12-16 16:13 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 26 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2012 | [5 empty] | 1 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.099 |  | 2406 | MECHANICAL PUNCTURE | 0.8 | 0.3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 105000 | 126136.878896656005 | 128306 | 154134.460797279479786 | 4150000 | 4985409.97543926115 | TOTAL PUBLIC DAMAGE COSTS ARE SHOWN IN THIS FIELD. |  | 140 | 161.132075471698113207547169811320754717 |  | 0 | 4383446 | 2181036.33243978494373166037735849056604 | 5265842.44720866833289920754716981132075 | 110 | 0 | 20 |  |  |  |  | 31.2 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 3143162 | JULIE |  | CONTRACT LOCATOR | YES | YES | 69 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JOHN BOZARTH | MANAGER - PIPELINE SAFETY AND QUALITY ASSURANCE | jbozarth@ameren.com | 217-625-6854 | 314-613-2640 |  |  |  | JOHN BOZARTH | MANAGER - PIPELINE SAFETY AND QUALITY ASSURANCE | 217-625-6854 | jbozarth@ameren.com | FINAL UPDATE 11/21/2018 - THE TOTAL DAMAGES IN PART D,2.D. ARE UPDATED TO SHOW BEST KNOWN PUBLIC DAMAGE ESTIMATES. SUPPLEMENTAL UPDATE 06/01/2017 - THE NUMBER OF INJURIES REQUIRING INPATIENT HOSPITALIZATION WAS UPDATED, INCLUDING A MEMBER OF THE PUBLIC AND AN AMEREN ILLINOIS CONTRACT LOCATOR. THE DOLLAR AMOUNT OF PUBLIC DAMAGES IS STILL THE BEST KNOWN ESTIMATE. SUPPLEMENTAL UPDATE 03/16/2017 - ESTIMATE OF $5MM PUBLIC DAMAGE ADDED. THIS IS UNSUBSTANTIATED ESTIMATE AND WILL BE UPDATED ONCE BETTER INFORMATION IS KNOWN. A THIRD PARTY CONTRACTOR WAS DIRECTIONAL BORING TO INSTALL TELECOMMUNICATION UTILITY FACILITIES AND HIT AN AMEREN ILLINOIS (AIC) GAS FACILITY. AIC RESPONDED TO THE HIT FACILITY AND HAD FOUR EMPLOYEES WORKING AT THE SCENE WHEN THE BUILDING AT 50 N 1ST AVENUE EXPLODED. ONE AIC EMPLOYEE WAS KILLED AND THREE WERE INJURED, TWO OF WHICH REQUIRED INPATIENT HOSPITALIZATION. ADDITIONAL CONTRIBUTING FACTORS TO THE INCIDENT ARE CURRENTLY UNDER INVESTIGATION BY THE NATIONAL TRANSPORTATION SAFETY BUREAU (NTSB). CLARIFICATION ON RESPONSES AS FOLLOWS: A.12 - THERE WERE NEWS REPORTS OF 12 INJURIES INCLUDING AIC EMPLOYEES. AT THIS TIME WE ARE ONLY AWARE OF THE INJURIES TO AIC EMPLOYEES REQUIRING INPATIENT HOSPITALIZATION, AND ARE NOTE AWARE IF OTHER INJURIES REQUIRED INPATIENT HOSPITALIZATION. A.16 - THE EAST SIDE OF THE SQUARE WAS EVACUATED BY EMERGENCY RESPONDERS AND THE TOTAL NUMBER OF INDIVIDUALS EVACUATED IS UNKNOWN AT THIS TIME. THE RESPONSE OF 50 IS AN UNSUBSTANTIATED ESTIMATE OF THE INDIVIDUALS IN AND AROUND THE SQUARE THAT WOULD HAVE BEEN EVACUATED. D.2.A. - THE EXTENT OF PUBLIC DAMAGES TO PROPERTY WILL MOST LIKELY BE IN THE MILLIONS OF DOLLARS. AT THIS TIME, AIC DOES NOT HAVE A VALID ESTIMATION OF THIS AMOUNT. G.13.A. - THIS DURATION REPRESENTS THE TIME THAT THE FIRST SYSTEM VALVES WERE CLOSED TO ISOLATE GAS MAINS TO THE TIME THE LAST GAS MAIN SEGMENT WAS REPRESSURIZED AND PUT BACK INTO SERVICE.
2025-03-31 10:13 | NO | YES | NO | 20160127 | 16589 | 2016-12-19 14:22 | SUPPLEMENTAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2016-11-23 16:15 |  |  | 2016 | 1401 WEST 5TH STREET | SHERIDAN | SHERIDAN | WY | 82801 | 44.8087 | -106.9742 | [9 empty] | 2016-11-23 20:48 | 1164817 |  | NATURAL GAS |  | 466.64 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-11-23 16:27 |  |  |  | 2016-11-23 17:03 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2000 | [5 empty] | 3 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | OTHER | [8 empty] | COMPLETE SEVER OF SERVICE LINE, DUE TO 3RD PARTY DIG IN. | CLASS 3 LOCATION | 200000 | 240260.7217079162 | 4500 | 5405.8662384281145 | 1500 | 1801.9554128093715 | 0 | 0 | NO OTHER COSTS WERE INCURRED |  | 200 | 230.188679245283018867924528301886792453 |  | 0 | 206200 | 102706.9867490145615795148247978436657682 | 247698.7320383989690188679245283018867925 | 2 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | YES | YES | [6 empty] | YES |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 2016470065 |  |  | CONTRACT LOCATOR | YES | YES | 6 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | MATT KLINGENSTEIN | STAFF ENGINEER | matt.klingenstein@mdu.com | 7012227973 |  |  |  |  | PAT DARRAS | VP OPERATIONS | 7012227611 | pat.darras@mdu.com | EXCAVATION SUB-CONTRACTORS DANIELS INC. WAS EXCAVATING IN THE AREA TO CONNECT A STORM SEWER SYSTEM WITH A LARGE EXCAVATOR WHEN THEY DUG THROUGH THE LIVE 3-PHASE ELECTRICAL PRIMARY AND 3 INCH PE GAS SERVICE FEEDING THE HOSPITAL. THE RESULTING DAMAGE TO THE GAS AND ELECTRICAL SERVICES CAUSED AN ESCAPE OF GAS AND EVENTUALLY A FIRE. THE FIRE CONSUMED THE VACATED EXCAVATOR BEFORE THE FIRE COULD BE CONTROLLED BY FIRST RESPONDERS. MDU DID NOT HAVE AN INSPECTOR ON SITE AT THE TIME OF THE INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20160128 | 16794 | 2016-12-28 18:44 | SUPPLEMENTAL FINAL | 8160 | INTERMOUNTAIN GAS CO | 555 SOUTH COLE ROAD | BOISE | ID | 83709 | 2016-12-14 17:33 |  |  | 2016 | 4056 N CAN-ADA RD, NAMPA | Not Within a Municipality | ADA COUNTY | ID | 83687 | 43.644 | -116.4999 | [10 empty] | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 12431 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-12-14 17:39 |  |  |  | 2016-12-14 19:15 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2008 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | REGULATOR RELIEF BLOWING GAS | CLASS 1 LOCATION | 0 | 0 | 9972 | 11979.399584356701732 | 2493 | 2994.849896089175433 | 0 | 0 |  |  | 70703 | 81375.150943396226415094339622641509434 |  | 0 | 83168 | 81478.6640125823551571832884097035040431 | 96349.400423842103580094339622641509434 | 0 | 0 | 0 |  |  |  |  | 544 | 495 | 500 |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA WORKED AS INTENDED, ALARM DUE TO HIGH PRESSURE | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | LANCE ELROY | DIRECTOR OF OPERATIONS SERVICES | lance.elroy@intgas.com | 208-377-6122 |  |  |  |  | HART GILCHRIST | VP OPERATIONS | 208-377-6086 | hart.gilchrist@intgas.com | PILOT REGULATOR FILTER FAILURE DUE TO CONTAMINANTS IN FILTER - CAUSED OVER PRESSURE AND THE RELIEF TO BLOW. IGC REQUESTED THIS INCIDENT BE RETRACTED, AND WAS DENIED BY BRIAN PIERZINA, PHMSA ACCIDENT INVESTIGATOR. IGC DISAGREES WITH THIS DECISION AND IS WORKING WITH INGAA, WHO IS SEEKING CLARIFICATION FROM PHMSA LEADERSHIP ON THE DEFINITION OF AN INCIDENT, SINCE THE RULEMAKING LANGUAGE IN 2010 SUPPORTS THAT REGULATOR STATION RELIEF'S IN EXCESS OF 3M CUBIC FEET SHOULD NOT BE REPORTED AS INCIDENTS. -LANCE ELROY, IGC DIRECTOR OF OPERATIONS. 2-8-18.
2025-03-31 10:13 | NO | NO | NO | 20170001 | 33918 | 2017-01-06 13:32 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2016-12-08 07:33 |  |  | 2016 | 4095 N GOLDEN STAVE BLVD | FRESNO | FRESNO | CA | 93722 | 36.7944 | -119.8618 | [9 empty] | 2016-12-09 09:39 | 1165979 |  | NATURAL GAS |  | 329 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-12-08 07:33 |  |  |  | 2016-12-08 08:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 348 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2016 | [5 empty] | 2 | PE2406/2709 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 24 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 50000 | 60065.18042697905 | 8900 | 10691.6021160022709 | 0 | 0 |  |  | 1000 | 1150.943396226415094339622641509433962264 |  | 0 | 59900 | 30370.027264815524797574123989218328841 | 71907.7259392077359943396226415094339623 | 1 | 0 | 0 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BORING | UNKNOWN/OTHER | YES | 631300829 | N/A |  | UTILITY OWNER | YES | YES | 25 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | ENZA BARBATO | PROGRAM MANAGER | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON DECEMBER 8, 2016, AT 0733 HOURS, PG&E WAS NOTIFIED OF A THIRD PARTY DIG-IN NEAR 4095 N GOLDEN STATE BLVD IN FRESNO. THE DIG-IN OCCURRED AT THE ASHLAND AVE ON-RAMP. THIRD PARTY CONTRACTOR, MCM CONSTRUCTION STRUCK A 2" PLASTIC MAIN WHILE PERFORMING HORIZONTAL DRILLING. THERE WAS A VALID USA TICKET (X 631300829) AND PG&E FACILITIES WERE PROPERLY LOCATED AND MARKED PER PG&E PROCEDURES AND AGREEMENT WITH THE CONTACTOR; THE CONTRACTOR FAILED TO EXCAVATE WITHIN A SAFE DISTANCE TO PROTECT THE GAS MAIN FROM DAMAGE. PG&E'S GSR ARRIVED ON SITE AT APPROXIMATELY 0815 HOURS. PG&E REPAIR CREWS ARRIVED ON SITE AND SHUT IN THE FLOW OF GAS AT 0917 HOURS. THE REPAIR CREW INSTALLED A DEAD END AS A TEMPORARY REPAIR. 310 FEET OF NEW 2-IN PL WAS INSTALLED; CONNECTED TO 267 FEET OF EXISTING 2-IN PL AND THE SERVICE LINE; AND ALL PIPE WAS TESTED BEFORE RETURNING TO OPERATIONS ON 10/3/2019. ONE COMMERCIAL TRUCKING COMPANY CUSTOMER SERVICE (4011 W ASHLAN AVE, FRESNO) WAS IMPACTED. CNG WAS SET UP AND THE CUSTOMER WAS RESTORED ON 12/9/16 AT 1000 HOURS. POLICE AND FIRE DEPARTMENT WERE REPORTED ON SITE. NO KNOWN INJURIES, FATALITIES, OR IGNITION HAVE BEEN REPORTED WITH THIS INCIDENT. THIS INCIDENT IS BEING REPORTED TO THE CPUC DUE TO THE UNINTENTIONAL RELEASE OF GAS AND PRESENCE OF MAJOR MEDIA. AFTER FURTHER REVIEW, ESTIMATED COSTS FOR REPAIRS ARE EXPECTED TO BE GREATER THAN $50,000. THE ESTIMATED REPAIR COSTS WERE DETERMINED 12/9/16 AT APPROXIMATELY 0900 HOURS, AND REPORTED TO THE DOT ON 12/9/16 AT 0939 HOURS.
2025-03-31 10:13 | NO | YES | NO | 20170002 | 16470 | 2017-01-09 15:19 | SUPPLEMENTAL FINAL | 2432 | FLORIDA CITY GAS | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2016-12-09 15:01 |  |  | 2016 | 251 E FLORIDA AVE | MELBOURNE | BREVARD | FL | 32901 | 28.0559 | -80.6183 | [9 empty] | 2016-12-12 19:22 | 1166238 |  | NATURAL GAS |  | 194.16 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2016-12-09 15:45 |  |  |  | 2016-12-09 15:54 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 24 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 3478 | 4178.133950500662718 | 126116 | 151503.605894577797396 | 0 | 0 |  |  | 1126 | 1295.962264150943396226415094339622641509 |  | 0 | 130720 | 65677.5485086085263866684636118598382749 | 156977.7021092294035102264150943396226415 | 167 | 0 | 721 |  |  |  |  | 50 | 51 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OF THE INCIDENT WAS THIRD PARTY EXCAVATION DAMAGE AND WAS NOT RELATED TO CONTROLLER ACTIVITIES. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | LANDSCAPING | YES | 342610733 | SUNSHINE ONE-CALL |  | UTILITY OWNER | NO | YES | 22 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | lquezad@southernco.com | (630)388-2316 |  |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | (630)388-2316 | lquezad@southernco.com | LANDSCAPING CONTRACTOR WAS DIGGING OUTSIDE THE EXTENT/SCOPE OF THE ONE-CALL TICKET. A 4" STEEL MAIN WAS PUNCTURED WHICH RESULTED IN A RELEASE OF GAS AND SERVICE INTERRUPTION TO APPROXIMATELY 888 CUSTOMERS. THE LOCATION OF THE DAMAGE WAS ABOUT 485 FEET AWAY FROM THE AREA REQUESTED FOR LOCATING ON THE ONE-CALL TICKET CALLED IN BY THE EXCAVATOR. COMPANY LOCATORS ACCURATELY MARKED OUT THE COMPANY FACILITIES LOCATED WITHIN THE EXTENT OF THE ONE-CALL TICKET. THERE WERE NO MARKS IN THE AREA OF THE HIT BECAUSE THE EXCAVATOR WAS DIGGING OUTSIDE THE EXTENT OF THE ONE-CALL TICKET.
2025-03-31 10:13 | NO | YES | YES | 20170003 | 31667 | 2017-01-11 08:52 | SUPPLEMENTAL FINAL | 15469 | PHILADELPHIA GAS WORKS | 800 W. MONTGOMERY AVENUE | PHILADELPHIA | PA | 19122 | 2016-12-14 12:09 |  |  | 2016 | 915 S. 49TH STREET | PHILADELPHIA | PHILADELPHIA | PA | 19143 | 39.9461 | -75.2189 | [9 empty] | 2016-12-14 17:56 | 1166398 |  | OTHER GAS | CO FROM SEPTA AND NATURAL GAS PRESENT | 18 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 2 | 0 | 0 | 2 | YES |  |  |  |  | NO | 0 | 2016-12-14 07:07 |  |  |  | 2016-12-14 07:29 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 36 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | OTHER | SEPTA ELECTRICAL LINES SHORTED | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 38376 | 46101.227281314960456 | 0 | 0 |  |  | 38 | 43.73584905660377358490566037735849056604 |  | 0 | 38414 | 19134.203922894667056107816711590296496 | 46144.9631303715642295849056603773584906 | 0 | 0 | 0 |  |  |  |  | 0.28 | 0.28 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 5 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | JOSEPH HAWKINSON | VP FIELD OPERATIONS | joseph.hawkinson@pgworks.com | 215-684-6342 |  |  |  |  | RAYMOND WELTE | SR. VP FIELD OPERATIONS | 215-684-6033 | raymond.welte@pgworks.com | ON WEDNESDAY, DECEMBER 14, 2016, BETWEEN 07:00 AND 08:00 HUNDRED HOURS PGW RECEIVED MULTIPLE CALLS FROM CUSTOMERS CONCERNING SMOKE/ODORS COMING FROM THE STREETS IN THE VICINITY OF 900 S. 49TH STREET. PGW RESPONDED WITH PERSONNEL TO INVESTIGATE THE AREA. UPON ARRIVAL AND INVESTIGATION ON THE SCENE PGW FOUND HIGH CARBON MONOXIDE READINGS IN VARIOUS STRUCTURES AND HEAVY SMOKE COMING FROM TWO SEPTA MANHOLES. THE CAUSE OF THE SMOKE AND ODORS WERE DETERMINED TO BE CAUSED BY AN UNDERGROUND SHORT IN SEPTA ELECTRICAL LINES CAUSING A BURN OUT. BETWEEN 11:30 AND 12:00 HUNDRED HOURS TWO SEPTA EMPLOYEES ATTEMPTED TO VENTILATE A SEPTA MANHOLE IN FRONT OF 915 S. 49TH STREET AND THE MANHOLE IGNITED. THE TWO SEPTA EMPLOYEES WERE BURNED AND TAKEN TO THE HOSPITAL BY THE PHILADELPHIA FIRE DEPARTMENT. AN ELECTRIC VENTILATOR USED BY THE SEPTA EMPLOYEES MAY HAVE BEEN THE IGNITION SOURCE. THROUGH INVESTIGATION PGW IDENTIFIED A LOCATION WITH HIGH NATURAL GAS READINGS NEAR THE SOUTH EAST CORNER OF 49TH STREET AND WARRINGTON STREET. PGW EXCAVATED AND FOUND A LEAKING 4 INCH CAST IRON MAIN THAT CROSSED OVER TOP OF THE SEPTA DUCT. ELECTRICAL ARCING FROM THE SEPTA WIRES CREATED A LARGE BURN HOLE IN THE BOTTOM OF THE 4 INCH CAST IRON GAS MAIN. A TEMPORARY REPAIR WAS MADE ON THE 4 INCH MAIN AS OF 16:20 HOURS ON 12/14/2016. THE MAIN WAS LATER ABANDONED PERMANENTLY.
2025-03-31 10:13 | NO | YES | NO | 20170004 | 16475 | 2017-01-12 17:13 | ORIGINAL | 15359 | BLACK HILLS ENERGY | 655 EAST MILLSAP RD SUITE #104 | FAYETTEVILLE | AR | 72703-1002 | 2016-12-16 15:58 |  |  | 2016 | N.W.CORNER W. KELLI AVE. AND HWY 62 | FARMINGTON | WASHINGTON | AR | 72730-0000 | 36.0387 | -94.2553 | [9 empty] | 2016-12-16 21:06 | 1166574 |  | NATURAL GAS |  | 2684 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 96 | 2016-12-16 16:00 |  |  |  | 2016-12-16 16:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2006 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.156 | [6 empty] | OTHER | [8 empty] | 2" POST REGULATOR SET HIT BY VEHICLE | CLASS 3 LOCATION | 105000 | 126136.878896656005 | 22114 | 26565.627999244294234 | 23430 | 28146.54354808238283 | 0 | 0 |  |  | 10494 | 12078 |  | 0 | 161038 | 86075.1099295566098811428571428571428571 | 192927.050443982682064 | 0 | 0 | 4 |  |  |  |  | 285 | 285 | 415 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CLEARLY CAUSED BY OUTSIDE FORCE DAMAGE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | PRESTON WALKER | COMPLIANCE COORDINATOR | preston.walker@blackhillscorp.com | 479-575-1496 |  |  |  |  | BILL STEPHENS | SR MANAGER CODES STANDARDS | 303-566-3509 | bill.stephens@blackhillscorp.com | AT 3:58 P.M. ON DECEMBER 16, 2016, ON THE NORTHWEST CORNER OF THE INTERSECTION OF WEST KELLI AVE. AND HWY 62 (MAIN ST.) IN FARMINGTON, ARKANSAS, A VEHICLE TRAVELLING WEST ON HWY 62 LEFT THE ROADWAY AND STRUCK A BLACK HILLS ENERGY ARKANSAS, INC. ("BHEA" OR THE "COMPANY") 2-INCH POST REGULATOR SETTING THAT WAS CONNECTED TO A 4-INCH TRANSMISSION PIPELINE. THE REGULATOR SETTING WAS LOCATED 28.5 FEET FROM THE CURB OF HWY 62. THE IMPACT OF THE CAR STRIKING THE SETTING BROKE TWO 2" X 1" SWAGES ON THE HIGH PRESSURE SIDE OF THE REGULATOR AND TWO 2" STEEL PIPES ON THE INTERMEDIATE PRESSURE SIDE OF THE REGULATOR. THE GAS ESCAPING FROM THE BROKEN PORTIONS OF THE REGULATOR SETTING IGNITED IMMEDIATELY, RESULTING IN A LARGE FIRE. THE FIRST BHEA EMPLOYEES ARRIVED AT THE SCENE AT 4:00 P.M. AND 4:10 P.M., AND STARTED THE PROCESS OF ISOLATING THE EFFECTED SEGMENT OF THE COMPANY'S SYSTEM WITH THE ASSISTANCE OF THE FARMINGTON AND FAYETTEVILLE FIRE DEPARTMENTS. THE EMERGENCY SHUT OFF VALVE FOR THE SETTING, WHICH WAS LOCATED 21 FEET FROM THE SETTING, WAS INACCESSIBLE DUE TO THE SIZE OF THE FIRE. RATHER THAN STOP THE FIRE BY COMPLETELY SHUTTING OFF THE FLOW OF GAS TO THE PORTION OF BHEA'S SYSTEM IN THE AREA OF THE INCIDENT, WHICH WOULD HAVE RESULTED IN LOSS OF SERVICE TO HUNDREDS OF CUSTOMERS, BHEA DECIDED, BASED ON ALL OF THE CIRCUMSTANCES AT THE TIME OF THE INCIDENT, TO TAKE MEASURES TO REDUCE OR STOP THE FLOW OF GAS TO THE ISOLATED PORTION OF ITS SYSTEM FEEDING INTO THE REGULATOR SETTING IN ORDER TO STOP THE FIRE WHILE AT THE SAME TIME AVOIDING LOSS OF SERVICE TO ITS CUSTOMERS. THIS DECISION WAS MADE FOLLOWING DISCUSSIONS BETWEEN BHEA AND THE FIRE DEPARTMENTS THAT RESPONDED TO THE SCENE, DURING WHICH ALL PARTIES AGREED THAT THERE WERE NO IMPENDING RISKS TO HUMAN LIFE OR PROPERTY, SINCE THE PERSON THAT WAS APPARENTLY IN THE CAR THAT STRUCK THE REGULATOR SETTING WAS EITHER DECEASED PRIOR TO THE CAR HITTING THE SETTING OR DIED WHEN THE FIRE ERUPTED*, THE OCCUPANTS OF A NEARBY DUPLEX THAT HAD CAUGHT FIRE HAD BEEN SAFELY EVACUATED, AND NO OTHER LIVES WERE IN DANGER. REGARDING PROPERTY, AS MENTIONED, A DUPLEX NEXT TO THE REGULATOR SETTING HAD CAUGHT FIRE ALMOST IMMEDIATELY AFTER THE CAR HIT THE SETTING AND THE FIRE BEGAN, AND IT WAS QUICKLY APPARENT THAT IT COULD NOT BE SAVED FROM TOTAL LOSS. THERE WAS NO OTHER IMMINENT RISK TO PROPERTY, GIVEN THE FIRE WAS UNDER CONTROL AND WAS NOT SPREADING. IN ADDITION, BHEA WAS AWARE THAT THE WEATHER WAS FORECASTED TO TURN VERY COLD THE FOLLOWING DAY, WITH TEMPERATURES FORECASTED TO FALL INTO THE SINGLE DIGITS BY THE FOLLOWING NIGHT, MAKING ANY LOSS OF GAS SERVICE TO CUSTOMERS ALL THE MORE CONSEQUENTIAL. BECAUSE GAS WAS FEEDING INTO THE SETTING FROM FOUR DIFFERENT DIRECTIONS, THE PROCESS OF ISOLATING THE FLOW OF GAS TO THE SETTING TOOK SEVERAL HOURS, AND WAS COMPLETED AT APPROXIMATELY 12:40 A.M. ON THE MORNING OF SATURDAY, DECEMBER 17. AFTER THE FIRE DEPARTMENTS COMPLETED THEIR INVESTIGATION OF THE DAMAGED FACILITIES, BHEA BEGAN THE PROCESS OF REPLACING THE SETTING IN ORDER TO BRING THE SEGMENT OF THE SYSTEM BACK INTO SERVICE, WHICH TOOK PLACE AT 1:15 P.M. ON SATURDAY, DECEMBER 17. *THERE WAS APPARENTLY ONE PERSON IN THE CAR AT THE TIME IT HIT THE REGULATOR SETTING. FOLLOWING THE INCIDENT, BONE FRAGMENTS FROM THAT PERSON WERE FOUND IN THE CAR. THE INCIDENT IS STILL UNDER INVESTIGATION, AND AS OF THE DATE OF THIS REPORT, NEITHER THE CAUSE OF DEATH, NOR THE TIME OF DEATH (EITHER BEFORE THE INCIDENT OR AT THE TIME OF THE INCIDENT) HAS BEEN ESTABLISHED. UNTIL THE RESULTS OF THE RELEVANT AUTHORITIES' INVESTIGATIONS ARE RELEASED, BHEA HAS STATED ON THIS REPORT TO PHMSA THAT THERE WERE NO FATALITIES THAT RESULTED FROM THE INCIDENT. BHEA WILL UPDATE THIS REPORT ONCE IT RECEIVES FURTHER INFORMATION.
2025-03-31 10:13 | NO | YES | YES | 20170005 | 31259 | 2017-01-13 16:25 | SUPPLEMENTAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2016-12-15 16:12 |  |  | 2016 | 14145 PARKER ROAD | HOMER GLEN | WILL | IL | 60491 | 41.6309 | -87.9505 | [9 empty] | 2016-12-15 18:17 | 1166478 |  | NATURAL GAS |  | 13585.8 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | YES | 50 | 2016-12-15 15:55 |  |  |  | 2016-12-15 14:31 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 64 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1963 | [5 empty] | 6.625 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 12.5 | 0.5 |  | CLASS 3 LOCATION | 275000 | 330358.492348384775 | 133122 | 159919.938976006101882 | 2000 | 2402.607217079162 | 0 | 0 |  |  | 4755 | 5472.735849056603773584905660377358490566 |  | 0 | 414877 | 209116.3110724993962649649595687331536388 | 498153.7743905266426555849056603773584906 | 0 | 0 | 23 |  |  |  |  | 54 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [26 empty] | YES | [15 empty] | YES |  |  |  | NO | [86 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | lquezad@southernco.com | 630-388-2316 |  |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | 630-388-2316 | lquezad@southernco.com | DISCOVERED CRACKED 6" STEEL MAIN AT THE INTERSECTION OF 143RD ST AND PARKER ROAD. THERE WAS EVIDENCE OF A DENT FROM PREVIOUS EXCAVATION DAMAGE AT THE LOCATION OF THE CRACK. GAS MIGRATED THROUGH A SEWER AND RESULTED IN AN EXPLOSION AT 14145 PARKER RD., WHICH WAS A ABOUT ONE BLOCK AWAY FROM THE LOCATION OF THE CRACKED MAIN.
2025-03-31 10:13 | NO | YES | NO | 20170006 | 30133 | 2017-01-14 14:21 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2016-12-17 19:31 |  |  | 2016 | INTERSECTION OF 43RD AVENUE AND 104TH STREET | CORONA | QUEENS | NY | 11368 | 40.7478 | -73.8606 | [9 empty] | 2016-12-23 14:07 | 1167066 |  | NATURAL GAS |  | 113.47 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-12-17 19:31 |  |  |  | 2016-12-17 19:42 |  | NO | PUBLIC PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 36 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2016 | [5 empty] | 8 | ASTM D 2513 11C | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | LEAK |  |  | OTHER | 1.1 INCH HOLE FROM ELECTRICAL | [5 empty] | CLASS 4 LOCATION | 138501 | 166381.751086340508081 | 21986 | 26411.861137351227866 | 10180 | 12229.27073493293458 | 322 | 386.819761949745082 | FOR 2A,SEE PART H NARRATIVE FOR MORE DETAIL. |  | 1682 | 1935.886792452830188679245283018867924528 |  | 0 | 172671 | 86865.3469778780790927196765498652291105 | 207345.5895130272457976792452830188679245 | 1 | 0 | 3 |  |  |  |  | 10.8 | 14 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NATIONAL GRID WAS NOTIFIED ON 12/17/2016 AT 19:31 BY FDNY OF A MANHOLE FIRE IN THE INTERSECTION OF 43RD AVE & 104TH STREET. SUBSEQUENTLY, 12/17/16 @ 19:33 CON EDISON EMERGENCY ADVISED GAS CONTROL OF A MANHOLE FIRE. GAS CONTROL THEN NOTIFIED CMS AND GAS FIRE AND PIPELINE DAMAGE WAS CONFIRMED. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 5169030596 |  |  |  |  | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAM | 5169030596 | corinne.byrnes@gmail.com | UPDATE 2/26/2018 - SUPPLEMENTAL REPORT IS BEING FILED. THIS INCIDENT IS STILL UNDER INVESTIGATION; THEREFORE SECTIONS OF PART D ARE NOT AVAILABLE AND PART G CAUSE INFORMATION IS STILL UNKNOWN. UPDATE 3/21/2018 - SUPPLEMENTAL REPORT IS BEING FILED. PART G STATES OTHER OUTSIDE FORCE - ELECTRICAL ARCING. COSTS HAVE BEEN UPDATED. NATIONAL GRID WAS NOTIFIED ON 12/17/2016 BY FDNY OF A MANHOLE FIRE IN THE INTERSECTION OF 43RD AVE & 104TH STREET. NATIONAL GRID ARRIVED ON SCENE AND SECURED NATURAL GAS BY CLOSING VALVE (BQ5290) EXTINGUISHING THE GAS FED FIRE. AFTER FURTHER INVESTIGATION IT WAS DETERMINED THE CAUSE OF DAMAGE TO NATIONAL GRID'S GAS MAIN WAS DUE TO A FAULTY UNDERGROUND ELECTRICAL CABLE. ADDITIONAL INCIDENT INVESTIGATION WILL BE REQUIRED TO DETERMINE RESPONSIBLE PARTIES FOR THE ELECTRICAL CABLE DAMAGE AND THE SUBSEQUENT FIRE. ALL FOUR CUSTOMERS WHO WERE OUT OF SERVICE HAVE HAD SERVICE RESTORED PRIOR TO 1/14/2017. PLEASE NOTE THAT FOR PART D, 2A IS LEFT UNANSWERED. THERE WERE MULTIPLE UTILITY SUBSTRUCTURES INVOLVED IN THIS INCIDENT INCLUDING ELECTRICAL CABLE, TELECOMMUNICATIONS AND NATURAL GAS. THOSE COSTS WILL BE ENTERED AS THEY BECOME AVAILABLE. PLEASE NOTE THAT ALTHOUGH THE INCIDENT OCCURRED ON DECEMBER 17, 2016 AT APPROXIMATELY 19:31, THE EXTENT AND COST OF DAMAGE TO NON-OPERATOR PRIVATE PROPERTY WAS UNKNOWN. IT WAS NOT UNTIL DECEMBER 23, 2016 WHEN NATIONAL GRID LEARNED THAT THE COST WOULD EXCEED $50,000.00, WHICH ELEVATED THIS FAILURE TO A REPORTABLE INCIDENT (THE EXACT COST IS STILL UNKNOWN AND CONTINUES TO BE INVESTIGATED).
2025-03-31 10:13 | NO | NO | NO | 20170007 | 16576 | 2017-01-15 14:33 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2016-12-16 11:45 |  |  | 2016 | E CANYON RIM RD & SERRANO AVE | ANAHEIM | ORANGE | CA | 92807 | 33.8431 | -117.742 | [9 empty] | 2016-12-16 17:45 | 1166572 |  | NATURAL GAS |  | 62.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2016-12-16 11:45 |  |  |  | 2016-12-16 12:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 44 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1975 | [5 empty] | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 25856 | 31060.906102399406336 | 38305 | 46015.934725108650205 | 200 | 240.2607217079162 | 0 | 0 |  |  | 376 | 432.754716981132075471698113207547169811 |  | 0 | 64737 | 32422.7480675540263704878706199460916442 | 77749.8562661971048164716981132075471698 | 0 | 0 | 0 |  |  |  |  | 44 | 44 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [9 empty] | YES |  |  |  | LONG SEAM |  | YES | [86 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 6268934536 |  |  |  |  | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 6268934536 | kle2@semprautilities.com | ON DECEMBER 16, 2016, ANAHEIM FIRE DEPARTMENT REPORTED AN EXPLOSION IN AN UNDERGROUND ELECTRICAL VAULT AT THE INTERSECTION OF E CANYON RIM RD & SERRANO AVE IN ANAHEIM. CREW ARRIVED, CENTERED A LEAK OVER A 4 INCH PLASTIC MAIN AND CONTROLLED THE GAS BY PINCHING AND CAPPING THE MAIN. THERE WERE NO INJURIES OR FURTHER DAMAGE RESULTED FROM THIS INCIDENT. ALL REPAIRS TO THE DAMAGED MAIN WERE COMPLETED. THE DAMAGED PIPE REMOVED AND SENT TO SOCALGAS LABORATORY FOR A THOROUGH VISUAL INSPECTION. INVESTIGATION INTO THE CAUSE OF THE LEAK IS ON-GOING. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO A GAS RELEASE AND DAMAGES EXCEEDING $50,000. INVESTIGATION CLOSED. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2025-03-31 10:13 | NO | YES | YES | 20170008 | 16766 | 2017-01-17 10:51 | SUPPLEMENTAL FINAL | 31191 | ENERGY WEST MONTANA | NO. 1 FIRST AVENUE SOUTH P.O. BOX 2229 | GREAT FALLS | MT | 59403-2229 | 2016-12-27 11:35 |  |  | 2016 | 114 GEYSER ST. | WEST YELLOWSTONE | GALLATIN | MT | 59758 | 44.6612 | -111.109 | [9 empty] | 2016-12-27 18:15 | 1167302 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO |  |  |  |  | YES | 7 | 2016-12-27 11:46 |  |  |  | 2016-12-27 11:48 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 20 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1995 | [5 empty] | 1 | D2513 | UPONOR - ALDYL | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | OTHER | [8 empty] | ELECTRIC LINE FAILURE MELTED PIPE. | CLASS 3 LOCATION | 30000 | 36039.10825618743 | 7050 | 8469.19044020404605 | 1000 | 1201.303608539581 | 0 | 0 |  |  | 7 | 8.05660377358490566037735849056603773585 |  | 0 | 38057 | 18938.9992122026732952830188679245283019 | 45717.6589087046419556603773584905660377 | 0 | 0 | 3 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | OVER HEATED ELECTRIC LINE MELTED PE(POLYETHYLENE) SERVICE LINE. | [154 empty] | EVAN MATHEWS | DISTRICT MANAGER | emathews@egas.net | 406-646-4437 | 406-646-4830 |  |  |  | IRA SHAULIS | SAFETY DIRECTOR | 406-791-7552 | ishaulis@egas.net | THE HEAT FROM AN ELECTRIC LINE FAILURE HAD MELTED THE PIPE ENOUGH TO EMBED THE SANDY SOIL THAT HAD TURNED TO GLASS INTO THE PIPE WALL AND WHEN THE GROUND FROZE TO THAT DEPTH, THE SOIL AND FROST MOVEMENT CAUSED THE PIPE TO LEAK.
2025-03-31 10:13 | NO | NO | NO | 20170009 | 16484 | 2017-01-18 15:22 | SUPPLEMENTAL FINAL | 7348 | DOMINION HOPE | 781 CHESTNUT RIDGE RD | MORGANTOWN | WV | 26505 | 2016-12-20 14:28 |  |  | 2016 | 219 DUNKARD AVE | WESTOVER | MONONGALIA | WV | 26501 | 39.6379 | -79.9771 | [9 empty] | 2016-12-20 16:57 | 1166852 |  | NATURAL GAS |  | 7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2016-12-20 14:37 |  |  |  | 2016-12-20 15:14 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1.25 | BARE STEEL | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | PIPE BROKE OUT OF FITTING IN BASEMENT DUE TO EXCAVATOR WORK ON PROPERTY DURING GARAGE DEMOLITION | CLASS 3 LOCATION | 53800 | 64630.1341394294578 | 2930 | 3519.81957302097233 | 430 | 516.56055167201983 | 0 | 0 |  |  | 17 | 19.56603773584905660377358490566037735849 |  | 0 | 57177 | 28457.7105371841053842587601078167115903 | 68686.0803018582990166037735849056603774 | 0 | 0 | 1 |  |  |  |  | 0.47 | 0.47 | 0.75 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | UNKNOWN/OTHER | BACKHOE/TRACKHOE | BUILDING DEMOLITION | NO | [5 empty] | YES |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | SCOTT WALLACE | TECHNICAL SPECIALIST | scott.a.wallace@dom.com | 3048441256 |  |  |  |  | KAREN SEARLES | MANAGER GAS OPERATIONS | 304-581-5841 | karen.m.searles@dom.com | TIMELINE OF INCIDENT: -SUNDAY 12/18/16 GARAGE ROOF COLLAPSES AT 219 DUNKARD AVE WESTOVER,WV PROPERTY OWNER, PHIL LEINBACH HIRES FRIEND JESSE MAYLE TO REMOVE/TEAR DOWN GARAGE ON TUESDAY 12/20/16 (NO MISS UTILITY CALLED PRIOR TO WORK BEING DONE, BECAUSE THEY WEREN'T DIGGING AND THOUGHT THEY DIDN'T NEED ONE) -TUESDAY 12/20/16 TIMELINE; 14:28 - 911 DISPATCHES FIRE/EXPLOSION AT 219 DUNKARD AVE 14:32 - FIRE DEPARTMENT ON SCENE, HOUSE IS ON FIRE 14:37 - DOMINION HOPE RECEIVES CALL FROM 911 TO ADVISE OF FIRE/EXPLOSION 14:59 - ORDER IS ASSIGNED TO FMS DOUG SLOAN 15:14 - FMS ONSITE AT 219 DUNKARD AVE 15:30 - FMS CALLS PAUL KREIG, ADVISES SERVICE LINE AND HOUSE IS ON FIRE NEEDS CREW TO ASSIST IN TURNING OFF GAS 15:34 - C&M CREW DISPATCHED 15:45 - FIRE DEPARTMENT EXTINGUISHES FIRE, GAS IS LEAKING AT SEVERED SERVICE LINE 16:00 - CREW ARRIVES ONSITE 16:15 - GAS SHUT OFF, MADE SAFE 16:30 - C&M SUPERVISOR ARRIVES ONSITE, BEGINS INVESTIGATION 18:00 - ANNETTE BARKER REQUESTED ODORANT LEVEL READINGS FROM PIPELINE 18:15 - DOUG SLOAN CONDUCTED A POST INCIDENT LEAK SURVEY TO AREA, THE PIPELINE SYSTEM WAS COMPLIANT PROPERTY OWNER - PHIL LEINBACH 304 STILL HOUSE RD SALEM, WV 26426 304-376-9345 TENANT - NICK & AMANDA FILLIPPELLI 219 DUNKARD AVE WESTOVER, WV EXCAVATOR - JESSE MAYLE 304-376-2361 HELPER - MIKE FITZHENRY WITNESSED EXPLOSION AND CALLED 911 WESTOVER VOL. FIRE DEPT CO.23 FIRE CHIEF KENNETH GOODWIN JR. 11 COTTAGE STREET WESTOVER, WV 26501 304-296-0840 OFC 304-692-4788 CELL NO PERSONS WERE INJURED AS A RESULT OF THIS EXPLOSION/FIRE, BUT THE TENANTS DOG DID PERISH IN THE HOME. FIRE CHIEF KENNETH GOODWIN JR. IS RULING THE FIRE ACCIDENTAL. PROPERTY OWNER DID NOT HAVE INSURANCE. EXCAVATOR DID NOT HAVE INSURANCE, AND THE HOME IS CONSIDERED TO BE A TOTAL LOSS. IN REGARDS TO PART A 13.B - THE SERVICE LINE FACILITY HAS BEEN CUT AND ABANDONED AT THE MAIN. THIS FACILITY WILL NEVER BE RESTARTED.
2025-03-31 10:13 | NO | YES | NO | 20170010 | 16526 | 2017-01-19 16:00 | SUPPLEMENTAL FINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2016-12-23 03:52 |  |  | 2016 | 201 US 41 | L' ANSE | BARAGA | MI | 49946 | 46.7516 | -88.4562 | [9 empty] | 2016-12-23 07:11 | 1167036 |  | NATURAL GAS |  | 282 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-12-23 04:10 |  |  |  | 2016-12-23 04:10 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1985 | [8 empty] | STEEL |  | OTHER | ERW | 0.154 | [6 empty] | OTHER | [8 empty] | VEHICLE RAN OFF ROAD (US-41) AND HIT ABOVE GRADE REGULATOR/ METERING STATION. | CLASS 2 LOCATION | 0 | 0 | 500000 | 600651.8042697905 | 0 | 0 | 0 | 0 |  |  | 800 | 920.754716981132075471698113207547169811 |  | 0 | 500800 | 249623.7149915238423180592991913746630728 | 601572.5589867716320754716981132075471698 | 151 | 1 | 1041 |  |  |  |  | 119 | 119 | 275 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VEHICLE ACCIDENT DAMAGED FACILITIES. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | STEPHEN MAKOWSKI | MANAGER CODES AND STANDARDS | steve.makowski@semcoenergy.com | 8108874228 | 8108874233 |  |  |  | STEPHEN MAKOWSKI | MANAGER CODES AND STANDARDS | 8108874228 | steve.makowski@semcoenergy.com | ON DECEMBER 23, 2016 AT APPROXIMATELY 03:52 HOURS SEMCO ENERGY GAS COMPANY (SEMCO) RECEIVED A TELEPHONE CALL IN THE SERVICE DISPATCH CENTER IN PORT HURON THAT THERE HAD BEEN AN INCIDENT AT THE L'ANSE CITY GATE STATION (SEMCO REGULATOR STATION NO. 8031) WHICH SERVES THE VILLAGE OF L'ANSE, MICHIGAN AND THE SURROUNDING AREA. A SEMCO MECHANIC WAS DISPATCHED TO THE SITE AND ARRIVED AT 04:10 HOURS. UPON ARRIVAL THE MECHANIC DETERMINED THAT A VEHICLE HAD HIT A DISTRIBUTION REGULATOR STATION (SEMCO REGULATOR STATION NO. 8019) AND CAUSED A RELEASE OF GAS AND SUBSEQUENT IGNITION. AS A RESULT OF THE IGNITION AND THE PROXIMITY OF THE REGULATION/ METERING STATIONS DAMAGE OCCURRED TO BOTH SEMCO DISTRICT REGULATOR STATION NO. 8019 AND SEMCO CITY GATE STATION NO. 8031. THE DAMAGE TO THE STATION(S) REQUIRED AN ISOLATION AND SHUTDOWN OF THE L'ANSE CITY GATE STATION AT 04:52 HOURS RESULTING IN LOSS OF SERVICE TO APPROXIMATELY 1,193 SEMCO CUSTOMERS. ONCE THE SYSTEM HAD BEEN ISOLATED, THE SHUTDOWN PROCESS WAS THEN INITIATED WITH ALL SEMCO CUSTOMERS ON THE SYSTEM BEING SHUT DOWN BY 22:05 HOURS ON DECEMBER 23, 2016. FOLLOWING THE SHUTDOWN PROCESS GAS WAS REINTRODUCED TO THE SYSTEM AND THE CUSTOMER TURN ON AND RELIGHT PROCESS COMMENCED AT 22:50 HOURS ON DECEMBER 23RD. THE TURN ON AND RELIGHT PROCESS CONTINUED ON INTO DECEMBER 24TH AND BY APPROXIMATELY 19:00 HOURS ON DECEMBER 24TH APPROXIMATELY 1,107 CUSTOMERS HAD BEEN RECONNECTED AND SERVICE ESTABLISHED. WITH THE CHRISTMAS HOLIDAY WEEKEND, THE BALANCE OF THOSE CUSTOMERS THAT COULD NOT HAVE SERVICE RE-ESTABLISHED ('CAN'T GET IN' (CGI)) BY THE END OF DECEMBER 24TH WERE COMPLETED THE FOLLOWING WEEK.
2025-03-31 10:13 | NO | NO | NO | 20170011 | 16784 | 2017-01-19 16:40 | SUPPLEMENTAL FINAL | 8160 | INTERMOUNTAIN GAS CO | 555 SOUTH COLE ROAD | BOISE | ID | 83709 | 2017-01-13 03:53 |  |  | 2017 | 7525 EL PASO RD, CALDWELL | Not Within a Municipality | GEM COUNTY | ID | 83607 | 43.8109 | -116.6878 | [10 empty] | NRC NOTIFICATION NOT REQUIRED |  |  |  | 178 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-01-13 03:53 |  |  |  | 2017-01-13 04:45 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2010 | [8 empty] | OTHER | REGULATOR | [9 empty] | OTHER | [8 empty] | REGULATOR RELIEF VALVE BLOWING DUE TO REGULATOR FAILURE | CLASS 1 LOCATION | 0 | 0 | 0 | 0 | 578 | 682.17410672853833 | 0 | 0 |  |  | 964 | 989.490384615384615384615384615384615385 |  | 0 | 1542 | 1197.872594145993267538461538461538461538 | 1671.664491343922945384615384615384615385 | 0 | 0 | 0 |  |  |  |  | 176 | 145 | 150 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SYSTEMS AND ALARMS WORKED AS DESIGNED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  | YES | [73 empty] | LANCE ELROY | DIRECTOR OF OPERATIONS SERVICES | lance.elroy@intgas.com | 2083776122 |  |  |  |  | HART GILCHRIST | VP OPERATIONS | 2083776086 | hart.gilchrist@intgas.com | REGULATOR FAILURE DUE TO SULFUR BUILD-UP. RELIEF DID NOT FULLY VENT DUE TO WELD SLAG DEBRIS IN THE BOOT.
2025-03-31 10:13 | NO | YES | NO | 20170012 | 16487 | 2017-01-20 16:57 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2016-12-21 14:25 |  |  | 2016 | 2845 W. BROAD ST. | COLUMBUS | FRANKLIN | OH | 43204 | 39.9543 | -83.0759 | [9 empty] | 2016-12-21 15:21 | 1166923 |  | NATURAL GAS |  | 445.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 50 | 2016-12-21 14:25 |  |  |  | 2016-12-21 14:39 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1996 | [5 empty] | 6 | ASTM D2513 | CSR POLYPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 4.5 | [7 empty] | CLASS 3 LOCATION | 1200000 | 1441564.3302474972 | 8432 | 10129.392027205746992 | 14700 | 17659.1630455318407 | 0 | 0 |  |  | 1422 | 1636.64150943396226415094339622641509434 |  | 0 | 1224554 | 610075.8864410762935423504043126684636119 | 1470989.52682966874995615094339622641509 | 7 | 0 | 8 |  |  |  |  | 43 | 43 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 634200344 | OHIO UTILITY PROTECTION SERVICE |  | CONTRACT LOCATOR | NO | YES | 24 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | ROB SMITH | OPERATIONS COMPLIANCE MANAGER | rrsmith@nisource.com | 6148182110 | 6148182151 |  |  |  | ROB SMITH | OPERATIONS COMPLIANCE MANAGER | 6148182110 | rrsmith@nisource.com | ON DECEMBER 7, 2016, A THIRD-PARTY CONTRACTOR CALLED IN AN OBTAINED AN EXCAVATION ONE CALL TICKET FOR AN EXCAVATION IN FRONT OF 2857 W. BROAD ST. COLUMBUS, OHIO. COLUMBIA GAS OF OHIO'S THIRD-PARTY LOCATOR CLEARED THE TICKET ON DECEMBER 8, 2016, STATING THAT COLUMBIA GAS OF OHIO, INC., HAD NO GAS FACILITIES IN CONFLICT WITHIN THE SCOPE OF THE TICKET. HOWEVER, COLUMBIA GAS OF OHIO'S MAPS AND RECORDS, AVAILABLE TO THE THIRD-PARTY LOCATOR AT ALL TIMES RELEVANT TO THIS REPORT, ACCURATELY DEPICTED THE PRESENCE OF A NATURAL GAS FACILITY WITHIN THE SCOPE OF THE TICKET. ON DECEMBER 21, 2016, SHORTLY AFTER 2PM A THIRD-PARTY CONTRACTOR BORING IN TELECOMMUNICATION CONDUIT STRUCK AND DAMAGED A 6-INCH PLASTIC MAIN LINE WITHIN THE SCOPE OF THE AFOREMENTIONED TICKET. THE UNCONTROLLED RELEASE OF NATURAL GAS 36 INCHES BELOW THE BLACKTOP MIGRATED INTO A PIZZA SHOP AND EXPLODED AND CAUGHT FIRE. THE EXPLOSION AND FIRE DAMAGED SOME NEARBY VEHICLES AND THE ADJACENT BUILDING. COLUMBIA RESPONDED AND ESTABLISHED A PERIMETER AND MADE THE SITUATION SAFE BY ISOLATING THE DAMAGED SECTION OF MAINLINE FROM ITS GAS SUPPLY.
2025-03-31 10:13 | NO | NO | NO | 20170013 | 16804 | 2017-01-23 18:48 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2016-12-25 22:41 |  |  | 2016 | 126 W 53 STREET | NEW YORK | NEW YORK | NY | 10019-6006 | 40.7617 | -73.9803 | [9 empty] | 2016-12-26 00:20 | 1167187 |  | NATURAL GAS |  | 162 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2016-12-25 22:41 |  |  |  | 2016-12-25 23:03 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1930 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | DUE TO ELECTRIC BURNOUT | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 29787 | 35783.230587568499247 | 1803 | 2165.950406196864543 | 0 | 0 |  |  | 678 | 780.339622641509433962264150943396226415 |  | 0 | 32268 | 16439.2724587170370045552560646900269542 | 38729.5206164068732239622641509433962264 | 0 | 0 | 0 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | NICKOLAS HELLEN | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | hellenn@coned.com | ON DECEMBER 25, 2016, AT 22:41, THE FIRE DEPARTMENT OF THE CITY OF NEW YORK (FDNY) REPORTED A BUILDING FIRE WITH AN OUTDOOR GAS ODOR AT 126 WEST 53RD STREET IN MANHATTAN TO CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC). CON EDISON GAS DISTRIBUTION SERVICES (GDS) AND SUPERVISION WERE DISPATCHED AND ARRIVED AT 23:03. AT 23:10, GDS REPORTED THAT THERE WAS AN ACTIVE FIRE IN THE BASEMENT OF A NEW YORK CITY (NYC) TRANSIT SUBSTATION AS PER NYC EMERGENCY MANAGEMENT (NYC EM). THE GERC THEN NOTIFIED CON EDISON'S ELECTRIC OPERATIONS DEPARTMENT, WHICH DISPATCHED A CREW TO THE LOCATION TO ASSIST. ADDITIONAL PERSONNEL FROM CON EDISON'S GAS CONSTRUCTION DEPARTMENT WERE ALSO DISPATCHED BY THE GERC. GDS INVESTIGATED OUTSIDE AND, AT 23:29, REPORTED DETECTING 50% GAS-IN-AIR INSIDE ELECTRIC MANHOLE M10262. ACCORDING TO THE FDNY, THERE MAY HAVE BEEN AN ELECTRICAL OR GAS EXPLOSION IN MANHOLE M10262 PRIOR TO GDS' ARRIVAL. GDS THEN OPENED AND VENTED MANHOLE M10262. AT 00:05, CON EDISON GDS SUPERVISION REPORTED A BLOWING GAS CONDITION INSIDE THE BASEMENT OF THE SUBSTATION AT AN ELECTRICAL CONDUIT, WHERE A FLAME WAS VISIBLE. A MULTIPLE RESOURCE RESPONSE EVENT (CODE MURRE) WAS THEN INITIATED BY THE GERC. ON DECEMBER 26, 2016, AT 00:42, CON EDISON GDS SUPERVISION REPORTED DETECTING 40% GAS-IN-AIR INSIDE A SECOND ELECTRIC MANHOLE (M10278), WHICH WAS THEN OPENED AND VENTED. AT 01:48, CON EDISON GDS SUPERVISION REPORTED THAT THE FDNY WAS STANDING BY THE SMALL FLAME THAT WAS VISIBLE AT THE ELECTRICAL CONDUIT IN THE SUBSTATION BASEMENT. CON EDISON GAS CONSTRUCTION CREWS DETECTED GAS READINGS RANGING FROM 80% TO 100% OVER AN 8-INCH LOW PRESSURE STEEL GAS MAIN (INSTALLED IN 1930) LOCATED ON THE SOUTH SIDE OF WEST 53RD STREET. NYC EM REPORTED MULTIPLE SUBWAY INTERRUPTIONS AS A RESULT OF THE SUBSTATION FIRE. AT 02:20, CON EDISON GDS SUPERVISION REPORTED THAT A SMALL FLAME AT THE OPEN-END OF A 4-INCH ELECTRICAL CONDUIT INSIDE THE SUBSTATION EXTINGUISHED WHILE CON EDISON GAS CONSTRUCTION PERSONNEL WORKED TO LOCATE THE SOURCE OF THE LEAK. PRESSURE AND ODORANT READINGS WERE TAKEN AT A STOVE INSIDE THE SHERATON HOTEL, LOCATED AT 811 SEVENTH AVE., AND WERE FOUND TO BE WITHIN ACCEPTABLE RANGES. EMERGENCY MAIN STOP-OFF EXCAVATIONS AND LEAK LOCATION OPERATIONS REMAINED ONGOING AND, AT 09:06, A REPAIR CLAMP WAS INSTALLED ON THE LEAK, WHICH WAS FOUND ON THE BOTTOM OF THE 8-INCH STEEL GAS MAIN. THE 4-INCH STEEL ELECTRICAL CONDUIT GOING INTO THE SUBSTATION WAS DIRECTLY UNDER THE GAS MAIN IN THE AREA WHERE THE LEAK WAS FOUND. FOLLOWING INSTALLATION OF THE REPAIR CLAMP, ALL GAS READINGS VENTED TO 0%. A SEGMENT OF NYC TRANSIT'S SUBWAY SYSTEM WAS AFFECTED, RESULTING IN APPROXIMATELY 1,200 EVACUATIONS FROM STRANDED SUBWAY TRAINS. FDNY FIRE MARSHALS AND NEWS MEDIA FROM CHANNELS 2, 4, 7, 11, AND 12 WERE ON LOCATION. THE FDNY FIRE MARSHAL INVESTIGATION DETERMINED THAT ELECTRICAL WIRING WAS THE CAUSE OF THE INCIDENT. NO INJURIES, ILLNESSES, OR BUILDING EVACUATIONS WERE REPORTED. THE U.S. DEPARTMENT OF TRANSPORTATION, THE NEW YORK STATE DEPARTMENT OF PUBLIC SERVICE AND THE NYC DEPARTMENT OF ENVIRONMENTAL PROTECTION WERE NOTIFIED.
2025-03-31 10:13 | NO | NO | NO | 20170014 | 16785 | 2017-01-30 16:21 | SUPPLEMENTAL FINAL | 8160 | INTERMOUNTAIN GAS CO | 555 SOUTH COLE ROAD | BOISE | ID | 83709 | 2017-01-25 16:46 |  |  | 2017 | 300 N 300 E | JEROME | JEROME | ID | 83338 | 42.7677 | -114.4634 | [10 empty] | NRC NOTIFICATION NOT REQUIRED |  |  |  | 48 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-01-25 16:46 |  |  |  | 2017-01-25 17:30 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2002 | [8 empty] | OTHER | REGULATOR | [9 empty] | OTHER | [8 empty] | REGULATOR FAILURE AND RELIEF BLOWING | CLASS 2 LOCATION | 0 | 0 | 200 | 236.046403712297 | 200 | 236.046403712297 | 0 | 0 |  |  | 264 | 270.980769230769230769230769230769230769 |  | 0 | 664 | 446.199759057647723076923076923076923077 | 743.073576655363230769230769230769230769 | 0 | 0 | 0 |  |  |  |  | 437 | 350 | 380 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | REGULATOR FAILED AND RELIEF BLEW FOR SHORT DURATION AND THE INCIDENT WAS HANDLED AS EXPECTED. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES |  |  | YES | [73 empty] | LANCE ELROY | DIRECTOR OF OPERATIONS SERVICES | lance.elroy@intgas.com | 2083776122 |  |  |  |  | HART GILCHRIST | VP OF OPERATIONS | 2083776086 | hart.gilchrist@intgas.com | PRIMARY REGULATOR FAILED DUE TO DEBRIS AND RELIEF DID NOT REACT AS QUICKLY DUE TO ICE BUILDUP. RELIEF PRESSURE WAS SET AT 416 PSIG AT THE TIME OF THE INCIDENT, JUST UNDER THE 418 PSIG LIMIT OF 110% OF MAOP; CORRECTIVE ACTION TAKEN TO CHANGE THE RELIEF SET PRESSURE TO 400 PSIG, AND BOTH PRIMARY AND SECONDARY RUNS WERE REBUILT AND SET TO 350 PSIG AND 330 PSIG RESPECTIVELY.
2025-03-31 10:13 | NO | NO | NO | 20170015 | 16512 | 2017-02-06 11:06 | SUPPLEMENTAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2017-01-19 18:24 |  |  | 2017 | 1317 SOUTH HILLS DRIVE | WENATCHEE | CHELAN | WA | 98801-1985 | 47.4058 | -120.3328 | [9 empty] | 2017-01-23 14:11 | 1169311 |  | NATURAL GAS |  | 3875 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-01-19 07:24 |  |  |  | 2017-01-19 07:50 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 34 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1967 | [5 empty] | 2.375 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 6.5 | 2.1 |  | CLASS 3 LOCATION | 2000 | 2360.46403712297 | 365 | 430.784686774942025 | 7642 | 9019.33308584686837 | 0 | 0 | N/A |  | 20000 | 20528.8461538461538461538461538461538462 |  | 0 | 30007 | 23881.9733856862403736153846153846153846 | 32339.4279635909342411538461538461538462 | 0 | 0 | 1 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | MATERIAL FAILURE OF PIPE OR WELD | BUTT WELD | [146 empty] | BUTT WELD |  |  | PIPE | [35 empty] | YES | NONE | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | CHRIS GRISSOM | MANAGER STANDARDS AND COMPLIANCE | christopher.grissom@cngc.com | 509-531-6427 |  |  |  |  | MIKE EUTSEY | DIRECTOR OPERATION SERVICES | 509-734-4576 | mike.eutsey@cngc.com | THE CASCADE NATURAL GAS CORPORATION (CNGC) PIPELINE AFFECTED WAS A 2" STEEL MAIN THAT WAS INSTALLED IN 1967. THE PIPELINE SEPARATED AT A GIRTH WELD CAUSING THE UNINTENTIONAL RELEASE OF MORE THAN 3 MILLION CUBIC FEET OF GAS, TOTAL GAS LOSS WAS ESTIMATED TO BE 3,875 MCF. THE AREA IN WHICH THE RELEASE OCCURRED WAS EXPERIENCING EXTREME COLD WEATHER AND SUBSTANTIAL UNDERGROUND FROST. THE DAMAGE TO THE PIPELINE OBSERVED WAS CONSISTENT WITH DAMAGE CAUSED BY FROST HEAVE. FROST HEAVE IS THOUGHT TO BE A CONTRIBUTING FACTOR TO THE RELEASE. THE SEPARATED GIRTH WELD WAS RETAINED BY CNGC AND UNDERWENT AN EXAMINATION BY QUALIFIED STAFF. THE EXAMINATION CONCLUDED THAT THE WELD HAD FAILED AND CNGC CLASSIFIED THE LEAK AS A "PIPE, WELD OR JOINT FAILURE" AS A RESULT. THE SUB CAUSE WAS DETERMINED TO BE A CONSTRUCTION DEFECT CAUSED BY POOR WORKMANSHIP. CNGC WORKED CLOSELY WITH EMERGENCY RESPONDERS AND QUICKLY MOBILIZED RESOURCES AND EQUIPMENT TO ENSURE PUBLIC SAFETY. NO INJURIES, DAMAGE TO PROPERTY (OTHER THAN CNGC PIPELINE) OR IGNITION OCCURRED.
2025-03-31 10:13 | NO | YES | YES | 20170016 | 16578 | 2017-02-11 01:12 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2017-01-12 06:24 |  |  | 2017 | 2209 S GEORGE WASHINGTON BLVD | YUBA CITY | SUTTER | CA | 95993 | 39.0951 | -121.6721 | [9 empty] | 2017-01-12 08:45 | 1168402 |  | NATURAL GAS |  | 531 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 6 | 2017-01-12 06:24 |  |  |  | 2017-01-12 07:15 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  | 55 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1974 | [5 empty] | 4 | ALDYL-A | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | UNKNOWN | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | 250000 | 295058.00464037125 | 90000 | 106220.88167053365 | 10000 | 11802.32018561485 | 0 | 0 |  |  | 1500 | 1539.663461538461538461538461538461538462 |  | 0 | 351500 | 172510.1257139032961538461538461538461538 | 414620.8699580582115384615384615384615385 | 0 | 0 | 6 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM OPERATED AS INTENDED | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 1973 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES |  |  |  | YES |  |  |  | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | YES | 1973 | 90 | [84 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON JANUARY 12, 2017 AT 0624 HOURS, PG&E WAS NOTIFIED OF A STRUCTURE FIRE AT 2209 S GEORGE WASHINGTON BLVD, YUBA CITY. THE FIRE DEPARTMENT CALLED BACK AT 0658 ADVISING PG&E OF AN EXPLOSION RESULTING IN A COLLAPSE OF A RESIDENTIAL HOME. PG&E'S GSR ARRIVED ON SCENE AT 0715 HOURS AND CLOSED THE SERVICE VALVE WITH NO VISIBLE DAMAGE TO THE METER. PG&E CREWS ARRIVED ON SCENE AT 0740 HOURS AND SQUEEZED THE 4-INCH PLASTIC MAIN AT 0859 HOURS. GAS SERVICE TO 6 CUSTOMERS WAS IMPACTED. CNG WAS DEPLOYED, AND THE CUSTOMERS THAT WANTED THEIR SERVICE RESTORED WERE COMPLETED BY 2130 HOURS. TWO CUSTOMERS WERE INJURED INSIDE THE HOUSE AND WERE TAKEN TO THE HOSPITAL. ONE OF THE CUSTOMERS WAS RELEASED AT 1500 HOURS. THE LEAK SOURCE APPEARED TO BE A BUTT FUSION JOINT SOUTH OF THE SERVICE TEE OF THE AFFECTED HOME. THE SITE WAS MONITORED UNTIL THE AREA WAS MADE SAFE. THE MAIN AND SERVICES ARE CURRENTLY BEING REPLACED. THERE WERE NO FATALITIES. POLICE AND FIRE DEPARTMENT WERE REPORTED ON-SITE. THE INCIDENT WAS REPORTED TO THE CPUC AND DOT DUE TO DAMAGE COSTS EXCEEDING $50,000. THIS INCIDENT WAS REPORTED TO DOT AT 0845 HOURS (DOT #1168402).
2025-03-31 10:13 | NO | NO | NO | 20170017 | 16583 | 2017-02-15 16:24 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2017-01-16 05:28 |  |  | 2017 | 1104 MEDA AVE. | GLENDORA | LOS ANGELES | CA | 91741 | 34.1388 | -117.856 | [9 empty] | 2017-01-16 13:16 | 1168730 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-01-16 05:30 |  |  |  | 2017-01-16 05:45 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1953 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.133 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 60000 | 70813.9211136891 | 200 | 236.046403712297 | 0 | 0 |  |  | 6 | 6.15865384615384615384615384615384615385 |  | 0 | 60206 | 29432.4627766375207846153846153846153846 | 71056.1261712475508461538461538461538462 | 0 | 0 | 61 |  |  |  |  | 47 | 47 | 52 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE MANAGER | tbauer@semprautilities.com | 909-376-7208 |  |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE MANAGER | 909-376-7208 | tbauer@semprautilities.com | ON JANUARY 16, 2017, SOCALGAS RECEIVED MULTIPLE REPORTS OF NO-GAS FROM CUSTOMERS. CREW RESPONDED AND DISCOVERED THAT WATER HAS ENTERED INTO A 0.75 INCH STEEL GAS SERVICE. NO INJURIES OR FURTHER DAMAGE RESULTED FROM THIS INCIDENT. THE GAS LEAK WAS ISOLATED FROM THE PIPELINE SYSTEM. ALL REPAIRS TO THE DAMAGED GAS SERVICE WERE COMPLETED AND THE AFFECTED CUSTOMERS WERE RESTORED. INVESTIGATION OF THE INCIDENT SHOWED THAT A TRANSFORMER EXPLODED NEARBY CREATING AN ARC THAT CAUSED PINHOLE LEAKS IN A WATER SERVICE AND A GAS SERVICE. THE WATER EVENTUALLY ENTERED INTO THE GAS PIPELINE SYSTEM CAUSING OUTAGES TO CUSTOMERS. FOR ANY FURTHER QUESTIONS, CONTACT MIKE BARRINGER AT 714-478-0745.
2025-03-31 10:13 | NO | NO | NO | 20170018 | 16775 | 2017-02-17 15:29 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2017-02-07 00:39 |  |  | 2017 | 726 EAST 900 NORTH STREET | MAYS | RUSH | IN | 46155 | 39.7436 | -85.432 | [9 empty] | 2017-02-07 02:33 | 1170417 |  | NATURAL GAS |  | 235 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 5 | 2017-02-07 00:39 |  |  |  | 2017-02-07 00:39 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1983 | [5 empty] | 3 | ALDYL "A" | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 60000 | 70813.9211136891 | 14283 | 16857.253921113690255 | 16000 | 18883.71229698376 | 0 | 0 |  |  | 759 | 779.069711538461538461538461538461538462 |  | 0 | 91042 | 44852.5237040424849948461538461538461538 | 107333.9570433250117934615384615384615385 | 2 | 0 | 0 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [9 empty] | YES |  |  |  | OTHER | 3" ALDYL "A" 90 DEGREE ELBOW | NO | [86 empty] | JOHN SPINKS | MANAGER GAS COMPLIANCE AND QMP | jaspinks@vectren.com | 937-440-1844 | 937-440-1818 |  |  |  | JIM FRANCIS | VICE PRESIDENT SAFETY AND SYSTEM INTEGRITY | 812-491-4369 | jmfrancis@vectren.com | ON MONDAY EVENING, FEBRUARY 6, 2017 AT APPROXIMATELY 10:09 PM EST, VECTREN RESPONDED TO AN OUTSIDE ODOR CALL AT 8944 CROSSWAY DRIVE IN MAYS, INDIANA. VECTREN'S FIRST RESPONDER DISCOVERED A GAS LEAK AGAINST THE BUILDING FOUNDATION AT THAT LOCATION AND INITIATED APPROPRIATE STEPS TO REMEDIATE THE LEAK. WHILE THOSE STEPS WERE UNDERWAY, AT APPROXIMATELY 12:39 AM, TUESDAY MORNING, FEBRUARY 7, 2017, THE FIRST RESPONDER WITNESSED WHAT HE DESCRIBED AS AN EXPLOSION AT 726 EAST 900 NORTH STREET WHICH IS APPROXIMATELY 200 FEET AWAY FROM 8944 CROSSWAY DRIVE. THE FIRST RESPONDER CONTACTED 911 AND NOTIFIED HIS SUPERVISION OF THE EVENT AND REQUESTED ADDITION SUPPORT. VECTREN'S INDEPENDENT INVESTIGATION INTO THE ORIGIN OF THIS INCIDENT IS ONGOING. UPDATE: FURTHER INVESTIGATION DISCOVERED A 3" ELBOW CONNECTING TWO SECTIONS OF MAIN IN THE VICINITY OF THE INCIDENT WAS CRACKED. THE ELBOW WAS CUT OUT AND REPLACED. SUBSEQUENT TO THAT REPLACEMENT, ALL THE ALDYL "A" PIPING IN THE VICINITY HAS BEEN REPLACED.
2025-03-31 10:13 | NO | YES | NO | 20170019 | 16495 | 2017-02-17 15:47 | ORIGINAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2017-01-19 13:29 |  |  | 2017 | 1974 E MILWAUKEE AVENUE | DETROIT | WAYNE | MI | 48211-2001 | 42.3761 | -83.0535 | [9 empty] | 2017-01-20 16:18 | 1169086 |  | NATURAL GAS |  | 9834 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-01-19 13:29 |  |  |  | 2017-01-19 13:52 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 60 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1901 | [5 empty] | 12 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | MECHANICAL PUNCTURE | 8 | 8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 120132 | 141783.63285382831602 | 9234 | 10898.26245939675249 | 0 | 0 |  |  | 34814 | 35734.5625 |  | 0 | 164180 | 96292.824402552215282 | 188416.45781322506851 | 0 | 0 | 0 |  |  |  |  | 10 | 10 | 10 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 63371000 |  |  | UTILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JOHN D LUEDERS | PRINCIPAL COMPLIANCE ENGINEER | john.lueders@dteenergy.com | 6166322646 | 6166322687 |  |  |  | JOHN D LUEDERS | PRINCIPAL COMPLIANCE ENGINEER | 6166322646 | john.lueders@dteenergy.com | A CONTRACTOR INSTALLING TELECOMMUNICATIONS CABLE BY DIRECTIONAL DRILLING STRUCK AND PUNCTURED A 12-INCH CAST IRON MAIN OPERATING AT 10 PSIG APPROX. 280 FEET WEST OF EAST GRAND BLVD. INVESTIGATION REVEALED THE MAIN TO HAVE BEEN CORRECTLY MARKED IN RESPONSE TO THE CONTRACTOR'S MARK-OUT REQUEST; HOWEVER, THERE WAS NO EVIDENCE OF POTHOLING OR OTHER METHOD HAVING BEEN USED TO VERIFY THE LOCATION AND DEPTH OF THE MAIN. RESPONSE BY DTE GAS ON 1/19/2017 FROM THE TIME OF THE CONTRACTOR'S DAMAGE REPORT UNTIL ARRIVAL ON THE SCENE TOOK 23 MINUTES. INITIAL CONTROL OF GAS FROM THE BREAK OCCURRED AT 03:17 ON 1/20/2017; HOWEVER, THE SHUT-OFF WAS NOT MAINTAINED AND FURTHER WORK WAS REQUIRED UNTIL, AT 11:00 ON 1/20/2017, THE SITUATION WAS MADE SAFE AND WORK PROCEEDED ON MAKING REPAIRS. ESTIMATES OF REPAIR AND LABOR COSTS ALREADY EXPENDED ALONG WITH COSTS FOR REMAINING REPAIR AND RECOVERY WORK WERE DETERMINED AT 16:18 ON 1/20/2017 TO LIKELY EXCEED THE $50,000 REPORTING THRESHOLD; TELEPHONIC NOTICE WAS THEN MADE TO THE NATIONAL RESPONSE CENTER. REPLACEMENT OF A 15-FOOT SECTION OF 12-INCH CAST IRON MAIN WITH NEW 8-INCH POLYETHYLENE PIPE WAS COMPLETED AT 18:30 ON 1/20/2017, AND REGULAR OPERATION RESUMED. THERE WAS NO INTERRUPTION OF SERVICE TO CUSTOMERS DURING THE EVENT. NOTE: THE ACTUAL TICKET NUMBER RECEIVED FROM OUR STATE ONE-CALL SYSTEM WAS B63371000. THE PHMSA FORM DOES NOT ALLOW ALPHABETIC CHARACTERS.
2025-03-31 10:13 | NO | YES | YES | 20170020 | 31894 | 2017-02-17 21:51 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2017-01-20 15:28 |  |  | 2017 | 1748 S MOUNTAIN AVE | ONTARIO | SAN BERNARDINO | CA | 91762 | 34.0414 | -117.6705 | [9 empty] | 2017-01-20 17:00 | 1169104 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 0 | 2017-01-20 15:28 |  |  |  | 2017-01-20 15:46 |  | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | BELOW CONCRETE UTILITY BOX LOCATED BELOW | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1983 | [5 empty] | 2 | UNKNOWN | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 100000 | 118023.2018561485 | 40000 | 47209.2807424594 | 200 | 236.046403712297 | 0 | 0 |  |  | 0 | 0 |  | 0 | 140200 | 68532.1020881670654 | 165468.529002320197 | 0 | 0 | 1 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | CRACKED ADYLA-A |  |  | YES | [11 empty] | YES |  |  |  | OTHER | EXCESSIVE BENDING STRAIN | YES | 1983 | 100 | [84 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 626-893-4536 | kle2@semprautilities.com | ON JANUARY 20, 2017, AT APPROXIMATELY 15:28, SOCALGAS COMPANY (SCG) WAS NOTIFIED OF AN EXPLOSION THAT OCCURRED AT 1748 S. MOUNTAIN AVENUE, UNIT A, ONTARIO, CA 91762. ACCORDING TO THE ONTARIO FIRE DEPARTMENT, AN INDIVIDUAL WENT INTO THE GARAGE TO SMOKE A CIGARETTE, AND THE EXPLOSION OCCURRED AFTER HE LIT A LIGHTER. THE INDIVIDUAL WAS TRANSPORTED TO ARROWHEAD REGIONAL TO BE TREATED FOR HIS INJURIES. SCG FIRST RESPONDERS ARRIVED TO THE SCENE AND REPORTED GAS INDICATIONS AT THE MSA. CONSEQUENTLY, A STEP II LEAK INVESTIGATION WAS CONDUCTED SUCCESSFULLY. PRESSURE AND LOCK-UP WAS WITHIN TOLERANCE AND THE METER WAS HARD CLOSED. UNDERGROUND SAMPLES WERE TAKEN TO DETERMINE THE LOCATION OF THE LEAK. LEAK INDICATIONS WERE FOUND AT THE MAIN TO MAIN TIE-IN, WHICH IS APPROXIMATELY 15 FT FROM THE GARAGE WHERE THE EXPLOSION OCCURRED. AFTER FURTHER INVESTIGATION, THE LEAK WAS FOUND ON A CRACKED ALDYL-A TEE FITTING AT THE MAIN TO MAIN TIE-IN. WE FOUND A HAIRLINE CRACK APPROXIMATELY 1 1/2 INCHES LONG ON ONE OF THE ARMS OF THE 'TEE'. THE CRACKED FITTING WAS FOUND UNDERGROUND WITH OTHER SUBSTRUCTURES, YET LOCATED DIRECTLY BELOW A CONCRETE ELECTRICAL BOX OWNER BY GTE. GTE WAS AN OLD TELCO COMPANY NOW OWNED BY FRONTIER. THE EDGE OF THE CONCRETE BOX, LINED UP WITH THE LOCATION OF THE CRACK. THE FITTING AND SEVERAL FEET OF PIPE WERE REPLACED AND SECURED AS EVIDENCE BY THE GAS COMPANY. UPDATED 3/3/2019 - FURTHER INVESTIGATION SHOWED THE IDENTIFIED LEAK CAUSE WAS "EXCESSIVE BENDING STRAIN". FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2025-03-31 10:13 | NO | YES | YES | 20170021 | 16498 | 2017-02-21 18:14 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2017-01-25 11:02 |  |  | 2017 | 445 HWY 36 N | ROSENBERG | FT. BEND | TX | 77471 | 29.5629 | -95.8232 | [9 empty] | 2017-01-25 12:32 | 1169490 |  | NATURAL GAS |  | 120.55 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2017-01-25 11:02 |  |  |  | 2017-01-25 11:02 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1996 | [5 empty] | 0.216 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | MECHANICAL PUNCTURE | 3 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1467 | 1731.400371229698495 | 522 | 616.08111368909517 | 0 | 0 |  |  | 649 | 666.161057692307692307692307692307692308 |  | 0 | 2638 | 1588.494407683384072230769230769230769231 | 3013.642542611101357307692307692307692308 | 1 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | STATE HIGHWAY |  |  |  |  | YES | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 570199464 | LONE STAR 811 |  | CONTRACT LOCATOR | YES | YES | 9 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | LESLIE J. DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steven.yarbrough@centerpointenergy.com | CONTRACTOR OPERATING BACKHOE DAMAGED 2" PLASTIC SERVICE LINE AND ESCAPING GAS IGNITED, CONTRACT EMPLOYEE WAS INJURED BY FLASH-FIRE AND HOSPITALIZED.
2025-03-31 10:13 | NO | YES | NO | 20170023 | 16745 | 2017-02-23 21:08 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2017-01-25 09:22 |  |  | 2017 | EAST BIDWELL ST AND OAK AVE PARKWAY | FOLSOM | SACRAMENTO | CA | 95630 | 38.6646 | -121.136 | [9 empty] | 2017-01-25 15:20 | 1169517 |  | NATURAL GAS |  | 40 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-01-25 09:22 |  |  |  | 2017-01-25 10:20 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | OVER PRESSURE EVENT | CLASS 3 LOCATION | 0 | 0 | 1862000 | 2197592.01856148507 | 1833000 | 2163365.290023202005 | 0 | 0 |  |  | 150 | 153.966346153846153846153846153846153846 |  | 0 | 3695150 | 1806320.15410271314961538461538461538462 | 4361111.27493084092115384615384615384615 | 0 | 0 | 0 |  |  |  |  | 114 | 54 | 60 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM OPERATED AS INTENDED | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON JANUARY 25, 2017 AT 0922 HOURS, PG&E DETECTED AN OVERPRESSURE EVENT WITH THE SCADA SYSTEM NEAR 1717 DORNIE CIRCLE, FOLSOM. THE REGULATOR AND MONITOR VALVES AT PG&E'S REGULATOR STATION A-55 NEAR THE INTERSECTION OF EAST BIDWELL STREET AND OAK AVENUE PARKWAY IN FOLSOM FAILED TO ACHIEVE LOCK-UP, RESULTING IN AN OVERPRESSURE EVENT. THE MAOP PLUS ALLOWABLE WAS EXCEEDED AT 0941 HOURS. PG&E CREWS ARRIVED ON-SITE AT 1020 HOURS. WHEN PG&E CREWS ARRIVED ON-SITE, THE PRESSURE WAS READING AT 114 PSIG. THE CREW SHUT IN TWO REG STATIONS TO REDUCE PRESSURE AND THE PRESSURE RETURNED TO NORMAL AT 1107 HOURS. GAS SERVICE REPRESENTATIVES (GSRS), GPOM CREWS, M&C CREWS, AND LEAK SURVEY PERSONNEL WERE DISPATCHED AND STAGED TO PERFORM LEAK SURVEY, INSPECT FILTERS AND REG STATIONS, AND PERFORM ANY NECESSARY REPAIRS. M&C COMPLETED REPAIRS ON ALL GRADE 1 LEAKS IDENTIFIED FROM THE POST-INCIDENT LEAK SURVEY AND THE REMAINING LEAKS ARE SCHEDULED FOR RECHECK/REPAIRS IN ACCORDANCE WITH PG&E PROCEDURES. THE CAUSE OF THE INCIDENT IS EQUIPMENT FAILURE DUE TO PIPELINE DEBRIS FROM PIGGING OPERATIONS. THERE WERE NO REPORTED INJURIES, FATALITIES OR IGNITION. CNG WAS MOBILIZED TO SUPPORT PEAK CONDITIONS. THERE WAS NO CUSTOMER IMPACT. THIS INCIDENT IS BEING REPORTED TO THE CPUC DUE TO AN UNPLANNED EVENT RESULTING IN AN OVERPRESSURE EVENT MAOP PLUS ALLOWABLE BUILDUP. AT 1500 HOURS, IT WAS DETERMINED THAT COSTS ASSOCIATED WITH THE INCIDENT WOULD EXCEED $50,000. AT 1520 HOURS, THE DOT WAS NOTIFIED DUE TO ESTIMATED COSTS EXCEEDING $50,000.
2025-03-31 10:13 | NO | YES | YES | 20170024 | 16501 | 2017-02-24 12:28 | ORIGINAL | 45 | ADAIRSVILLE, CITY OF | 116 PUBLIC SQUARE | ADAIRSVILLE | GA | 30103 | 2017-01-31 16:45 |  |  | 2017 | APPX. 250 FEET SOUTH OF THE INTERSECTION OF HWY 140 AND HALL STATION ROAD | ADAIRSVILLE | BARTOW | GA | 30103 | 34.3759 | -84.9404 | [9 empty] | 2017-01-31 20:02 | 1169958 |  |  |  | 0 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2017-01-31 16:45 |  |  |  | 2017-01-31 16:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 42 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | INCOMPLETE PURGE. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 6 |  |  |  |  | 285 | 285 | 285 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | STEVE SMITH | GAS SYSTEM MANAGER | ssmith@adairsville.net | 7707732589 | 7707732587 |  |  |  | MAURICE CHANEY | ANALYST | 7708513094 | mchaney@gasauthority.com | 4:25 PM: I, STEVE SMITH, (CITY OF ADAIRSVILLE) ARRIVED ON SITE. BRADLEY ATKINS (SOUTHEASTERN NATURAL GAS SERVICES OF ROME) WAS IN THE HOLE AND HAD A 2" STEEL GAS LINE EXPOSED WITH A SHORT SECTION CUT OUT. AT THE TIME I ARRIVED HE STILL HAD GAS BLEEDING FROM THE SOUTH END OF THE LINE WHERE HE WAS WELDING ON SOMETHING AND GAS FROM THE NORTH END OF THE LINE WHICH WAS OPEN AND HAD BEEN SET ON FIRE. I SPOKE WITH BRADLEY AND HE TOLD ME HE THOUGHT THERE MUST BE ANOTHER FEED ON THE NORTH END OF THE LINE SO I TOLD HIM I WOULD SEE IF I COULD FIND WHERE IT WAS COMING FROM. 4:35 PM: I ASKED SHANE FERGUSON TO PULL THE BACKHOE TO A VALVE ABOUT 100 FEET NORTH OF THE HOLE WHERE THE LINE WAS EXPOSED. I WAS TOLD THAT SOMEONE HAD TRIED TO OPERATE THE VALVE AND THEY THOUGHT IT WAS STRIPED. I INSTRUCTED SHANE TO DIG THE VALVE UP. ONCE THE VALVE WAS EXPOSED I PUT A PIPE WRENCH ON THE VALVE TO SEE IF IT WOULD MOVE AND PARTIALLY OPERATED IT. 4:45 PM: I RETURNED TO THE HOLE WHERE THE LINE WAS EXPOSED AND SOMEONE TOLD ME BRADLEY HAD BEEN BURNED. BRADLEY WAS OVER AT HIS TRUCK SO I WALKED OVER AND ASKED HIM IF HE WAS OK, HE SAID HE WAS FINE BUT I TOLD HIM HE NEEDED TO GET CHECKED OUT. BRADLEY WANTED HIS WIFE TO DRIVE HIM TO THE DOCTOR SO WHILE WE WERE WAITING BRADLEY GAVE ME INSTRUCTIONS TO GIVE TO LONNIE TANNER WHO WAS COMING TO FINISH THE JOB. I WROTE THE INSTRUCTIONS DOWN ON A PIECE OF PAPER. 5:15 PM: BRADLEY LEFT FOR THE HOSPITAL WITH HIS WIFE. 5:20 PM: AT THIS TIME WE PINCHED OFF THE LINE WHICH WAS STILL BURNING ON THE NORTH SECTION OF THE CUT OUT SECTION AND THE GAS HAD BLED OFF OF THE SOUTH END OF THE LINE. I WALKED OVER ACROSS HIGHWAY 140 TO THE REGULATOR STATION FEEDING SHAW TO SEE IF I COULD FIGURE OUT WHERE THE GAS WHICH WAS STILL ON THE NORTH END OF THE LINE WAS COMING FROM. AT THE REGULATOR STATION SOUTHEASTERN NATURAL GAS SERVICES OF ROME HAD TAKEN OUT A 1/4" PLUG ON THE INLET SIDE OF REGULATOR WHICH WAS STILL BLEEDING GAS OFF THE LINE ON THE NORTH SECTION OF LINE. A 2" VALVE ON THE OUTLET SIDE TO SHAW HAD BEEN PREVIOUSLY TURNED OFF TRAPPING THE LINE PACK BETWEEN THE REGULATOR STATION AND SHAW WHICH IS ABOUT 350 FEET OF 4" HDPE LINE. 5:35 PM: I BLED THE GAS OFF ON THE SHAW SIDE OF REGULATOR STATION AND THE GAS ALSO STOPPED ON THE BLEEDING PLUG ON THE INLET SIDE SO THE GAS HAD BEEN BLEEDING BACK THROUGH A VALVE ON THE REGULATOR STATION. ALL THE GAS WAS OFF BOTH ENDS OF THE LINE BY 5:45 PM. 5:45 PM: WE WAITED FOR LONNIE TANNER TO ARRIVE. 6:15 PM: LONNIE TANNER ARRIVED AND I GAVE HIM THE PAPER WITH THE INSTRUCTIONS WHICH BRADLEY HAD LEFT FOR HIM. LONNIE COMPLETED THE JOB PER THE INSTRUCTIONS. 7:30 PM: AT THIS TIME I KNEW BRADLEY WAS ADMITTED TO THE HOSPITAL SO I CAME BACK TO THE OFFICE TO MAKE TELEPHONE CALLS. 7:35 PM: I CALLED JEFF BAGGETT WITH GEORGIA PUBLIC SERVICE COMMISSION AND INFORMED HIM OF THE INCIDENT. 8:02 PM: I CALLED THE NATIONAL RESPONSE CENTER TO INFORM THEM OF THE INCIDENT. THE CASE NUMBER I WAS GIVEN IS 1169958.
2025-03-31 10:13 | NO | YES | NO | 20170025 | 30281 | 2017-03-20 15:43 | SUPPLEMENTAL FINAL | 21220 | VICKSBURG, CITY OF | 801 WASHINGTON STREET | VICKSBURG | MS | 39180 | 2017-02-23 09:33 |  |  | 2017 | 3444 WISCONSIN AVE | VICKSBURG | WARREN | MS | 39180 | 32.3136 | -90.8629 | [9 empty] | 2017-02-23 12:43 | 1171759 |  | NATURAL GAS |  | 10.52 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 21 | 2017-02-23 09:33 |  |  |  | 2017-02-23 09:33 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2013 | [8 empty] | OTHER | CONNECTION BETWEEN 1-1/4" RISER & VALVE | [9 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 1000000 | 1180232.018561485 | 71 | 83.796473317865435 | 500 | 590.1160092807425 | 0 | 0 |  |  | 132 | 135.490384615384615384615384615384615385 |  | 0 | 1000703 | 489221.1562136356382785384615384615384615 | 1181041.42142869899255038461538461538462 | 1 | 0 | 0 |  |  |  |  | 26 | 26 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SYSTEM WAS ON MANUAL; PRESSURE POINT WAS BEING READ BY PERSONNEL. | [12 empty] | YES | 3 | 1 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | EMPLOYEE TRIED TO CHANGE GAS VALVE WITHOUT USING EXTRACTION TOOL |  |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | HAROLD DANE LOVELL | SUPERVISOR OF WATER AND GAS DEPT. | danel@vicksburg.org | 601-415-5092 | 601-801-3624 |  |  |  | HAROLD DANE LOVELL | SUPERVISOR OF WATER AND GAS DEPT. | 601-415-5092 | danel@vicksburg.org | ON FEB. 23, 2017, AT 8:33 AM, THE DISPATCHER SENT UNITS #2 AND #3 TO A SMELL ODOR COMPLAINT, AT 3444 WISCONSON AVE. THE GUY ON UNIT 2 AND #3 WERE JERMAINE MALLORY, THORNE SIMMS, AND KENNETH KING. THEY FOUND A LEAK ON THE VALVE ON THE METER SET. THEY MADE A DECISION TO CHANGE IT. AT 9:33 AM, JERMAINE CALLED ME AND TOLD ME THEY WERE CHANGING THE VALVE AT 3444 WISCONSIN AVE AND THE GAS IGNITED AND THE BUILDING WAS ON FIRE. I TOLD JERMAINE TO CALL 911; HE SAID HE HAD. I, DANE, ARRIVED ON SCENE AT 9:40 AM. THEY HAD PUT A VALVE ON AND CUT THE GAS OFF AND THE FIRE DEPT WERE WORKING ON PUTTING THE FIRE OUT. EMT WERE THERE GETTING KENNETH KING LOADED INTO THE AMBULANCE TO TRANSPORT TO THE EMERGENCY ROOM FOR BURNS ON HIS ARM. THEN WE CHECKED THE SERVICE LINE COMING IN AND THE MAIN AT THE STREET. ALSO THE PROPERTY AROUND THE BUILDING FOR ANY OTHER LEAKS.
2025-03-31 10:13 | NO | NO | NO | 20170026 | 31351 | 2017-03-23 16:47 | SUPPLEMENTAL FINAL | 13840 | NORTHWEST NATURAL GAS CO | 250 SW TAYLOR ST | PORTLAND | OR | 97204 | 2017-02-20 13:43 |  |  | 2017 | 23070 YAMHILL RIVER RD | WILLAMINA | POLK | OR | 97396-9714 | 45.05 | -123.5014 | [9 empty] | 2017-03-10 10:50 | 1172923 |  | NATURAL GAS |  | 272 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 6 | 2017-02-20 13:43 |  |  |  | 2017-02-20 14:06 |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | UNDER SOIL |  | 8 |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1965 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | 0 | 0 | 48345 | 57058.316937354992325 | 22152 | 26144.49967517401572 | 0 | 0 |  |  | 903 | 926.877403846153846153846153846153846154 |  | 0 | 71400 | 35317.5271414867096036153846153846153846 | 84129.6940163751618911538461538461538462 | 0 | 0 | 6 |  |  |  |  | 50 | 59 | 125 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FILLET WELD | MATERIAL/WELD/EQUIP FAILURE | FILLET WELD | MATERIAL FAILURE OF PIPE OR WELD | FILLET WELD | [146 empty] | FILLET WELD |  |  |  |  | BRANCH | [26 empty] | YES | [10 empty] | YES |  |  |  |  | NO | [86 empty] | J.R. GONZALEZ | SR. MANAGER CODE COMPLIANCE | j9g@nwnatural.com | 5032264211 |  |  |  |  | JON HUDDLESTON | VP ENGINEERING AND UTILITY OPERATIONS | 5032264211 | jon.huddleston@nwnatural.com | AT APPROXIMATELY 1:43PM ON FEBRUARY 20, 2016 NW NATURAL RECEIVED AN ODOR CALL TO A RESIDENCE AT 23070 YAMHILL RIVER RD. IN WILLAMINA. THERE WAS A LEAK ON A 2 INCH STEEL MAIN DUE TO A CRACKED WELD AT THE WILLAMINA-SHERIDAN REGULATOR STATION. NWN FIRST RESPONDER ARRIVED ON SITE AT 2:06PM. GAS WAS CONTROLLED AT 9:03AM ON FEBRUARY 21, 2017 BY ACTIVATING A BYPASS DISTRICT REGULATOR AND INSOLATED THE LEAKING SECTION OF PIPE. SIX SERVICES WERE INTERRUPTED AND RELIT BY 5:49PM FEBRUARY 21, 2017. REPAIRS WERE COMPLETED BY 5:50PM FEBRUARY 22, 2017 AND THE DISTRICT REGULATOR WAS REACTIVATED. HIGH FLOW THROUGH A DISTRICT REGULATOR CAUSED ICING AND FROST HEAVE WHICH RESULTED IN A CRACKED FILLET WELD AT A 2" LATERAL ON THE REGULATOR OUTLET PIPE. NW NATURAL IS REPORTING THIS INCIDENT DUE TO COSTS OF RESPONSE AND REPAIR EXCEEDING $50,000. NW NATURAL COST DATA REFLECTED THIS AS OF FEBRUARY 28, 2017.
2025-03-31 10:13 | NO | YES | NO | 20170027 | 16662 | 2017-03-24 21:19 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2017-02-24 16:08 |  |  | 2017 | 11074 E CONEJO AVE | KINGSBURG | FRESNO | CA | 93631 | 36.5181 | -119.5866 | [9 empty] | 2017-02-24 19:45 | 1171888 |  | NATURAL GAS |  | 2938 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-02-24 16:08 |  |  |  | 2017-02-24 16:47 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1992 | [5 empty] | 0.75 | 40-55 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 1 LOCATION | 0 | 0 | 536674 | 633399.83832946640089 | 0 | 0 | 0 | 0 |  |  | 17628 | 18094.125 |  | 0 | 554302 | 279073.341519721623798 | 651493.96332946640089 | 0 | 4 | 0 |  |  |  |  | 370 | 380 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | CASING WAS PUSHED ONTO A 0.75 INCH HIGH PRESSURE STEEL GAS SERVICE, CAUSE OF WHAT INITIALLY PUSHED THE CASING IS STILL UNDER INVESTIGATION | [154 empty] | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 626-893-4536 |  |  |  |  | KHOA LE | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 626-893-4536 | kle2@semprautilities.com | ON FEBRUARY 24, 2017, SOCALGAS WAS NOTIFIED OF A GAS RELEASE AT 11074 E CONEJO AVE, KINGSBURG. INITIAL REPORT SHOWED 11301 E CONEJO AVE, KINGSBURG. CREW RESPONDED AND CONTROLLED THE GAS. THERE WERE NO INJURIES OR FURTHER DAMAGE THAT RESULTED FROM THE ESCAPED GAS. ALL REPAIRS WERE COMPLETED AND THE AFFECTED CUSTOMERS WERE RESTORED. INVESTIGATION SHOWED THAT A VALVE CASING WAS PUSHED ONTO A 0.75 INCH A HIGH PRESSURE STEEL GAS SERVICE CAUSING THE SERVICE TO LEAK. INVESTIGATION INTO WHAT OUTSIDE FORCE INITIALLY PUSHED THE VALVE CASING IS ONGOING. THIS INCIDENT WAS INITIALLY REPORTED DOT AND CPUC DUE TO THE POSSIBILITY THAT THE GAS LOSS ESTIMATE COULD EXCEED 3MILLION CUBIC FEET OF GAS. HOWEVER, FURTHER ANALYSIS HAS DETERMINED THAT THE ESTIMATED GAS LOSS DID NOT EXCEEDED 3 MILLION CUBIC FEET OF GAS. THIS INCIDENT IS NOW BEING REPORTED DUE TO THE ASSOCIATED COST EXCEEDING $50,000. UPDATE 9-19-2017: CHANGED DOT NOTIFICATION TIME TO 19:45 FROM 22:45, AS LOCAL TIME OF INITIAL TELEPHONIC REPORT. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536.
2025-03-31 10:13 | NO | YES | YES | 20170028 | 16568 | 2017-03-27 11:51 | SUPPLEMENTAL FINAL | 31632 | NORTHWESTERN CORPORATION | 3010 W. 69TH ST. | SIOUX FALLS | SD | 57108 | 2017-03-09 02:11 |  |  | 2017 | 2117 SOUTH LOCUST | GRAND ISLAND | HALL | NE | 68801 | 40.9003 | -98.3397 | [9 empty] | 2017-03-09 06:20 | 1172806 |  | NATURAL GAS |  | 11.29 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2017-03-09 02:11 |  |  |  | 2017-03-09 02:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 2002 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | CAR HIT 3/4" ANODELESS METER RISER CAUSING IT TO BREAK | CLASS 3 LOCATION | 50000 | 59011.60092807425 | 2500 | 2950.5800464037125 | 200 | 236.046403712297 | 0 | 0 |  |  | 39 | 40.03125 |  | 0 | 52739 | 25797.6716212297029 | 62238.2586281902595 | 1 | 0 | 0 |  |  |  |  | 28 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DENNIS PLACKE | OPERATIONS SUPERVISOR | dennis.placke@northwestern.com | 3083854519 | 3083821105 |  |  |  | MELISSA BARUTH | DOT SUPERVIOSR | 6053537462 | melissa.baruth@northwestern.com | A THIRD PARTY VEHICLE WAS TRAVELING SOUTH BOUND ON A ROAD BEHIND SONIC DRIVE IN AT 2117 SOUTH LOCUST STREET IN GRAND ISLAND NE. THE VEHICLE JUMPED THE MEDIAN AND CONTINUED UNTIL THE VEHICLE STRUCK THE BUILDING. BEFORE STRIKING THE BUILDING THE VEHICLE STRUCK AND BROKE A NATURAL METER SET AT THIS LOCATION AND CAUGHT ON FIRE. THIS WAS ON A 1.1 M ROOTS METER SET AND IT BROKE OFF THE 3/4" PIPING BELOW THE LOCK WING. THE GAS CAUGHT FIRE AND HELPED FUEL THE FLAME UNTIL THE FIRE DEPARTMENT EXTINGUISHED IT. NORTHWESTERN ENERGY PERSONNEL INSERTED A RUBBER PLUG AND STOPPED THE FLOW OF GAS. THE GAS BLEW FOR 30 MINUTES AT APPROXIMATELY 28 PSI. THIS INCIDENT OCCURRED AT 2:11 AM MARCH 9 2017. AS INDICATED BY THE POLICE REPORT THE INDIVIDUAL WAS TRANSPORTED VIA POLICE CAR TO A MEDICAL FACILITY. UNSURE IF THIS WAS FOR AN INJURY OR SUBSTANCE TESTING. POLICE REPORT INDICATES AT THE TIME OF THE INCIDENT THE DRIVER HAD A BLOOD ALCOHOL LEVEL OF .081. INCIDENT WAS REPORTED DUE TO THE OWNER OF SONIC DRIVE IN INITIAL ASSESSMENT FOLLOWING THE FIRE THAT REPAIRS WILL EXCEED $50,000. FOLLOW UP CALL ON MARCH 21 2017 WITH THE OWNER OF SONIC -- STILL BELIEVED REPAIRS WOULD EXCEED $50,000.
2025-03-31 10:13 | NO | NO | NO | 20170029 | 16537 | 2017-03-27 14:34 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2017-03-03 11:00 |  |  | 2017 | 7117 ROOSEVELT AVENUE | JACKSON HEIGHTS | QUEENS | NY | 11372 | 40.7471 | -73.8944 | [9 empty] | 2017-03-03 11:45 | 1172376 |  | NATURAL GAS |  | 966 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-03-03 10:30 |  |  |  | 2017-03-03 10:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 43 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2006 | [5 empty] | 12.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.5 | [6 empty] | MECHANICAL PUNCTURE | 6 | 6 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 8197 | 9674.361856148492545 | 62249 | 73468.262923433879765 | 0 | 0 | NA |  | 9264 | 9508.961538461538461538461538461538461538 |  | 0 | 79710 | 43231.5277779760902881538461538461538462 | 92651.5863180439107715384615384615384615 | 5 | 0 | 697 |  |  |  |  | 8.6 | 12 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DUE TO A DAMAGE BY A THIRD PARTY CONTRACTOR. CMS RESPONDED AND FIELD OPERATIONS AND INSTR. AND REGULATION RESPONDED. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | UNKNOWN/OTHER | NO | [5 empty] | YES | 12 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CORINNE BYRNES | PRINCIPAL PROGRAM MGR FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 6317703549 | 5164924469 |  |  |  | CORINNE BYRNES | PRINCIPAL PROGRAM MGR FEDERAL PROGRAMS | 6317703549 | corinne.byrnes@gmail.com | AT 10:20 ON 3/3/2017, NATIONAL GRID'S DISPATCH AND SCHEDULE RECEIVED NOTIFICATION BY THE FDNY OF A THIRD PARTY CONTRACTOR DAMAGE TO HP GAS MAIN IN FRONT OF 7117 ROOSEVELT AVE. AT THE REQUEST OF FDNY, THE E, F, M, & R NYC MTA SUBWAY LINES WERE STOPPED IN ALL DIRECTIONS AS A PRECAUTION. CONTRACTOR WAS PERFORMING PILE BORING USING A BORING DRILL RIG. OUT OF AN ABUNDANCE OF CAUTION, EMERGENCY MOBILE COMMAND CENTER WAS SENT TO THE LOCATION. UNDER DIRECTION FROM NATIONAL GRID'S GAS CONTROL, AT 11:30 ON 3/3/2017, FIELD OPERATIONS AND I&R CLOSED TWO ISOLATION VALVES TO SECURE THE GAS, WITH 702 CUSTOMERS BEING TAKEN OUT OF SERVICE. AT 23:00 ON 3/3/2017, FIELD OPERATIONS MADE REPAIRS TO THE MAIN. AT APPROX. 13:41 ON 3/3/2017,ALL MTA TRAIN RESTRICTIONS HAVE BEEN LIFTED AND TRAIN SERVICE IS BACK TO RUNNING NORMAL. ALL SERVICES WERE RESTORED NO LATER THAN 3/5/2017 AT 12:00.
2025-03-31 10:13 | NO | NO | NO | 20170030 | 16521 | 2017-03-27 15:08 | ORIGINAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2017-02-27 12:14 |  |  | 2017 | 1583 VICTORY BOULEVARD | STATEN ISLAND | RICHMOND | NY | 10314 | 40.6137 | -74.1153 | [9 empty] | 2017-02-27 14:42 | 1172040 |  | NATURAL GAS |  | 0.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 875 | 2017-02-27 11:23 |  |  |  | 2017-02-27 10:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2015 | [8 empty] | OTHER | RELIEF VALVE | [9 empty] | LEAK |  |  | OTHER | FLANGE LEAK/RELIEF VALVE VENTG | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 5 | 5.13221153846153846153846153846153846154 |  | 0 | 5 | 4.74759615384615384615384615384615384615 | 5.13221153846153846153846153846153846154 | 1 | 0 | 0 |  |  |  |  | 39.47 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT BEING RELATED TO CUSTOMER'S METER AND REGULATOR EQUIPMENT AND CUSTOMER OWNED PIPING (FLANGE) AND NOT BEING RELATED TO CONTROLLER ACTIONS OR CONTROL ROOM ISSUES. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [6 empty] | YES | [76 empty] | CORINNE BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 631-770-3549 |  |  |  |  | CORINNE BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | 631-770-3549 | corinne.byrnes@nationalgrid.com | DISPATCH AND SCHEDULE WAS NOTIFIED BY THE FDNY TO RESPOND TO AN OUTSIDE GAS ODOR AT 1583 VICTORY BLVD. CUST. METER SERVICES (CMS) WAS DISPATCHED TO THE LOCATION. THERE ARE NO INJURIES REPORTED. CMS SUPERVISOR REPORTED THAT PRIOR TO NATIONALGRID'S ARRIVAL, THE PRINCIPAL OF THE SCHOOL (P.S . 029 BARDWELL) HAD EVACUATED APPROXIMATELY 875 STUDENTS AND FACULTY MEMBERS FOR SAFETY. CMS SUPERVISOR REPORTED THAT A COMPLETE INVESTIGATION REVEALED A GAS LEAK ON A 3" FLANGE IN THE BASEMENT (SECONDARY CAUSE) AND ALSO A RELIEF VALVE (PRIMARY INCIDENT CAUSE) ON THE OUTSIDE M&R SETUP WAS VENTING. THE SERVICE PERSON LOCKED THE SERVICE VALVE AND AN "A" CLASS WARNING TAG WAS ISSUED FOR THE LEAK ON THE FLANGE. ALL OCCUPANTS HAVE BEEN ALLOWED BACK INTO THE BUILDING. A PHMSA INCIDENT REPORT IS BEING FILED FOR THIS EVENT BECAUSE IT INVOLVED: LOSS OF SERVICE, EVACUATION OF 875 PEOPLE, INVOLVEMENT OF FDNY AND NYPD, AND MEDIA COVERAGE.
2025-03-31 10:13 | NO | YES | NO | 20170031 | 31247 | 2017-04-05 17:22 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2017-03-02 04:30 |  |  | 2017 | 97 SUMAC CT | PAGOSA SPRINGS | ARCHULETA | CO | 81147 | 37.2831 | -107.1009 | [9 empty] | 2017-03-06 08:50 | 1172553 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-03-02 04:02 |  |  |  | 2017-03-02 04:49 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2016 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 385011 | 454402.309698375901335 | 300 | 354.0696055684455 | 500 | 590.1160092807425 | 0 | 0 |  |  | 100 | 102.644230769230769230769230769230769231 |  | 0 | 385911 | 188685.8138256291603739230769230769230769 | 455449.1395439943201042307692307692307692 | 0 | 0 | 1 |  |  |  |  | 38 | 38 | 80 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | CUSTOMER NEGLIGENTLY ALLOWED SNOW TO PILE UP TO THE EAVE LEVEL OVER THE METER SET. THE DOWNWARD FORCE OF THE ACCUMULATED SNOW CAUSED A CRACK IN AN ABOVE-GROUND PIPE SECTION JUST UPSTREAM OF THE METER | [154 empty] | BILL STEPHENS | SR MGR COMPLIANCE CODES STANDARDS | bill.stephens@blackhillscorp.com | 3039816474 |  |  |  |  | BILL STEPHENS | SR MGR COMPLIANCE CODES STANDARDS | 3039816474 | bill.stephens@blackhillscorp.com | AT APPROXIMATELY 4:30 AM ON MARCH 2, 2017 A FIRE OCCURRED AT THE RESIDENCE OF SAMUEL SITTON AT 97 SUMAC COURT, PAGOSA SPRINGS, COLORADO. GAS LEAKED FROM A CRACKED SECTION OF JURISDICTIONAL PIPE ABOVE THE RISER AND NEXT TO THE GAS METER. THIS GAS MIGRATED INTO THE RESIDENCE, WHERE IT WAS IGNITED. THERE WAS NO EXPLOSION, BUT A SUSTAINED FIRE CAUSED SUBSTANTIAL DAMAGE TO THE RESIDENCE. NO ONE WAS INJURED. BLACK HILLS WAS NOTIFIED AT 4:45_ A.M. AND RESPONDED TO THE SCENE AT 4:55 A.M. IT WAS CONFIRMED THAT GAS SERVICE TO THE RESIDENCE WAS OFF. INVESTIGATION REVEALED THAT THE HOMEOWNER NEGATIVE NEGLIGENTLY ALLOWED A LARGE ACCUMULATION OF SNOW, UP TO THE EAVE LEVEL, TO DEVELOP OVER THE GAS METER AND PIPING. THE GAS PIPE DEVELOPED A CRACK AS A RESULT OF THE DOWNWARD FORCE OF THE ACCUMULATED SNOW. THERE WERE NO REPAIRS UNDERTAKEN, AS THE HOMEOWNER DECIDED TO TEAR DOWN THE HOUSE AND CONSTRUCT A NEW HOUSE AT THIS LOCATION. BLACK HILLS REESTABLISHED NATURAL GAS SERVICE TO THE NEW HOUSE. THE ORIGINAL SERVICE LINE AND METER WERE NOT USED. A NEW SERVICE LINE AND METER WERE INSTALLED ONCE THE NEW HOUSE WAS CONSTRUCTED. IN ORDER TO PREVENT A RECURRENCE, THE NEW GAS METER WAS LOCATED ON THE GABLE END OF THE HOUSE.
2025-03-31 10:13 | YES | NO | NO | 20170032 | 16791 | 2017-04-07 10:39 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2017-03-14 12:50 |  |  | 2017 | 159 THORNBURY ROAD | NEW ROCHELLE | WESTCHESTER | NY | 10583 | 40.9831 | -73.785 | [9 empty] | 2017-03-14 14:11 | 1173223 |  | NATURAL GAS |  | 0.03 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-03-14 13:16 |  |  |  | 2017-03-14 13:16 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | 2002 | [8 empty] | OTHER | ALUMINUM BODY OF SERVICE REGULATOR MELTE | [9 empty] | OTHER | [8 empty] | ALUMINUM BODY OF SERVICE REGULATOR MELTED FROM PRIMARY, NON-NATURAL GAS IGNITION. | CLASS 4 LOCATION | 250000 | 295058.00464037125 | 100 | 118.0232018561485 | 450 | 531.10440835266825 | 0 | 0 |  |  | 2 | 2.05288461538461538461538461538461538462 |  | 0 | 250552 | 122474.9245605033233115384615384615384615 | 295709.1851351954513653846153846153846154 | 0 | 0 | 1 |  |  |  |  | 65 | 65 | 89 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | (718) 319-2310 | (718) 904-4607 |  |  |  | NICKOLAS HELLEN | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | (718) 319-2350 | hellenn@coned.com | AT 12:50 P.M. ON MARCH 14, 2017, CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A REPORT FROM WESTCHESTER COUNTY FIRE CONTROL OF A BUILDING FIRE AT 159 THORNBURY ROAD IN NEW ROCHELLE. THE GERC DISPATCHED PERSONNEL, INCLUDING SUPERVISION FROM CON EDISON'S GAS DISTRIBUTION SERVICES (GDS) DEPARTMENT. AT 1:16 P.M., AS GDS PERSONNEL WERE ARRIVING AT THE LOCATION, WESTCHESTER COUNTY FIRE CONTROL PROVIDED UPDATED INFORMATION TO THE GERC INDICATING THAT THE FIRE WAS GAS FED, ACCORDING TO THE NEW ROCHELLE FIRE DEPARTMENT (NRFD). ADDITIONAL PERSONNEL FROM CON EDISON'S GDS AND GAS CONSTRUCTION DEPARTMENTS WERE THEN DISPATCHED TO THE LOCATION. THE RESIDENTIAL BUILDING INVOLVED WAS SUPPLIED BY A 0.5-INCH HIGH-PRESSURE POLYETHYLENE (HPPE) GAS SERVICE SUPPLIED FROM A 1.25-INCH HPPE GAS MAIN. THE GERC IDENTIFIED THE LOCATION OF THE CURB AND MAIN VALVES TO ISOLATE THE AREA, IF REQUIRED. AT 1:25 P.M., GDS REPORTED THAT THE NRFD HAD CLOSED THE SERVICE VALVE IN THE GARAGE, SECURING THE REPORTED GAS FED FIRE. AT 1:42 P.M., GDS PROVIDED AN UPDATED REPORT TO THE GERC INDICATING THAT THE INCIDENT HAD INVOLVED A SECONDARY NATURAL GAS IGNITION CAUSED BY ANOTHER FIRE THAT HAD RESULTED FROM THE HOMEOWNER ATTEMPTING TO FILL A SNOW BLOWER WITH GASOLINE INSIDE THE GARAGE. THE GASOLINE-RELATED PRIMARY IGNITION SPREAD TO A VEHICLE, THE GARAGE AND HOUSE. THE CURB VALVE, WHICH COULD NOT INITIALLY BE LOCATED BECAUSE IT WAS COVERED WITH ICE AND SNOW, WAS LOCATED WITH ASSISTANCE FROM GDS SUPERVISION AND CLOSED AT 1:50 P.M. AT 2:05 P.M., GDS SUPERVISION REPORTED TO THE GERC THAT THE GASOLINE-RELATED PRIMARY IGNITION APPEARED TO HAVE MELTED THE GAS SERVICE REGULATOR AND GAS METER, AND DAMAGED THE GAS METER PIPING, HOUSE PIPING, AND EXTENSION SERVICE. ODORANT READINGS TAKEN AT 149 THORNBURY ROAD WERE WITHIN THE ACCEPTABLE RANGE (0.25% GAS-IN-AIR). NO NATURAL GAS READINGS WERE DETECTED IN TEST POINTS CHECKED OUTSIDE THE BUILDING. THE CURB VALVE AND SERVICE VALVE WERE LEFT OFF AND LOCKED, AND WERE VERIFIED TO BE HOLDING. GAS CONSTRUCTION RESPONDED TO CUT AND CAP THE GAS SERVICE AT THE MAIN. DAMAGE WAS ESTIMATED TO EXCEED $50,000. NO INJURIES OR ILLNESSES WERE REPORTED. CHANNEL 12 NEWS WAS ON LOCATION. NOTIFICATIONS WERE MADE TO THE NEW YORK STATE PUBLIC SERVICE COMMISSION (NYSPSC) AND THE U.S. DEPARTMENT OF TRANSPORTATION (VIA THE NATIONAL RESPONSE CENTER). THE NYSPSC INQUIRED AND WAS PROVIDED WITH AN UPDATE.
2025-03-31 10:13 | NO | YES | NO | 20170033 | 32424 | 2017-04-07 16:09 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2017-03-10 14:39 |  |  | 2017 | 2121 MAIN ST. | DALLAS | DALLAS | TX | 75201 | 32.7819 | -96.7921 | [9 empty] | 2017-03-10 16:07 | 1172951 |  | NATURAL GAS |  | 105 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 25 | 2017-03-10 14:39 |  |  |  | 2017-03-10 15:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2017 | [5 empty] | 6 | HDPE | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 5 | 4 | [7 empty] | CLASS 4 LOCATION | 700000 | 826162.4129930395 | 19095 | 22536.530394431556075 | 7625 | 8999.269141531323125 | 0 | 0 |  |  | 588 | 603.548076923076923076923076923076923077 |  | 0 | 727308 | 355791.1934097805371323076923076923076923 | 858301.7606059254561230769230769230769231 | 2 | 0 | 0 |  |  |  |  | 23 | 23 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | AUGER | TRAFFIC SIGNAL | YES | 1756101500 | TEXAS 811 |  | CONTRACT LOCATOR | NO | YES | 8 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | TOMMY LOONEY | COMPLIANCE SUPERVISOR | tommy.looney@atmosenergy.com | 214-426-7037 | 214-426-7081 |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | AT 2:39 PM ON MARCH 10, 2017, ATMOS ENERGY WAS NOTIFIED BY DALLAS FIRE & RESCUE (DFR) OF AN EVENT IN THE 2100 BLOCK OF MAIN ST. IN DALLAS. ATMOS ENERGY'S FIRST RESPONDERS ARRIVED ON-SITE AT 3:20 PM DISCOVERING A THIRD PARTY DAMAGE AND GAS IGNITION HAD OCCURRED ON A 6" POLY MAIN STRUCK BY A TRUCK-MOUNTED AUGER NORTHWEST OF THE INTERSECTION OF MAIN STREET AND CESAR CHAVEZ BOULEVARD. ATMOS ENERGY PERSONNEL ELIMINATED GAS FLOW TO THE DAMAGED SECTION OF PIPE - ISOLATION POINTS WERE IDENTIFIED AND LOCATED, AND THE VALVES WERE CLOSED AT 4:09 PM. ALL OF THE ROADS EXCEPT THE 2100 BLOCK OF MAIN STREET WERE REOPENED. AS A RESULT OF THE MAIN ISOLATION, TWO COMMERCIAL SERVICES WERE TEMPORARILY INTERRUPTED. GAS FLOW WAS REINSTATED AT 12:20 AM (MARCH11TH) ALLOWING THE INTERRUPTED SERVICES TO BE RESTORED. APPROXIMATELY 29 YARDS OF MAIN WAS DEACTIVATED AS A RESULT OF THE INCIDENT. THE 2100 BLOCK OF MAIN STREET WAS REOPENED UPON COMPLETION OF THE DEACTIVATION. FIRST RESPONDERS WERE NOTIFIED BY DALLAS FIRE & RESCUE THAT APPROXIMATELY 25 PEOPLE WERE EVACUATED FROM THE ADDRESSES OF 2121 MAIN ST. AND 2108 MAIN ST. AN AREA SURROUNDING THE LOCATION OF THE INCIDENT WAS CORDONED OFF, FROM US 75 TO PEARL STREET TO PACIFIC AVENUE TO JACKSON STREET. THIS 6" POLY MAIN HAD BEEN INSTALLED AND HAD BEEN PLACED IN SERVICE ON FEBRUARY 27, 2017. THE CONTRACTORS ON ATMOS ENERGY'S PROJECT AND THE CITY OF DALLAS' PROJECT WERE WORKING SIMULTANEOUSLY IN THE SAME AREA IN THE MONTHS LEADING UP TO THE INCIDENT. ATMOS ENERGY FOLLOWED IT APPROVED PROCEDURES, IN COMPLIANCE WITH PART 192.603(B), TO RECORD THIS NEW ASSET IN THE GIS ELECTRONIC MAPPING SYSTEM USED BY ITS LOCATORS. DUE TO THE TIME IT TAKES TO COMPLETE THIS PROCESS, THIS ASSET WAS NOT REFLECTED IN THE ELECTRONIC MAPPING AT THE TIME THE LOCATE TICKET WAS COMPLETED IN THIS AREA ON MARCH 3, 2017. AS A RESULT, THE NEW ASSET WAS NOT MARKED WITH THE LOCATE TICKET. HOWEVER, THERE WERE EXISTING VISUAL INDICATORS IN PLACE, INCLUDING A FRESH DITCH LINE COVERED WITH NEW ASPHALT IN-LINE WITH THE POINT OF DAMAGE; VISIBLE AND YELLOW PAINTED GAS VALVE BOXES ON MAIN STREET 15 YARDS FROM THE POINT OF DAMAGE; AND A LARGE CAPACITY METER IN THE ALLEY FOR 2121 MAIN STREET. BECAUSE THE THIRD-PARTY CONTRACTOR HAD AN OBLIGATION PER 18 TAC 18.4 TO MAKE A VISUAL CHECK FOR ANY UNMARKED UNDERGROUND PIPELINES, INCLUDING BUT NOT LIMITED TO ABOVE-GROUND PIPELINE VALVES, METER SETS, AND OTHER VISUAL MARKINGS, THE PRIMARY CAUSE THAT LED TO THE INCIDENT WAS DETERMINED TO BE INSUFFICIENT EXCAVATION PRACTICES. A PROJECT TO REPLACE THE DEACTIVATED MAIN WAS COMPLETED ON AUGUST 16, 2017.
2025-03-31 10:13 | YES | NO | NO | 20170034 | 16536 | 2017-04-15 19:38 | ORIGINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2017-03-17 06:30 |  |  | 2017 | 10611 CHEVROLET WAY | ESTERO | LEE COUNTY | FL | 33928 | 26.4299 | -81.78 | [9 empty] | 2017-03-17 09:45 | 1173420 |  | NATURAL GAS |  | 9.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 150 | 2017-03-17 07:01 |  |  |  | 2017-03-17 07:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2016 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | UNDER INVESTIGATION | [5 empty] | CLASS 4 LOCATION | 25000 | 29505.800464037125 | 1000 | 1180.232018561485 | 3000 | 3540.696055684455 | 0 | 0 |  |  | 75 | 76.98317307692307692307692307692307692308 |  | 0 | 29075 | 14246.8983970640753076923076923076923077 | 34303.7117113599880769230769230769230769 | 1 | 0 | 0 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MARK WITECKI | GAS COMPLIANCE MANAGER - REGULATORY AFFAIRS | mgwitecki@tecoenergy.com | 813-228-4465 | 813-228-1770 |  |  |  | LUKE BUZARD | DIRECTOR OF PIPELINE SAFETY AND OPERATIONAL SVCS. | 813-228-4733 | labuzard@tecoenergy.com | ESTERO FIRE RESCUE CONTACTED THE PEOPLES GAS SYSTEM (PGS) CALL CENTER AT APPROXIMATELY 7:01 A.M. ON MARCH 17, 2017, TO NOTIFY THEM OF A NATURAL GAS LEAK AND IGNITION INCIDENT AT THE HAMPTON INN LOCATED AT 10611 CHEVROLET WAY, ESTERO, FL 33928. PGS IMMEDIATELY DISPATCHED STAFF, WHO ARRIVED ONSITE AT 7:45 A.M. BY THE TIME THE PGS EMPLOYEES ARRIVED AT THE SCENE, THE FIRE HAD BEEN EXTINGUISHED, AND THE GAS METER WAS TURNED OFF BY THE FIRE DEPARTMENT. THE PGS EMPLOYEES PROCEEDED TO EXCAVATE THE SERVICE LINE THAT SUPPLIED THE GAS METER, SQUEEZED THE GAS LINE OFF, THEN REMOVED THE GAS METER AND RISER PIPE. A NEW GAS METER AND RISER PIPE WERE INSTALLED, AND GAS SERVICE WAS RESTORED THE SAME DAY TO THE HAMPTON INN. IT IS BELIEVED THAT MULCH UNDER AND AROUND THE METER CAUGHT FIRE DUE TO AN UNEXTINGUISHED CIGARETTE THAT WAS LEFT THERE BY AN UNIDENTIFIED INDIVIDUAL. WHEN THE MULCH IGNITED, THE FIRE COMPROMISED THE GAS METER, WHICH BREACHED THE CASING AND ALLOWED GAS TO ESCAPE.
2025-03-31 10:13 | NO | YES | NO | 20170035 | 31581 | 2017-04-21 09:44 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2017-03-23 15:45 |  |  | 2017 | 111 CONVAIR DR | CORAOPOLIS | ALLEGHENY | PA | 15108 | 40.5114 | -80.2287 | [9 empty] | 2017-03-23 17:12 | 1173942 |  | NATURAL GAS |  | 21.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2017-03-23 15:57 |  |  |  | 2017-03-23 16:37 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | UNDETERMINED AT THIS TIME | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNDETERMINED AT THIS TIME AS PER ALLEGHENY COUNTY FIRE MARSHALL. | CLASS 3 LOCATION | 139900 | 165114.4593967517515 | 0 | 0 | 15161 | 17893.497633410674085 | 0 | 0 |  |  | 178 | 182.706730769230769230769230769230769231 |  | 0 | 155239 | 75965.4215692486301239230769230769230769 | 183190.6637609316563542307692307692307692 | 0 | 0 | 2 |  |  |  |  | 0.4 | 0.4 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | DANIEL P. KUEHN | MANAGER PROCESS WORK MANAGEMENT | daniel.kuehn@peoples-gas.com | 724-444-3251 |  |  |  |  | JOSEPH A. GREGORINI | SR. VICE PRESIDENT RATES - REGULATORY AFFAIRS | 412-208-7905 | joseph.a.gregorini@peoples-gas.com | THERE WAS A FIRE/EXPLOSION AT 111 CONVAIR DRIVE, CORAPOLIS, PA 15108 AT APPROXIMATELY 15:45 ON THURSDAY MARCH 23, 2017. NO RESIDENTS WERE PRESENT AT THE TIME OF THE EXPLOSION. THE INCIDENT APPEARS TO HAVE BEEN A NATURAL GAS EXPLOSION THAT DESTROYED THE HOUSE. THE ALLEGHENY COUNTY FIRE MARSHALL HAS CLOSED THEIR INVESTIGATION. THE FINAL REPORT FILED BY THE ALLEGHENY COUNTY FIRE MARSHAL STATES THE CAUSE OF THE INCIDENT HAS BEEN CLASSIFIED AS UNDETERMINED.
2025-03-31 10:13 | NO | YES | NO | 20170036 | 31845 | 2017-04-21 15:15 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2017-03-24 11:30 |  |  | 2017 | 200 BLOCK OF PECAN ST. | FORT WORTH | TARRANT | TX | 76102 | 32.7583 | -97.3287 | [9 empty] | 2017-03-24 12:10 | 1174002 |  | NATURAL GAS |  | 5408 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 300 | 2017-03-24 11:30 |  |  |  | 2017-03-24 11:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 96 |  | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 2003 | [5 empty] | 12 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 129445 | 152775.133642691425825 | 0 | 0 | 0 | 0 |  |  | 30296 | 31097.0961538461538461538461538461538462 |  | 0 | 159741 | 92041.5130376584083996153846153846153846 | 183872.2297965375796711538461538461538462 | 7 | 0 | 55 |  |  |  |  | 28 | 28 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 1757295504 | TEXAS811 |  | CONTRACT LOCATOR | YES | YES | 22 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | STEVE KLEIN | FIELD SUPERVISOR | william.klein@atmosenergy.com | 469-261-2011 | 817-517-2088 |  |  |  | MARLO SUTTON | DIRECTOR REGULATORY AND COMPLIANCE | 214-206-2033 | marlo.sutton@atmosenergy.com | ATMOS ENERGY RECEIVED PRIOR NOTIFICATION OF THE EXCAVATION ACTIVITY AND MARKED THE LOCATION OF THE LINE. ON MARCH 24, 2017 AT APPROXIMATELY 11:30, THE THIRD PARTY CONTRACTOR FAILED TO EXPOSE THE ACTIVE PIPE PRIOR TO BORING AND BORED INTO AN ELECTRIC CONDUIT THEN INTO A 12" GAS LINE/MAIN. GAS THEN MIGRATED INTO THE ELECTRIC CONDUIT, TRAVELING UP A POLE AND IGNITING. A REPRESENTATIVE FROM THE CITY OF FORT WORTH WAS AT THE LOCATION WHEN THE INCIDENT OCCURRED AND IMMEDIATELY NOTIFIED ATMOS ENERGY. THE LINE WAS SHUTDOWN AT 22:13 ON MARCH 24, 2017 SO REPAIRS COULD COMMENCE. APPROXIMATELY 300 PEOPLE WERE EVACUATED FROM NEARBY HOUSING. REPAIRS WERE COMPLETED AND THE PIPELINE RESTARTED AT 19:15 ON MARCH 25, 2017. THE NATIONAL RESPONSE CENTER REPORT NUMBER INDICATED ON THE ORIGINAL INCIDENT REPORT, 1174102, WAS INCORRECT. THE REPORT NUMBER HAS BEEN CHANGED ON THIS SUPPLEMENTAL REPORT TO THE CORRECT NUMBER, 1174002.
2025-03-31 10:13 | NO | NO | NO | 20170038 | 30106 | 2017-04-27 12:16 | SUPPLEMENTAL FINAL | 31840 | UNISOURCE ENERGY SERVICES | 2901 W SHAMRELL #110 | FLAGSTAFF | AZ | 86005 | 2017-04-22 12:11 |  |  | 2017 | 1659 W WHITE MOUNTAIN BLVD | LAKESIDE | NAVAJO | AZ | 85929-9402 | 34.1525 | -109.9737 | [9 empty] | 2017-04-22 13:40 | 1176382 |  | NATURAL GAS |  | 47 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 6 | 2017-04-22 12:11 |  |  |  | 2017-04-22 12:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1997 | [8 empty] | STEEL |  | OTHER | WELDED | 0.121 | [6 empty] | LEAK |  |  | OTHER | STOP BROKEN OFF OF RISER | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 143 | 168.773178654292355 | 619 | 730.563619489559215 | 0 | 0 |  |  | 149 | 152.939903846153846153846153846153846154 |  | 0 | 911 | 513.956694850972758615384615384615384615 | 1052.276701990005416153846153846153846154 | 1 | 0 | 0 |  |  |  |  | 48 | 48 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DUNCAN JAKES | GAS ENGINEER | djakes@uesaz.com | 9282262214 |  |  |  |  | MARTIN ANAYA | DIRECTOR UES GAS | 9282262258 | manaya@uesaz.com | THE DRIVER OF A CHEVY TRUCK PULLED OUT OF THE CIRCLE K AT 1654 W WHITE MOUNTAIN BLVD IN LAKESIDE AZ AND CROSSED 4 LANES OF TRAFFIC STRIKING ONE VEHICLE IN THE PROCESS. THE VEHICLE THEN PROCEEDED NE TO 1659 W WHITE MOUNTAIN BLVD LAKESIDE AZ AND STRUCK AND BROKE THE HIGH PRESSURE SIDE OF THE GAS METER ON THE SW CORNER OF THE BUILDING WHERE THE VEHICLE CAME TO A STOP. TIMBER MESA FIRE DEPARTMENT ARRIVED AND REMOVED THE DRIVER FROM THE VEHICLE. TWO BUSINESSES WERE EVACUATED WITH A TOTAL OF 6 PEOPLE. THE DRIVER WAS TRANSPORTED TO SUMMIT REGIONAL MEDICAL CENTER FOR OBSERVATION AND TREATMENT. TIMBER MESA FIRE DEPARTMENT PULLED THE TRUCK OFF OF THE GAS METER AND UES SERVICE TECHNICIAN MATT JEFFS USED AN X-PANDER PLUG TO STOP GAS FLOW. NOTE: WITNESSES AT THE SCENE OF THE ACCIDENT REPORTED THAT THE DRIVER WAS OBSERVED HOLDING HIS HEAD WITH BOTH HANDS HAS HE PULLED OUT OF THE CIRCLE K PARKING LOT AND PRIOR TO LOSING CONTROL OF HIS VEHICLE.
2025-03-31 10:13 | NO | YES | NO | 20170039 | 34154 | 2017-04-28 16:17 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2017-03-29 19:59 |  |  | 2017 | 30 ALLENS AVENUE | PROVIDENCE | PROVIDENCE | RI | 02905 | 41.8139 | -71.406 | [9 empty] | 2017-03-29 22:56 | 1174380 |  | NATURAL GAS |  | 19000 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 30 | 2017-03-29 19:59 |  |  |  | 2017-03-29 20:39 |  | NO | PRIVATE PROPERTY | UNDERGROUND | OTHER | EXPOSED COUPLING |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2005 | [5 empty] | 12 | API 5L X42 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 4 LOCATION | 25000 | 29505.800464037125 | 875000 | 1032703.016241299375 | 12000 | 14162.78422273782 | 0 | 0 |  |  | 59028 | 60588.8365384615384615384615384615384615 |  | 0 | 971028 | 501849.0564206675778461538461538461538462 | 1136960.43746653585846153846153846153846 | 53 | 0 | 0 |  |  |  |  | 90 | 90 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | CONTROLLER |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS IS A MECHANICAL FAILURE OF ON EXPOSED PIPE NOT RELATED TO ANY ACTIVITIES WITHIN THE CONTROL ROOM. CONTROLLERS ACTIONS DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | OTHER COMPRESSION TYPE FITTING | INSULATING MECHANICAL COUPLING | COUPLING |  | DRESSER |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | LOSS OF SUPPORT DUE TO THIRD PARTY ENCROACHMENT, AS PERFORMED BY A CONRACTOR OF ENBRIDGE, THE NATURAL GAS SUPPLY COMPANY. THIS WAS DONE OUTSIDE OF THE PUBLIC RIGHT OF WAY. | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | MICHAEL GALLINARO | PRINCIPAL ENGINEER | michael.gallinaro@nationalgrid.com | 7189635577 |  |  |  |  | CORINNE BYRNES | PRIN. PROGRAM MGR REGULATORY MANAGEMENT OF CHANGE | 5164924469 | corinne.byrnes@nationalgrid.com | **SUPPLEMENTAL REPORT ISSUED ON AUGUST 14, 2020 TO PROVIDE ACTUAL ENVIRONMENTAL REMEDIATION COSTS AND TO UPDATE THE APPARENT CAUSE SECTION, PART G3. *** ON MARCH 29, 2017 THERE WAS AN EMERGENCY RESPONSE TO AN UNCONTROLLED RELEASE OF GAS FROM 12 INCH, 99 PSIG STEEL PIPELINE AT 30 ALLENS AVE, PROVIDENCE RI THIS SUBSEQUENTLY RESULTED IN UNPLANNED SUPPLY INTERRUPTION. WHAT HAPPENED: GAS CONTROL PRESSURE ALARMS INITIATED EMERGENCY RESPONSE WITH GAS INSTRUMENTATION & REGULATION (I&R) AT 7:59 PM. RI GAS DISPATCH INITIATED CMS RESPONSE BASED ON NUMEROUS ODOR CALLS AT 8:05 PM. PROVIDENCE LNG INITIATED RESPONSE ACTIVITIES AFTER LOW PRESSURE READING DURING ROUNDS AT 8:00 PM THE RELEASE WAS CONTROLLED AT 11:16 PM. CMS COMPLETED 59 SHUTOFFS AT 3:11 AM ON 3/30/17, C&M COMPLETED REPAIRS AT 3:30 AM ON 3/30/17, CMS BEGAN RELIGHTS AT 3:40 AM ON 3/30/17. A 12 INCH DRESSER COUPLING FAILED BY SEPARATION ALLOWING TWO 12 INCH 99 PSIG PIPE SEGMENTS TO BE PULLED APART. ROOT CAUSE: THERE WAS INSUFFICIENT SUPPORT OF A LIVE GAS MAIN DUE TO THE FACT THAT THE EARTH WAS REMOVED DURING CONSTRUCTION ACTIVITY ALLOWING VIBRATION AND PRESSURE TO PULL THE SEGMENTS OUT FROM THE COUPLING. CONTRIBUTING FACTORS: MARCH, 2017 - ENBRIDGE EXCAVATED AROUND A PRESSURIZED 99 PSIG OUTLET MAIN IN PREPARATION OF TIE-IN FOR OUTLET PIPING FOR THE NEWLY CONSTRUCTED CRARY ST GATE STATION. THE PIPING WAS LEFT INSUFFICIENTLY SUPPORTED IN EXCAVATION. REMOVAL OF TWO 750 TO 99 PSIG REGULATOR RUNS ALLOWED A PIPING HEADER TO SHIFT AND ALLOW PIPING TO MOVE OUT OF ALIGNMENT, FURTHER ADDING TO THE FORCES ACTING TO PULL THE SEGMENTS FROM THE COUPLING PIPING CHANGE IN 2005 UTILIZED UNRESTRAINED, SHORT-BARREL, INSULATING DRESSER COUPLINGS USE OF MECHANICAL COUPLING; DESIGN & MATERIAL CHOICE UNRESTRAINED MECHANICAL COUPLING USED AS PERMANENT METHOD OF JOINING TWO PIPE SEGMENTS. CONSTRUCTION ACTIVITY AROUND A PRESSURIZED 99 PSIG MAIN CONDUCTED WITH INSUFFICIENT SAFEGUARDS. ENBRIDGE PROCEEDED WITH TIE-IN EXCAVATION WHILE 99 PSIG MAIN WAS STILL IN SERVICE.
2025-03-31 10:13 | NO | YES | NO | 20170040 | 16654 | 2017-05-01 15:40 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2017-04-01 17:17 |  |  | 2017 | 172 WYTHE AVE | NEW YORK | BROOKLYN | NY | 11211 | 40.7419 | -73.9893 | [9 empty] | 2017-04-02 08:00 | 1174636 |  | NATURAL GAS |  | 250 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 100 | 2017-04-01 17:17 |  |  |  | 2017-04-01 17:43 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2000 | [5 empty] | 24 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 273399 | 322674.253642691437515 | 0 | 0 | 0 | 0 |  |  | 1693 | 1737.766826923076923076923076923076923077 |  | 0 | 275092 | 135249.5344799661130653076923076923076923 | 324412.0204696145144380769230769230769231 | 0 | 0 | 4456 |  |  |  |  | 10.58 | 12 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | NOTIFIED FROM DISPATCH |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY. - AT 19:04 HRS LUCIANO RUSSO FROM DISP NYC NOTIFIED GAS CONTROL ABOUT A CONTRACTOR DAMAGE, ON A 24 INCH CAST IRON HP MAIN. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 1707200590 | YES, NEW YORK 811 |  | CONTRACT LOCATOR | YES | YES | 3 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | MICHAEL GALLINARO | PRINCIPAL ENGINEER | michael.gallinaro@nationalgrid.com | 718 963 5577 | 347 429 8087 |  |  |  | MICHAEL GALLINARO | PRINCIPAL ENGINEER | 718 963 5577 | michael.gallinaro@nationalgrid.com | ON 4/1/2017 AT 17:17, DISPATCH AND SCHEDULE WAS NOTIFIED BY THE FDNY OF A DAMAGED MAIN BY 172 WYTHE AVENUE BETWEEN NORTH 6 STREET AND NORTH 7 STREET. NATIONAL IMMEDIATELY RESPONDED TO THE LOCATION AND REPORTED THAT A CONTRACTOR STRUCK A 24 INCH, HIGH PRESSURE, CAST IRON MAIN IN FRONT OF 149 WYTHE AVENUE WITH A BACK HOE. THERE ARE NO REPORTS OF ANY INJURIES. ON 4/1/2017 AT 20:35 THE GAS WAS SECURED AND OCCUPANTS WERE ALLOWED TO RE-ENTER THE PREMISES. BY ON 4/2/2017 AT 13:43 ALL REPAIRS A HAVE BEEN COMPLETED AND THE MAIN WAS GASSED IN AND BY 4/3/2017 AT 16:00 THE RESTORATION BY WAS COMPLETED TO 3452 CUSTOMERS.
2025-03-31 10:13 | NO | YES | NO | 20170041 | 16559 | 2017-05-10 11:05 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2017-04-15 12:45 |  |  | 2017 | 110 TOLL GATE ROAD | WARWICK | WARWICK | RI | 02886 | 41.6998 | -71.467 | [9 empty] | 2017-04-15 17:07 | 1175780 |  | NATURAL GAS |  | 24.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2017-04-15 12:25 |  |  |  | 2017-04-15 12:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1984 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 7 |  |  | UNKNOWN | LEAK |  |  | OTHER | VEHICLE HIT SERV RISR & METERS | [5 empty] | CLASS 3 LOCATION | 200000 | 236046.403712297 | 476 | 561.79044083526686 | 3790 | 4473.07935034802815 | 0 | 0 | HOME WAS DESTROYED IN FIRE. VALUE UNKNOWN BUT ESTIMATED. |  | 70 | 71.85096153846153846153846153846153846154 |  | 0 | 204336 | 99915.0994784044437358461538461538461538 | 241153.1244650187565484615384615384615385 | 0 | 0 | 1 |  |  |  |  | 31 | 31 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT WAS NOT THE RESULT OF ANY OPERATION THAT THE CONTROL ROOM CAN DETECT UNDER PRESENT OPERATING CONDITIONS OR ALARMS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | CORINNE D BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE D BYRNES | PRINCIPAL PROGRAM MANAGER FEDERAL PROGRAMS | 631-770-3549 | corinne.byrnes@nationalgrid.com | NATIONAL GRID DISPATCH WAS NOTIFIED BY WARWICK FIRE DEPARTMENT THAT AN VEHICLE ACCIDENT OCCURRED ON SATURDAY, APRIL 15 AT 12:25. VEHICLE DRIVER LOST CONTROL, CRASHED INTO A SERVICE RISER AND (3) METER ASSEMBLY AT 110 TOLL GATE ROAD, CAUSING A BREAK IN THE SERVICE AND ALLOWING GAS TO ESCAPE. THE GAS IGNITED, CAUSING A FIRE AT THE CUSTOMER'S RESIDENCE. ONE PERSON WAS HOSPITALIZED. NO ADDITIONAL PEOPLE WERE EVACUATED. GAS WAS SHUTDOWN ON 4/15/2017 AT 14:50. A 5/8" PE PLASTIC END CAP WAS INSTALLED AND LEAK TESTED. SERVICE IS NOT RESTARTED AT THIS TIME.
2025-03-31 10:13 | NO | YES | NO | 20170042 | 16550 | 2017-05-10 16:49 | ORIGINAL FINAL | 31470 | VECTREN ENERGY DELIVERY OF OHIO | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2017-04-17 23:04 |  |  | 2017 | 126 N. OHIO STREET | SIDNEY | SHELBY | OH | 45365 | 40.2866 | -84.1256 | [9 empty] | 2017-04-18 01:47 | 1176016 |  | NATURAL GAS |  | 87 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-04-17 23:05 |  |  |  | 2017-04-17 23:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2010 | [8 empty] | STEEL |  |  |  | 0.133 | [6 empty] | OTHER | [8 empty] | NIPPLE BETWEEN RISER SHUT-OFF VALVE AND THE REGULATOR WAS BROKE OFF. | CLASS 2 LOCATION | 550000 | 649127.61020881675 | 942 | 1111.77856148491887 | 280 | 330.4649651972158 | 0 | 0 |  |  | 216 | 221.711538461538461538461538461538461538 |  | 0 | 551438 | 269651.6181028021176401538461538461538462 | 650791.5652739604231315384615384615384615 | 1 | 0 | 0 |  |  |  |  | 50 | 50 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JOHN SPINKS | MANAGER GAS COMPLIANCE AND QMP | jaspinks@vectren.com | 937-440-1844 | 937-440-1818 |  |  |  | JIM FRANCIS | VICE PRESIDENT SAFETY AND SYSTEM INTEGRITY | 812-491-4369 | jmfrancis@vectren.com | ON THE EVENING OF 4/17/17 THE DRIVER OF A PICKUP TRUCK JUMPED THE STREET CURB AND STRUCK A SERVICE REGULATOR LOOP OUTSIDE OF A COMMERCIAL BUILDING IN SIDNEY, OHIO. DESPITE PROTECTION BARRIERS, THE TRUCK'S IMPACT SHEARED OFF THE ONE INCH NIPPLE JUST ABOVE THE SERVICE RISER SHUT-OFF VALVE AND ALLOWED NATURAL GAS TO ESCAPE. THE NATURAL GAS IGNITED CAUSING THE ADJACENT BUILDING AND PICKUP TRUCK TO CATCH FIRE. VECTREN WAS NOTIFIED OF THE INCIDENT BY THE SIDNEY FIRE DEPARTMENT AND SENT A FIRST RESPONDER TO THE SITE. THE REGULATOR ISOLATION VALVE AND THE SERVICE CURB VALVE WERE CLOSED, ELIMINATING THE SOURCE OF NATURAL GAS. THE SERVICE METER WAS LOCATED INSIDE THE BUILDING AND SUSTAINED NO DAMAGE BY THE VEHICLE.
2025-03-31 10:13 | NO | NO | NO | 20170043 | 16562 | 2017-05-30 16:14 | SUPPLEMENTAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2017-05-10 18:45 |  |  | 2017 | NEAR GEAR RAOD EAST OF ROUTE 99 | BURLINGTON | SKAGIT | WA | 98233 | 48.4929 | -122.3338 | [9 empty] | 2017-05-11 16:17 | 1178094 |  | NATURAL GAS |  | 6500 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-05-10 23:41 |  |  |  | 2017-05-11 00:01 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1975 | [8 empty] | OTHER | REGULATOR STATION DIAPHRAGM | [9 empty] | OTHER | [8 empty] | RELEASE OF GAS FROM RELIEF VALVE | CLASS 3 LOCATION | 0 | 0 | 5201 | 6138.386728538283485 | 2323 | 2741.678979118329655 | 0 | 0 |  |  | 32400 | 33256.7307692307692307692307692307692308 |  | 0 | 39924 | 34442.2799678743536710769230769230769231 | 42136.7964768873823707692307692307692308 | 0 | 0 | 0 |  |  |  |  | 271 | 240 | 249 |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | VICKI GANOW | PIPELINE SAFETY SPECIALIST | vicki.ganow@cngc.com | 3607882381 | 3607331416 |  |  |  | CHRIS GRISSOM | MGR STANDARDS AND COMPLIANCE | 5095316427 | christopher.grissom@cngc.com | ON 05/10/17 AT 1141, CASCADE NATURAL GAS CORPORATION'S CUSTOMER SERVICE CENTER RECEIVED A CALL THAT THE RELIEF VALVE WAS CHATTERING AT THE R18 REGULATOR STATION. CASCADE NATURAL GAS RESPONDED TO THE SCENE AND FOUND THE SYSTEM PRESSURE ELEVATED AND THE RELIEF VALVE RELIEVING GAS TO THE ATMOSPHERE. IT WAS DETERMINED ON THE SCENE THAT THE R18 OPERATING REGULATOR FAILED TO LOCK UP DUE TO EXCESSIVE METAL SHAVINGS IN THE DIAPHRAGM. WHILE INVESTIGATING THE INCIDENT, A REVIEW OF THE PRESSURE INFORMATION FOR THE SYSTEM INDICATED THAT THE SYSTEM PRESSURE HAS BEEN ELEVATED BEGINNING MID-DAY 05/08/17 AND CONTINUED INTERMITTENTLY UNTIL R18 WAS REMEDIATED ON 05/11/17. IT WAS ALSO IDENTIFIED THAT A TAP HAD BEEN PERFORMED ON AN EXISTING PIPELINE JUST UPSTREAM OF THE R18 REGULATOR STATION ON 05/08/17. CASCADE NATURAL GAS BELIEVES THAT THE PERFORMANCE OF THE TAP RESULTED IN METAL SHAVINGS IN THE PIPELINE THAT ULTIMATELY MIGRATED IN TO THE DIAPHRAGM OF THE R18 OPERATING REGULATOR. THE REQUIRED CONFIRMATION CALL WAS MADE TO THE NRC AT 18:58 ON 12-MAY-17. THE INCIDENT REPORT NUMBER WAS 1178165.
2025-03-31 10:13 | NO | NO | NO | 20170044 | 16581 | 2017-05-31 16:08 | SUPPLEMENTAL FINAL | 11032 | LACLEDE GAS CO | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2017-04-25 15:41 |  |  | 2017 | 2760 UNION ROAD | SAINT LOUIS | ST. LOUIS COUNTY | MO | 63125-3939 | 38.5225 | -90.3197 | [9 empty] | 2017-05-01 15:55 | 1177165 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-04-25 15:41 |  |  |  | 2017-04-25 16:21 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 108 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1964 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 56612 | 66815.29503480278882 | 500 | 590.1160092807425 | 0 | 0 |  |  | 1 | 1.02644230769230769230769230769230769231 |  | 0 | 57113 | 27918.2491944047880547692307692307692308 | 67406.4374863912236276923076923076923077 | 0 | 0 | 0 |  |  |  |  | 25 | 25 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY EXCAVATION DAMAGE CAUSED THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [5 empty] | YES | [6 empty] | CONTRACTOR | DIRECTIONAL DRILLING | WATER | YES | 170803850 |  |  | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | NICOLE CHRISTIANER | MANAGER OF PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  |  |  |  | CRAIG HOEFERLIN | VP OF OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | ON 4/25/17, A UTILITY CONTRACTOR STRUCK AN 8 INCH NATURAL GAS DISTRIBUTION MAIN WITH DIRECTIONAL BORE. CONTRACTOR MADE A LOCATE REQUEST AND A PORTION OF THE MAIN WAS MARKED. HOWEVER, THE DAMAGED MAIN WAS NOT COMPLETELY MARKED WITHIN THE FULL SCOPE OF THE REQUEST. GAS LOSS WAS INSIGNIFICANT DUE TO THE DAMAGE RUNNING HORIZONTALLY WITH THE MAIN CREATING ONLY A PIN HOLE LEAK. THE RELEASE OF NATURAL GAS DID NOT MEET FEDERAL REPORTING REQUIREMENTS OF AT LEAST $50,000 ESTIMATED PROPERTY DAMAGE (LEAK REPAIR COST) UNTIL 5/1/17. THE 48 HOUR FOLLOW-UP NOTICE NRC NUMBER IS 1177229.
2025-03-31 10:13 | NO | NO | NO | 20170045 | 16556 | 2017-05-31 16:33 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2017-05-05 01:20 |  |  | 2017 | 75TH AVENUE & BUCKEYE ROAD | PHOENIX | MARICOPA | AZ | 85043 | 33.4381 | -112.2218 | [9 empty] | 2017-05-05 14:11 | 1177559 |  | NATURAL GAS |  | 762 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-05-05 01:20 |  |  |  | 2017-05-05 01:51 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2012 | [8 empty] | STEEL |  | SEAMLESS | SEAMLESS | 0.237 | [6 empty] | OTHER | [8 empty] | DISTRICT REGULATOR STATION STRUCK BY VEHICLE. | CLASS 3 LOCATION | 0 | 0 | 37000 | 43668.584686774945 | 0 | 0 | 0 | 0 |  |  | 2000 | 2052.884615384615384615384615384615384615 |  | 0 | 39000 | 19985.2565589862605384615384615384615385 | 45721.4693021595603846153846153846153846 | 6 | 0 | 0 |  |  |  |  | 265 | 275 | 275 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | SHAWN BRINK | ADMINSTRATOR DIVISION COMPLIANCE | shawn.brink@swgas.com | 602-484-5489 |  |  |  |  | LYNN MALLOY | GENERAL MANAGER OPERATIONS | 602-484-5477 | lynn.malloy@swgas.com | P/L # 2017-0079 SOUTHWEST GAS CORPORATION (SWG) RESPONDED TO A REPORT OF A VEHICLE STRIKING A DISTRICT REGULATOR STATION AT THE NORTHEAST CORNER OF 75TH AVENUE AND BUCKEYE ROAD IN PHOENIX. SWG WAS NOTIFIED OF THE INCIDENT ON MAY 5, 2017 AT 01:20 BY THE FIRE DEPARTMENT. SWG CREWS RESPONDED AND CONTROLLED THE FLOW OF GAS BY UTILIZING ONE VALVE RESULTING IN AN OUTAGE OF SIX COMMERCIAL CUSTOMERS. SUBSEQUENT REPAIRS WERE MADE AND THE FACILITY WAS PLACED BACK IN SERVICE ON MAY 6, 2017 AT 07:58. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THE INCIDENT. SWG NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) ON MAY 5, 2017 AT 14:11 AFTER DETERMINING THE SIGNIFICANCE OF THE EVENT WITH AN ESTIMATED REPAIR COSTS EXCEEDING $25,000 AND WAS GIVEN NRC REPORT #1177559. SWG PROVIDED AN UPDATE TO THE NRC ON MAY 6, 2017 AT 15:55 AND WAS GIVEN NRC REPORT #1177639. SWG LATER RECEIVED AN E-MAIL THAT A CORRECTION WAS MADE TO NRC REPORT #1177639 AND WAS ISSUED NRC REPORT #1177642.
2025-03-31 10:13 | NO | NO | NO | 20170047 | 16780 | 2017-06-13 11:47 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2017-05-12 16:30 |  |  | 2017 | CR10 WEST OF CR3 HALF MILE | Not Within a Municipality | WELD | CO | 80156 | 40.0579 | -105.0313 | [9 empty] | 2017-05-19 07:15 | 1178739 |  | NATURAL GAS |  | 3390 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-05-12 17:42 |  |  |  | 2017-05-12 18:14 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 32 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1955 | [5 empty] | 4 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.125 | [6 empty] | MECHANICAL PUNCTURE | 5 | 3 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 13159 | 15530.673132250581115 | 1000 | 1180.232018561485 | 0 | 0 |  |  | 16936 | 17383.8269230769230769230769230769230769 |  | 0 | 31095 | 23002.2134231661622006923076923076923077 | 34094.7320738889891919230769230769230769 | 0 | 0 | 0 |  |  |  |  | 250 | 250 | 250 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | XCEL ENERGY CONTROLLER NOTIFIED BLACK HILLS |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 71140037300 |  |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | BILL STEPHENS | MGR CODES AND STANDARDS | bill.stephens@blackhillscorp.com | 3035663509 |  |  |  |  | BILL STEPHENS | MGR CODES AND STANDARDS | 3035663509 | bill.stephens@blackhillscorp.com | CONTRACTOR WAS DIGGING A SEWER LINE. THE BACK HOE SLID OFF OF THE SPOIL PILE OF DIRT INTO THE 4-INCH HIGH PRESSURE GAS PIPELINE DAMAGING THE MAIN. LOCATES WERE MARKED PROPERLY.
2025-03-31 10:13 | NO | YES | YES | 20170048 | 16569 | 2017-06-16 09:39 | ORIGINAL | 38967 | LIBERTY ENERGY (GEORGIA) CORP D/B/A LIBERTY UTILITIES GEORGIA | 2300 VICTORY DRIVE | COLUMBUS | GA | 31901 | 2017-05-15 10:55 |  |  | 2017 | 4313 WOODRUFF RD. | COLUMBUS | MUSCOGEE | GA | 31904 | 32.5062 | -84.9625 | [9 empty] | 2017-05-16 16:40 | 1178487 |  | NATURAL GAS |  | 35.2 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 3 | 2017-05-15 10:55 |  |  |  | 2017-05-15 11:12 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2006 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 50000 | 59011.60092807425 | 2500 | 2950.5800464037125 | 10000 | 11802.32018561485 | 0 | 0 |  |  | 232 | 238.134615384615384615384615384615384615 |  | 0 | 62732 | 30771.3325450651490384615384615384615385 | 74002.6357754774278846153846153846153846 | 2 | 0 | 0 |  |  |  |  | 45 | 45 | 80 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | TYPE OF FACILITY INVOLVED. (SERVICE LINE) | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | HAROLD WOODS | DIRECTOR OPERATIONS | harold.woods@libertyutilities.com | 706-478-1810 |  |  |  |  | HAROLD WOODS | DIRECTOR OPERATIONS | 706-478-1810 | harold.woods@libertyutilities.com | A FORKLIFT DRIVER WORKING AT THE LOCATION STRUCK THE METER SET LOCATED ON THE REAR OF THE BUILDING AT 4313 WOODRUFF RD. THE RISER FOR THE METER SET WAS DAMAGED BY THE FORK OF THE FORKLIFT. IT IS BELIEVED THAT THE FORKLIFT WAS THE SOURCE OF IGNITION AND THE THE ESCAPING GAS IGNITED DAMAGING THE FORKLIFT, EXTERIOR OF THE BUILDING (SHEET METAL) AND SOME INVENTORY. THE FORKLIFT OPERATOR RECEIVED SOME BURNS AS WELL THAT REQUIRED OVERNIGHT HOSPITALIZATION.
2025-03-31 10:13 | NO | YES | NO | 20170049 | 31402 | 2017-06-16 13:53 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2017-05-08 13:55 |  |  | 2017 | 6205 ARCHIBALD AVE | RANCHO CUCAMONGA | SAN BERNARDINO | CA | 91737 | 34.1417 | -117.5934 | [9 empty] | 2017-06-13 17:20 | 1181092 |  | NATURAL GAS |  | 225 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-05-08 13:55 |  |  |  | 2017-05-08 19:13 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1983 | [5 empty] | 2 | ASTM 2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 126060 | 148780.0482598607991 | 20354 | 24022.44250580046569 | 200 | 236.046403712297 | 0 | 0 |  |  | 1350 | 1385.697115384615384615384615384615384615 |  | 0 | 147964 | 72949.2233977333697164615384615384615385 | 174424.2342847581771746153846153846153846 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | 2" PLASTIC SOCKET FUSION COUPLING |  |  | YES | [10 empty] | YES |  |  |  | POOR CONSTRUCTION/INSTALLATION PROCEDURES |  |  | NO | [86 empty] | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE MANAGER | tbauer@semprautilities.com | 909-376-7208 | 909-885-6270 |  |  |  | TROY A. BAUER | PIPELINE SAFETY AND COMPLIANCE MANAGER | 909-376-7208 | tbauer@semprautilities.com | ON MAY 8TH, 2017 A LEAK WAS DISCOVERED NEAR 6205 ARCHIBALD AVE. IN RANCHO CUCAMONGA. RESPONDING SOCALGAS CREWS LOCATED THE LEAK ON A ALDYL-A PLASTIC 2 INCH COUPLING AND AFFECTED A REPAIR. NO INJURIES OR FURTHER DAMAGE RESULTED FROM THIS INCIDENT. INVESTIGATION IMMEDIATELY FOLLOWING THE LEAK REPAIR REVEALED ELEVATED METHANE CONCENTRATIONS IN THE SOIL SURROUNDING THE REPAIRED LEAK. CREWS BEGAN TO PERFORM VACUUM EXTRACTION OF RESIDUAL GAS PER GAS STANDARD 184.0426 MITIGATION OF PERSISTENT RESIDUAL GAS INDICATIONS. EXTRACTION OPERATIONS CONTINUED, INCLUDING THE USE OF CONTRACTORS, UNTIL METHANE CONCENTRATIONS WERE RETURNED TO NORMAL CONCENTRATIONS. EXTRACTION EQUIPMENT WAS REMOVED FROM THE SITE WEDNESDAY JUNE 7TH, 2017. POST EXTRACTION MONITORING CONTINUES FOR 6 WEEKS UNTIL JULY 19TH, 2017 TO VERIFY METHANE CONCENTRATIONS REMAIN AT NORMAL CONCENTRATIONS. THIS INCIDENT WAS REPORTED TO THE CPUC DUE TO MEDIA COVERAGE OF GAS EXTRACTION OPERATION ON MAY 18TH. THIS INCIDENT WAS REPORTED TO PHMSA ON JUNE 13TH, WHEN CLAIMS OF PROPERTY DAMAGE ESTIMATES BEGAN COMING IN, AND IT WAS DETERMINED THOSE COULD POTENTIALLY EXCEED THE $50,000 THRESHOLD. WHEN THOSE COSTS ARE FINALIZED, A SUPPLEMENTAL AND FINAL REPORT WILL BE SUBMITTED OR RESCINDED AS APPROPRIATE. NOTE: THE GAS LOSS CALCULATION WAS BASED ON THE TIME SOCALGAS IDENTIFIED THE LEAK UNTIL THE TIME GAS WAS CONTROLLED. 12-26-18 - SUPPLEMENTAL REPORT SUBMITTED WITH FINAL COSTS.
2025-03-31 10:13 | NO | YES | YES | 20170050 | 16577 | 2017-06-20 10:37 | ORIGINAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2017-04-06 20:47 |  |  | 2017 | 1112 W. WASHINGTON STREET | ALEXANDRIA | MADISON | IN | 46001 | 40.264 | -85.692 | [9 empty] | 2017-04-07 00:03 | 1175059 |  | NATURAL GAS |  | 10440 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 4 | 4 | YES |  |  |  |  | NO | 90 | 2017-04-06 21:20 |  |  |  | 2017-04-06 21:20 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1983 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | VEHICLE DAMAGED ABOVEGROUND PIPING, SHEARING 2" RISER. | CLASS 2 LOCATION | 25000 | 29505.800464037125 | 17000 | 20063.944315545245 | 3000 | 3540.696055684455 | 0 | 0 |  |  | 45083 | 46275.0985576923076923076923076923076923 |  | 0 | 90083 | 64803.9272209084457692307692307692307692 | 99385.5393929591326923076923076923076923 | 0 | 0 | 65 |  |  |  |  | 225 | 230 | 240 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | VEHICLE DAMAGING THE FACILITIES WAS THE KNOWN CAUSE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JOHN SPINKS | GAS COMPLIANCE AND QMP MANAGER | jaspinks@vectren.com | 937-440-1844 | 937-440-1818 |  |  |  | NANCY CONDER | COMPLIANCE AND QUALITY ASSURANCE DIRECTOR | 812-491-4545 | nconder@vectren.com | A VEHICLE TRAVELING ON W. WASHINGTON STREET VEERED OFF THE ROADWAY AND STRUCK AND DAMAGED AN ABOVEGROUND REGULATOR STATION, SHEARING A 2" RISER ALLOWING NATURAL GAS TO ESCAPE AND IGNITE. BEFORE ENCOUNTERING THE REGULATOR STATION, THE VEHICLE DESTROYED THE PROTECTIVE BARRIER AS WELL AS SNAPPING A UTILITY POLE.
2025-03-31 10:13 | NO | YES | YES | 20170051 | 30065 | 2017-06-22 13:17 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2017-05-23 06:55 |  |  | 2017 | 6952 WEIMAN CT | COMMERCE CITY | ADAMS | CO | 80022-0000 | 39.8226 | -104.9242 | [9 empty] | 2017-05-25 22:21 | 1179380 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | YES | 2 | 2017-05-23 06:55 |  |  |  | 2017-05-23 07:25 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 47 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1959 | [5 empty] | 2.38 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 100000 | 118023.2018561485 | 4000 | 4720.92807424594 | 5000 | 5901.160092807425 | 0 | 0 |  |  | 4 | 4.10576923076923076923076923076923076923 |  | 0 | 109004 | 53284.8189585936199230769230769230769231 | 128649.3957924326342307692307692307692308 | 1 | 0 | 12 |  |  |  |  | 14 | 14 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | TREE ROOT GROWTH | NO | [218 empty] | DANIEL MAY | ENGINEER | daniel.l.may@xcelenergy.com | 303-571-3191 |  |  |  |  | MARK A. NOLAN | PRINCIPAL ENGINEER | 303-571-3931 | mark.nolan@xcelenergy.com | INCIDENT IS STILL UNDER INVESTIGATION. DELAY IN NOTICE DUE TO ORIGINAL BELIEF THAT GAS SOURCE WAS BIOGENIC AND NOT NATURAL GAS. MARCH 19, 2008 SUPPLEMENTAL REPORT: AFTER SITE INVESTIGATION AND LABORATORY INVESTIGATION, DEPTH OF COVER, LEAK DESCRIPTION, AND APPARENT CAUSE WERE COMPLETED. THERE WAS EXTENSIVE TREE ROOT GROWTH AROUND THE 2" STEEL MAIN. A TREE ROOT DIRECTLY UNDER THE THREADED COUPLING APPEARS TO HAVE CAUSED BENDING STRESSES AND THE GAS LEAK.
2025-03-31 10:13 | NO | YES | NO | 20170052 | 16580 | 2017-06-22 16:19 | ORIGINAL FINAL | 15329 | PEOPLES GAS LIGHT & COKE CO | 200 E RANDOLPH STREET | CHICAGO | IL | 60601 | 2017-05-25 08:31 |  |  | 2017 | 10044 S CENTRAL PARK AVE | CHICAGO | COOK | IL | 60655 | 41.7115 | -87.7139 | [9 empty] | 2017-05-25 10:57 | 1179301 |  | NATURAL GAS |  | 51 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2017-05-25 08:31 |  |  |  | 2017-05-25 09:17 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2016 | [5 empty] | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | DR11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 3.1 | [7 empty] | CLASS 4 LOCATION | 100000 | 118023.2018561485 | 5114 | 6035.70654292343429 | 0 | 0 | 0 | 0 |  |  | 662 | 679.504807692307692307692307692307692308 |  | 0 | 105776 | 52010.0608955024184472307692307692307692 | 124738.4132067642419823076923076923076923 | 1 | 0 | 0 |  |  |  |  | 22 | 22 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY A THIRD PARTY DAMAGE VIA DIRECTIONAL DRILL | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | DIRECTIONAL DRILLING | IRRIGATION | NO | [5 empty] | YES | 7 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | SHAWN BARTELS | PRINCIPAL ENGINEER | srbartels@peoplesgasdelivery.com | 3122405421 |  |  |  |  | TOM WEBB | COMPLIANCE MANAGER | 3122404650 | tjwebb@peoplesgasdelivery.com | ILLINOIS IRRIGATION SERVICES LLC HAD HIT A 2 INCH MEDIUM PRESSURE SERVICE WITH A DIRECTIONAL BORING MACHINE WHILE INSTALLING A SPRINKLER SYSTEM. NATURAL GAS MIGRATED INTO THE CENTERLINE SEWER AND ENTERED THE BUILDING. AN EXPLOSION WAS REPORTED IN THE UTILITY ROOM OF THE BUILDING. PGL PERFORMED A LEAK INVESTIGATION FOLLOWING THE EXPLOSION, CHECKING SEWER, BASINS, BUILDINGS AND ANY POTENTIAL MIGRATORY PATHS. AN INITIAL READING OF 100% GAS AT THE SPOT OF THE HIT AND IN THE NEARBY SEWER BASIN. GAS WAS SECURED AT THE SITE. THE EXCAVATED AREA WAS AERATED TO ELIMINATE ANY RESIDUAL GAS IN THE GROUND. DISTRIBUTION CREW EMPLOYEES TOOK A FINAL ROUND OF BAR-HOLE READINGS USING THE CGI. NO OTHER READINGS (ZERO READS) WERE OBSERVED. SERVICE WAS PERMANENTLY REPAIRED USING 4 FEET OF NEW 2 INCH YELLOW PLASTIC PIPE AND 2 ELECTROFUSION COUPLINGS. THE SERVICE WAS PRESSURE TESTED FOR 1 HOUR, FROM THE POINT OF THE HIT TO THE RISER. THE LINE WAS PLACED BACK IN SERVICE. DUE TO MECHANICAL DAMAGE IN THE UTILITY ROOM, THE GAS WAS LEFT LOCKED OFF AT THE RISER, PENDING FOLLOW-UP BUILDING REPAIRS BY THE BUILDING OWNER AND THE UNIVERSITY CONTRACTORS. THE ILLINOIS COMMERCE COMMISSION WAS ON SITE TO INVESTIGATE THE EXPLOSION. PGL CONSIDERS THIS INCIDENT CLOSED.
2025-03-31 10:13 | NO | NO | NO | 20170053 | 16586 | 2017-06-30 13:41 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2017-06-07 01:58 |  |  | 2017 | 67TH AVENUE & NORTHERN AVENUE | GLENDALE | MARICOPA | AZ | 85301 | 33.5528 | -112.2035 | [9 empty] | 2017-06-07 03:55 | 1180455 |  | NATURAL GAS |  | 207 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-06-07 02:25 |  |  |  | 2017-06-07 02:25 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1994 | [8 empty] | STEEL |  | SEAMLESS | SEAMLESS | 0.133 | [6 empty] | OTHER | [8 empty] | DISTRICT REGULATOR STATION STRUCK BY VEHICLE. | CLASS 3 LOCATION | 0 | 0 | 65739 | 77587.272668213462415 | 2000 | 2360.46403712297 | 0 | 0 |  |  | 544 | 558.384615384615384615384615384615384615 |  | 0 | 68283 | 33628.4932643226900914615384615384615385 | 80506.1213207210477996153846153846153846 | 0 | 0 | 0 |  |  |  |  | 396 | 400 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | SHAWN BRINK | ADMINISTRATOR DIVISION COMPLIANCE | shawn.brink@swgas.com | 602-484-5489 | 602-484-5322 |  |  |  | LYNN MALLOY | GENERAL MANAGER OPERATIONS | 602-484-5477 | lynn.malloy@swgas.com | P/L # 2017-0079 SOUTHWEST GAS CORPORATION (SWG) RESPONDED TO A REPORT OF A VEHICLE STRIKING A DISTRICT REGULATOR STATION AT THE NORTHEAST CORNER OF 67TH AVENUE AND NORTHERN AVENUE IN GLENDALE. SWG WAS NOTIFIED OF THE INCIDENT ON JUNE 7, 2017 AT 01:58 BY THE PHOENIX FIRE DEPARTMENT. THE ENTIRE INTERSECTION OF 67TH AVENUE AND NORTHERN INCLUDING A PORTION OF THE US 60 WAS CLOSED BY THE FIRE DEPARTMENT. SWG CREWS RESPONDED AND CONTROLLED THE FLOW OF GAS BY UTILIZING TWO VALVES RESULTING IN NO OUTAGE. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THE INCIDENT. SWG NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) ON JUNE 7, 2017 AT 03:55 AFTER DETERMINING THE SIGNIFICANCE OF THE EVENT WITH ESTIMATED REPAIR COSTS EXCEEDING $50,000 AND WAS GIVEN NRC REPORT #1180455. SWG PROVIDED AN UPDATE TO THE NRC ON JUNE 8, 2017 AT 14:50 AND WAS GIVEN NRC REPORT #1180643.
2025-03-31 10:13 | NO | YES | NO | 20170055 | 16591 | 2017-07-09 16:55 | ORIGINAL FINAL | 30769 | MISSOURI GAS ENERGY | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2017-06-09 09:54 |  |  | 2017 | 6512 E 155TH ST | GRANDVIEW | JACKSON | MO | 64030 | 38.843 | -94.5195 | [9 empty] | 2017-06-09 13:36 | 1180714 |  | NATURAL GAS |  | 309.85 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-06-09 09:56 |  |  |  | 2017-06-09 10:08 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 25 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1960 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 6 | 6 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 154784 | 182681.03276102089424 | 500 | 590.1160092807425 | 0 | 0 |  |  | 1798 | 1845.543269230769230769230769230769230769 |  | 0 | 157082 | 77612.6488483848071910769230769230769231 | 185116.6920395324059707692307692307692308 | 4 | 0 | 948 |  |  |  |  | 10 | 10 | 10 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | CURB/SIDEWALK | YES | 171570049 |  |  | CONTRACT LOCATOR | YES | YES | 14 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | NICOLE CHRISTIANER | MANAGER OF PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  |  |  |  | CRAIG HOEFERLIN | VP OF OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | ON FRIDAY, JUNE 9, 2017, AN EXCAVATOR GRADING FOR NEW CURBS AND SIDEWALKS SEVERED A 6-INCH STEEL NATURAL GAS DISTRIBUTION MAIN WHILE EXCAVATING WITH A TRACKHOE. THE EXCAVATOR HAD A VALID LOCATE TICKET AND THE GENERAL AREA WAS MARKED. HOWEVER, THE LOCATE MARKS WERE INCOMPLETE AT THE POINT OF THE DAMAGE. THE CONTRACT LOCATOR WAS AT THE SCENE IN THE PROCESS OF COMPLETING THE LOCATE WHEN THE DAMAGE OCCURRED. IN ADDITION, THE EXCAVATOR DID NOT UTILIZE THE MISSOURI POSITIVE RESPONSE PROCESS AS REQUIRED BY MISSOURI REVISED STATUTE 319.030.4. THE 48 HOUR UPDATE NRC REPORT NUMBER IS 1180834.
2025-03-31 10:13 | NO | YES | NO | 20170056 | 30257 | 2017-07-11 18:24 | SUPPLEMENTAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2017-06-12 14:40 |  |  | 2017 | 9130 15TH PL. S. UNIT A | SEATTLE | KING | WA | 98108-5124 | 47.5214 | -122.3122 | [9 empty] | 2017-06-12 15:37 | 1180971 |  | NATURAL GAS |  | 98.88 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2017-03-07 15:23 |  |  |  | 2017-03-07 15:54 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1981 | [5 empty] | 2 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3406 | LEAK |  |  | OTHER | UNKNOWN SOURCE/NOT EXCAVATED | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 143000 | 168773.178654292355 | 39000 | 46029.048723897915 | 0 | 0 |  |  | 1374 | 1410.331730769230769230769230769230769231 |  | 0 | 183374 | 90269.2797943066370769230769230769230769 | 216212.5591089595007692307692307692307692 | 0 | 0 | 0 |  |  |  |  | 35 | 35 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | GROUND PATROL BY OPERATOR OR ITS CONTRACTOR |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | UNKNOWN - LEAK SOURCE WAS NOT EXPOSED | [11 empty] | YES | LEAK SOURCE WAS NOT EXPOSED. |  | YES |  |  |  | OTHER | LEAK SOURCE WAS NOT EXPOSED, SUSPECTED DUPONT MATERIAL FAILURE | NO | [86 empty] | MONICA FERGUSON | REGULATORY COMPLIANCE ANALYST | monica.ferguson@pse.com | 425-462-3087 |  |  |  |  | CHERYL MCGRATH | MANAGER COMPLIANCE PROGRAMS | 425-462-3207 | cheryl.mcgrath@pse.com | ON FEBRUARY 1, 2017, A LEAK WAS IDENTIFIED NEAR THIS ADDRESS BY PSE'S LEAK SURVEY CONTRACTOR, AND THE LEAK WAS MONITORED IN ACCORDANCE WITH PSE STANDARDS. ON 3/7/17, PSE RESPONDED TO AN ODOR CALL 9130 15TH PL S, SEATTLE, AND EVACUATED TWO PEOPLE FROM ONE STRUCTURE AS A PRECAUTION. PSE VENTILATED THE AREA TO MAKE IT SAFE, AND SEARCHED FOR THE SOURCE OF GAS. SITE CONDITIONS INCLUDING HEAVY RAIN, SATURATED SOIL CONDITIONS, CLAY SOILS, WALL TO WALL PAVEMENT, AND A NEARBY STREAM MADE PINPOINTING THE LEAK SOURCE DIFFICULT. PSE AND CONTRACTOR PERSONNEL MONITORED THE LEAK INDICATIONS DAILY FOR SEVERAL WEEKS WHILE TRYING TO NARROW DOWN THE SOURCE OF THE GAS. IN MAY, SEVERAL SHUT-IN TESTS WERE PERFORMED AND THE LEAK LOCATION WAS NARROWED DOWN TO A 650 FOOT SECTION OF PIPING. PSE REPLACED THIS SECTION OF MAIN AND SERVICES AND THE LEAK WAS ELIMINATED. PSE FIRST RESPONSE COSTS ALONG WITH LEAK MONITORING COSTS AND PIPE REPLACEMENT CHARGES TOTALED OVER $50K. THIS EVENT WAS REPORTED AS A FEDERAL INCIDENT ON 6/12 AFTER DISCOVERING COSTS HAD ACCUMULATED PAST $50K. COST INFORMATION ESTIMATED GFR COSTS= $39,000 ESTIMATED IFS LEAK MONITORING COSTS $41,000 IFS MAIN REPLACEMENT WORK- PHASE 1 $132,000 IFS MAIN REPLACEMENT WORK- PHASE 2 $20,000 (FOR 130 FEET) GAS LOSS COST $400 .
2025-03-31 10:13 | NO | YES | NO | 20170057 | 16595 | 2017-07-14 14:13 | ORIGINAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2017-06-21 05:08 |  |  | 2017 | HIGHWAY 24 AND HIGHWAY 300 | LEADVILLE | LAKE | CO | 80461 | 39.2215 | -106.3492 | [9 empty] | 2017-06-21 12:58 | 1181851 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-06-21 05:08 |  |  |  | 2017-06-21 05:35 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1972 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.133 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 180000 | 212441.7633410673 | 50000 | 59011.60092807425 | 0 | 0 |  |  | 27 | 27.71394230769230769230769230769230769231 |  | 0 | 230027 | 112453.4792466089792307692307692307692308 | 271481.0782114492423076923076923076923077 | 0 | 0 | 177 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DANIEL MAY | GAS ENGINEERING SUPERVISOR | daniel.l.may@xcelenergy.com | 303-571-3191 | 303-571-0000 |  |  |  | MARK NOLAN | PRINCIPAL ENGINEER | 303-571-3931 | mark.nolan@xcelenergy.com | DRIVER LOST CONTROL OF VEHICLE AND DAMAGED REGULATOR STATION, BUT WAS NOT INJURED. STATION WAS SHUT-IN, WHICH CAUSED CUSTOMER OUTAGE. INCIDENT WAS TELEPHONICALLY REPORTED ONCE IT BECAME EVIDENT THAT COSTS OF RESPONSE, REPAIR, AND RESTORATION WOULD EXCEED INCIDENT CRITERIA.
2025-03-31 10:13 | NO | YES | NO | 20170059 | 16773 | 2017-07-21 09:55 | SUPPLEMENTAL FINAL | 31470 | VECTREN ENERGY DELIVERY OF OHIO | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2017-06-22 12:50 |  |  | 2017 | 311 COUNTY ROAD 11 | BELLEFONTAINE | LOGAN | OH | 43311 | 40.347 | -83.767 | [9 empty] | 2017-06-22 13:59 | 1181945 |  | NATURAL GAS |  | 345 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 80 | 2017-06-22 12:50 |  |  |  | 2017-06-22 12:50 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 43 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1985 | [5 empty] | 4 | ASTM D2513 | PLEXCO PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | MECHANICAL PUNCTURE | 2 | 4 | [7 empty] | CLASS 3 LOCATION | 200000 | 236046.403712297 | 45000 | 53110.440835266825 | 25000 | 29505.800464037125 | 0 | 0 |  |  | 1085 | 1113.689903846153846153846153846153846154 |  | 0 | 271085 | 133010.7388062199053846153846153846153846 | 319776.3349154471038461538461538461538462 | 1 | 1 | 4 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 714600077 | OHIO UTILITIES PROTECTION SERVICE |  | CONTRACT LOCATOR | YES | YES | 21 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JOHN SPINKS | MANAGER GAS COMPLIANCE AND QMP | jaspinks@vectren.com | 937-440-1844 | 937-440-1818 |  |  |  | NANCY CONDER | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | 812-491-4545 | nconder@vectren.com | ON THURSDAY, JUNE 22, 2017, VECTREN ENERGY DELIVERY OF OHIO WAS NOTIFIED BY THE BELLEFONTAINE FIRE DEPARTMENT OF A HIT NATURAL GAS MAIN AT THE INTERSECTION OF COUNTY ROAD 11 AND COUNTY ROAD 18 IN LOGAN COUNTY, OHIO. NATURAL GAS WAS VENTING FROM A DIRECTIONAL BORING EXCAVATION SITE. VECTREN PERSONNEL WERE DISPATCHED TO THE SCENE AND UPON ARRIVAL WITNESSED A STRUCTURE EXPLOSION AND ENSUING FIRE AT 311 COUNTY ROAD 11. VECTREN PERSONNEL EVACUATED HOMES AND BUSINESSES IN THE IMMEDIATE VICINITY AND ISOLATED THE ESCAPING NATURAL GAS AT THE EXCAVATION SITE WITH A SHUTOFF VALVE.
2025-03-31 10:13 | NO | NO | NO | 20170060 | 16599 | 2017-07-21 13:19 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2017-07-07 03:16 |  |  | 2017 | 67TH AVENUE AND CAMELBACK ROAD | GLENDALE | MARICOPA | AZ | 85301-7211 | 33.5088 | -112.2029 | [9 empty] | 2017-07-07 10:34 | 1183372 |  | NATURAL GAS |  | 4 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-07-07 03:40 |  |  |  | 2017-07-07 03:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2011 | [8 empty] | STEEL |  | SEAMLESS | SEAMLESS | 0.237 | [6 empty] | OTHER | [8 empty] | DISTRICT REGULATOR STATION STRUCK BY VEHICLE. | CLASS 3 LOCATION | 0 | 0 | 51366 | 60623.79786542923851 | 500 | 590.1160092807425 | 0 | 0 |  |  | 11 | 11.29086538461538461538461538461538461538 |  | 0 | 51877 | 25363.4119505175843204615384615384615385 | 61225.2047400945963946153846153846153846 | 0 | 0 | 0 |  |  |  |  | 270 | 275 | 720 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | SHAWN BRINK | ADMINISTRATOR DIVISION COMPLIANCE | shawn.brink@swgas.com | 602-484-5489 | 602-484-5322 |  |  |  | MICHAEL CHASE | GENERAL MANAGER OPERATIONS | 602-484-5477 | lynn.malloy@swgas.com | P/L 2017-0342 SOUTHWEST GAS CORPORATION (SWG) RESPONDED TO A REPORT OF A VEHICLE STRIKING A DISTRICT REGULATOR STATION AT THE SOUTHEAST CORNER OF 67TH AVENUE AND CAMELBACK ROAD IN GLENDALE. SWG WAS NOTIFIED OF THE INCIDENT ON JULY 7, 2017 AT 03:16 BY THE PHOENIX FIRE DEPARTMENT. THE ENTIRE INTERSECTION OF 67TH AVENUE AND CAMELBACK ROAD WAS CLOSED BY THE FIRE DEPARTMENT. UPON ARRIVAL AT 03:40 SWG CONFIRMED THAT FIRE DEPARTMENT HAD SECURED THE FLOW OF GAS UTILIZING A CLIMAX PLUG. THERE WERE TWO PEOPLE TRANSPORTED TO THE HOSPITAL AS A RESULT OF THE VEHICLE ACCIDENT AND NOT DUE TO THE INCIDENT. SWG NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) ON JULY 7, 2017 AT 10:34 AFTER DETERMINING THE SIGNIFICANCE OF THE EVENT WITH ESTIMATE REPAIR COSTS EXCEEDING $25,000 AND WAS GIVEN THE NRC REPORT #1183372. SWG PROVIDED AN UPDATE TO THE NRC ON JULY 8, 2017 AT 13:30 AND WAS GIVEN THE NRC REPORT #1183484.
2025-03-31 10:13 | NO | YES | NO | 20170061 | 16706 | 2017-07-24 14:10 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2017-06-20 19:23 |  |  | 2017 | 4955 MARMOL DR | WOODLAND HILLS | LOS ANGELES | CA | 91364 | 34.1602 | -118.5902 | [9 empty] | 2017-06-20 20:47 | 1181797 |  | NATURAL GAS |  | 49 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2017-06-20 19:23 |  |  |  | 2017-06-20 19:38 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 20 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1966 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.3 | 0.3 | [7 empty] | CLASS 3 LOCATION | 1300000 | 1534301.6241299305 | 2750 | 3245.63805104408375 | 200 | 236.046403712297 | 0 | 0 |  |  | 291 | 298.694711538461538461538461538461538462 |  | 0 | 1303241 | 637180.0363142514058038461538461538461538 | 1538082.00329622534228846153846153846154 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | HAND TOOLS | SEWER (SANITARY/STORM) | NO | [7 empty] | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MATT BEZECK | PIPELINE SAFETY AND COMPLIANCE ADVISOR | mbezeck@semprautilities.com | 858-547-2020 |  |  |  |  | NADIA HANG | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 714-323-9825 | nhang@semprautilities.com | ON JUNE 20, 2017, A THIRD PARTY CONTRACTOR WAS EXCAVATING TO REPAIR A SEWER LINE WHEN HE STRUCK A 3/4 INCH STEEL NATURAL GAS SERVICE CAUSING A LEAK. CREWS RESPONDED, AT WHICH POINT THE HOUSE THAT HAD THE DAMAGED SERVICE EXPLODED. ONCE IT WAS DEEMED SAFE TO DO SO, SOCAL CREWS CONTROLLED THAT GAS. NO INJURIES RESULTED FROM THIS INCIDENT. THE DAMAGED SERVICE WAS ABANDONED AND WILL NOT BE RESTORED UNTIL REPAIRS TO THE HOUSE HAVE BEEN MADE. INVESTIGATION OF THE INCIDENT SHOWED THERE WAS NO VALID USA TICKET FOR THE CONTRACTOR. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO MORE THAN $50,000 OF DAMAGE ASSOCIATED WITH A RELEASE OF GAS. FOR ANY FURTHER QUESTIONS, CONTACT MATT BEZECK AT (619) 328-8631.
2025-03-31 10:13 | NO | YES | NO | 20170062 | 30650 | 2017-07-25 10:17 | SUPPLEMENTAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2017-07-07 11:12 |  |  | 2017 | 139 LINCOLN AVENUE | FAIR LAWN BOROUGH | BERGEN | NJ | 07410 | 40.9467 | -74.1468 | [9 empty] | 2017-07-07 19:15 | 1183417 |  | NATURAL GAS |  | 54 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 30 | 2017-07-07 11:12 |  |  |  | 2017-07-07 11:35 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1970 | [5 empty] | 1.66 | ASTM A53 | UNKNOWN | STEEL |  | OTHER | ERW | 0.14 | [6 empty] | RUPTURE |  |  |  |  | LONGITUDINAL |  | 1.5 | 1.5 |  | CLASS 3 LOCATION | 350000 | 413081.20649651975 | 1000 | 1180.232018561485 | 10000 | 11802.32018561485 | 1000 | 1180.232018561485 | POLICE DEPARTMENT TRAFFIC CONTROL |  | 400 | 410.576923076923076923076923076923076923 |  | 0 | 362400 | 177331.4550240942663076923076923076923077 | 427654.5676423344930769230769230769230769 | 1 | 0 | 0 |  |  |  |  | 13.54 | 13.54 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | MICHAEL DONOHUE | PRINCIPAL REGULATORY SPECIALIST | michael.donohue@pseg.com | 908-608-4053 |  |  |  |  | CHRIS LAROSSA | DISTRICT MANAGER- REGULATORY POLICY AND PROCEDURE | 973-896-7617 | christopher.laross@pseg.com | ON FRIDAY, JULY 7, 2017, AT 11:12 AM, PSE&G RECEIVED A CALL FROM THE FAIR LAWN POLICE DISPATCH NOTIFYING OF A DOWNED POWER LINE IN FRONT OF THE VALLEY NATIONAL BANK AT 139 LINCOLN AVENUE, FAIR LAWN AND THE AREA OF THE DOWNED POWER LINE HAD IGNITED. AT 11:35 AM, PSE&G ARRIVED ON THE SCENE AND DISCOVERED THE DOWNED POWER LINE HAD MADE CONTACT WITH THE CURB VALVE BOX LOCATED AT GRADE, FOR THE NATURAL GAS SERVICE FEEDING 139 LINCOLN AVENUE, CAUSING A RUPTURE OF THE UNDERGROUND GAS SERVICE AT THE AREA OF THE CURB VALVE. THE IGNITION IN FRONT OF 139 LINCOLN AVENUE WAS NATURAL GAS FUELED AND IT WAS ALSO DISCOVERED THAT THE DOWNED POWER LINE CAUSED THE INSIDE METER SET TO RUPTURE FUELING A FIRE INSIDE THE BANK. THE VALLEY NATIONAL BANK, LINCOLN AVENUE CAT HOSPITAL, AND SEVERAL HOMES WERE EVACUATED AT THE DISCOVERY OF THE IGNITION WITH THE HELP OF THE POLICE AND FIRE DEPARTMENTS, APPROXIMATELY 30 PEOPLE. THE CATS THAT WERE CURRENTLY BOARDED IN THE LINCOLN AVENUE CAT HOSPITAL WERE RELOCATED TO ANOTHER VETERINARY FACILITY, UNHARMED. THE FLAMES AT THE CURB VALVE BOX LOCATION WERE ONLY A FEW FEET FROM THE SERVICE CONNECTION TO THE MAIN, WHICH REQUIRED PSE&G TO THROTTLE THE 20 INCH CAST IRON, 15PSI GAS MAIN FOR THE SAFE DISCONNECTION OF THE DAMAGED SERVICE. AT 5:38 PM, PSE&G AND THE FIRE DEPARTMENT WERE ABLE TO EXTINGUISH THE FLAMES IN FRONT OF 139 LINCOLN AVENUE AND CREWS WERE ABLE TO PHYSICALLY DISCONNECT THE SERVICE AT 6:25 PM. EVACUEES WERE ALLOWED TO RETURN TO THEIR DWELLINGS DURING THE RESPONSE WHEN THE AREA WAS DECLARED SAFE AND THE IGNITION WAS CONFIRMED TO BE UNDER CONTROL, EXCEPT FOR THE VALLEY NATIONAL BANK, WHICH WAS DAMAGED FROM THE INSIDE FIRE AND THE FIRE DEPARTMENT'S WATER RESPONSE. BY 6:43 PM, THE GAS MAIN FEEDING THE AREA WAS BACK AT FULL PRESSURE, AND THE ONLY SERVICE LEFT WITHOUT GAS WAS THE VALLEY NATIONAL BANK AT 139 LINCOLN AVENUE. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. AT APPROXIMATELY 7:00 PM, IT WAS DETERMINED THE EXTENT OF THE DAMAGE DUE TO THE NATURAL GAS FUELED IGNITION HAD MET PHMSA REPORTING CRITERIA AND THE INCIDENT REPORT- NRC #: 1183417 WAS MADE FRIDAY, JULY 7, 2017 @ 7:29 PM. FOLLOW UP INCIDENT REPORT- NRC #: 1183576 MADE SUNDAY, JULY 9, 2017 @ 6:03 PM.
2025-03-31 10:13 | NO | YES | YES | 20170064 | 33969 | 2017-08-01 13:43 | SUPPLEMENTAL FINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2017-07-02 12:32 |  |  | 2017 | 206 SPRINGDALE LANE | MILLERSVILLE | LANCASTER | PA | 17551 | 39.998 | -76.3739 | [9 empty] | 2017-07-02 13:52 | 1182921 |  | NATURAL GAS |  | 120 |  | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2 | 0 | 0 | 1 | 0 | 3 | YES |  |  |  |  | YES | 1 | 2017-07-02 10:26 |  |  |  | 2017-07-02 11:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1998 | [5 empty] | 0.5 | ASTM 2513 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 7 |  |  | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 1617000 | 1908435.174013921245 | 27000 | 31866.264501160095 | 588000 | 693976.42691415318 | 0 | 0 |  |  | 230 | 236.081730769230769230769230769230769231 |  | 0 | 2232230 | 1091257.27573398198707692307692307692308 | 2634513.94716000375076923076923076923077 | 0 | 0 | 22 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FAILURE OCCURRED ON A MEDIUM PRESSURE DISTRIBUTION SYSTEM. PRESSURES AND FLOW RATES WERE WITHIN NORMAL RANGES BEFORE, DURING, AND AFTER THE INCIDENT. ACTIONS BY THE CONTROL ROOM DID NOT IMPACT THE INCIDENT. | [12 empty] | YES | 8 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | BOLTED |  | SERVICE OR MAIN TEE |  | PERFECTION CORPORATION |  | OTHER | MATERIALS JOINED: 1ST PLASTIC, 2ND PLASTIC | [22 empty] | YES | 2 OUT OF 4 NYLON BOLTS ON A 2" PERFECTION MECHANICAL TAPPING TEE FRACTURED ALLOWING THE TEE TO SEPARATE FROM THE MAIN, ALLOWING GAS TO ESCAPE. |  |  | YES |  |  |  |  | NO | [86 empty] | JOHN TOUMEH | SENIOR ENGINEER | jtoumeh@ugi.com | 717 675 4606 |  |  |  |  | HANS BELL | CHIEF OPERATING OFFICER | 610 796-3450 | hbell@ugi.com | THIS IS A SUPPLEMENTAL AND FINAL REPORT BEING FILED TO PROVIDE UPDATED INCIDENT INFORMATION: AFTER RESPONDING TO A GAS ODOR COMPLAINT AT 202 SPRINGDALE LANE, MILLERSVILLE, PA, UGI WORKERS DETECTED A NATURAL GAS LEAK NEAR 206 SPRINGDALE LANE. NATURAL GAS WAS TRACED TO AN AREA ABOVE A MECHANICAL TAPPING TEE THAT WAS BURIED UNDER APPROXIMATELY 3 FEET OF SOIL, NEAR 206 SPRINGDALE LANE. DURING THE COMPANY RESPONSE, AT APPROXIMATELY 12:32 PM, THERE WAS AN EXPLOSION AT 206 SPRINGDALE LANE. AS A RESULT OF THE EXPLOSION, 1 EMPLOYEE FATALITY OCCURRED, AND 3 NON-FATAL INJURIES WERE SUSTAINED. THE EXPLOSION AND SUBSEQUENT FIRE RENDERED THE DWELLING AT 206 SPRINGDALE LANE A TOTAL LOSS AND NEARBY RESIDENCES SUSTAINED VARYING DEGREES OF DAMAGE. THE PROBABLE CAUSE OF THIS ACCIDENT WAS A LEAK IN THE CONNECTION OF A PERFECTION PERMALOCK MECHANICAL TAPPING TEE ASSEMBLY THAT CONNECTED THE GAS MAIN TO THE SERVICE LINE FOR 206 SPRINGDALE LANE, MILLERSVILLE, PA. FOR FURTHER DETAILS, PLEASE REFER TO NTSB PIPELINE ACCIDENT BRIEF PAB-19-01.
2025-03-31 10:13 | NO | YES | NO | 20170065 | 16666 | 2017-08-02 18:36 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2017-07-03 08:42 |  |  | 2017 | 201 ESSEX STREET | CONCORD | CONTRA COSTA | CA | 94520 | 38.0257 | -122.0285 | [9 empty] | 2017-07-03 11:32 | 1183022 |  | NATURAL GAS |  | 340 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-07-03 08:42 |  |  |  | 2017-07-03 09:07 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 16281 | 19215.357494199537285 | 60922 | 71902.09503480278917 | 86385 | 101954.342923433881725 | SERVICE RESTORATION |  | 1000 | 1026.442307692307692307692307692307692308 |  | 0 | 164588 | 80914.0664233446508452307692307692307692 | 194098.2377601285158723076923076923076923 | 316 | 0 | 246 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | YES | YES | OTHER | [12 empty] | UTILITY | AUGER | POLE | YES | 716700615 | N/A |  | UTILITY OWNER | YES | YES | 11 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON JULY 3, 2017, AT 0842 HOURS, PG&E WAS NOTIFIED OF A DIG-IN NEAR 201 ESSEX ST, CONCORD. PG&E ELECTRIC CREW STRUCK A 2 IN. STEEL DISTRIBUTION MAIN WITH AN AUGER RESULTING IN AN UNINTENTIONAL RELEASE OF GAS. PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SITE AT 0907 HOURS. THERE IS A VALID USA TICKET (X716700615) AND FACILITIES WERE PROPERLY LOCATED & MARKED. THE CAUSE OF THE DIG-IN WAS FAILURE TO EXPOSE THE MARKED LINE PRIOR TO USING POWER EQUIPMENT. THE FLOW OF GAS WAS STOPPED AT 1032 HOURS. 562 CUSTOMERS GAS SERVICES WERE IMPACTED. THE REPAIR CREW REPLACED 3 SECTIONS OF THE 2 IN MAIN (DAMAGE POINT AND SQUEEZE POINTS) BY 2100 HOURS. GSRS WERE DISPATCHED AND BEGAN RELIGHTING THE CUSTOMERS AT 2130 HOURS. ALL IMPACTED CUSTOMERS GAS SERVICE THAT WAS ACCESSIBLE AND REQUESTED WERE RESTORED. THERE WERE NO POLICE, FIRE DEPARTMENT, OR MEDIA REPORTED ONSITE. THERE WERE NO INJURIES, FATALITIES, OR IGNITION ASSOCIATED WITH THIS INCIDENT. THIS INCIDENT IS BEING REPORTED TO THE DOT (#1183022) AND CPUC DUE TO THE UNINTENTIONAL RELEASE OF GAS AND ESTIMATED COSTS GREATER THAN $50K (ASSOCIATED WITH CUSTOMER RELIGHTS). THE TOTAL CUSTOMER OUTAGE TOTAL WAS PROVIDED TO THE DOT (SAME REPORT NUMBER) ON 7/5/17.
2025-03-31 10:13 | YES | NO | NO | 20170066 | 16621 | 2017-08-03 13:38 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2017-07-03 23:06 |  |  | 2017 | 878 VIA PANORAMA | BANNING | RIVERSIDE | CA | 92220 | 33.9333 | -116.8911 | [9 empty] | 2017-07-04 03:04 | 1183061 |  | NATURAL GAS |  | 40 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2017-07-03 23:06 |  |  |  | 2017-07-03 23:38 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1980 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | DEBRIS FROM THE COLLAPSING STRUCTURE DUE TO THE HOUSE EXPLOSION REPORTEDLY FELL ONTO THE MSA, SHEARING OFF THE STOPCOCK FROM THE SERVICE RISER, CAUSING A GAS LEAK. SOURCE OF EXPLOSION STILL UNDER INVESTIGATION. | CLASS 3 LOCATION | 200000 | 236046.403712297 | 1583 | 1868.307285382830755 | 200 | 236.046403712297 | 0 | 0 |  |  | 240 | 246.346153846153846153846153846153846154 |  | 0 | 202023 | 98862.7858682848647256153846153846153846 | 238397.1035552382816011538461538461538462 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | ALEXANDER HUGHES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | ahughes@semprautilities.com | 949-697-2539 |  |  |  |  | ALEXANDER HUGHES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 949-697-2539 | ahughes@semprautilities.com | ON JULY 3RD, 2017, FIRE DEPARTMENT REPORTED AN EXPLOSION AND STRUCTURE FIRE AT A VACANT HOUSE LOCATED AT 878 VIA PANORAMA, BANNING. DEBRIS FROM THE COLLAPSING STRUCTURE REPORTEDLY FELL ONTO THE MSA, BREAKING THE SERVICE RISER AT THE THREADS BELOW THE STOPCOCK, RESULTING IN AN ESCAPE OF GAS AND AN IGNITION AT THE RISER. SOCALGAS CREW RESPONDED AND CONTROLLED THE GAS BY 2:48 AM OF 7/4/2017 BY PINCHING THE SERVICE. THE STOPCOCK WAS FOUND IN THE OFF POSITION AND CLAM-SHELLED. UNDERGROUND SAMPLES WERE NEGATIVE. THE SERVICE TO THIS VACANT UNIT WAS ABANDONED, AND THE SERVICE TO THE NEXT DOOR NEIGHBOR AFFECTED BY THIS INCIDENT WAS RESTORED ON THE SAME DAY. THERE WERE NO INJURIES THAT RESULTED FROM THIS INCIDENT. INVESTIGATION REGARDING THE CAUSE OF THE STRUCTURE FIRE AND THE EXPLOSION IS ONGOING. THIS WAS REPORTED TO DOT AND CPUC DUE TO DAMAGES EXCEEDING $50,000 AND A RELEASE OF GAS. 8/17/17 - AFTER FURTHER REVIEW AND RECEIVING A COPY OF THE CAL FIRE INVESTIGATION REPORT #0082038, THE ORIGIN, HEAT SOURCE, MATERIAL AND CAUSE OF THE FIRE HAVE BEEN FINALIZED AS UNDETERMINED. FOR ANY FURTHER QUESTIONS, CONTACT ALEXANDER HUGHES (949)697 2539.
2025-03-31 10:13 | NO | YES | NO | 20170067 | 16619 | 2017-08-04 14:40 | SUPPLEMENTAL FINAL | 31159 | KANSAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2017-07-22 23:50 |  |  | 2017 | 4505 W 91ST STREET | PRARIE VILLAGE | JOHNSON | KS | 66207 | 38.9635 | -94.6385 | [9 empty] | 2017-07-27 15:45 | 1185458 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-07-23 01:09 |  |  |  | 2017-07-23 01:38 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1994 | [8 empty] | OTHER | ALUMINUM METER | [9 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 450000 | 531104.40835266825 | 500 | 590.1160092807425 | 100 | 118.0232018561485 | 0 | 0 |  |  | 50 | 51.32211538461538461538461538461538461538 |  | 0 | 450650 | 220308.2833861324677384615384615384615385 | 531863.8696791897563846153846153846153846 | 0 | 0 | 1 |  |  |  |  | 0.5 | 0.5 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | RANDY SPECTOR | DIRECTOR OF ENGINEERING | randy.spector@onegas.com | 913-599-8931 |  |  |  |  | RANDY SPECTOR | DIRECTOR OF ENGINEERING | 913-599-8931 | randy.spector@onegas.com | ON THE EVENING OF JULY 22ND, A STRONG THUNDERSTORM OCCURRED RESULTING IN HIGH WINDS AND NUMEROUS LIGHTING STRIKES. IT APPEARS THAT LIGHTNING STRUCK THE GAS METER LOCATED ON THE WEST SIDE OF THE HOME LOCATED AT 4505 W. 91ST STREET. THEN, EITHER THE GAS ESCAPING FROM THE METER WAS IGNITED CAUSING THE HOUSE TO CATCH FIRE, OR THE HOUSE CAUGHT FIRE AND IGNITED THE GAS ESCAPING FROM THE METER. KGS HAS PARTICIPATED IN AN INVESTIGATION WITH THE PRAIRIE VILLAGE FIRE DEPARTMENT, THE KANSAS CORPORATION COMMISSION AND THE HOMEOWNER'S INSURANCE CARRIER. NO EVIDENCE OR INFORMATION HAS BEEN LOCATED WHICH CAN PROVIDE A DEFINITIVE DETERMINATION OF THE CAUSE OF THE FIRE OR THE RELEASE OF NATURAL GAS.
2025-03-31 10:13 | NO | NO | NO | 20170068 | 16647 | 2017-08-07 11:38 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2017-07-10 14:58 |  |  | 2017 | INTERSECTION BAKER STREET AND WATER STREET | WARREN | BRISTOL | RI | 02885 | 41.7305 | -71.2852 | [9 empty] | 2017-07-11 15:11 | 1183760 |  | NATURAL GAS |  | 1369 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 50 | 2017-07-10 13:29 |  |  |  | 2017-07-10 13:29 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 3 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 3 | 9.4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 67019 | 79097.969651972163215 | 0 | 0 | 0 | 0 |  |  | 1512 | 1551.980769230769230769230769230769230769 |  | 0 | 68531 | 34195.6798518650780360769230769230769231 | 80649.9504212029324457692307692307692308 | 7 | 0 | 303 |  |  |  |  | 56.5 | 56 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER ACTIONS WERE NOT A CONTRIBUTING FACTOR TO THIRD PARTY DAMAGE TO THE DISTRIBUTIONS SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | LIQUID PIPELINE | YES | 20172300446 | DIG SAFE |  | UTILITY OWNER | NO | YES | 7 | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | MICHAEL GALLINARO | PRINCIPAL ENGINEER | michael.gallinaro@nationalgrid.com | 718 963 5577 | 347 4298087 |  |  |  | MICHAEL GALLINARO | PRONCIPAL ENGINEER | 718 963 5577 | michael.gallinaro@nationalgrid.com | ON 7/10/2017 AT 13:29, NATIONAL GRID DISPATCH RECEIVED CALL FOR A HIT MAIN. CB UTILITIES WAS TRENCHING FOR INSTALL OF THEIR WATER MAIN AND HIT WITH A BACKHOE A NATIONAL GRID MARKED 3 INCH GAS MAIN THAT WAS DEAD ENDED AND CAPPED OFF. THE CONTRACTOR HIT THE DRESSER END CAP WITH THE BACKHOE AND PULLED CAP OFF RESULTING IN BLOWING GAS FROM NATIONAL GRID'S 3 INCH, 60# GAS MAIN. DURING PIPE REPAIR PROCESS 310 CUSTOMERS WERE SHUT OFF. AFTER MAIN REPAIR WE RESTORED ALL 310 CUSTOMERS AFFECTED. THE GAS MAIN WAS APPROPRIATELY MARKED PRIOR TO EXCAVATION, BUT THE CONTRACTOR FAILED TO MAINTAIN MARKS AS THEIR SPOIL PILE WAS COVERING THE MARKS FOR THE STUB THAT WAS HIT. NATIONAL GRID HAD THE C+M CREW CLEAR OUT THE SPOIL PILE FROM THE AREA OF THE DAMAGE AND MARKS WERE FOUND FOR THE STUB AND WERE ACCURATE IN REGARDS TO THE STUB LOCATION. THERE WERE NO NATIONAL GRID PERSONNEL ON SITE AT THE TIME OF THE INCIDENT
2025-03-31 10:13 | NO | YES | NO | 20170070 | 16623 | 2017-08-18 11:05 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2017-07-21 09:11 |  |  | 2017 | FIG TREE LN & AIRPORT RD | REDDING | SHASTA | CA | 96002 | 40.4912 | -122.2955 | [9 empty] | 2017-07-21 12:55 | 1184823 |  | NATURAL GAS |  | 2618 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-07-21 09:11 |  |  |  | 2017-07-21 09:11 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1973 | [5 empty] | 3 | UNKNOWN | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 1 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 96800 | 114246.459396751748 | 0 | 0 | 0 | 0 | N/A |  | 8000 | 8211.538461538461538461538461538461538462 |  | 0 | 104800 | 54913.6109227199797538461538461538461538 | 122457.9978582902095384615384615384615385 | 10 | 0 | 372 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM WAS NOT INVOLVED IN THE INCIDENT | [12 empty] | YES | 4 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | YES | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 718400466 | N/A |  | UTILITY OWNER | YES | YES | 6 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON JULY 21, 2017 AT 0911 HOURS, PG&ES GAS CONSTRUCTION CREW WAS EXCAVATING TO INSTALL A NEW GAS MAIN AND STRUCK THE EXISTING 3-INCH PLASTIC GAS DISTRIBUTION MAIN RESULTING IN AN UNINTENTIONAL RELEASE OF GAS NEAR THE INTERSECTION OF FIG TREE AND AIRPORT ROAD IN REDDING. THERE WAS A VALID USA TICKET (#X718400466) AND GAS FACILITIES WERE PROPERLY LOCATED & MARKED. THE DIG-IN WAS A RESULT OF NOT EXPOSING THE GAS LINE COMPLETELY USING HANDTOOLS PRIOR TO USING POWER DRIVEN EQUIPMENT. GAS FLOW WAS STOPPED AT 1145 HOURS BY DIGGING AND SQUEEZING THE MAIN RESULTING IN 382 CUSTOMERS WITHOUT GAS SERVICE AND ACTIVATION OF THE OEC AT 1201 HOURS. AT THAT TIME, THIS EVENT WAS DEEMED SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR. FOUR PG&E EMPLOYEES WERE ADMINISTERED FOR POST-ACCIDENT TESTING (PAT). REPAIRS TO THE MAIN WERE COMPLETED AT 1730 HOURS. ALL SERVICES THAT WERE IMPACTED AS A RESULT OF THIS INCIDENT WERE RESTORED. THERE WERE NO INJURIES, NO FATALITIES AND NO IGNITION ASSOCIATED WITH THIS INCIDENT. THERE WAS NO FIRE, POLICE OR MEDIA REPORTED. THIS INCIDENT WAS REPORTED TO THE DOT AT 1300 HOURS (1184823) AND CPUC DUE SIGNIFICANT IN THE JUDGMENT OF THE OPERATOR AND ESTIMATED DAMAGES GREATER THAN $50K. AN UPDATE WAS PROVIDED TO THE DOT ON 7/24/17 (1185098).
2025-03-31 10:13 | NO | YES | NO | 20170072 | 16630 | 2017-08-25 15:23 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2017-07-27 14:01 |  |  | 2017 | 216 W TADDEI RD | ACAMPO | SAN JOAQUIN | CA | 95220 | 38.1904 | -121.3211 | [9 empty] | 2017-07-27 15:56 | 1185473 |  | NATURAL GAS |  | 4900 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 10 | 2017-07-27 14:17 |  |  |  | 2017-07-27 14:41 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1946 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | ELECTRIC RESISTANCE WELDED | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 6 | 6 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 248476 | 293259.33104408354686 | 0 | 0 | 0 | 0 |  |  | 14700 | 15088.7019230769230769230769230769230769 |  | 0 | 263176 | 135417.1523674817275596923076923076923077 | 308348.0329671604699369230769230769230769 | 0 | 0 | 738 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EVENT WAS CAUSED BY A 3RD PARTY DIG IN. THIRD PARTY CONTRACTOR WAS RIPPING/PLOWING THE FIELD AND SEVERED THE 6" STEEL GAS MAIN. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | FARM EQUIPMENT | AGRICULTURE | YES | 719900024 | 811 |  | UTILITY OWNER | YES | YES | 22 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ENZA BARBATO | SENIOR PROGRAM MANAGER | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON JULY 27, 2017 AT 1401 HOURS, PG&E RECEIVED AN ERX ALARM IN ACAMPO. AT 1417 HOURS, PG&E WAS NOTIFIED OF A THIRD PARTY DIG-IN AT 216 W TADDEI RD, ACAMPO. THIRD PARTY CONTRACTOR WAS RIPPING/PLOWING THE FIELD AND SEVERED A 6' STEEL GAS MAIN, RESULTING IN AN UNINTENTIONAL RELEASE OF GAS. THERE WAS A VALID USA TICKET (#W719900024) AND PG&E FACILITIES WERE PROPERLY LOCATED & MARKED. THE DIG-IN WAS A RESULT OF FAILING TO RAISE THE RIPPER SHANK PRIOR TO DRIVING OVER THE GAS PIPELINE. IN ADDITION, THE EXCAVATOR DID NOT DETERMINE THE EXACT LOCATION OF THE LINE USING HAND TOOLS WITHIN THE TOLERANCE ZONE. PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON SITE AT 1441 HOURS. THE FLOW OF GAS WAS STOPPED AT 1527 HOURS BY SHUTTING IN THE REG STATION AND CLOSING VALVES. APPROXIMATELY 738 CUSTOMER GAS SERVICES WERE IMPACTED. REPAIRS TO THE MAIN WERE COMPLETED BY 2030 HOURS. GSRS WERE DEPLOYED AND SERVICE RESTORATION OPERATIONS BEGAN ON 7/28/17 AT 1300 HOURS. ALL SERVICES HAVE BEEN RESTORED. FIRE DEPARTMENT, HIGHWAY PATROL AND THE LOCAL SHERIFF WERE REPORTED ON-SITE. MEDIA WAS REPORTED ON SITE ON 7/28/17. THERE WERE NO INJURIES, FATALITIES, OR IGNITION ASSOCIATED WITH THIS INCIDENT. APPROXIMATELY 4.9 MMCF OF NATURAL GAS WAS UNINTENTIONALLY RELEASED. THIS INCIDENT WAS REPORTED TO DOT (1185473) DUE TO THE LARGE CUSTOMER OUTAGE RESULTING IN DAMAGES GREATER THAN $50K AND UNINTENTIONAL RELEASE OF GAS GREATER THAN 3 MMCF. THE VOLUME UPDATE WAS PROVIDED TO THE DOT (1185576) ON 7/28/17.
2025-03-31 10:13 | YES | NO | NO | 20170073 | 16727 | 2017-08-27 22:19 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2017-07-28 15:59 |  |  | 2017 | 7509 GLEN TERRA DR | LANSING | EATON COUNTY | MI | 48917 | 42.734 | -84.6608 | [9 empty] | 2017-07-28 18:38 | 1185583 |  | NATURAL GAS |  | 26 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | NO | 2 | 2017-07-28 15:59 |  |  |  | 2017-07-28 16:22 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 2001 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 5/8" |  |  | 2708 | OTHER | [8 empty] | RELEASE CAUSED BY FIRE | CLASS 3 LOCATION | 70000 | 82616.24129930395 | 1900 | 2242.4408352668215 | 165 | 194.738283062645025 | 0 | 0 |  |  | 75 | 76.98317307692307692307692307692307692308 |  | 0 | 72140 | 35297.7898123773040626923076923076923077 | 85130.4035907103396019230769230769230769 | 4 | 0 | 4 |  |  |  |  | 24.5 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | KARLI MCNEILL | GENERAL ENGINEER II | karli.mcneill@cmsenergy.com | 9892954218 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING TECHNICAL ANALYST LEAD | 9897915749 | jason.pionk@cmsenergy.com | ON FRIDAY, JULY 28 2017 AT APPROXIMATELY 1600 HOURS, A HOUSE FIRE OCCURRED AT 7509 GLEN TERRA DRIVE, LANSING MICHIGAN. THE FIRE SPREAD TO THE GAS METER, CAUSING EQUIPMENT FAILURE AND NATURAL GAS TO IGNITE. TWO RESIDENTS WERE TAKEN TO THE HOSPITAL. CONSUMERS ENERGY PERSONNEL PERFORMED A SQUEEZE-OFF PROCEDURE STOPPING THE FLOW OF GAS AT APPROXIMATELY 1815. NATURAL GAS SERVICE WAS INTERRUPTED TO 4 CUSTOMERS, AND WAS RESTORED TO THE TWO UNAFFECTED SERVICES AT 0200 ON 7/29/2017. DUE TO DAMAGE ON THE METERS AND SERVICE RISER, SERVICE WAS NOT RESTORED TO THE 2 REMAINING CUSTOMERS. INITIAL DAMAGE TO THE HOME WAS CONTAINED TO ONE CORNER, HOWEVER THE FIRE REKINDLED THE NEXT MORNING AND ADDITIONAL SMOKE/FIRE DAMAGE WAS DONE TO THE REMAINDER OF THE HOME. DAMAGE TO THE HOME IS ESTIMATED TO $70,000, HOWEVER A TOTAL PRICE HAS NOT BEEN DETERMINED AT THIS TIME. A JOINT SCENE INVESTIGATION ON AUGUST 18, 2017 WITH REPRESENTATIVES FROM FIRE FINDINGS, LLC, DELTA TOWNSHIP FIRE DEPARTMENT, HERNDON CONSULTANTS, CONSUMERS ENERGY, AND THE MPSC. THE FIRE DEPARTMENT LEFT THE CAUSE OF IGNITION AS UNDETERMINED, HOWEVER THE CONSUMERS ENERGY INVESTIGATOR CONCLUDED HOT ASHES FROM A CIGARETTE WERE DISCARDED IN COMBUSTIBLE MATERIALS (LEAVES, MULCH AND GARDEN MATERIALS) AT THE NORTH WEST CORNER OF THE PROPERTY NEAR THE PORCH AREA CAUSING AN IGNITION. THE FIRE SPREAD THE SIDE OF THE HOME TO THE LOCATION OF CONSUMERS ENERGY GAS EQUIPMENT RESULTING IN EQUIPMENT FAILURE.
2025-03-31 10:13 | NO | YES | NO | 20170074 | 16634 | 2017-08-29 18:13 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2017-08-01 14:06 |  |  | 2017 | 447 LOVE BRIDGE ROAD SE | CALHOUN | GORDON | GA | 30701 | 34.5011 | -84.8698 | [9 empty] | 2017-08-01 15:28 | 1185932 |  | NATURAL GAS |  | 374.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2017-08-01 14:06 |  |  |  | 2017-08-01 14:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1991 | [5 empty] | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 4.5 | 1 | [7 empty] | CLASS 3 LOCATION | 100000 | 118023.2018561485 | 2468 | 2912.81262180974498 | 15466 | 18253.46839907192701 | 0 | 0 |  |  | 1056 | 1083.923076923076923076923076923076923077 |  | 0 | 118990 | 58650.8016348384895103076923076923076923 | 140273.4059539532489130769230769230769231 | 0 | 0 | 11 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | AUGER | POLE | YES | 7117280036 |  |  | CONTRACT LOCATOR | YES | YES | 10 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@southernco.com | A 4-INCH PLASTIC MAIN WITH ONE-WAY FEED WAS RUPTURED BY A CONTRACT CREW WHILE INSTALLING A POWER POLE. THE ESCAPING GAS IGNITED CAUSING EXTENSIVE DAMAGES TO THE CONTRACTOR'S VEHICLE. NOTIFICATION TO THE ONE-CALL CENTER WAS MADE WHERE THE MAIN WAS LOCATED, HOWEVER, THE PIPE ITSELF WAS MIS-LOCATED BY 24 INCHES, 6 INCHES OUTSIDE THE STATE DEFINED TOLERANCE ZONE. ADDITIONAL NRC REPORT NUMBER 1186139 WAS CREATED FOR THE SAME EVENT AFTER A 48 HOUR SUPPLEMENTAL CALL WAS PLACED WITH THE NRC.
2025-03-31 10:13 | NO | NO | NO | 20170075 | 16707 | 2017-09-01 14:01 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2017-08-02 10:24 |  |  | 2017 | 4149 CASE RD. | AVON | LORAIN | OH | 44011-2107 | 41.4282 | -82.0614 | [9 empty] | 2017-08-02 14:11 | 1186041 |  | NATURAL GAS |  | 150.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-08-02 10:59 |  |  |  | 2017-08-02 11:21 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 2 | ASTM D2513 | CELANESE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | MECHANICAL PUNCTURE | 1.5 | 2 | [7 empty] | CLASS 3 LOCATION | 64000 | 75534.84918793504 | 0 | 0 | 5261 | 6209.200649651972585 | 14401 | 16996.521299303945485 | MAIN LINE CAMERA INSERTION AND VACUUM EXCAVATION FOR PROPERTY |  | 507 | 520.40625 |  | 0 | 84169 | 41376.789451856155674 | 99260.97738689095807 | 0 | 0 | 1 |  |  |  |  | 41 | 41 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 720601462 | OHIO UTILITIES PROTECTION SERVICE |  | CONTRACT LOCATOR | NO | YES | 307 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | ROB R. SMITH | OPERATIONS COMPLIANCE MANAGER | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB R. SMITH | OPERATIONS COMPLIANCE MANAGER | 614-818-2110 | rrsmith@nisource.com | ON AUGUST 2, 2017, A THIRD-PARTY CONTRACTOR, WHO WAS INSTALLING A WATER LINE ON BEHALF OF THE PROPERTY OWNER, DAMAGED A 2-INCH GAS SERVICE LINE THAT WAS NOT MARKED BY COLUMBIA'S SECOND-PARTY LOCATOR DUE TO A LACK OF RECORDS ACCURATELY IDENTIFYING THE 2-INCH IDLE CUSTOMER-OWNED SERVICE LINE. THE SECOND-PARTY LOCATOR IDENTIFIED AND MARKED THE ACTIVE GAS SERVICE LINE AT THE PROPERTY. COLUMBIA HAS COMPLETED A SAFETY INSPECTION AT THE PROPERTY THAT INCLUDED THE USE OF AN IN-PIPE CAMERA TO ENSURE SAFETY OF THE COLUMBIA FACILITIES. AT THIS POINT IN THE INVESTIGATION, COLUMBIA HAS ENOUGH INFORMATION TO FINALIZE THIS INCIDENT REPORT, AND HAS DETERMINED THAT INSUFFICIENT RECORDS LED TO THE FACILITY DAMAGE AND SUBSEQUENT PROPERTY DAMAGE AS A RESULT OF THE FIRE THAT ENSUED. PLEASE CONSIDER THIS FILE CLOSED AND FINAL.
2025-03-31 10:13 | NO | YES | NO | 20170077 | 16674 | 2017-09-08 16:10 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2017-08-10 14:00 |  |  | 2017 | INTERSECTION OF POTTER RD. & STATE RD. | DAVISON | GENESEE | MI | 48423 | 43.049 | -83.5178 | [9 empty] | 2017-09-06 14:30 | 1189560 |  | NATURAL GAS |  | 182 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-08-09 05:24 |  |  |  | 2017-08-09 05:56 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1968 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 200000 | 236046.403712297 | 133 | 156.970858468677505 | 0 | 0 |  |  | 5374 | 5516.100961538461538461538461538461538462 |  | 0 | 205507 | 102931.0700352489909448461538461538461538 | 241719.4755323041390434615384615384615385 | 0 | 0 | 0 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELEASE WAS NOT SIGNIFICANT ENOUGH TO CAUSE A PRESSURE DROP AND INITIATE A SCADA ALARM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE LIKELY CAUSE OF THE FAILURE AT THIS LOCATION IS THE WATER MAIN CONSTRUCTION DISTURBED THE AREA CAUSING THE ROAD TO SETTLE AND PLACED STRESS OF THE GAS COMPONENT RESULTING IN A GAS LEAK. | [154 empty] | CARMELLA KING | SENIOR ENGINEER TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 734-513-6256 |  |  |  |  | JASON PIONK | SR. ENG. TECH ANAL LEAD - GAS REGULATORY SERVICES | 989-791-5749 | jason.pionk@cmsenergy.com | AT APPROXIMATELY 5:24 A.M ON AUGUST 9, 2017 CONSUMERS ENERGY GAS DISPATCH WAS NOTIFIED BY A PASSERBY OF A STRONG ODOR AT THE INTERSECTION OF POTTER ROAD AND STATE ROAD (M-15), DAVISON, MICHIGAN (GENESEE COUNTY). CONSUMERS ENERGY PERSONNEL ARRIVE ONSITE AT APPROXIMATELY 5:56 A.M. TO INVESTIGATE AND MAKE SAFE. A WATER MAIN CONSTRUCTION PROJECT WAS UNDERWAY AND THE INITIAL ASSESSMENT WAS THE CONSTRUCTION MAY HAVE IMPACTED NEARBY UNDERGROUND GAS FACILITIES. A DISTRIBUTION CREW WAS NOTIFIED AND ARRIVED ONSITE AT APPROXIMATELY 7:30 A.M. THE CREW WORKED THROUGHOUT THE DAY UNTIL THE LEAK SOURCE WAS IDENTIFIED AS A SEPARATION AT A 6"S-MP INSULATING FLANGE. DUE TO UNSTABLE SOIL CONDITIONS AND EXCAVATION DEPTH AS WELL AS THE ON-GOING WATER MAIN CONSTRUCTION PROJECT, ACCESS AND REPAIR WAS DELAYED. AN INCIDENT REPORT WAS MADE TO THE MICHIGAN PUBLIC SERVICE COMMISSION ON AUGUST 10, 2017 DUE TO ANTICIPATED GAS LOSS AND REPAIR COSTS EXPECTED TO EXCEED STATE REPORTING REQUIREMENTS. THE LOCATION WAS CONTINUOUSLY MONITORED BY CONSUMERS ENERGY PERSONNEL UNTIL THE LEAKING SEGMENT WAS RETIRED SATURDAY, AUGUST 12, 2017 AT 3:25 P.M. THE PIPELINE SEGMENT WAS ISOLATED (STOPPLE/CUT AND CAP) AT FOUR LOCATIONS BECAUSE OF LIMIT ACCESS TO LEAKING COMPONENT. THE SYSTEM WILL BE TIED-IN ALLOWING FOR A TWO-WAY FEED ONCE WATER MAIN INSTALLATION IS COMPLETE. THE FLANGE LOCATION WAS APPROXIMATELY 16' FROM THE WATER CASING BORE AND MUCH OF THE AREA AND ROAD HAD SIGNIFICANT SETTLING. THE LIKELY CAUSE OF THE FAILURE AT THIS LOCATION IS THE WATER MAIN CONSTRUCTION DISTURBED THE AREA CAUSING THE ROAD TO SETTLE AND PLACED STRESS ON THE GAS COMPONENT RESULTING IN A LEAK.
2025-03-31 10:13 | NO | NO | NO | 20170078 | 16695 | 2017-09-13 15:47 | SUPPLEMENTAL FINAL | 5330 | FLORIDA PUBLIC UTILITIES CO | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2017-09-12 16:33 |  |  | 2017 | 560 NE 36TH ST. | BOCA RATON | PALM BEACH | FL | 33431 | 26.3827 | -80.0772 | [9 empty] | 2017-09-12 19:06 | 1190081 |  | NATURAL GAS |  | 0.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-09-12 16:33 |  |  |  | 2017-09-12 17:09 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1991 | [5 empty] | 1.25 | D2513 | CHEVRON PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 10000 | 11802.32018561485 | 10000 | 11802.32018561485 | 1000 | 1180.232018561485 | 0 | 0 |  |  | 12 | 12.31730769230769230769230769230769230769 |  | 0 | 21012 | 10276.5450428341977692307692307692307692 | 24797.1896974834926923076923076923076923 | 2 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | DOWNED PRIMARY ELECTRICAL LINE ARCED A HOLE IN THE GAS PIPE. | [154 empty] | MICHAEL MCCARTY | COMPLIANCE AND MEASURMENT MANAGER | mmccarty@fpuc.com | 8638457005 | 8632940629 |  |  |  | MICHAEL MCCARTY | COMPLIANCE AND MEASUREMENT MANAGER | 8638457005 | mmccarty@fpuc.com | ORIGINALLY REPORTED TO THE OPERATOR AS 560 NE 35TH ST, BOCA RATON AND SUBSEQUENTLY REPORTED TO THE NRC. ACTUAL INCIDENT ADDRESS IS 560 NE 36TH ST., BOCA RATON, FL. AN ENERGIZED PRIMARY POWER LINE FELL FROM A POLE IN A REAR UTILITY EASEMENT STRIKING A METAL STORAGE SHED AND A METAL GUY WIRE FOR THE POLE THAT WAS ANCHORED IN THE GROUND. THE CURRENT FROM THE DOWNED POWER LINE ARCED A HOLE IN A 1.25" PE GAS MAIN THAT WAS IN THE GROUND NEAR THE GUY WIRE ANCHOR CAUSING A HOLE AND IGNITED THE ESCAPING NATURAL GAS. THE RESULTING FIRE FROM THE STORAGE SHED AND THE GAS MAIN SCORCHED THE ROOF AND WALL OF A NEARBY HOUSE THAT WAS 5' AWAY FROM THE SHED. OPERATOR CREWS DUG UP AND SQUEEZED OFF THE PE GAS MAIN STOPPING THE FLOW OF GAS AND EXTINGUISHING THE FLAMES. HURRICANE IRMA HAD PASSED NEAR THE AREA TWO DAYS EARLIER ON SEPTEMBER 10TH, RESULTING IN MANY POWER LINES BEING DAMAGED. DAMAGE ESTIMATES ARE PRELIMINARY AND MAY BE HIGHER THAN ACTUAL COSTS TO REPAIR AT THIS TIME. A SUPPLEMENTAL AND FINAL REPORT WILL BE FILED WHEN MORE DETAILS ARE KNOWN. SUPPLEMENTAL - DUE TO ERROR ENTERING INCIDENT ADDRESS ON ORIGINAL REPORT. 11/15/17 - SUPPLEMENTAL AND FINAL REPORT - PART A (13B) PIPELINE RESTARTED AT 15:00 ON 9/15/17. PART C (5) CHANGED TO LEAK AND PINHOLE. PART D (2) ESTIMATED COST REVISED DUE TO MAJORITY OF DAMAGE ALREADY CAUSED BY PREVIOUS ELECTRICAL INCIDENT 2 DAYS PRIOR. PART G(4) CHANGED TO OTHER. NEW REPORTS FROM BOCA RATON FIRE DEPARTMENT SHOW THAT TWO (2) INCIDENTS OCCURRED AT THIS RESIDENCE. INCIDENT #1 WAS ELECTRICAL IN NATURE WHEN THE ELECTRICAL SERVICE DROPPED ONTO THE ROOF OF THE STRUCTURE IGNITING A CANVAS AWNING AND ARCING IN THE ROOF AND EAVES OF THE STRUCTURE AND CAUSED EXTENSIVE DAMAGE TO THE STRUCTURE ON 9/10/17 AT 09:00 HOURS. FIRE DEPARTMENT DAMAGE ESTIMATES OF $40,000 FOR THE STRUCTURE AND $5000 FOR THE CONTENTS. NATURAL GAS WAS NOT INVOLVED IN THIS INCIDENT OR THE EXTENSIVE DAMAGE TO THE STRUCTURE. INCIDENT #2, IN WHICH THE NATURAL GAS PIPELINE WAS INVOLVED, OCCURRED ON 9/12/17 AROUND 15:11 HOURS. THIS INCIDENT RESULTED FROM A DOWNED PRIMARY POWER LINE THAT DROPPED FROM A POWER POLE ONTO A METAL GUY WIRE ANCHORED IN THE GROUND IN CLOSE PROXIMITY TO THE NATURAL GAS MAIN IN A UTILITY EASEMENT AND ONTO A METAL SHED NEAR THE GAS MAIN. THE METAL SHED CONTAINED FLAMMABLE LIQUIDS AND MATERIAL AND IGNITED ALONG WITH ESCAPING NATURAL GAS FROM THE LINE DAMAGED BY THE DOWNED ELECTRICAL PRIMARY LINE. FIRE DEPARTMENT REPORTS PUT DAMAGE TO THE SHED AT $1000 AND CONTENTS AT $5000. THERE WAS ADDITIONAL SCORCHING DAMAGE TO THE CORNER OF THE HOUSE NEAR THE SHED. WE REVISE OUR ESTIMATE OF PROPERTY DAMAGE TO $10,000.
2025-03-31 10:13 | NO | YES | NO | 20170081 | 16640 | 2017-09-14 18:12 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2017-05-25 23:31 |  |  | 2017 | COUNTY RD 20 & COUNTY RD P | ORLAND | GLENN | CA | 95963 | 39.7249 | -122.1043 | [9 empty] | 2017-08-16 15:23 | 1187477 |  | NATURAL GAS |  | 179 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-05-25 23:31 |  |  |  | 2017-05-25 23:40 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | VEHICLE DAMAGE, PIPE WAS FULLY SEVERED. | CLASS 1 LOCATION | 0 | 0 | 380000 | 448488.1670533643 | 0 | 0 | 0 | 0 |  |  | 537 | 551.199519230769230769230769230769230769 |  | 0 | 380537 | 186260.2398547653369230769230769230769231 | 449039.3665725950692307692307692307692308 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ENZA BARBATO | REGULATORY COMPLIANCE SENIOR PROGRAM MANAGER | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | REGULATORY COMPLIANCE MANAGER | 925-786-0267 | gsr8@pge.com | ON MAY 25, 2017 AT APPROXIMATELY 2331 HOURS, PG&E WAS NOTIFIED OF A VEHICLE INCIDENT AT COUNTY RD 20 AND COUNTY RD P, IN THE CITY OF ORLAND, GLENN COUNTY. A VEHICLE STRUCK A FENCED-IN DISTRIBUTION GAS REGULATOR STATION, HIT THE BOLLARDS, AND DAMAGED THE EQUIPMENT ON SITE RESULTING IN AN UNINTENTIONAL RELEASE OF GAS. PG&E GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ONSITE AT 2340 HOURS AND SHUT IN GAS AT 0025 HOURS ON MAY 26, 2017. THERE WAS NO CUSTOMER IMPACT. THE CUSTOMERS DOWNSTREAM WERE SERVED THROUGH CNG (COMPRESSED NATURAL GAS). THE REG STATION WAS REBUILT AND BROUGHT BACK ON LINE ON 8/03/17. THE FIRE DEPARTMENT AND POLICE DEPARTMENT WAS REPORTED ON SITE. THERE WAS NO MEDIA, NO INJURIES OR FATALITIES. NO IGNITION WAS REPORTED. THIS INCIDENT IS NOW BEING REPORTED TO THE DOT AND CPUC DUE TO ESTIMATED COST OF REPAIRS EXCEEDING $50K. THE $50K CRITERION WAS DETERMINED ON AUGUST 16, 2017 AT 1500 HOURS. THIS SECONDARY REPORT IS BEING PROVIDED 30 DAYS AFTER DETERMINATION.
2025-03-31 10:13 | NO | YES | YES | 20170083 | 31501 | 2017-09-15 13:41 | SUPPLEMENTAL FINAL | 32061 | TEXAS COMMUNITY PROPANE, LTD. | 2579 WESTERN TRAILS BLVD., SUITE 240 | AUSTIN | TX | 78745 | 2017-09-14 16:55 |  |  | 2017 | 22320 CHIPOTLE PASS | SPICEWOOD | TRAVIS | TX | 78669 | 30.353 | -98.0869 | [9 empty] | 2017-09-14 21:47 | 1190371 |  | PROPANE GAS |  | 88 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2017-09-14 14:09 |  |  |  | 2017-09-14 14:25 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 32 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2014 | [5 empty] | 2 | PE2406 ASTM 2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.25 |  | 2406 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 175 | 206.540603248259875 | 2655 | 3133.516009280742675 | 0 | 0 |  |  | 5194 | 5331.341346153846153846153846153846153846 |  | 0 | 8024 | 6315.154160717473025384615384615384615385 | 8671.397958682848703846153846153846153846 | 0 | 0 | 25 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | HOMEBUILDER CALLED IN LEAK - HIS CONTRACTOR CAUSED DAMAGE |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | TCP EMPLOYEES WERE TO REPAIR A DAMAGED MAIN AND USED AN ELECTRICAL TOOL IN A GAS ENVIRONMENT, AGAINST COMPANY POLICY. THIS RESULTED IN AN IGNITION AND BURN INJURIES TO ONE EMPLOYEE. |  |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | JACKIE BURGE | OFFICE MANAGER | customerservicemanager@texascommunitypropane.com | 5122725503 |  |  |  |  | JACKIE BURGE | OFFICE MANAGER | 5122725503 | customerservicemanager@texascommunitypropane.com | CONCRETE COMPANY DROVE A METAL STAKE INTO A SILT FENCE AND A BOBCAT IMPALED THE STAKE DOWN INTO THE 2 INCH MAIN, CAUSING A SLOW RELEASE. OPERATOR EMPLOYEES ARRIVED AND DURING ATTEMPTED REPAIR OF DAMAGED PIPE, CAUSED IGNITION, BURNING ONE EMPLOYEE, OTHER EMPLOYEE CLOSED ISOLATION VALVE SHUTTING GAS SUPPLY OFF. BURNED EMPLOYEE TAKEN TO HOSPITAL, MAIN WAS REPAIRED AND SERVICE RESTORED TO CUSTOMERS. BURNED EMPLOYEE RELEASED THE FOLLOWING MORNING. BOTH EMPLOYEES WERE WRITTEN UP FOR NOT FOLLOWING POLICY AND BOTH ADMITTED THEY KNEW BETTER, BUT BELIEVED THEMSELVES TO BE OUT OF THE GAS ENVIRONMENT. ADDITIONALLY, BOTH EMPLOYEES WERE SUSPENDED WITHOUT PAY.
2025-03-31 10:13 | NO | NO | NO | 20170084 | 30032 | 2017-09-15 16:02 | SUPPLEMENTAL FINAL | 18308 | NV ENERGY | PO BOX 10100 | RENO WASHOE | NV | 89520 | 2017-08-18 18:43 |  |  | 2017 | 2945 SANTA ANA DR. | RENO | WASHOE | NV | 89502 | 39.4894 | -119.7533 | [9 empty] | 2017-08-18 20:24 | 1187759 |  | NATURAL GAS |  | 35 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2017-08-18 18:46 |  |  |  | 2017-08-18 19:06 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1976 | [8 empty] | STEEL |  | OTHER | ERW | 0.133 | [6 empty] | OTHER | [8 empty] | RESIDENTIAL METER AND RISER HIT BY VEHICLE. | CLASS 3 LOCATION | 57000 | 67273.225058004645 | 1957 | 2309.714060324826145 | 2439 | 2878.585893271461915 | 0 | 0 |  |  | 133 | 136.516826923076923076923076923076923077 |  | 0 | 61529 | 30137.6764985275797843076923076923076923 | 72598.0418385240099830769230769230769231 | 0 | 0 | 1 |  |  |  |  | 87 | 87 | 90 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | SUSAN BURNETTE | SR GAS COMPLIANCE ANALYST | sburnette@nvenergy.com | 775-834-7278 |  |  |  |  | JAY WIGGINS | GAS COMPLIANCE MANAGER | 775-834-7850 | jwiggins@nvenergy.com | ON AUGUST 18, 2017 AT 18:43, A VEHICLE LEFT THE ROAD AND HIT A RESIDENTIAL HOME AND GAS METER IMMEDIATELY CAUSING AN IGNITION AND STRUCTURE FIRE. RENO FIRE DEPARTMENT DISPATCH CONTACTED NV ENERGY (NVE) GAS DISPATCH AT 18:46 TO REPORT THAT A VEHICLE HIT A GAS LINE AND A STRUCTURE CAUGHT ON FIRE. NVE GAS DISPATCH CONTACTS NVE GAS SERVICEMAN AND DUTY SUPERVISOR TO RESPOND. NVE DUTY SUPERVISOR IS FIRST NVE RESPONDER ON SCENE. RENO FIRE DEPARTMENT SECURED THE GAS FLOW BY CLOSING THE RISER METER VALVE. RENO FIRE DEPARTMENT EXTINGUISHED THE STRUCTURE AND VEHICLE FIRE. THE HOME, VEHICLE, AND GAS METER WERE SEVERELY DAMAGED BY FIRE. NEWS REPORTS AND FIRE DEPARTMENT REPORT INDICATE THAT TWO VEHICLES WERE RACING, HIT EACH OTHER, AND ONE OF THE VEHICLES LOST CONTROL. THERE WERE TWO INDIVIDUALS IN THE HOME WHEN THE INCIDENT OCCURRED AND THEY EXITED SAFELY. THERE WERE TWO INDIVIDUALS IN THE VEHICLE THAT HIT THE HOUSE AND THEY EXITED THE VEHICLE AFTER THE IMPACT WITH THE HOME. THE FIRE DEPARTMENT REPORT STATES THAT TWO INDIVIDUALS WERE TRANSPORTED TO THE HOSPITAL AND AMBULANCE SERVICE INFORMATION REPORTED THEM IN STABLE CONDITION. THEIR CONDITION IS UNKNOWN AT THIS POINT DUE TO CONFIDENTIALITY. NO POLICE REPORT WAS AVAILABLE AT THE TIME OF THIS INVESTIGATION. ON AUGUST 18, 2017 AT 20:05 THE NVE DUTY SUPERVISOR ON SCENE DETERMINED THAT PROPERTY DAMAGE AND REPAIR COSTS EXCEEDED $50,000 FOR THIS EVENT. NVE NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) AT 20:24 AND WAS GIVEN NRC INCIDENT REPORT # 1187759. NVE PROVIDED AN UPDATE TO THE NRC ON AUGUST 20, 2017 AT 15:58 AND WAS GIVEN NRC INCIDENT REPORT #1187900. __ SUPPLEMENTAL REPORT SUBMITTED TO DOCUMENT DATE SERVICE RESTORED. THE HOME AT 2945 SANTA ANA IN RENO, NV HAS BEEN REPAIRED. A NEW GAS SERVICE LINE WITH AN EXCESS FLOW VALVE WAS INSTALLED ON MARCH 7, 2018. SERVICE WAS RESTORED TO THIS CUSTOMER ON MARCH 8, 2017.
2025-03-31 10:13 | NO | NO | NO | 20170086 | 16697 | 2017-09-18 23:14 | SUPPLEMENTAL FINAL | 31286 | ONEOK GAS TRANSPORTATION, LLC | 100 WEST FIFTH STREET | TULSA | OK | 74103 | 2017-08-22 21:15 |  |  | 2017 | SW/4 SEC 11, T13N, R16E | Not Within a Municipality | MUSKOGEE | OK | 74450 | 35.6124 | -95.5809 | [9 empty] | 2017-08-22 22:54 | 1188110 |  | NATURAL GAS |  | 4441 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-08-22 21:15 |  |  |  | 2017-08-22 21:49 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1.31 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | 0 | 0 | 0 | 0 | 500 | 590.1160092807425 | 0 | 0 |  |  | 11039 | 11330.8966346153846153846153846153846154 |  | 0 | 11539 | 10726.1511411297519615384615384615384615 | 11921.0126438961271153846153846153846154 | 0 | 0 | 1 |  |  |  |  | 555 | 555 | 850 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM THIRD PARTY - LOCAL DISTRIBUTION COMPANY |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LEAK RESULTED IN SMALL VOLUME RELEASED, NOT DETECTED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | KAREN PEREZ | REGULATORY COMPLIANCE COORDINATOR | karen.perez@oneok.com | 918-595-1703 |  |  |  |  | WESLEY DUNBAR | VP NATURAL GAS PIPELINE OPS | 918-588-7424 | wesley.dunbar@oneok.com | AT SOME TIME DURING THE EVENING OF 8-22-2017, LIGHTNING APPARENTLY STRUCK A FARM TAP RISER ON OGT LINE R-900. AT 21:15 ON 8-22-17, OGT PERSONNEL RECEIVED A CALL FROM A THIRD PARTY LOCAL DISTRIBUTION COMPANY THAT THERE WAS A METER IN AN AGRICULTURAL FIELD BLOWING GAS AND IT WAS ON FIRE. AT 21:49, OGT PERSONNEL ARRIVED ON LOCATION AND CONFIRMED THAT IT WAS AN OGT 1-INCH FARM TAP RISER. AT 23:54, OGT PERSONNEL CONTACTED NRC AFTER IT HAD BEEN DETERMINED THAT A SECTION OF LINE R-900 WOULD HAVE TO BE BLOWN DOWN TO COMPLETE A REPAIR. AT 23:56, OGT PERSONNEL BEGAN TO ISOLATE THE LINE SECTION. AT 01:01 ON 8-23-2017, THE LINE WAS ISOLATED. AT 03:06, OGT PERSONNEL BEGAN BLOWING THE LINE DOWN. AT 07:00, OGT PERSONNEL EXTINGUISHED THE FIRE AND ISOLATED THE 1-INCH FARM TAP RISER. 2017-11-20 SUPPLEMENTAL/FINAL SUBMITTED TO CORRECT PART A, 7 LOCAL TIME; PART C, 5 LEAK TYPE; PART D, 2C ADDED EMERGENCY RESPONSE COSTS.
2025-03-31 10:13 | NO | YES | YES | 20170087 | 16691 | 2017-09-28 11:31 | SUPPLEMENTAL FINAL | 31159 | KANSAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2017-09-01 14:53 |  |  | 2017 | 4550 SE 29TH STREET | TOPEKA | SHAWNEE | KS | 66605 | 39.0151 | -95.5924 | [9 empty] | 2017-09-01 16:11 | 1189057 |  | NATURAL GAS |  | 2 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2017-09-01 14:58 |  |  |  | 2017-09-01 15:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1968 | [5 empty] | 3 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.155 | [6 empty] | LEAK |  |  | OTHER | TAP TEE WAS REMOVED | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 150 | 177.03480278422275 | 0 | 0 |  |  | 10 | 10.26442307692307692307692307692307692308 |  | 0 | 160 | 82.81769810815635769230769230769230769231 | 187.299225861145826923076923076923076923 | 0 | 0 | 0 |  |  |  |  | 40 | 40 | 58 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | BASED ON ALL FACTS AVAILABLE TO KGS, INCLUDING INTERVIEWS, INSPECTIONS OF THE FACILITIES, AND PHOTOGRAPHS, THE COMPANY IS UNABLE TO DETERMINE THE SOURCE OF IGNITION. | [47 empty] | RANDY SPECTOR | DIRECTOR OF ENGINEERING | randy.spector@onegas.com | 913-599-8931 |  |  |  |  | RANDY SPECTOR | DIRECTOR OF ENGINEERING | 913-599-8931 | randy.spector@onegas.com | BASED ON AVAILABLE INFORMATION, A CONTRACTOR EMPLOYEE HAD REMOVED AN EXISTING SERVICE TEE, AND INSTALLED A BOILER PIN INTO THE TAP HOLE. THEN IT APPEARS THAT A CONTRACT WELDER BEGAN TO BUFF OFF THE PIPELINE AROUND THE BOILER PIN TO PREPARE FOR WELDING THE PIN INTO THE PIPELINE. IT IS ASSUMED THAT DURING THE BUFFING OPERATION, THE BOILER PIN RELEASED FROM THE PIPELINE, AND IT IS FURTHER ASSUMED THAT THIS RESULTED IN A RELEASE OF GAS AND THIS GAS THEN IGNITED CAUSING BURNS TO THE WELDERS FACE AND LEFT ELBOW. HOWEVER, THE COMPANY HAS NOT BEEN ABLE TO CONFIRM THESE ASSUMPTIONS WITH ANY REASONABLE AMOUNT OF CERTAINTY.
2025-03-31 10:13 | NO | YES | NO | 20170088 | 30716 | 2017-09-29 10:07 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2017-09-01 17:24 |  |  | 2017 | NECHES RIVER PIPELINE CROSIIING | VIDOR | ORANGE | TX | 77662 | 30.078 | -94.0768 | [9 empty] | 2017-09-01 20:25 | 1189083 |  | NATURAL GAS |  | 14000 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-09-01 17:24 |  |  |  | 2017-09-01 17:50 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | UNDERWATER CROSSING |  |  | YES | [6 empty] | YES | UNCASED | NECHES RIVER | 48 |  | PRIVATELY OWNED |  | MAIN |  | 1975 | [5 empty] | 16 | GRADE B | PHOENIX | STEEL |  | SEAMLESS | SEAMLESS | 0.5 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 16 | 16 |  | CLASS 3 LOCATION | 0 | 0 | 1750000 | 2065406.03248259875 | 300000 | 354069.6055684455 | 200000 | 236046.403712297 | USE OF CONTRACTORS & EQUIPMENT WHO SPECIALIZE IN UNDERWATER REPAIR AND REMOVAL. |  | 41000 | 42084.1346153846153846153846153846153846 |  | 0 | 2291000 | 1138767.87546849921153846153846153846154 | 2697606.17637872586538461538461538461538 | 0 | 2 | 0 |  |  |  |  | 35.6 | 72 | 78 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | NO | NO | NO | NO | OTHER | KINDER MORGAN PIPELINE PERSONNEL |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA SYSTEM FOR THIS PIPELINE WAS DOWN DUE TO HURRICANE HARVEY FLOODING | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY BOATS, BARGES, DRILLING RIGS, OR OTHER MARITIME EQUIPMENT OR VESSELS SET ADRIFT OR WHICH HAVE OTHERWISE LOST THEIR MOORING | OTHER OUTSIDE FORCE DAMAGE | MARITIME EQUIPMENT OR VESSEL ADRIFT | OTHER OUTSIDE FORCE DAMAGE | FISHING OR MARITIME ACTIVITY | [112 empty] | DAMAGE BY BOATS, BARGES, DRILLING RIGS, OR OTHER MARITIME EQUIPMENT OR VESSELS SET ADRIFT OR WHICH HAVE OTHERWISE LOST THEIR MOORING |  | YES | YES |  | YES | [163 empty] | LESLIE J. DAVENPORT | COMPLIANCE COORDINATOR II | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steve.yarbrough@centerpointenergy.com | DURING HURRICANE/TROPICAL STORM HARVEY, PORTIONS OF SOUTH TEXAS INCLUDING THE BEAUMONT/VIDOR AREA EXPERIENCED RECORD FLOODING. DURING THIS TIME THAT INCLUDED HIGH FLOOD WATERS AND SEVERE TURBULENCE IN THE NECHES RIVER THE INCIDENT DESCRIBED IN THIS REPORT OCCURRED. CENTERPOINT ENERGY IS AWARE OF TWO LARGE SHIPS AND SEVERAL TUGBOATS NEAR THE LOCATION WHERE CENTERPOINT ENERGY'S PIPELINE WAS DAMAGED.
2025-03-31 10:13 | NO | YES | NO | 20170089 | 32037 | 2017-10-06 19:58 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2017-09-06 16:01 |  |  | 2017 | 6221 BRYNHURST AVE | LOS ANGELES | LOS ANGELES | CA | 90043 | 33.9831 | -118.334 | [9 empty] | 2017-09-09 10:39 | 1189796 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-09-06 16:01 |  |  |  | 2017-09-06 16:41 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1951 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 30738 | 36277.97178654292593 | 0 | 0 | 158784 | 187401.96083526683424 | 0 | 0 |  |  | 0 | 0 |  | 0 | 189522 | 92641.519628770317894 | 223679.93262180976017 | 0 | 0 | 0 |  |  |  |  | 17 | 17 | 20 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | [197 empty] | OTHER EQUIPMENT FAILURE | [23 empty] | A LEAK WAS FOUND APPROXIMATELY 1,200 FEET AWAY FROM THE LOCATION OF THE INCIDENT; UNKNOWN IF THE LEAK AND THE INCIDENT ARE RELATED | [59 empty] | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | amatin@semprautilities.com | 909-919-0463 |  |  |  |  | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE MANAGER | 9093357915 | tbauer@semprautilities.com | ON SEPTEMBER 6, 2017, SOCALGAS BECAME AWARE OF AN EXPLOSION THAT HAD OCCURRED INSIDE AN ELECTRICAL VAULT NEAR 6221 BRYNHURST AVE, LOS ANGELES. THE INITIAL REPORT SHOWED 6426 BRYNHURST AVE, LOS ANGELES. SOCALGAS CREW RESPONDED, INVESTIGATED, AND FOUND NO INDICATION OF GAS. ADDITIONAL GAS FACILITIES WERE SURVEYED, AND GAS INDICATION WAS DETECTED NEAR 6544 BRYNHURST AVE, APPROXIMATELY 1,200 FEET SOUTH OF THE INCIDENT SITE. THE CREW IDENTIFIED AND REMEDIATED THE SOURCE OF THE LEAK. NO FURTHER DAMAGES OR INJURIES RESULTED FROM THIS INCIDENT. INVESTIGATION OF THE CAUSE OF THE EXPLOSION IS ONGOING. A REPORT WAS MADE TO THE CPUC DUE TO A POTENTIAL RELEASE OF GAS AND MEDIA COVERAGE, AND TO THE DOT DUE TO A POTENTIAL RELEASE OF GAS APPROXIMATELY 1,200 FEET AWAY AND ESTIMATED DAMAGE OF $50,000 OR MORE. THE 48-HOUR UPDATE WAS MADE TO THE DOT PER NRC #1189923. FOR ANY FURTHER QUESTIONS, CONTACT IK SONG AT (818) 279-5388. UPDATED ON 12/27/2017: UPDATED LATITUDE AND LONGITUDE ON PART A. UPDATED ON 7/12/2018: UPDATED COST INFORMATION TO DATE ON PART D. UPDATED ON 8/6/2018: UPDATED COST INFORMATION TO DATE ON PART D. UPDATED ON 1/22/2019: INVESTIGATION IS ONGOING. UPDATED ON 4/29/2019: NO UPDATES TO YTD COST INFORMATION AND INVESTIGATION IS ONGOING. FOR ANY FURTHER QUESTIONS, PLEASE CONTACT ALI MATIN AT (909) 919-0463.
2025-03-31 10:13 | NO | NO | NO | 20170091 | 16665 | 2017-10-10 17:30 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2017-09-11 13:22 |  |  | 2017 | SONOMA BLVD AND MARITIME ACADEMY DRIVE | VALLEJO | SOLANO | CA | 94590 | 38.0775 | -122.2338 | [9 empty] | 2017-09-26 14:55 | 1189958 |  | NATURAL GAS |  | 4401 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 1 | 2017-09-11 13:22 |  |  |  | 2017-09-11 13:22 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 49 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 4 | TR-148 | PLEXCO | PLASTIC |  |  |  |  | UNKNOWN |  |  |  | UNKNOWN |  | MECHANICAL PUNCTURE | 3 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 36454 | 43024.17800464037419 | 5000 | 5901.160092807425 | 0 | 0 |  |  | 13000 | 13343.75 |  | 0 | 54454 | 32607.157703016244858 | 62269.08809744779919 | 1 | 0 | 0 |  |  |  |  | 44 | 44 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | YES | YES | CITY STREET | [12 empty] | UTILITY | BORING | NATURAL GAS | YES | 724901037 | 811 |  | UTILITY OWNER | YES | YES | 12 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ENZA BARBATO | REGULATORY COMPLIANCE SENIOR PROGRAM MANAGER | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | MANAGER OF GAS OPS COMPLIANCE AND RISK | 925-786-0267 | gsr8@pge.com | ON MONDAY, SEPTEMBER 11, 2017, AT 1322 HOURS, PG&E WAS NOTIFIED OF A DIG IN AT SONOMA BLVD AND MARITIME ACADEMY DRIVE, VALLEJO. A PG&E GC CREW STRUCK A 4' PLASTIC DISTRIBUTION MAIN WITH BORING EQUIPMENT RESULTING IN AN UNINTENTIONAL RELEASE OF GAS. USA MARKED (MULTIPLE TICKETS INCLUDING W724901037). THE FLOW OF GAS WAS STOPPED AT 1605 HOURS BY SQUEEZING THREE ISOLATION POINTS. THERE WAS 1 CUSTOMER IMPACTED AND EVACUATED. THERE WERE NO INJURIES, NO FATALITIES AND NO IGNITION. FIRE DEPARTMENT, POLICE DEPARTMENT AND HIGHWAY PATROL WERE REPORTED ONSITE. THE CUSTOMER WAS RESTORED ON SEPTEMBER 12, 2017 AT 0430 HOURS.THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO DAMAGES EXPECTED TO EXCEED THE $50K THRESHOLD. AT 1457 HOURS THIS INCIDENT WAS REPORTED TO THE DOT (1189958) AND CPUC (170911-8516).
2025-03-31 10:13 | NO | YES | YES | 20170092 | 30683 | 2017-10-20 17:47 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2017-09-20 21:02 |  |  | 2017 | 1847 E. LEVEE ST. AND TURTLE CREEK | DALLAS | DALLAS | TX | 75207 | 32.7914 | -96.8285 | [9 empty] | 2017-09-20 22:43 | 1191038 |  |  |  | 1 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2017-09-20 21:02 |  |  |  | 2017-09-20 21:02 |  | NO | OPERATOR-CONTROLLED PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2017 | [5 empty] | 16 | API-5L 45TH-PSL2 | CSI TUBULAR | STEEL |  |  |  | 0.375 | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 179.39526682134572 | 2 OVERTIME HOURS FOR SR. FIELD CONSTRUCTION COORDINATOR |  | 7 | 7.18509615384615384615384615384615384615 |  | 0 | 159 | 80.94677382652151938461538461538461538462 | 186.580362975191873846153846153846153846 | 0 | 0 | 0 |  |  |  |  | 21 | 21 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO INVESTIGATION OF THE CONTROL ROOM WAS REQUIRED SINCE THE CONTROL OF PRESSURE DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | YES | 8 | 0 | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER EQUIPMENT FAILURE | EQUIPMENT FAILURE | OTHER EQUIPMENT FAILURE | [197 empty] | OTHER EQUIPMENT FAILURE | [23 empty] | ELECTRONIC MALFUNCTION IN THE SUL AIR COMPRESSOR | [59 empty] | MONICA DAVIDSON | OPERATIONS SUPERVISOR | monica.davidson@atmosenergy.com | 214-426-7082 | 214-426-7081 |  |  |  | MARLO SUTTON | DIRECTOR REGULATORY AND COMPLIANCE | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT NUMBER 1191273 ON SEPTEMBER 20, 2017, GAS IGNITION OCCURRED WHILE PERFORMING A TIE-IN WELD ON A 16" MAIN AT 1847 LEVEE ST. AND TURTLE CREEK IN DALLAS, TEXAS. THERE WAS A MALFUNCTION WITH THE CONFIGURATION OF THE GAS MOVER SYSTEM AND THE STOPPLE VALVES, WHICH REINTRODUCED A SMALL AMOUNT OF GAS INTO THE PIPE NEAR WHERE THE WELDING OPERATIONS WERE OCCURRING. THE AIR COMPRESSOR WAS IDENTIFIED TO BE THE SOURCE OF THE MALFUNCTION. THE HOSES WERE THEN DISCONNECTED AND RECONNECTED TO A SECONDARY COMPRESSOR. WHEN WELDING COMMENCED ON THE 16" TIE-IN, THE FLASH/IGNITION OCCURRED WITHIN THE MAIN. TWO EMPLOYEES OF DRIVER PIPELINE WERE INJURED AND TRANSPORTED BY AMBULANCE TO PARKLAND HOSPITAL. ONE WELDER WAS RELEASED FROM THE EMERGENCY ROOM NOT REQUIRING HOSPITALIZATION, AND THE OTHER WELDER WAS HOSPITALIZED AND RELEASED ON THE AFTERNOON OF SEPTEMBER 23, 2017 WITH MINOR INJURIES.
2025-03-31 10:13 | NO | YES | NO | 20170093 | 16670 | 2017-10-26 10:03 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2017-09-26 12:00 |  |  | 2017 | 1789 JONESTOWN ROAD | WINSTON-SALEM | FORSYTH | NC | 27103 | 36.0379 | -80.3338 | [9 empty] | 2017-09-28 13:40 | 1191780 |  | NATURAL GAS |  | 90.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-09-26 14:11 |  |  |  | 2017-09-26 14:43 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 55 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1980 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 0.8 | 0.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 167805 | 198048.833874709990425 | 3817 | 4504.945614849188245 | 0 | 0 |  |  | 272 | 279.192307692307692307692307692307692308 |  | 0 | 171894 | 84149.9698340175053632307692307692307692 | 202832.9717972514863623076923076923076923 | 1 | 0 | 0 |  |  |  |  | 273 | 275 | 275 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CITY OF WINSTON-SALEM WATER CREW TAPPED LINE THINKING IT WAS A WATER MAIN. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | CITY OF WINSTON-SALEM WATER CREW INSTALLED SADDLE TEE AND TAPPED IT THINKING THE GAS MAIN WAS A WATER MAIN. | [154 empty] | CHRISTOPHER RANSOME | PIPELINE SAFETY AND COMP ANALYST | christopher.ransome@piedmontng.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER - PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | THE WINSTON-SALEM WATER DEPARTMENT CREW TAPPED A NPS 8" STEEL GAS PIPE MISTAKING IT FOR A WATER LINE. THE TAPPING BIT CUT THROUGH THE MAIN CAUSING A SMALL GAS LEAK BUT DID NOT RESULT IN A MAJOR FLOW OR PRESSURE ISSUE. A LOCATE REQUEST HAD BEEN MADE AND THE LINE WAS PROPERLY MARKED.
2025-03-31 10:13 | NO | YES | NO | 20170094 | 30616 | 2017-10-26 14:10 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2017-09-27 08:04 |  |  | 2017 | WIGWAM PARKWAY & JESSUP ROAD | HENDERSON | CLARK COUNTY | NV | 89074 | 36.0349 | -115.1102 | [9 empty] | 2017-09-27 11:34 | 1191661 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 4 | 2017-09-27 08:04 |  |  |  | 2017-09-27 08:04 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 65 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1984 | [5 empty] | 4 | ASTM D2513 | CHEVRON | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 1200 | 1416.278422273782 | 799 | 943.005382830626515 | 110025 | 129855.027842227387125 | 0 | 0 |  |  | 26 | 26.6875 |  | 0 | 112050 | 54783.890098607898248 | 132240.99914733179564 | 126 | 0 | 1966 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [8 empty] | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | ALYSE BAKER | COMPLIANCE SPECIALIST | alyse.baker@swgas.com | 702-365-2077 | 702-365-2205 |  |  |  | ANTHONY HILLS | DIRECTOR OF GAS OPERATIONS | 702-365-2049 | anthony.hills@swgas.com | A HAZARDOUS GRADE 1 LEAK WAS DISCOVERED BY CONTRACTOR PERSONNEL (HEATH CONSULTANTS, INC.). THE LEAK WAS DISCOVERED WHILE PERFORMING LEAK SURVEYING WORK IN EXCESS OF THE MINIMUM REQUIREMENTS OF 49 CFR PART 192. THE FLOW OF GAS TO THE SECTION OF PIPE WAS TAKEN OUT OF SERVICE WHILE REPAIRS WERE COMPLETED, WHICH RESULTED IN A SERVICE OUTAGE OF 2092 CUSTOMERS. PART A, 6: SOUTHWEST GAS NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) TELEPHONICALLY OF THE INCIDENT ON SEPTEMBER 27, 2017 AT 11:34 AM PDT. THE NRC ISSUED REPORT NUMBER 1191661 FOR THE INCIDENT. SOUTHWEST GAS PROVIDED A 48-HOUR UPDATE TELEPHONICALLY TO THE NRC ON SEPTEMBER 28, 2017 AT 4:29 PM PDT. THE NRC ISSUED REPORT NUMBER 1191822 FOR THE UPDATED REPORT. PART A, 16: FOUR OCCUPANTS WERE EVACUATED FROM TWO STRUCTURES AS A RESULT OF THE INCIDENT. PART G, 25: A CONTRIBUTING FACTOR WAS POOR SHADING (I.E., MATERIAL PLACED BETWEEN THE PIPE AND THE FIRST LAYER OF BACKFILL) WHICH WAS NOTED ADJACENT TO THE LEAK, WITH BACKFILL MATERIAL CONSISTING OF A MIXTURE OF SAND AND ROCK. SUPPLEMENTAL: BASED ON COMMUNICATIONS THE PUBLIC UTILITIES COMMISSION OF NEVADA'S REGULATORY OPERATIONS STAFF ("STAFF") HAD WITH THE PIPELINE AND HAZARDOUS MATERIAL SAFETY ADMINISTRATION'S ACCIDENT INVESTIGATION DIVISION REGARDING THE INCIDENT REPORT - GAS DISTRIBUTION SYSTEMS FILED BY SOUTHWEST GAS CORPORATION FOR THE SEPTEMBER 27, 2017, FEDERAL REPORTABLE INCIDENT AT WIGWAM PARKWAY AND JESSUP ROAD; STAFF REQUESTED THAT SOUTHWEST GAS CORPORATION SUPPLEMENT THE REPORT TO UPDATE PART A- LINE 4 "LOCAL TIME AND DATE OF THE INCIDENT." PART A, 4: INCIDENT REPORTING TIME HAS BEEN CHANGED FROM 11:19 TO 08:04. THE TIME REPORTED IN PART A, 4 (08:04) REFLECTS THE TIME OUR CONTRACTOR PERSONNEL (HEATH CONSULTANTS, INC.) IDENTIFIED AND REPORTED A GRADE 1 LEAK ON THE PIPELINE. AT THAT TIME, NO REPORTING CRITERIA HAD BEEN MET. THE SHUTDOWN TIME REPORTED IN PART A, 13A (11:19) IS THE EARLIEST DATE AND TIME A REPORTING CRITERIA WAS MET. DUE TO THE SHUTDOWN OF THE PIPELINE, THE INCIDENT WAS ESTIMATED TO REACH PROPERTY DAMAGE OF $50,000 OR MORE. TELEPHONIC NOTIFICATION WAS MADE WITHIN ONE HOUR OF THE SHUTDOWN TIME. SUPPLEMENTAL 2: PART D, 2C: ESTIMATED COST OF OPERATOR'S EMERGENCY RESPONSE HAS BEEN UPDATED FROM $140,298 TO $110,025
2025-03-31 10:13 | NO | NO | NO | 20170095 | 31027 | 2017-10-28 18:18 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2017-09-28 03:45 |  |  | 2017 | 20058 MONICA STRRET | DETROIT | WAYNE COUNTY | MI | 48221 | 42.4411 | -83.1447 | [9 empty] | 2017-09-28 07:05 | 1191718 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2017-09-28 03:45 |  |  |  | 2017-09-28 04:05 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1953 | [5 empty] | 1 | UNKNOWN | UNKNOWN | COPPER | [10 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 21864 | 25804.59285382830804 | 1000 | 1180.232018561485 | 5000 | 5901.160092807425 | 0 | 0 |  |  | 0 | 0 |  | 0 | 27864 | 13620.388677494201928 | 32885.98496519721804 | 0 | 0 | 1 |  |  |  |  | 2 | 2 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | JOHN D LUEDERS | PRINCIPAL COMPLIANCE ENGINEER | john.lueders@dteenergy.com | 616.632.2646 | 616.632.2687 |  |  |  | JOHN D LUEDERS | PRINCIPAL COMPLIANCE ENGINEER | 616.632.2646 | john.lueders@dteenergy.com | DETROIT FIRE AND ARSON HAS COMPLETED ITS INVESTIGATION. THE CAUSE OF THE EXPLOSION AND FIRE REMAINS UNKNOWN.
2025-03-31 10:13 | NO | YES | NO | 20170096 | 16726 | 2017-10-30 18:35 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2017-09-30 07:32 |  |  | 2017 | 13698 S. AIRPORT RD | LANSING | CLINTON | MI | 48906 | 42.8178 | -84.6056 | [9 empty] | 2017-10-01 10:07 | 1191994 |  | NATURAL GAS |  | 422 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 6 | 2017-09-30 07:32 |  |  |  | 2017-09-30 08:15 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2015 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | RELIEF VALVE CAUSED BY OVERPRESSURE | CLASS 3 LOCATION | 120000 | 141627.8422273782 | 0 | 0 | 3800 | 4484.881670533643 | 0 | 0 |  |  | 1215 | 1247.127403846153846153846153846153846154 |  | 0 | 125015 | 61669.1739860342779846153846153846153846 | 147359.8513017579968461538461538461538462 | 0 | 0 | 0 |  |  |  |  | 500 | 393 | 400 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLERS PERFORMED AS EXPECTED AND REPORTED ALARMS IMMEDIATELY UPON RECEIPT | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | KARLI MCNEILL | G ENGINEER II | karli.mcneill@cmsenergy.com | 9892954218 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING TECHNICAL ANALYST LEAD | 9897915749 | jason.pionk@cmsenergy.com | AT 07:32 AM ON SEPTEMBER 30, 2017 CONSUMERS ENERGY GAS CONTROL RECEIVED A HIGH-HIGH ALARM ON THE OUTLET PRESSURE AT LANSING CITY GATE, AIRPORT RD, LOCATED AT 13698 S. AIRPORT RD, LANSING MI (CLINTON COUNTY). THIS ALARM IS SET TO 400 PSI, WHICH IS THE MAOP OF OUTLET OF THE FACILITY. THE HIGHEST PRESSURE RECORDED WAS 500 PSIG, HOWEVER THAT IS THE UPPER LIMIT OF THE TRANSDUCER SO PRESSURE MAY HAVE BEEN HIGHER THAN 500 PSIG. CONSUMERS ENERGY PERSONNEL ARRIVED ONSIDE AT APPROXIMATELY 08:15. IT WAS FOUND THAT WITH THE RELEASE OF NATURAL GAS THROUGH THE RELIEF VALVE, AN OIL-LIKE SUBSTANCE WAS ALSO RELEASED. THIS SUBSTANCE AFFECTED 3 HOMES AND A FARMERS FIELD NEARBY. LAB ANALYSIS HAS DETERMINED THIS SUBSTANCE WAS COMPRISED OF MID-RANGE AND HEAVY HYDROCARBONS. THE FACILITY WAS OPERATING PROPERLY ON THE SECONDARY RUN WHEN PERSONNEL ARRIVED WITHIN NORMAL OPERATING PRESSURES. THE REGULATOR FAILURE WAS CAUSED BY AN INFLUX OF HYDROCARBONS AFFECTING THE FUNCTION OF THE REGULATORS. CONSUMERS ENERGY CREW REBUILT THE PRIMARY AND SECONDARY RUN REGULATORS AND PILOTS AT THE CITY GATE AND RE-TESTED THE RELIEF VALVE. ADDITIONAL PERSONNEL COMPLETED LEAK SURVEY AND FOUND NO LEAKS. PERSONNEL ALSO CHECKED SURROUNDING REGULATOR STATIONS AND ALL WERE FOUND TO BE OPERATING CORRECTLY. ALL WORK WAS COMPLETED BY 19:15 ON SEPTEMBER 30, 2017. CONSUMERS ENERGY HAS BEEN WORKING WITH A THIRD-PARTY CONTRACTOR FOR ENVIRONMENTAL CLEANUP. THE DEQ WAS NOTIFIED AT 13:00 ON SEPTEMBER 30, 2017. ENVIRONMENTAL CLEANUP HAS BEEN COMPLETED. AFTER LAB ANALYSIS AND INVESTIGATION, THE CAUSE/SOURCE OF THE HYDROCARBONS IS BELIEVED TO BE A RESULT OF FREE LIQUIDS FROM STORAGE FIELDS, AND LIQUIDS NOT RECOVERED IN PIGGING OPERATIONS. CONSUMERS ENERGY HAS PROVIDED THESE SOURCES AND AFFILIATED ACTION PLANS TO THE MPSC.
2025-03-31 10:13 | NO | YES | YES | 20170097 | 16675 | 2017-11-02 16:13 | ORIGINAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2017-10-09 09:00 |  |  | 2017 | 174 OAKLAND HEIGHTS | FOREST CITY | RUTHERFORD | NC | 28160 | 35.3324 | -81.9172 | [9 empty] | 2017-10-09 17:47 | 1192754 |  | NATURAL GAS |  | 1.93 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO |  |  |  |  | NO | 0 | 2017-10-09 09:00 |  |  |  | 2017-10-09 09:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1970 | [5 empty] | 2 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | OTHER | [8 empty] | IMPROPER PROCEDURE / TOOL USED ON TAPPING EQUIPMENT RESULTED IN PLUG BLOWING OUT OF TAPPING FITTING. | CLASS 3 LOCATION | 0 | 0 | 189 | 223.063851508120665 | 0 | 0 | 0 | 0 |  |  | 8 | 8.21153846153846153846153846153846153846 |  | 0 | 197 | 99.98251115473854915384615384615384615385 | 231.275389969659126538461538461538461538 | 0 | 0 | 0 |  |  |  |  | 60 | 60 | 66 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | OPERATOR EMPLOYEE DID NOT USE THE CORRECT TOOL TO INSERT A PLUG IN A MUELLER TAPPING FITTING. |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | TOM BROOKSHIRE | SUPERVISOR - OPERATIONS | tbrookshire@scana.com | (828) 890-7553 |  |  |  |  | SCOTT SWINDLER | GENERAL MANAGER - OPERATIONS AND MAINTENANCE | (704) 810-3230 | mswindler@scana.com | PSNC EMPLOYEES ARRIVE AT CONSTRUCTION SITE TO TAP/STOP 2-INCH SHORT STOP H-17190 MUELLER FITTING. EMPLOYEES MADE THE TAP AND STOP OFF SO CONTRACTORS COULD TIE IN THE NEW MAIN EXTENSION. THE FITTING WAS AIR TESTED BEFORE THE TAP WAS MADE. AFTER THE TIE-IN WAS COMPLETED, EMPLOYEES STARTED THE COMPLETION PROCESS TO PUT THE PLUG BACK IN THE FITTING. BOTH EMPLOYEES CHANGED OUT TOOLS ON THE D-5 MACHINE TO COMPLETE TAP/STOP AND INSTALLING COMPLETION PLUG. WHILE INSTALLING THE COMPLETION PLUG EMPLOYEE 1 WAS OPERATING THE MACHINE, BOTH EMPLOYEES HEARD A LOUD POP. ONCE THE POP WAS HEARD, EMPLOYEE 1 BEGAN TURNING THE MACHINE COUNTERCLOCKWISE IN ORDER TO BRING THE PLUG BACK OUT TO REMOVE THE MACHINE AND FIGURE OUT WHAT WENT WRONG. WHEN THE MACHINE WAS REMOVED, THEY OPENED THE VALVE TO LOOK AT THE PLUG AND NOTICED IT WAS NOT PROPERLY SEATED IN THE FITTING. THE VALVE WAS REMOVED FROM THE FITTING AND EMPLOYEES BOTH NOTICED THE PLUG WAS NOT TIGHT IN THE FITTING BECAUSE THE RUBBER O-RING WAS STICKING OUT OF THE TOP OF THE FITTING. EMPLOYEE 1 ATTEMPTED TO TIGHTEN THE PLUG INTO THE FITTING BUT THE PLUG BLEW FROM THE FITTING AND METAL SHAVINGS BLEW INTO EMPLOYEES ARM. EMPLOYEE REQUIRED 3 NIGHTS OF HOSPITALIZATION TO MONITOR INFECTION. SUBSEQUENT INVESTIGATION DETERMINED THAT INADEQUATE JOB PLANNING, NOT FOLLOWING PROCEDURES, AND USING THE INCORRECT EQUIPMENT/TOOLS FOR THE JOB ALL CONTRIBUTED TO THE TAPPING AND STOPPING OPERATION FAILING AND THE SUBSEQUENT INJURY.
2025-03-31 10:13 | NO | YES | NO | 20170098 | 31740 | 2017-11-02 17:04 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2017-10-03 15:27 |  |  | 2017 | 601 S. RIVERFRONT BLVD | DALLAS | DALLAS | TX | 75207 | 32.7686 | -96.812 | [9 empty] | 2017-10-04 22:55 | 1192328 |  | NATURAL GAS |  | 1828 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-10-03 15:27 |  |  |  | 2017-10-03 15:50 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1953 | [5 empty] | 16 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.341 | [6 empty] | MECHANICAL PUNCTURE | 5 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 198971 | 234831.944965197231935 | 16526 | 19504.51433874710111 | 0 | 0 |  |  | 13182 | 13530.5625 |  | 0 | 228679 | 117855.096049884009219 | 267867.021803944333045 | 0 | 0 | 0 |  |  |  |  | 22.5 | 22.5 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | GRADER/SCRAPER | ROAD WORK | YES | 1776364804 | TEXAS811 |  | CONTRACT LOCATOR | NO | YES | 45 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MONICA DAVIDSON | OPERATIONS SUPERVISOR | monica.davidson@atmosenergy.com | 214-426-7082 | 214-426-7081 |  |  |  | MARLO SUTTON | DIRECTOR REGULATORY AND COMPLIANCE | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT NUMBER 1192503 ON THE AFTERNOON OF OCTOBER 3, 2017, ATMOS ENERGY WAS NOTIFIED OF AN EVENT IN THE AREA OF 601 S. RIVERFRONT BLVD. IN DALLAS. A THIRD PARTY CONTRACTOR PERFORMING GRADING WORK ALONG A LEVEE DAMAGED A 16-INCH STEEL DISTRIBUTION MAIN OWNED BY ATMOS ENERGY. ATMOS ENERGY PERFORMED EMERGENCY ACTIONS NEEDED TO ELIMINATE GAS FLOW BY ISOLATING THE DAMAGED SECTION OF PIPE. BY UTILIZING ENGINEERING CONTROLS, THE FLOW OF GAS WAS ELIMINATED AT 11:54 PM ON OCTOBER 4, 2017. THE DAMAGED SECTION OF 16-INCH MAIN WAS REPLACED AND GAS FLOW REINSTATED ON THE EVENING OF OCTOBER 6, 2017. THE REPORT OF THIS INCIDENT WAS ORIGINALLY MADE DUE TO THE EXPECTATION THAT THE GAS LOSS WOULD EXCEED THE REPORTING CRITERIA. UPON FURTHER INVESTIGATION, IT WAS DETERMINED THAT ONLY THE REPAIR COST WOULD QUALIFY THIS AS A REPORTABLE INCIDENT. THE FINAL GAS LOSS CALCULATION DID NOT EXCEED THE REPORTING CRITERIA. THE ONE-CALL TICKET NUMBER IS 1776364804. THE INVESTIGATION INDICATES THAT THE CONTRACTOR WAS WORKING OUTSIDE THE SCOPE OF THE TICKET. THE LOCAL TIME AND DATE OF THE INCIDENT (PART A, ITEM 4.) AS ORIGINALLY SUBMITTED WAS THE TIME THAT ATMOS ENERGY DETERMINED THAT THE INCIDENT REPORTING CRITERIA HAD BEEN MET, AS PER THE PHMSA INSTRUCTIONS FOR FORM 7100.1. AT PHMSA'S REQUEST, WE HAVE CHANGED PART A, ITEM 4. TO REFLECT THE TIME THAT THE LINE WAS DAMAGED.
2025-03-31 10:13 | NO | NO | NO | 20170099 | 16678 | 2017-11-02 17:13 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2017-09-14 13:27 |  |  | 2017 | 30W020 ESTES ST. | WARRENVILLE | DUPAGE | IL | 60563 | 41.817 | -88.2053 | [9 empty] | 2017-10-02 18:04 | 1192128 |  | NATURAL GAS |  | 2549 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-09-14 14:02 |  |  |  | 2017-09-14 14:02 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 37 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1963 | [5 empty] | 12 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 17016 | 20082.82802784222876 | 34032 | 40165.65605568445752 | 0 | 0 |  |  | 8413 | 8635.459134615384615384615384615384615385 |  | 0 | 59461 | 32941.4204624754639575384615384615384615 | 68883.9432181420708953846153846153846154 | 0 | 0 | 0 |  |  |  |  | 144 | 150 | 155 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | GRADING | YES | 2152017 | J.U.L.I.E. ONE CALL CENTER TICKET IN 9A. STARTS WITH AN X BUT DB ONLY ALLOWS NUMBERS FOR ENTRY. |  | CONTRACT LOCATOR | YES |  |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | lquezad@southernco.com | 630-388-2316 |  |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | 630-388-2316 | lquezad@southernco.com | WHILE GRADING PARALLEL TO A MAIN, WITHIN THE TOLERANCE ZONE, A THIRD PARTY EXCAVATOR STRUCK A 1" GAUGE TEE LOCATED ON THE SIDE OF A 12" STEEL MAIN AND CAUSED A RELEASE OF NATURAL GAS INTO THE ATMOSPHERE.
2025-03-31 10:13 | NO | NO | NO | 20170100 | 16679 | 2017-11-02 17:46 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2017-10-03 15:26 |  |  | 2017 | MATT HIGHWAY @ POOLES MILL ROAD | BALL GROUND | FORSYTH | GA | 30107 | 34.2978 | -84.2402 | [9 empty] | 2017-10-03 23:09 | 1192225 |  | NATURAL GAS |  | 6561.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 1 | 2017-10-03 15:26 |  |  |  | 2017-10-03 15:59 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1997 | [5 empty] | 6 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 2 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 46652 | 55060.18412993039822 | 4200 | 4956.974477958237 | 0 | 0 |  |  | 18496 | 18985.0769230769230769230769230769230769 |  | 0 | 69348 | 42419.6147920756781116923076923076923077 | 79002.2355309655582969230769230769230769 | 0 | 0 | 1 |  |  |  |  | 200 | 200 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 9197400116 |  |  | CONTRACT LOCATOR | YES | YES | 29 | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@southernco.com | A 6-INCH STEEL MAIN WAS RUPTURED BY A CONTRACT CREW WHILE INSTALLING A SEWER LINE. ONCE THE INCIDENT WAS MADE SAFE IT WAS IDENTIFIED THAT REPAIRS TO THE AFFECTED PIPELINE WOULD EXCEED THE $50,000 THRESHOLD FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. NOTIFICATION TO THE ONE-CALL CENTER WAS MADE WHERE THE MAIN WAS CORRECTLY LOCATED, HOWEVER, THE EXCAVATOR FAILED TO MAINTAIN LOCATE MARKINGS. AN ADDITIONAL NRC REPORT NUMBER WAS NOT CREATED FOR THE SAME EVENT AFTER A 48 HOUR SUPPLEMENTAL CALL WAS PLACED WITH THE NRC.
2025-03-31 10:13 | NO | YES | NO | 20170101 | 16681 | 2017-11-03 11:00 | ORIGINAL FINAL | 12876 | DOMINION ENERGY UTAH/WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2017-10-04 14:55 |  |  | 2017 | 6580 S 3000 E | COTTONWOOD HEIGHTS | SALT LAKE COUNTY | UT | 84121 | 40.6302 | -111.807 | [9 empty] | 2017-10-04 16:09 | 1192313 |  | NATURAL GAS |  | 545 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-10-04 16:06 |  |  |  | 2017-10-04 15:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1984 | [5 empty] | 3 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 3 | [7 empty] | CLASS 3 LOCATION | 300000 | 354069.6055684455 | 12512 | 14767.06301624130032 | 0 | 0 | 0 | 0 |  |  | 2538 | 2605.110576923076923076923076923076923077 |  | 0 | 315050 | 155170.9660257897823163076923076923076923 | 371441.7791616098772430769230769230769231 | 0 | 0 | 0 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 72680035 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | LAUREN SKUFCA | ENGINEER-PIPELINE COMPLIANCE | lauren.l.skufca@dominionenergy.com | 2166338865 |  |  |  |  | REID HESS | MANAGER-GAS OPERATIONS | 8013243374 | reid.hess@dominionenergy.com | ON OCTOBER 4, 2017 DOMINION ENERGY UTAH (DEU) WAS NOTIFIED BY PHONE AT 14:55 THAT A 3RD PARTY EXCAVATOR HAD STRUCK A NATURAL GAS PIPELINE WHILE EXCAVATING CAUSING GAS TO ESCAPE AND IGNITE. MINOR INJURIES NOT REQUIRING MEDICAL ATTENTION WERE SUSTAINED BY THE EQUIPMENT OPERATOR AND THE EXCAVATING EQUIPMENT WAS DAMAGED. DEU ISOLATED THE DAMAGED PIPELINE BY SQUEEZING OFF THE LINE IN 2 LOCATIONS. THE LINE WAS ISOLATED AT 16:03. IN ADDITION TO DEU, THE LOCAL FIRE AND HEALTH DEPARTMENT WERE CONTACTED AND DISPATCHED TO THE SITE. PURSUANT TO CFR 49 PART 191.5 DEU CONTACTED THE NATIONAL RESPONSE CENTER UPON DISCOVERY OF THE REPORTABLE INCIDENT DUE TO COST OF PROPERTY DAMAGE EXCEEDING $50,000. THE UTAH DIVISION OF PUBLIC UTILITIES- PIPELINE SAFETY WAS ALSO CONTACTED AND REPORTED TO THE SITE. DUE TO THE RELEASE OF FLUIDS FROM THE DAMAGED EXCAVATING EQUIPMENT, THE SITE HAD TO BE REMEDIATED PRIOR TO THE PIPELINE REPLACEMENT. DEU REPLACED THE AFFECTED SECTION OF PIPELINE AND RETURNED TO SERVICE ON OCTOBER 27, 2017.
2025-03-31 10:13 | NO | YES | YES | 20170102 | 31516 | 2017-11-09 11:36 | SUPPLEMENTAL FINAL | 15469 | PHILADELPHIA GAS WORKS | 800 W. MONTGOMERY AVENUE | PHILADELPHIA | PA | 19122 | 2017-10-12 11:23 |  |  | 2017 | 8053 RODNEY STREET | PHILADELPHIA | PHILADELPHIA | PA | 19150 | 40.0689 | -75.1753 | [9 empty] | 2017-10-12 13:30 | 1193050 |  | NATURAL GAS |  | 0.06 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2017-10-12 11:23 |  |  |  | 2017-10-12 09:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 50 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1953 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 682 | 804.91823665893277 | 0 | 0 |  |  | 1 | 1.02644230769230769230769230769230769231 |  | 0 | 683 | 334.322512270212444769230769230769230769 | 805.944678966625077692307692307692307692 | 0 | 0 | 0 |  |  |  |  | 0.23 | 0.23 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | EQUIPMENT NOT INSTALLED PROPERLY | INCORRECT OPERATION | INCORRECT INSTALLATION | INCORRECT OPERATION | INCORRECT INSTALLATION | [222 empty] | EQUIPMENT NOT INSTALLED PROPERLY |  | YES |  |  |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | THOMAS PENDERGAST | DIRECTOR DISTRIBUTION MAINTENANCE AND CORROSION | thomas.pendergast@pgworks.com | 215-684-6344 |  |  |  |  | RAYMOND WELTE | VP FIELD OPERATIONS | 215-684-6033 | raymond.welte@pgworks.com | ON WEDNESDAY, OCTOBER 11TH, 2017, PGW RECEIVED AN ODOR COMPLAINT AT 8053 RODNEY STREET IN FRONT OF THE PROPERTY. PGW RESPONDED TO INVESTIGATE THE AREA AND IT WAS DETERMINED THAT THE SOURCE OF THE LEAK WAS A RUSTED OUT STEEL SERVICE PIPE IN THE FOOTWAY. PGW DISCONNECTED THE SERVICE ADJACENT TO THE MAIN CONNECTION AND INSERTED PLASTIC TO THE FRONT WALL OF THE PROPERTY IN ORDER TO ELIMINATE THE LEAK AND RESTORE SERVICE TO THE CUSTOMER. THE SERVICE CONNECTION TO THE MAIN WAS A STEEL NIPPLE COMING OFF THE SIDE OF A 6' LOW PRESSURE STEEL MAIN. THIS MAIN CONNECTION REQUIRED THE SERVICES OF A WELDER IN ORDER TO BE PERMANENTLY ABANDONED AND REPLACED WITH A NEW SERVICE TEE. THE STEEL SERVICE CONNECTION WAS TEMPORARILY WRAPPED WITH WAX-TAPE AS A PREVENTATIVE MEASURE AND LEFT OVERNIGHT UNTIL A WELDER WAS AVAILABLE. ON THURSDAY, OCTOBER 12TH, 2017, PGW DISPATCHED A MAINTENANCE CREW AND WELDER TO THE SITE TO ABANDON THE STEEL NIPPLE SERVICE CONNECTION AND INSTALL A NEW SERVICE TEE. BETWEEN 09:30 AND 11:00, THE CREW WORKED TO CONTINUE PREPARATION OF THE EXCAVATION AND MAIN FOR THE WELDER TO PERMANENTLY ABANDON THE SERVICE CONNECTION. BETWEEN 11:00 AND 11:23, THE WELDER BEGAN HIS WORK BY CUTTING OFF THE STEEL NIPPLE SERVICE CONNECTION FLUSH WITH THE MAIN. HE PROCEEDED TO USE A SELF-TAPPING TAPERED SCREW PLUG TO ATTEMPT TO SEAL THE OPENING IN THE MAIN. THE WELDER ATTEMPTED TO WELD THE PLUG SHUT AND IGNITED A SMALL AMOUNT OF GAS WHICH HE WAS UNAWARE WAS BYPASSING. THE WELDER THEN ATTEMPTED TO ADJUST THE PLUG WITH A PIPE WRENCH INSTEAD OF EXTINGUISHING THE FLAME. DURING THIS PROCESS, THE PLUG EVACUATED THE OPENING IN THE MAIN AND ALLOWED THE GAS FROM THE MAIN TO ESCAPE AND MAKE CONTACT WITH THE PREVIOUSLY IGNITED FLAME. WHILE HIS FR CLOTHING AND SAFETY GLASSES PROTECTED HIS UPPER TORSO AND EYES, THE PGW WELDER SUSTAINED BURNS TO HIS FACE AND NECK AND WAS TAKEN TO THE HOSPITAL BY THE PHILADELPHIA FIRE DEPARTMENT. THE FIRE WAS IMMEDIATELY EXTINGUISHED AND THE SERVICE CONNECTION WAS LATER ABANDONED AND REPLACED WITH A STREET TEE.
2025-03-31 10:13 | NO | YES | YES | 20170103 | 16735 | 2017-11-13 15:44 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2017-10-13 12:34 |  |  | 2017 | HIGHWAY 42 @ BISCAYNE BLVD. | REX | CLAYTON | GA | 30273 | 33.5766 | -84.27 | [9 empty] | 2017-10-14 12:24 | 1193254 |  | NATURAL GAS |  | 423.25 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2017-10-13 12:48 |  |  |  | 2017-10-13 13:14 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2008 | [8 empty] | OTHER | 1-INCH AG REGULATOR STATION | [9 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 35000 | 41308.120649651975 | 44000 | 51930.20881670534 | 4055 | 4785.840835266821675 | 0 | 0 |  |  | 1193 | 1224.545673076923076923076923076923076923 |  | 0 | 84248 | 41731.4479040246367926923076923076923077 | 99248.7159747010597519230769230769230769 | 0 | 0 | 0 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@southernco.com | A 1-INCH REGULATOR STATION WAS DAMAGED BY AN OUT OF CONTROL VEHICLE WHILE BEING CHASED BY LAW ENFORCEMENT. THE ESCAPING GAS IGNITED CAUSING THE VEHICLE TO BURN. ONCE THE INCIDENT WAS MADE SAFE AND ALL COST ESTIMATES ASSOCIATED WITH THE INCIDENT WERE IDENTIFIED, IT WAS DETERMINED THAT THE INCIDENT EXCEEDED THE $50,000 THRESHOLD FOR REPORTING. THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. IN ADDITION, AT THE TIME OF NOTIFICATION TO THE NRC IT WAS REPORTED THAT ONE PERSON WAS INJURED AND TAKEN TO THE HOSPITAL BUT WAS TREATED AND RELEASED INTO POLICE CUSTODY THE SAME DAY. HOWEVER, IT WAS DISCOVERED LATER THAT THE PERSON WAS TAKEN BACK TO THE HOSPITAL AFTER COMPLAINING OF INJURIES. THE 1-INCH REGULATOR STATION WAS PROTECTED BY BOLLARDS WHICH TOGETHER WITH THE STATION, STOPPED THE VEHICLE. ADDITIONAL NRC REPORT NUMBER 1193463 WAS CREATED FOR THE SAME EVENT AFTER A 48 HOUR SUPPLEMENTAL CALL WAS PLACED WITH THE NRC.
2025-03-31 10:13 | NO | YES | NO | 20170104 | 16699 | 2017-11-13 15:54 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2017-07-13 19:15 |  |  | 2017 | 14822 DELFBUSH STREET | MORENO VALLEY | RIVERSIDE | CA | 92553 | 33.9054 | -117.2278 | [9 empty] | 2017-10-13 10:22 | 1193174 |  | NATURAL GAS |  | 25.43 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 8 | 2017-07-13 19:15 |  |  |  | 2017-07-13 19:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1973 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 221958 | 261961.93837587008763 | 13 | 15.343016241299305 | 1768 | 2086.65020881670548 | 0 | 0 |  |  | 153 | 157.045673076923076923076923076923076923 |  | 0 | 223892 | 109512.6372775745328606923076923076923077 | 264220.9772740050154919230769230769230769 | 0 | 0 | 2 |  |  |  |  | 44 | 45 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | IK SONG | PIPELINE SAFETY AND COMPLIANCE ADVISOR | isong@semprautilities.com | 818-279-5388 |  |  |  |  | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE MANAGER | 909-335-7915 | tbauer@semprautilities.com | AN RV STRUCK THE MSA AND THE SERVICE RISER OF 14822 DELFBUSH STREET, MORENO VALLEY, CAUSING A RELEASE OF GAS AND IGNITING THE RV AS WELL AS THE TWO HOUSES AT 14832 AND 14822 DELFBUSH STREET. SOCALGAS CREW RESPONDED AND CONTROLLED THE GAS BY 21:31 OF THE INCIDENT DATE. NO FURTHER DAMAGES OR INJURIES RESULTED FROM THIS EVENT. ALL REPAIRS TO THE DAMAGED SERVICE WERE COMPLETED BY CUTTING THE DAMAGED SERVICE RISER, CLAMPING, AND PLUGGING THE STOPCOCK. THE SERVICES TO THE DAMAGED HOMES WILL BE RESTORED UPON COMPLETION OF REPAIRS AND AT THE REQUEST OF THE CUSTOMERS. THIS INCIDENT WAS REPORTED TO THE DOT AND TO THE CPUC WHEN PIPELINE SAFETY AND COMPLIANCE BECAME AWARE THAT THE DAMAGE COST EXCEEDED $50,000. THE 48-HOUR UPDATE WAS SUBMITTED UNDER NRC 1193302. FOR ANY FURTHER QUESTIONS, PLEASE CONTACT IK SONG AT (818) 279-5388.
2025-03-31 10:13 | NO | NO | NO | 20170106 | 16692 | 2017-11-15 15:15 | ORIGINAL FINAL | 31159 | KANSAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 7421 W 129TH | OVERLAND PARK | KS | 66213 | 2015-03-05 11:30 |  |  | 2015 | 1001 CREST DRIVE | TOPEKA | SHAWNEE | KS | 66604 | 39.051 | -95.7402 | [9 empty] | 2017-11-15 13:58 | 1197383 |  | NATURAL GAS |  | 232.09 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2015-03-05 11:30 |  |  |  | 2015-03-05 11:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 108 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2013 | [5 empty] | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 187 | 226.505286217735074 | 56577 | 68529.356033908006854 | 1437 | 1740.578055052862574 | MEALS AND FIELD SUPPORT |  | 1173 | 1175.753521126760563380281690140845070423 |  | 0 | 59374 | 30285.1517508709752792112676056338028169 | 71672.1928963053650653802816901408450704 | 0 | 0 | 160 |  |  |  |  | 5 | 5 | 58 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [5 empty] | YES | [6 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 15058192 |  |  | CONTRACT LOCATOR | YES | YES | 18 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | RANDY SPECTOR |  | randy.spector@onegas.com | 9135303219 |  |  |  |  | RANDY SPECTOR | DIRECTOR OF ENGINEERING | 9135998931 | randy.spector@onegas.com | ON 3/5/15 RYLIE CONSTRUCTION WHILE DIRECTIONAL BORING CAUSED DAMAGE TO KGS FACILITIES. THE QUANTITY OF GAS RELEASED DID NOT MEET THE CRITERIA OF A REPORTABLE INCIDENT ON IT'S OWN. LIKEWISE, INITIAL REPAIR ESTIMATES WERE NOT EXPECTED TO EXCEED $50,000. HOWEVER, RECENTLY, KGS CONDUCTED AN INTERNAL AUDIT AND DISCOVERED THE ACTUAL COST ASSOCIATED WITH THIS EVENT WAS ACTUALLY $58,201. IN LIGHT OF THE RESULTS FROM THIS RECENTLY COMPLETED INTERNAL AUDIT, THE COMPANY IS NOW ISSUING THIS REPORT.
2025-03-31 10:13 | NO | YES | NO | 20170107 | 30738 | 2017-11-15 15:36 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2017-10-21 16:31 |  |  | 2017 | KASSON RD AND DURHAM FERRY RD | TRACY | SAN JOAQUIN | CA | 95304 | 37.6672 | -121.2787 | [9 empty] | 2017-10-21 20:48 | 1193949 |  | NATURAL GAS |  | 357 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2017-10-21 16:31 |  |  |  | 2017-10-21 17:06 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1999 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | VEHICLE IMPACT TO REG STATION | CLASS 1 LOCATION | 0 | 0 | 1218000 | 1437522.59860788873 | 177000 | 208901.067285382845 | 0 | 0 | N/A |  | 1000 | 1026.442307692307692307692307692307692308 |  | 0 | 1396000 | 682848.8231750848957692307692307692307692 | 1647450.10820096388269230769230769230769 | 0 | 1 | 3 |  |  |  |  | 700 | 54 | 60 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON OCTOBER 21, 2017 AT APPROXIMATELY 1631 HOURS, PG&E WAS NOTIFIED OF A VEHICLE IMPACT NEAR THE INTERSECTION OF KASSON RD AND DURHAM FERRY RD, IN THE CITY OF TRACY. THE VEHICLE DROVE THROUGH THE FENCING & BOLLARDS AND STRUCK DISTRICT REG STATION TYHP-75, SPECIFICALLY THE SENSING LINES, RESULTING IN AN UNINTENTIONAL RELEASE OF GAS AND SUBSEQUENT OVERPRESSURE OF THE DISTRIBUTION SYSTEM DOWNSTREAM OF THE REG STATION. THE STATION IS FED OFF LINE 108 NEAR MILE POINT (MP) 5.70. PG&E GSR ARRIVED ON-SITE AT 1706 HOURS. PG&E M&C ARRIVED ON-SITE AND STOPPED THE FLOW OF GAS BY CLOSING THE STATION VALVES BY 1755 HOURS. THE OVERPRESSURIZATION OF THE 6-INCH PLASTIC DISTRIBUTION MAIN DOWNSTREAM OF THE REG STATION RESULTED IN A FUSION FAILURE NEAR 560 E DURHAM FERRY RD. THE FUSION FAILURE WAS FIRST REPORTED AT 1948 HOURS. APPROXIMATELY 9,500 FT OF 6-INCH PLASTIC MAIN AND 4 SERVICES WERE IMPACTED. THE SERVICES THAT WERE IMPACTED ARE 560 E DURHAM FERRY RD, 120 E DURHAM FERRY RD, 272 W DURHAM FERRY RD, AND 492 W DURHAM FERRY RD. THERE WERE NO REPORTED INJURIES, FATALITIES OR IGNITION. FOUR CUSTOMERS GAS SERVICE WAS IMPACTED. CNG TANKS WERE PROVIDED TO THE IMPACTED CUSTOMERS. THE STATION REBUILD WAS COMPLETED ON 12/20/2017. POLICE & FIRE DEPARTMENT WAS REPORTED ON-SITE. NO MEDIA WAS REPORTED ON-SITE. THIS INCIDENT WAS REPORTED TO THE DOT & CPUC DUE TO THE UNINTENTIONAL RELEASE OF GAS AND ESTIMATED DAMAGE COSTS EXCEEDING $50,000. AN UPDATE ON THE GAS FLOW STOP TIME & VOLUME WAS PROVIDED TO THE DOT (1194060) ON 10/23/17. PLEASE NOTE FOR THE PHMSA7100 REPORT THAT THE INCIDENT IS SPECIFIC TO THE VEHICLE IMPACT INCIDENT TO THE DISTRICT REG STATION. FOR PART E, THE MAOP OF THE DISTRICT REG STATION IS 720 AND OPERATING PRESSURE IS 700 PSIG. THE MAOP OF THE DISTRIBUTION SYSTEM DOWNSTREAM OF THE DISTRICT REG STATION IS 60 PSIG AND OPERATING PRESSURE IS 54 PSIG. THE DISTRIBUTION SYSTEM DOWNSTREAM OF THE DISTRICT REG STATION EXCEEDED 110% MAOP.
2025-03-31 10:13 | NO | NO | NO | 20170108 | 16746 | 2017-11-15 16:00 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2017-10-16 08:13 |  |  | 2017 | 7433 LYNCH ROAD | OTTAWA LAKE | MONROE COUNTY | MI | 49267 | 41.7375 | -83.7245 | [9 empty] | 2017-10-17 09:30 | 1193478 |  | NATURAL GAS |  | 112 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-10-16 08:13 |  |  |  | 2017-10-16 08:50 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2010 | [5 empty] | 4 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.409 |  | UNKNOWN | MECHANICAL PUNCTURE | 1 | 3.7 | [7 empty] | CLASS 3 LOCATION | 50000 | 59011.60092807425 | 4964 | 5858.67174013921154 | 0 | 0 | 0 | 0 |  |  | 323 | 331.540865384615384615384615384615384615 |  | 0 | 55287 | 27174.0161036498351664615384615384615385 | 65201.8135335980769246153846153846153846 | 1 | 0 | 0 |  |  |  |  | 46 | 46 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 72760312 |  |  | CONTRACT LOCATOR | YES | YES | 12 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | KARLI MCNEILL | GENERAL ENGINEER II | karli.mcneill@cmsenergy.com | 989-295-4218 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING TECHINICAL ANALYST LEAD | 989-598-5031 | jason,pionk@cmsenergy.com | ON OCTOBER 16, 2017, THIRD-PARTY CONTRACTOR HANKS PLUMBING AND HEATING WERE EXCAVATING NEAR 7433 LYNCH RD, OTTAWA LAKE, MI FOR WATER MAIN WORK. AT APPROXIMATELY 8:13 AM, THE CONTRACTOR STRUCK A CONSUMERS ENERGY 4" PLASTIC MAIN, SEVERING THE LINE. APPROXIMATELY 112 MCF OF GAS WAS LOST, AND ONE CUSTOMER WAS AFFECTED. THE EXCAVATOR THEN CAUGHT ON FIRE AND THE MACHINE OPERATOR OBTAINED INJURIES TO HIS HANDS AND VISITED THE HOSPITAL FOR THOSE INJURIES. THE EMPLOYEE WAS DISCHARGED AND RETURNED TO WORK THE SAME DAY, AND THIS REPORT HAS BEEN UPDATED TO REMOVE ANY INJURIES. THE EXCAVATOR WAS A COMPLETE LOSS. IN ADDITION TO THE EXCAVATOR, THE BUSINESS BUILDING HAD MELTING FIRE DAMAGE TO THE SIDING. CONSUMERS ENERGY REPLACED APPROXIMATELY 10 FEET OF 4" PLASTIC MEDIUM PRESSURE MAIN AND RETURNED THE ONE CUSTOMER LOST BACK TO SERVICE THE NEXT MORNING. THE SITE HAD BEEN MARKED FOR GAS ASSETS. A RETIRED MAIN WAS HAND-EXPOSED BY THE CONTRACTOR AND WAS THOUGHT TO BE THE ACTIVE MAIN, HOWEVER THE ACTIVE MAIN WAS PROPERLY MARKED AS SHOWN FROM A PRE-DIG PHOTO TAKEN OCTOBER 5. THE RETIRED MAIN THAT WAS HAND-EXPOSED WAS NOT MARKED.
2025-03-31 10:13 | NO | NO | NO | 20170109 | 16717 | 2017-11-27 09:56 | SUPPLEMENTAL FINAL | 12036 | MADISONVILLE GAS SYSTEM | 209 HWY 22 | MADISONVILLE | LA | 70447 | 2017-11-01 11:00 |  |  | 2017 | INTERSECTION OF PINECREST AND MISTLETOE DR. | COVINGTON | ST. TAMMANY | LA | 70433 | 30.4236 | -90.1169 | [9 empty] | 2017-11-01 12:45 | 1194884 |  | NATURAL GAS |  | 8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-11-01 11:00 |  |  |  | 2017-11-01 11:05 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1965 | [5 empty] | 1.5 | SCH 40 | UNKNOWN | STEEL |  | OTHER | WELDED | 0.145 | [6 empty] | LEAK |  |  | OTHER | VALVE CRACKED IN HALF | [5 empty] | CLASS 3 LOCATION | 2500 | 2950.5800464037125 | 5000 | 5901.160092807425 | 5000 | 5901.160092807425 | 5000 | 5901.160092807425 | MEDICAL EXPENSES |  | 100 | 102.644230769230769230769230769230769231 |  | 0 | 17600 | 8649.244266464395576923076923076923076923 | 20756.7045555952182692307692307692307692 | 0 | 0 | 375 |  |  |  |  | 40 | 40 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 6 | 1 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | PROCEDURES FOR WORKING ON LEAKS WHILE GAS IS PRESENT NEEDS TO BE MORE IN DEPTH. | YES |  |  |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | NO, BUT THEY WERE PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | KYLE MATTHEWS | PUBLIC WORKS DIRECTOR | kylem@townofmadisonville.org | 985-264-9862 |  |  |  |  | KYLE MATTHEWS | PUBLIC WORKS DIRECTOR | 985-264-9862 | kylem@townofmadisonville.org | 10/30/2017 KIRK OSTENDORF CALLED OUT TO VALVE LEAKING AT MISTLETOE AND PINECREST DR. 10/31/2017 KIRK, KYLE MATTHEWS, AND TROY HALEY GREASED THE VALVE AND IT STOPPED LEAKING. THAT NIGHT THE VALVE STARTED LEAKING AGAIN. 11/1/2017 KIRK, TROY, HUEY BYERS DUG UP THE VALVE TO INVESTIGATE THE PROBLEM. AS THEY EXCAVATED THE DIRT FROM AROUND THE VALVE IT GRADUALLY STARTED LEAKING MORE AND MORE UNTIL IT EVENTUALLY CRACKED OPEN. BRYAN RAIFORD AND JOHN MORSE CAME OUT TO HELP. WE DECIDED TO CUT THE BLOWING VALVE OUT AND SLIDE ON A COMPRESSION COUPLING TO STOP THE FLOW OF GAS. IN THE PROCESS THE GAS IGNITED. KIRK, HUEY, TROY, BRYAN, AND JOHN WERE INJURED. I THEN CUT OFF GAS TO THE ENTIRE NEIGHBORHOOD OF 375 CUSTOMERS. I NOTIFIED WAYNE STEWART AND THE NRC. ALL EMPLOYEES WERE DISCHARGED FROM THE HOSPITAL WITHIN A FEW HOURS. WE THEN LOCKED OFF ALL CUSTOMER METERS. FELICIANA WELDERS REPAIRED THE BROKEN SECTION WITH A NEW VALVE AND SECTION OF PIPE. STARTED RE CONNECTING SERVICE ON 11/2/2017 AT 10:00. ALSO JUST WANTED TO STATE THAT THE EMPLOYEE WHO HAD A POSITIVE DRUG SCREEN WAS DUE TO THE FACT THAT HE WAS ADMINISTERED MORPHINE BEFORE THE DRUG SCREEN WAS ADMINISTERED. THE MEDICAL RECORDS PROVIDE THIS TIMELINE.
2025-03-31 10:13 | NO | NO | NO | 20170110 | 16703 | 2017-11-30 12:23 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2017-11-02 15:46 |  |  | 2017 | 47071 BAYSIDE PARKWAY | FREMONT | ALAMEDA | CA | 94538-6517 | 37.4766 | -121.9384 | [9 empty] | 2017-11-02 21:25 | 1195070 |  | NATURAL GAS |  | 1000 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-11-02 15:46 |  |  |  | 2017-11-02 16:00 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1984 | [5 empty] | 3 | UNKNOWN | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 1.5 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 15000 | 17703.480278422275 | 50000 | 59011.60092807425 | 0 | 0 | N/A |  | 3000 | 3079.326923076923076923076923076923076923 |  | 0 | 68000 | 34621.6435391754473076923076923076923077 | 79794.4081295734480769230769230769230769 | 300 | 0 | 41 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM OPERATED AS INTENDED | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | AUGER | STREET LIGHT | YES | 721201560 | USA NORTH |  | UTILITY OWNER | NO | YES | 8 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | STEPHEN RAMOS | GAS ENGINEER | s3rc@pge.com | 925-413-7311 |  |  |  |  | SUSIE RICHMOND | MANAGER REGULATORY COMPLIANCE | 925-328-5776 | gsr8@pge.com | ON 11/2/17 AT APPROXIMATELY 1546 HOURS, PG&E WAS NOTIFIED OF A DIG-IN AT 47071 BAYSIDE PARKWAY, FREMONT. A THIRD PARTY CONTRACTOR, EXPERICON CONSTRUCTION, HIT A 3-INCH PLASTIC MAIN WITH AN AUGER. THE CONTRACTOR PROVIDED AN EXPIRED USA TICKET (NUMBER W721201560) AND FAILED TO REQUEST REMARK WHEN WORK LOCATION WAS CHANGED. PG&ES GSR ARRIVED ONSITE AT 1600 HOURS. A PG&E GAS CREW ARRIVED ONSITE AND SHUTIN A DISTRIBUTION REGULATOR STATION AT 1937 HOURS TO STOP THE FLOW OF GAS. THIS LEFT 341 CUSTOMERS WITHOUT GAS. REPAIRS WERE COMPLETED BY REPLACING 3 FEET OF PLASTIC MAIN. PG&E ACTIVATED AN OEC TO EXPEDITE RESTORATION OF SERVICE TO THE AFFECTED CUSTOMERS. POLICE AND FIRE DEPARTMENT WERE REPORTED ON SITE. NO REPORTS OF ONSITE MEDIA, FATALITIES, OR INJURIES WERE ASSOCIATED WITH THIS INCIDENT. THIS EVENT WAS REPORTED TO THE DOT (1195070) AND CPUC DUE TO ESTIMATED COST EXCEEDING $50,000.
2025-03-31 10:13 | NO | YES | YES | 20170111 | 33303 | 2017-12-05 12:41 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2017-08-02 10:22 |  |  | 2017 | 3100 W. RIVER PARKWAY | MINNEAPOLIS | HENNEPIN | MN | 55406 | 44.946 | -93.2059 | [9 empty] | 2017-08-02 12:06 | 1186035 |  | NATURAL GAS |  | 0 |  | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 0 | 1 | 0 | 0 | 1 | 2 | YES |  |  |  |  | YES | 45 | 2017-08-02 10:22 |  |  |  | 2017-08-02 10:25 |  | NO | PRIVATE PROPERTY | TRANSITION AREA | OTHER | BASEMENT/ METER ROOM |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | 1959 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | LIVE GAS PIPING WAS DISASSEMBLED. | CLASS 3 LOCATION | 48000000 | 56651136.89095128 | 14622 | 17257.35257540603367 | 8807 | 10394.303387470998395 | 0 | 0 |  |  | 0 | 0 |  | 0 | 48023429 | 23474654.342737823148183 | 56678788.546914157032065 | 1 | 0 | 0 |  |  |  |  | 10 | 10 | 15 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 2 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | KNOWING THAT THE GAS WAS STILL ON TO THE BUILDING, MASTER MECHANICAL'S JOURNEYMAN/PIPEFITTER FAILED TO RECOGNIZE THAT CENTERPOINT ENERGY'S JURISDICTIONAL VALVE WAS IN THE OPEN POSITION BEFORE HE AND HIS MASTER MECHANICAL HELPER DISASSEMBLED PIPING. THE MASTER MECHANICAL PERSONNEL ALSO FAILED TO PURGE THE JURISDICTIONAL PIPING DOWNSTREAM OF THE VALVE. |  |  |  | YES | PER MASTER MECHANICAL'S BID FOR THE WORK AT MINNEHAHA ACADEMY, MASTER MECHANICAL WAS HIRED TO ONLY WORK ON NON-JURISDICTIONAL CUSTOMER PIPING. WORK ON JURISDICTIONAL EQUIPMENT, INCLUDING THE PIPING THAT MASTER MECHANICAL ULTIMATELY DISASSEMBLED, WAS NOT WITHIN THEIR SCOPE OF WORK, AND CENTERPOINT ENERGY DID NOT REQUEST THEY WORK ON JURISDICTIONAL EQUIPMENT. MASTER MECHANICAL'S UNAUTHORIZED WORK ON JURISDICTIONAL PIPING UPSTREAM OF THE GAS METER LED TO THE GAS RELEASE THAT CAUSED THE INCIDENT. | OTHER MAINTENANCE | NO | [50 empty] | AARON ABRAHAMSON | OPERATIONS SPECIALIST II | aaron.abrahamson@centerpointenergy.com | 6123215514 |  |  |  |  | DEAN HEADLEE | MANAGER OF PIPELINE SAFETY AND COMPLIANCE | 6123215366 | dean.headlee@centerpointenergy.com | SUPPLEMENTAL UPDATE 12/08/2017 - THE NTSB PRELIMINARY REPORT ADOPTED ON AUGUST 21, 2017 PUBLICLY DESCRIBES THE EVENT AS FOLLOWS: ON AUGUST 2, 2017, AT 10:22 A.M., A BUILDING AT THE MINNEHAHA ACADEMY (NORTH CAMPUS) IN MINNEAPOLIS, MINNESOTA, WAS DESTROYED BY A NATURAL GAS EXPLOSION. [REFERENCE TO FIGURE REMOVED] AS A RESULT OF THE EXPLOSION, TWO INDIVIDUALS WERE KILLED AND NINE WERE INJURED. AT THE TIME OF THE EXPLOSION, TWO WORKERS WERE INSTALLING NEW PIPING TO SUPPORT THE RELOCATION OF GAS METERS FROM THE BASEMENT OF THE BUILDING TO THE OUTSIDE. TWO NEW METERS MOUNTED ON A WALL WERE READY FOR THE NEW PIPING TO BE CONNECTED. WHILE WORKERS WERE REMOVING THE EXISTING PIPING, A FULL-FLOW NATURAL GAS LINE AT PRESSURE WAS OPENED. THE WORKERS WERE UNABLE TO MITIGATE THE RELEASE OF THE GAS, SO THEY EVACUATED THE AREA. HTTPS://WWW.NTSB.GOV/INVESTIGATIONS/ACCIDENTREPORTS/PAGES/DCA17MP007-PRELIM-REPORT.ASPX FINAL UPDATE AS OF 1/21/2020 ON DECEMBER 4, 2019, THE NTSB RELEASED THE PUBLIC DOCKET FOR ITS INVESTIGATION INTO THE INCIDENT. AS DESCRIBED IN THE DOCUMENTS INCLUDED IN THE PUBLIC DOCKET, THE NTSB FOUND THAT THE RELEASE OF NATURAL GAS AT MINNEHAHA ACADEMY OCCURRED WHEN MASTER MECHANICAL DISASSEMBLED EXISTING PIPING IN THE ACADEMY'S BOILER ROOM. THE MASTER MECHANICAL PERSONNEL BELIEVED A 3-INCH WALWORTH PLUG VALVE UPSTREAM OF THE DISASSEMBLED EXISTING PIPING WAS IN THE CLOSED POSITION ON THE DAY OF THE EXPLOSION, WHEN IN FACT IT WAS OPEN. THE NTSB ALSO PERFORMED A POST-INCIDENT ANALYSIS OF EVIDENCE TAKEN FROM THE SCENE OF THE EXPLOSION AND FOUND THAT INDICATORS ON THE 3-INCH WALWORTH PLUG VALVE CONFIRMED THAT THE VALVE'S ORIENTATION WAS IN THE OPEN POSITION. THE NTSB ALSO NOTED THAT "CONFIRMATION OF WHETHER THE VALVE IS OPEN OR CLOSED IS THE RESPONSIBILITY OF THE CREW WORKING ON THE PIPING. THIS CONFIRMATION WOULD ENTAIL REMOVAL OF THE HANDLE AND NOTING THE POSITION OF THE PLUG ASSEMBLY." THE MASTER MECHANICAL PERSONNEL DID NOT PERFORM EITHER OF THESE FUNCTIONS TO CONFIRM THE ORIENTATION OF THE VALVE ON THE DAY OF THE EXPLOSION. AS NOTED IN PARD D 2A OF THIS REPORT, THE EXPLOSION CAUSED AN ESTIMATED $48 MILLION IN "PROPERTY DAMAGE" (AS DEFINED IN PHMSA F7100.1) TO THE SCHOOL. THIS FIGURE IS BASED ON ESTIMATES FROM THE SCHOOL AND THE SCHOOL'S PROPERTY INSURER. IN ITS DECEMBER 6, 2019 ACCIDENT BRIEF, THE NTSB STATED THAT "THE PROBABLE CAUSE OF THE NATURAL GAS EXPLOSION AT THE MINNEHAHA ACADEMY WAS THE DISASSEMBLING OF PIPING UPSTREAM OF A GAS SERVICE METER IN THE BUILDING BY A PIPEFITTING CREW [MASTER MECHANICAL], RESULTING IN THE RELEASE OF NATURAL GAS, WHICH SUBSEQUENTLY IGNITED. CONTRIBUTING TO THE ACCIDENT WAS THE LACK OF DETAILED DOCUMENTATION THAT CLEARLY ESTABLISHED THE SCOPE OF WORK TO BE PERFORMED."
2025-03-31 10:13 | YES | NO | NO | 20170114 | 16725 | 2017-12-13 12:52 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2017-11-15 06:57 |  |  | 2017 | 2315 UNIVERSITY AVE | NEW YORK | BRONX | NY | 10468 | 40.8616 | -73.9063 | [9 empty] | 2017-11-15 09:03 | 1197341 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-11-15 06:57 |  |  |  | 2017-11-15 07:22 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUM METER | [9 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 4 LOCATION | 100000 | 118023.2018561485 | 0 | 0 | 700 | 826.1624129930395 | 0 | 0 |  |  | 10 | 10.26442307692307692307692307692307692308 |  | 0 | 100710 | 49233.3374196858912076923076923076923077 | 118859.6286922184625769230769230769230769 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | OSCAR LEON | GAS EMERGENCY RESPONSE CENTER-OPER. GEN'L. SUPV. | leono@coned.com | 718-319-2310 | 718-904-4607 |  |  |  | NICHOLAS HELLEN | GAS EMERGENCY RESPONSE CENTER DEPARTMENT MANAGER | 718-319-2341 | hellenn@coned.com | AT 06:57 ON NOVEMBER 15, 2017, THE FIRE DEPARTMENT OF THE CITY OF NEW YORK (FDNY) NOTIFIED CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) OF A GAS-FED FIRE IN APARTMENT 2B AT 2315 UNIVERSITY AVENUE IN THE BRONX. A CON EDISON GAS DISTRIBUTION SERVICES (GDS) MECHANIC AND SUPERVISOR WERE THEN DISPATCHED TO THE LOCATION. AT 06:59, THE FDNY CALLED BACK AND REPORTED THAT THEY HAD TURNED OFF GAS SERVICE TO THE ENTIRE BUILDING AND THAT THERE WERE NO REPORTED INJURIES. AT 07:22, CON EDISON'S GDS MECHANIC AND SUPERVISOR ARRIVED ON LOCATION AND BEGAN INVESTIGATING. FDNY CHIEF MCCORMACK OF DIVISION 7 WAS ON LOCATION. THE GDS SUPERVISOR REPORTED THAT THE FDNY HAD CLOSED THE METER CONTROL VALVE IN APARTMENT 2B PRIOR TO GDS' ARRIVAL AND THAT GAS SERVICE WAS NOT SHUT OFF TO THE ENTIRE BUILDING, AS HAD BEEN INITIALLY REPORTED. GDS INVESTIGATED APARTMENT 2B AND THE ADJACENT APARTMENTS (2A, 2C, 3B & 1B) AND DETECTED NO NATURAL GAS ODORS OR READINGS IN ANY OF THE APARTMENTS. NO GAS PIPING DAMAGE WAS OBSERVED INSIDE APARTMENT 2B, AND ALL POINTS-OF-ENTRY WERE CLEAR OF NATURAL GAS READINGS. PRESSURE AND ODORANT READINGS WERE MONITORED AT AN ADJACENT APARTMENT (2C) AND WERE WITHIN THE ACCEPTABLE RANGE (6.2" WATER COLUMN AND 0.33% GAS-IN-AIR, RESPECTIVELY). GDS CLOSED, PLUGGED AND LOCKED THE METER BAR, AND THE SHUTDOWN WAS VERIFIED. A WARNING TAG WAS ALSO ISSUED. AT 08:37, THE CON EDISON GDS SUPERVISOR REPORTED THAT THE FACE OF THE GAS METER WAS MELTED, WITH THE METER NUMBER TAGS DAMAGED BY THE FIRE. THE FDNY FIRE MARSHAL INVESTIGATED AND DETERMINED THAT THE PRIMARY FIRE AND SOURCE OF IGNITION WERE RELATED TO ELECTRICAL WIRING IN THE KITCHEN. THE OCCUPANT OF THE APARTMENT, MR. ESTANIS LAO CRUZ (AGE 90), WAS SLEEPING IN A BEDROOM WHEN HE SMELLED SMOKE AND VACATED THE APARTMENT. THERE WERE NO REPORTED INJURIES OR ILLNESSES. THE NY STATE DEPARTMENT OF PUBLIC SAFETY (NYSDPS), NY CITY DEPARTMENT OF ENVIRONMENTAL PROTECTION (NYCDEP), AND THE NATIONAL RESPONSE CENTER (NRC) WERE NOTIFIED. NYSDPS RESPONDED TO LOCATION, AND AN UPDATE WAS PROVIDED TO THE NRC WITHIN 48 HOURS.
2025-03-31 10:13 | NO | YES | NO | 20170115 | 30525 | 2017-12-18 16:46 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2017-11-13 11:05 |  |  | 2017 | 10871 WALNUT GROVE BEND | CAMBY | HENDRICKS | IN | 46113 | 39.6339 | -86.3287 | [9 empty] | 2017-11-13 13:13 | 1197183 |  | NATURAL GAS |  | 42 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2017-11-13 11:05 |  |  |  | 2017-11-13 11:34 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1998 | [5 empty] | 1 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 300000 | 354069.6055684455 | 7000 | 8261.624129930395 | 1000 | 1180.232018561485 | 0 | 0 |  |  | 220 | 225.817307692307692307692307692307692308 |  | 0 | 308220 | 150764.4394743887467692307692307692307692 | 363737.2790246296876923076923076923076923 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 1710254520 |  |  | CONTRACT LOCATOR | NO | YES | 5 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JO COHORST | MANAGER GAS COMPLIANCE AND QMP | jcohorst@vectren.com | 620-755-5903 |  |  |  |  | NANCY CONDER | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | 812-491-4545 | nconder@vectren.com | ON MONDAY, NOVEMBER 13, 2017, A CONTRACTOR INSTALLING TELECOMMUNICATION FACILITIES USING BORING EXCAVATION EQUIPMENT, STRUCK AND DAMAGED A 1 INCH PLASTIC NATURAL GAS SERVICE LINE TO 10871 WALNUT GROVE BEND IN CAMBY, INDIANA. THE RESULTING RELEASE OF NATURAL GAS IGNITED CAUSING AN EXPLOSION AND FIRE WHICH DESTROYED THE HOUSE, ALSO RESULTING IN PARTIAL FIRE DAMAGE TO THE HOUSES ON EITHER SIDE. VECTREN PERSONNEL ISOLATED THE ESCAPING NATURAL GAS ON THE SERVICE LINE AND MADE IT SAFE. ASSOCIATED NRC REPORT NUMBERS: 1197183 (INITIAL), 1197261 (48 HOUR), 1197265 (UPDATE/CORRECTION)
2025-03-31 10:13 | YES | NO | NO | 20170116 | 31457 | 2017-12-20 20:47 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2017-10-09 07:29 |  |  | 2017 | 8537 & 8531 SONOMA HIGHWAY | KENWOOD | SONOMA | CA | 95452 | 38.4268 | -122.5518 | [9 empty] | 2017-10-09 10:08 | 1192712 |  | NATURAL GAS |  | 376 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-10-09 07:29 |  |  |  | 2017-10-09 08:10 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | WILDFIRE | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 15700000 | 18529642.6914153145 | 0 | 0 | SEE NARRATIVE FOR FURTHER INFORMATION |  | 1128 | 1157.826923076923076923076923076923076923 |  | 0 | 15701128 | 7675493.33147421159230769230769230769231 | 18530800.51833839142307692307692307692308 | 2 | 0 | 0 |  |  |  |  | 33 | 33 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | ENZA BARBATO | REGULATORY COMPLIANCE PROGRAM MANAGER | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | MANAGER OF GAS OPERATIONS COMPLIANCE AND RISK | 925-328-5776 | gsr8@pge.com | PLEASE NOTE, A GAS TRANSMISSION PHMSA 7100 WAS SUBMITTED ON 11/8/17 (PG&E INCIDENT NO. 20170101-17485 ). THE INCIDENT WAS INITIALLY REPORTED BASED ON THE INFORMATION AVAILABLE AT THE TIME IN ACCORDANCE WITH §191.15. UPON SUBSEQUENT INVESTIGATION, IT WAS DETERMINED THAT NO TRANSMISSION LINES FAILED DURING THIS INCIDENT AND AS SUCH, IT SHOULD BE REPORTED A GAS DISTRIBUTION INCIDENT REPORT. SUMMARY: IN THE EARLY MORNING HOURS OF OCTOBER 9, 2017, MULTIPLE WILDFIRES WERE REPORTED AS PART OF THE OCTOBER 2017 NORTHERN CALIFORNIA WILDFIRES. PG&E FIRST RECEIVED NOTIFICATION OF POSSIBLE GAS PIPELINE INVOLVEMENT AT 0729 HOURS WHEN IT RECEIVED NOTIFICATION OF GAS IGNITIONS NEAR 8537 AND 8531 SONOMA HIGHWAY IN THE CITY OF KENWOOD, SONOMA COUNTY. PG&E'S GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON-SITE AT 0810 HOURS AND OBSERVED GAS HAD IGNITED FROM THE RISER AFTER THE METER HAD MELTED AWAY. THIS SERVICE RISER IS FED FROM A HIGH PRESSURE REGULATOR (HPR) OFF OF DISTRIBUTION FEEDER MAIN (DFM) 1305-01, WHICH IS FED FROM TRANSMISSION LINE L-21 LINE SERIES. ON 10/9/17 AT 1011 HOURS THIS GAS RELEASE INCIDENT WAS REPORTED TO THE DOT (1192712) AND CPUC (171009-8550). PER 191.5(C), PG&E PROVIDED AN UPDATE TO THE DOT (1192859) ON 10/10/17. FOLLOWING THE INITIAL NOTIFICATION DESCRIBED ABOVE, PG&E RECEIVED OTHER REPORTS OF HPRS AND CUSTOMER METER SETS/RISERS IN MULTIPLE NORTHERN CALIFORNIA LOCATIONS AFFECTED BY THE WILDFIRES. IN RESPONSE, PG&E ACTIVATED THE LOCAL OEC, GEC AND EOC PER THE COMPANY'S GAS EMERGENCY RESPONSE PLAN. PG&E CREWS WERE DEPLOYED TO ASSESS, MAKE-SAFE, AND IF POSSIBLE, REPAIR GAS FACILITIES. ON 10/9/17, AT 2011 HOURS, L-21E WAS ISOLATED AND GAS WAS VENTED. IT WAS DETERMINED THAT THE GAS RELEASES MET THE CRITERIA OF A REPORTABLE INCIDENT UNDER BOTH THE DOT CRITERIA OF RELEASE OF GAS WITH PROPERTY DAMAGE IN EXCESS OF $50,000, AS WELL AS THE CPUC CRITERIA OF BOTH PROPERTY DAMAGE AND HAVING ATTRACTED PUBLIC ATTENTION. THERE ARE NO REPORTS OF INJURIES OR FATALITIES ASSOCIATED WITH PG&E GAS FACILITIES. IN TOTAL, APPROXIMATELY 42,500 GAS CUSTOMERS WERE ISOLATED IN THE AREAS IMPACTED BY THE OCTOBER 2017 NORTHERN CALIFORNIA WILDFIRES. ON 10/12/17, AT 1700 HOURS, L-21E WAS RESTORED. BY 10/19/17, ALL AFFECTED CUSTOMERS WHOSE PROPERTY COULD ACCEPT GAS SERVICE WERE RESTORED OR HAD RECEIVED AT LEAST ONE ATTEMPTED RELIGHT. ESTIMATED DAMAGE COST CALCULATIONS ARE ONGOING DUE TO THE LARGE SCALE NATURE OF THE WILDFIRES AND TOTAL COMPANY COSTS ARE NOT KNOWN AT THIS TIME. THE NUMBERS PROVIDED HEREIN ARE FOR ESTIMATION PURPOSES ONLY AND ARE THE BEST ESTIMATE AT THE TIME OF COMPLETING THIS REPORT. NOTE: THE DATA FIELDS (SERVICE ADDRESS, PIPE VINTAGE, SIZE, MATERIAL, ETC.) IN THE ACCOMPANYING REPORT REFER TO THE GAS ASSETS AT THE LOCATION OF THE FIRST REPORTED GAS-RELATED
2025-03-31 10:13 | NO | YES | NO | 20170117 | 31497 | 2017-12-21 17:14 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2017-11-27 09:57 |  |  | 2017 | 3976 MISSION STREET | SAN FRANCISCO | SAN FRANCISCO | CA | 91344 | 37.7343 | -122.4256 | [9 empty] | 2017-11-27 11:50 | 1198192 |  | NATURAL GAS |  | 525 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 20 | 2017-11-27 09:57 |  |  |  | 2017-11-27 10:20 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1992 | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | UNKNOWN |  |  |  | UNKNOWN |  | LEAK |  |  | OTHER | ON THE SERVICE TEE | [5 empty] | CLASS 3 LOCATION | 777000 | 917040.278422273845 | 144000 | 169953.41067285384 | 8000 | 9441.85614849188 | 0 | 0 |  |  | 1575 | 1616.646634615384615384615384615384615385 |  | 0 | 930575 | 455606.2120460022214615384615384615384615 | 1098052.19187823494961538461538461538462 | 0 | 0 | 464 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | A RUBBER X-PANDER PLUG THAT HAD BEEN INSERTED INTO THE SERVICE TEE DISLODGED ON 11/27/17 |  |  | YES |  |  | CONSTRUCTION | NO | [50 empty] | ENZA BARBATO | REGULATORY COMPLIANCE | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | MANAGER GAS OPS COMPLIANCE AND RISK | 925-328-5776 | gsr8@pge.com | ON MONDAY, NOV. 27, 2017, AT 0957 HOURS PG&E RECEIVED A CALL ABOUT A GAS ODOR IN THE 3900 BLOCK OF MISSION STREET IN SAN FRANCISCO. A GSR WAS DISPATCHED AT 1004 HOURS. AT 1016 HOURS, PG&E WAS NOTIFIED THAT AN EXPLOSION IN THAT VICINITY HAD BLOWN OUT WINDOWS AND RESULTED IN ADDITIONAL PROPERTY DAMAGE TO RESIDENTIAL STRUCTURES. THE GSR ARRIVED ON SITE AT 1020 HOURS. AT 1033 HOURS, MULTIPLE PG&E GAS CREWS ARRIVED ON THE SCENE AND WORKED TO MAKE THE SITUATION SAFE. BY 1250 HOURS, CREWS HAD SHUT OFF GAS AND GAS WAS ISOLATED WITH 2 VALVES AND 2 SQUEEZE LOCATIONS. THIS GAS SHUT-IN IMPACTED 464 CUSTOMERS WHO LOST GAS SERVICE. IN RESPONSE TO THIS INCIDENT, PG&E ACTIVATED AN OEC TO EXPEDITE RESTORATION OF SERVICE TO THE AFFECTED CUSTOMERS. THE CREWS TIED THE MAIN BACK IN AT MISSION AND COLLEGE AND MISSION COLLEGE TERRACE. ON 11/28/17 AT 1345 HOURS, THE 6" MAIN WAS PRESSURE TESTED. ON 11/28/17 AT 1515 HOURS, THE MAIN WAS RE-PRESSURIZED. AS OF 11/29/17, 448 CUSTOMERS HAD BEEN PUT BACK IN SERVICE, THE REMAINING 16 WERE 'CANT GET INS' (CGIS) AND HAD 2 TO 3 ATTEMPTED RELIGHTS EACH. POLICE, FIRE DEPARTMENT AND MEDIA WERE REPORTED ON-SITE. THERE WERE NO REPORTS OF INJURIES, FATALITIES OR IGNITION ASSOCIATED WITH THIS INCIDENT. THE INCIDENT IS BEING REPORTED TO THE DOT (1198192) AND CPUC DUE TO THE UNINTENTIONAL RELEASE OF GAS AND DAMAGES ESTIMATED TO BE OVER $50,000.
2025-03-31 10:13 | NO | NO | NO | 20180001 | 30383 | 2018-01-03 16:19 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2017-12-03 16:40 |  |  | 2017 | 1323 LENORE AVE. | COLUMBUS | FRANKLIN | OH | 43224-3359 | 40.0358 | -82.9787 | [9 empty] | 2017-12-03 18:07 | 1198707 |  | NATURAL GAS |  | 262 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2017-12-03 16:49 |  |  |  | 2017-12-03 17:18 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 22 |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | CUSTOMER OWNED SERVICE LINE | 1949 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | LOCALIZED CORROSION | [5 empty] | CLASS 3 LOCATION | 59000 | 69633.689095127615 | 0 | 0 | 1500 | 1770.3480278422275 | 0 | 0 | 0 |  | 907 | 930.983173076923076923076923076923076923 |  | 0 | 61407 | 30434.6246151615258076923076923076923077 | 72335.0202960467655769230769230769230769 | 0 | 0 | 1 |  |  |  |  | 0.45 | 0.45 | 1 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | NO | NONE | [250 empty] | ROB SMITH | MANAGER OF OPERATIONS COMPLIANCE | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB SMITH | MANAGER OF OPERATIONS COMPLIANCE | 614-818-2110 | rrsmith@nisource.com | ON DECEMBER 03, 2017 A DETACHED GARAGE EXPLODED WHEN THE HOMEOWNER STARTED THEIR VEHICLE PARKED IN THE GARAGE. THE HOME WAS SERVED BY A 1.25 INCH BARE STEEL CUSTOMER OWNED SERVICE LINE. THE SERVICE LINE WAS LEAK SURVEYED IN 2015 AND NO LEAKS WERE FOUND. THE COMPANY'S RECORDS SHOW NO RECENT CALLS FROM EITHER THE CUSTOMER OR ANYONE ELSE IN THE IMMEDIATE VICINITY CONCERNING AN ODOR OF GAS. THE LEAKING CUSTOMER OWNED SERVICE LINE THAT RAN PAST THE GARAGE WAS LEAKING DUE TO EXTERNAL CORROSION AND THE ESCAPED GAS HAD MIGRATED INTO THE GARAGE. THE HOMEOWNER SUSTAINED MINOR INJURIES AND WAS TREATED AND RELEASED. PLEASE CONSIDER THIS REPORT FINAL.
2025-03-31 10:13 | NO | YES | NO | 20180002 | 16749 | 2018-01-04 17:28 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2017-12-05 16:28 |  |  | 2017 | BURNETT FERRY ROAD @ RADIO SPRINGS ROAD SW | ROME | FLOYD | GA | 30165 | 34.2416 | -85.2669 | [9 empty] | 2017-12-06 01:01 | 1198937 |  | NATURAL GAS |  | 323.51 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-12-05 16:38 |  |  |  | 2017-12-05 17:04 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2002 | [8 empty] | OTHER | 2-INCH AG REGULATOR STATION | [9 empty] | MECHANICAL PUNCTURE | 2 | 3 | [7 empty] | CLASS 3 LOCATION | 5200 | 6137.206496519722 | 75782 | 89440.34283062645627 | 31136 | 36747.70412993039696 | 0 | 0 |  |  | 912 | 936.115384615384615384615384615384615385 |  | 0 | 113030 | 55671.1129073710608475384615384615384615 | 133261.3688416919598453846153846153846154 | 0 | 0 | 69 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@southernco.com | A 2-INCH ABOVE GROUND REGULATOR STATION WAS DAMAGED BY AN OUT OF CONTROL VEHICLE WHERE IT WAS IDENTIFIED THAT THE DRIVER WAS TRAVELING TOO FAST FOR CONDITIONS. THE ESCAPING GAS IGNITED CAUSING THE VEHICLE TO BURN. ONCE THE INCIDENT WAS MADE SAFE AND ALL COST ESTIMATES ASSOCIATED WITH THE INCIDENT WERE IDENTIFIED, IT WAS DETERMINED THAT THE INCIDENT EXCEEDED THE $50,000 THRESHOLD FOR REPORTING. THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. THERE WERE NO FATALITIES OR INJURIES REQUIRING HOSPITALIZATION. THE 2-INCH REGULATOR STATION WAS PROTECTED BY A FENCE WHICH TOGETHER WITH THE STATION, STOPPED THE VEHICLE.
2025-03-31 10:13 | NO | NO | NO | 20180003 | 30764 | 2018-01-05 09:37 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2017-12-08 19:20 |  |  | 2017 | 47-55 37 STREET | NEW YORK | QUEENS | NY | 11101-1803 | 40.7407 | -73.9284 | [9 empty] | 2017-12-08 20:03 | 1199191 |  | NATURAL GAS |  | 30 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2017-12-08 19:20 |  |  |  | 2017-12-07 14:04 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1907 | [5 empty] | 4 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 25000 | 29505.800464037125 | 15000 | 17703.480278422275 | 25055 | 29570.713225058006675 | 0 | 0 |  |  | 78 | 80.0625 |  | 0 | 65133 | 31874.033265661258485 | 76860.056467517406675 | 2 | 0 | 2 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | A COMPANY EMPLOYEE FAILED TO MAINTAIN ADEQUATE CLEARANCE FROM UNDERGROUND ELECTRIC FACILITIES WHILE USING A TOWABLE BACKHOE TO REMOVE LARGE PIECES OF CONCRETE FROM THE EXCAVATION. THE BACKHOE DAMAGED A SECONDARY CABLE, CAUSING AN ARC, WHICH IGNITED THE GAS THAT WAS LEAKING FROM THE CRACKED MAIN. |  |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | KEVIN FAGAN | OPERATIONS MANAGER-GAS EMERGENCY RESPONSE CENTER | fagank@coned.com | 718-319-2310 | 718-824-2219 |  |  |  | NICKOLAS HELLEN | DEPARTMENT MANAGER-GAS EMERGENCY RESPONSE CENTER | 718-319-2350 | hellenn@coned.com | AT 19:20 ON DECEMBER 8, 2017, A SUPERVISOR FROM CON EDISON'S QUEENS GAS CONSTRUCTION DEPARTMENT REPORTED A GAS IGNITION TO CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC). THE SUPERVISOR REPORTED THAT THE IGNITION - LOCATED IN AN EXCAVATION IN THE ROADWAY IN FRONT OF 47-55 37TH STREET IN QUEENS - OCCURRED WHILE CON EDISON EMPLOYEES WERE WORKING TO REPAIR A TYPE 1 GAS LEAK ASSOCIATED WITH A CRACKED 4-INCH LOW PRESSURE RADIAL CAST IRON GAS MAIN. A COMPANY EMPLOYEE FAILED TO MAINTAIN ADEQUATE CLEARANCE FROM UNDERGROUND ELECTRIC FACILITIES WHILE USING A TOWABLE BACKHOE TO REMOVE LARGE PIECES OF CONCRETE FROM THE EXCAVATION. THE BACKHOE DAMAGED A SECONDARY CABLE, CAUSING AN ARC, WHICH IGNITED THE GAS THAT WAS LEAKING FROM THE CRACKED MAIN. THE FIRE DEPARTMENT OF THE CITY OF NEW YORK (FDNY) RESPONDED TO THE IGNITION AND PROVIDED ASSISTANCE. A MULTIPLE RESOURCE RESPONSE EVENT ("CODE MURRE") WAS INITIATED BY THE GERC AND ADDITIONAL CREWS FROM GAS CONSTRUCTION AND GAS DISTRIBUTION SERVICES (GDS) WERE DISPATCHED, TOGETHER WITH SUPERVISORS, FROM QUEENS, BRONX AND WESTCHESTER. CON EDISON CREWS BEGAN DIGGING A FIRE BANK EXCAVATION IN FRONT OF 47-31 37TH STREET TO ALLOW FOR STOPPER INSTALLATION AND ISOLATION OF THE 4-INCH RADIAL GAS MAIN. AT 20:26, WHILE MONITORING THE AREA, GDS DETECTED A 0.7% GAS READING IN THE ATMOSPHERE INSIDE THE BUILDING AT 47-55 37TH STREET AND A 1% GAS READING IN THE BASEMENT OF THAT BUILDING AT THE ELECTRIC SERVICE POINT-OF-ENTRY. THE BUILDING AT 47-55 37TH STREET WAS THEN VENTED BY GDS, AND THE GERC NOTIFIED CON EDISON'S ELECTRIC OPERATIONS DEPARTMENT TO RESPOND. GDS ALSO REPORTED DETECTING A 6% GAS READING IN ELECTRIC MANHOLE M17797. THE ADJACENT ELECTRIC MANHOLES WERE CHECKED WITH NO GAS READINGS DETECTED, AND POWER VENTILATION EQUIPMENT WAS INSTALLED ON MANHOLE M17797. THE ATMOSPHERIC READINGS IN 47-55 37TH STREET VENTED DOWN TO 0% AND THE ELECTRIC POINT-OF-ENTRY VENTED DOWN FROM 1% TO 0.1%. AT 22:15, STOPPERS WERE INSTALLED, ELIMINATING THE GAS LEAK AND EXTINGUISHING THE FIRE. AT 22:18, M17797 WAS CONFIRMED VENTED TO 0%. FOUR GAS SERVICES WERE INTERRUPTED: TWO COMMERCIAL BUILDINGS, A SIXTEEN-FAMILY RESIDENTIAL BUILDING, AND A THREE-FAMILY RESIDENTIAL BUILDING. GAS CONSTRUCTION WORKED TO RESTORE GAS SERVICE TO THE AFFECTED BUILDINGS. THREE CON EDISON EMPLOYEES SUSTAINED MINOR BURN INJURIES AND WERE TREATED ON LOCATION. FIRE-RELATED DAMAGE SUSTAINED BY A PRIVATE VEHICLE AND CON EDISON'S TOWABLE BACKHOE, TOGETHER WITH CON EDISON'S RESPONSE COSTS, ARE ESTIMATED TO BE IN EXCESS OF $50,000. DRUG AND ALCOHOL TESTING WAS ADMINISTERED. THERE WERE NO REPORTED EVACUATIONS. NEW YORK CITY EMERGENCY MANAGEMENT, FDNY, AND THE NEW YORK CITY DEPARTMENT OF TRANSPORTATION RESPONDED. THE NATIONAL RESPONSE CENTER, THE NEW YORK STATE DEPARTMENT OF PUBLIC SERVICE, AND THE NEW YORK CITY DEPARTMENT OF ENVIRONMENTAL PROTECTION WERE NOTIFIED AND UPDATED. THE OCCUPATIONAL SAFETY AND HEALTH ADMINISTRATION AND THE NEW YORK STATE DEPARTMENT OF PUBLIC SERVICE WERE ON LOCATION.
2025-03-31 10:13 | NO | NO | NO | 20180004 | 16752 | 2018-01-05 19:00 | SUPPLEMENTAL FINAL | 4483 | ENSTAR NATURAL GAS CO | 3000 SPENARD ROAD | ANCHORAGE | AK | 99503 | 2017-12-15 10:37 |  |  | 2017 | 2405 OLD GLENN HIGHWAY | PALMER | MATANUSKA-SUSITNA BOROUGH | AK | 99645-7553 | 61.6072 | -149.0593 | [9 empty] | 2017-12-15 11:57 | 1199761 |  | NATURAL GAS |  | 142 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2017-12-15 10:37 |  |  |  | 2017-12-15 10:50 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1997 | [5 empty] | 2 | ASTM D2513 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 2 | 6.3 | [7 empty] | CLASS 3 LOCATION | 60000 | 70813.9211136891 | 2135 | 2519.795359628770475 | 3720 | 4390.4631090487242 | 0 | 0 |  |  | 2078 | 2132.947115384615384615384615384615384615 |  | 0 | 67933 | 34164.1250914688616234615384615384615385 | 79857.1266977512100596153846153846153846 | 1 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RUPTURE WAS DUE TO THIRD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY | 2016-01-01 | NO |  |  | YES | YES | [8 empty] | NO | YES | OTHER | [5 empty] | YES | [6 empty] | CONTRACTOR | DRILLING | ENGINEERING/SURVEYING | YES | 2017500024 | NO |  | UTILITY OWNER | YES | YES | 7 | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | RUSTY ALLEN | COMPLIANCE ENGINEER | rusty.allen@enstarnaturalgas.com | 9073347765 |  |  |  |  | STEVE COOPER | DIRECTOR OF OPERATIONS | 9073347730 | steve.cooper@enstarnaturalgas.com | A THIRD PARTY CONTRACTOR DRILLING ENVIRONMENTAL MONITORING WELLS RUPTURED A 2 INCH PE MAIN. THE NATURAL GAS IGNITED AND CONSUMED THE DRILLING RIG IN FLAMES. THE CONTRACTOR WAS WORKING UNDER A VALID LOCATE TICKET HELD BY THE PROJECT OWNER. THE PROJECT OWNER FAILED TO MAINTAIN THE LOCATE MARKS AND FAILED TO OPERATE WITH PROPER REGARD FOR PUBLIC SAFETY AND FAILED TO TAKE ALL THE PROPER STEPS TO PREVENT DAMAGE TO NATURAL GAS FACILITY'S.
2025-03-31 10:13 | NO | YES | NO | 20180005 | 16753 | 2018-01-10 18:31 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2017-12-12 05:21 |  |  | 2017 | 1814 MORRO ST | SAN LUIS OBISPO | SAN LUIS OBISPO | CA | 93401 | 35.2751 | -120.6566 | [9 empty] | 2017-12-12 09:00 | 1199461 |  | NATURAL GAS |  | 8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2017-12-12 05:21 |  |  |  | 2017-12-12 06:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2012 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 350000 | 413081.20649651975 | 345 | 407.180046403712325 | 200 | 236.046403712297 | 0 | 0 |  |  | 48 | 49.26923076923076923076923076923076923077 |  | 0 | 350593 | 171397.8288952347257919230769230769230769 | 413773.7021774049900942307692307692307692 | 0 | 0 | 1 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | MIKE BARRINGER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | mbarringer@semprautilities.com | 714-478-0745 |  |  |  |  | MIKE BARRINGER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 714-478-0745 | mbarringer@semprautilities.com | ON DECEMBER 12, 2017 A VEHICLE STRUCK A UTILITY POLE CAUSING IN HIGH VOLTAGE POWER LINES TO HIT THE GROUND. THE RESULTING ELECTRICAL SURGE INTO STRUCTURE AT 1814 MORRO ST. CAUSED A SHORT IN THE GAS METER RESULTING IN AN IGNITED PINHOLE LEAK. THE IGNITED LEAK AT THE GAS METER CAUSED FIRE DAMAGE TO THE STRUCTURE. THE GAS LEAK WAS CONTROLLED BY RESPONDING FIRE DEPARTMENT PERSONNEL CLOSING THE SERVICE VALVE. NO INJURIES OR FURTHER DAMAGE RESULTED FROM THIS INCIDENT. SOCALGAS CREWS ARRIVING ON SCENE PERFORMED BAR HOLE SAMPLING TO CONFIRM NO GAS WAS LEAKING FROM THE SERVICE. THE METER SET ASSEMBLY WAS REMOVED AND THE SERVICE VALVE WAS LEFT CLOSED POSITION AND LOCKED TO PREVENT UNAUTHORIZED OPERATION. THIS INCIDENT WAS REPORTED TO THE DOT AND THE CPUC DUE TO THE RELEASE OF GAS AND THE ESTIMATED DAMAGE EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, CONTACT MIKE BARRINGER AT (714) 478-0745.
2025-03-31 10:13 | NO | YES | YES | 20180006 | 30868 | 2018-01-10 19:24 | SUPPLEMENTAL FINAL | 18104 | CPS ENERGY | 500 MCCULLOUGH | SAN ANTONIO | TX | 78215 | 2017-12-11 18:29 |  |  | 2017 | 2131 LIME BLOSSOM | SAN ANTONIO | BEXAR | TX | 78247 | 29.5491 | -98.4614 | [9 empty] | 2017-12-11 20:38 | 1199404 |  | NATURAL GAS |  | 45 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 2 | 2017-12-11 19:19 |  |  |  | 2017-12-11 19:43 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | INSIDE A RESIDENTIAL HOME |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1979 | [5 empty] | 1.315 | ASTM D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 58000 | 68453.45707656613 | 4200 | 4956.974477958237 | 1800 | 2124.417633410673 | 0 | 0 |  |  | 160 | 164.230769230769230769230769230769230769 |  | 0 | 64160 | 31436.1922184544049230769230769230769231 | 75699.0799571658092307692307692307692308 | 0 | 0 | 1 |  |  |  |  | 9 | 9 | 33 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 1979 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [6 empty] | YES | [8 empty] | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | MICHAEL R. FUENTES | DIRECTOR GAS OPERATIONS AND CONSTRUCTION | mrfuentes@cpsenergy.com | 2102191309 | 2103535807 |  |  |  | MICHAEL R. FUENTES | DIRECTOR GAS OPERATIONS AND CONSTRUCTION | 2102191309 | mrfuentes@cpsenergy.com | THE SAN ANTONIO POLICE DEPARTMENT REPORT STATED THAT THE TWO RESIDENTS OF THE HOME SMELLED THE ODOR OF GAS IN THE HOME FOR A WEEK. THE MALE RESIDENT WENT INTO A BACK ROOM OF THE HOME AND LIT A CANDLE. UPON LIGHTING THE CANDLE, AN IGNITION AND SUBSEQUENT EXPLOSION OCCURRED. THE MALE RESIDENT WAS TRANSPORTED TO THE HOSPITAL FOR BURNS TO HIS ARMS AND HANDS. CPS ENERGY GAS TROUBLEMAN CONDUCTED AN OUTSIDE LEAK INVESTIGATION AND FOUND GAS READS UNDER THE SLAB, IN THE YARD AND IN THE SEWER VENT. CPS ENERGY LEAK CREWS FOUND THE CAUSE OF THE GAS LEAK TO BE A CRACKED POLYETHYLENE BUTT FUSE ON THE 1" GAS SERVICE SERVING THE HOUSE NEXT DOOR. THE AREA AROUND THE CRACKED POLYETHYLENE BUTT FUSE WAS SURROUNDED BY DENSE TREE ROOTS. CPS ENERGY LEAK SURVEYED THE SURROUNDING AREA INCLUDING THE ENTIRE 2K GRID MAP THAT IS ON THE LEAK SURVEY CYCLE.
2025-03-31 10:13 | NO | NO | NO | 20180007 | 16757 | 2018-01-12 15:43 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2017-12-20 09:42 |  |  | 2017 | 8615 E APACHE TRAIL C-63 | MESA | MARICOPA | AZ | 85207 | 33.4128 | -111.6451 | [9 empty] | 2017-12-20 13:49 | 1200173 |  | NATURAL GAS |  | 187 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 6 | 2017-12-20 09:42 |  |  |  | 2017-12-20 10:02 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1966 | [5 empty] | 2 | ASTM D 2661 | UNKNOWN | PLASTIC |  |  |  |  | ACRYLONITRILE BUTADIENE STYRENE (ABS) |  |  |  | UNKNOWN |  | MECHANICAL PUNCTURE | 1 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 52016 | 61390.94867749420376 | 3500 | 4130.8120649651975 | 0 | 0 |  |  | 469 | 481.401442307692307692307692307692307692 |  | 0 | 55985 | 27582.4727326878505627692307692307692308 | 66003.1621847670935676923076923076923077 | 0 | 0 | 697 |  |  |  |  | 36 | 40 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 4 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 20170800871 |  |  | CONTRACT LOCATOR | YES | YES | 12 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | SHAWN BRINK | ADMINISTRATOR DIVISION COMPLIANCE | shawn.brink@swgas.com | 6024845489 | 6024845322 |  |  |  | MICHAEL CHASE | GENERAL MANAGER OPERATIONS | 4807303700 | michael.chase@swgas.com | P/L # 2017-0431 SOUTHWEST GAS CORPORATION (SWG) RESPONDED TO A REPORT OF A LINE BREAK AT 8615 E APACHE TRAIL IN MESA ARIZONA. SWG WAS NOTIFIED OF THE INCIDENT ON DECEMBER 20, 2017 AT 09:42 BY MESA FIRE DEPARTMENT. FIRE DEPARTMENT EVACUATED 6 PEOPLE FROM 5 MOBILE HOMES. SWG CREWS RESPONDED AND CONTROLLED THE FLOW OF GAS BY UTILIZING VALVES RESULTING IN AN OUTAGE OF 697 SERVICES. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THE INCIDENT. SWG NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) ON DECEMBER 20, 2017 AT 13:49 AND WAS GIVEN NRC REPORT #1200173. SWG PROVIDED AN UPDATE WITH REVISED OUTAGE OF 697 TO THE NRC ON DECEMBER 21, 2017 AT 14:10 AND WAS GIVEN NRC REPORT #1200270.
2025-03-31 10:13 | NO | YES | YES | 20180008 | 16758 | 2018-01-12 16:25 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2017-12-14 00:18 |  |  | 2017 | 14852 LINCOLN ST. WEST | NORTH LAWRENECE | STARK | OH | 44618-0494 | 40.7971 | -81.6344 | [9 empty] | 2017-12-14 07:07 | 1199588 |  | NATURAL GAS |  | 139 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2017-12-14 01:25 |  |  |  | 2017-12-14 03:33 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2007 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | VEHICLE STRUCK A METER SETTING SHEARING THE INLET PIPING JUST DOWN STREAM OF THE SHUT OFF VALVE. | CLASS 3 LOCATION | 12000 | 14162.78422273782 | 1000 | 1180.232018561485 | 1500 | 1770.3480278422275 | 0 | 0 |  |  | 481 | 493.71875 |  | 0 | 14981 | 7544.5609773781915 | 17607.0830191415325 | 1 | 0 | 0 |  |  |  |  | 49.7 | 49.7 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ROB SMITH | MANAGER OPERATIONS COMPLIANCE | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB SMITH | MANAGER OPERATIONS COMPLIANCE | 614-818-2110 | rrsmith@nisource.com | A 3/4 TON PICKUP TRUCK WAS TRAVELING DOWN A SNOW-COVERED ROAD AND LOST CONTROL, TRAVELING OFF THE ROAD, HITTING A FENCE, AND STRIKING THE METER SETTING, WHICH RESULTED IN A GAS FED FIRE. THE TRUCK ROLLED OVER AND CAME TO REST ON THE DRIVER'S SIDE DOOR WITH THE FIRE IMPINGING ON THE CAB AND BED OF THE TRUCK. THE DRIVER WAS TRANSPORTED TO THE HOSPITAL WITH THIRD-DEGREE BURNS. ACCORDING TO THE STATE HIGHWAY PATROL'S REPORT, THE DRIVER TRAVELED AT AN UNSAFE SPEED FOR THE WEATHER CONDITIONS (HIGH WINDS, BLOWING SNOW, AND BLACK ICE), FAILED TO CONTROL HIS VEHICLE, CROSSED THE CENTERLINE, AND TRAVELED 18 FEET, 9 INCHES OFF THE ROAD BEFORE HITTING THE METER SETTING. PLEASE CONSIDER THIS REPORT FINAL.
2025-03-31 10:13 | NO | NO | NO | 20180010 | 30520 | 2018-01-17 18:23 | SUPPLEMENTAL FINAL | 25000 | ZIA NATURAL GAS CO | NATURAL GAS PROCESSING COMPANY P.O. BOX 541 | WORLAND | WY | 82401 | 2017-12-19 11:03 |  |  | 2017 | 641 SUDDERTH DRIVE | RUIDOSO | LINCOLN | NM | 88345 | 33.3238 | -105.6508 | [9 empty] | 2017-12-19 11:48 | 1200061 |  | NATURAL GAS |  | 57 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 62 | 2017-12-19 09:09 |  |  |  | 2017-12-19 09:16 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 53 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2010 | [5 empty] | 2 | ASTM D2513 | COEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 1 | 2.5 | [7 empty] | CLASS 3 LOCATION | 50000 | 59011.60092807425 | 4644 | 5480.99749419953634 | 2146 | 2532.77791183294681 | 0 | 0 |  |  | 216 | 221.711538461538461538461538461538461538 |  | 0 | 57006 | 27964.9968499018431761538461538461538462 | 67247.0878725682716115384615384615384615 | 1 | 0 | 0 |  |  |  |  | 40 | 40 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | UTILITY | AUGER | POLE | YES | 270924 |  |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | KAJEN STOCKERT | REGULATORY COMPLIANCE TECH | kstockert@zngc.com | (575)378-4277 | (575)378-7011 |  |  |  | LESLIE GRAHAM | DIVISION MANAGER | (575)915-1556 | lgraham@zngc.com | ZIA NATURAL GAS COMPANY FORM 7100.1 INCIDENT DESCRIPTION: AT 9:09AM ON DECEMBER 19, 2017, ZIA NATURAL GAS COMPANY ('ZIA') RECEIVED AN EMERGENCY NOTIFICATION PHONE CALL FROM PUBLIC SERVICE COMPANY OF NEW MEXICO ('PNM') THAT THERE WAS BLOWING GAS FROM A HIT LINE AT 641 SUDDERTH DR, RUIDOSO, LINCOLN COUNTY, NM. PNM IS THE LOCAL ELECTRIC COMPANY AND WAS THE EXCAVATOR ON SITE. ZIA PERSONNEL ARRIVED ON SCENE AT 9:16AM AND ASSESSED THE SITUATION. A 16' CORE BARREL AUGER UTILIZED TO DRILL A HOLE FOR A POWER POLE HAD STRUCK A 2' PE DISTRIBUTION GAS MAIN APPROXIMATELY 53' DEEP. AT THE TIME OF THE HIT, PNM HAD IMMEDIATELY SHUT DOWN THE AUGER EQUIPMENT AND LEFT IT IN PLACE. THE GAS MAIN HAD A TWO-WAY SUPPLY AT THE LOCATION OF THE DAMAGE. ZIA PERSONNEL DETERMINED THAT THE BUILDING AT 641 SUDDERTH DR. WAS VACANT. ZIA PERSONNEL EXCAVATED THE MAIN ON EACH SIDE OF THE DAMAGE TO SQUEEZE OFF THE LINE AND SHUT OFF THE FLOW OF GAS. BETWEEN 9:45AM AND 9:55AM, ZIA PERSONNEL WERE ABLE TO EXCAVATE THE MAIN ON THE EAST SIDE OF THE DAMAGE AND INSTALL SQUEEZE OFF EQUIPMENT. AT APPROXIMATELY 9:55AM, ZIA PERSONNEL REQUESTED A MECHANICAL EXCAVATOR TO ASSIST WITH EXCAVATING THE MAIN ON THE WEST SIDE OF THE DAMAGE DUE TO MULTIPLE LAYER OF ASPHALT AND GRAVEL. AT APPROXIMATELY 10:41AM, ZIA PERSONNEL REQUESTED TRAFFIC CONTROL ASSISTANCE FROM LOCAL EMERGENCY RESPONDERS WHICH ARRIVED AT 10:45AM. AT APPROXIMATELY 11:05AM, AN EXPLOSION AT 641 SUDDERTH DR OCCURRED. IMMEDIATELY FOLLOWING THE EXPLOSION, THE AREA WAS EVACUATED. AT APPROXIMATELY 11:20AM, THE MAIN WAS MECHANICALLY SQUEEZED SHUT AND THE FLOW OF GAS WAS STOPPED. POST-INCIDENT, ZIA PERSONNEL PERFORMED A LEAK SURVEY OF THE AREA AND CHECKED SYSTEM PRESSURE TO VERIFY NO ADDITIONAL ABNORMAL OPERATING CONDITIONS. THE DAMAGE TO THE GAS MAIN WAS REPAIRED ON DECEMBER 28, 2017 AND FLOW WAS RE-ESTABLISHED THROUGH THE MAIN. AN INVESTIGATION OF THE EXCAVATION DAMAGE REVEALED THAT THE MOST RECENT LINE LOCATE TICKET, 17NV270924, HAD EXPIRED ON DECEMBER 13, 2017. THE MARKS WERE STILL VISIBLE ON THE GROUND AND WERE ACCURATE. PNM HAD EXPOSED AN ABANDONED STEEL LINE WITH YELLOW COATING APPROXIMATELY 12' AWAY FROM THE ACTIVE 2' PE GAS LINE. ZIA DETERMINED THAT PNM VIOLATED NMAC 18.60.5.15 (B)(2), FAILURE TO MAINTAIN 18' CLEARANCE WITH MECHANICAL EQUIPMENT FROM MARKED FACILITIES, AND NMAC 18.60.5.10, EXCAVATOR SHALL MAKE A LOCATE REQUEST PRIOR TO EXCAVATION.
2025-03-31 10:13 | NO | YES | YES | 20180011 | 16795 | 2018-01-18 18:50 | SUPPLEMENTAL FINAL | 15259 | UGI PENN NATURAL GAS | 1 UGI DRIVE | DENVER | PA | 17517 | 2017-12-22 20:52 |  |  | 2017 | 41 SPRING ST | WILKES-BARRE | LUZERNE | PA | 18702 | 41.2454 | -75.8612 | [9 empty] | 2017-12-23 02:34 | 1200395 |  | NATURAL GAS |  | 834 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | NO |  |  |  |  | NO | 0 | 2017-12-22 20:52 |  |  |  | 2017-12-22 20:52 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | 10" BOTTOM OUT FITTING | 2015 | [8 empty] | STEEL |  | OTHER | SMAW | 0.365 | [6 empty] | OTHER | [8 empty] | THE STOPPER FITTING DISLODGED WHILE UNDER PRESSURE RESULTING IN A RELEASE OF NATURAL GAS. | CLASS 3 LOCATION | 0 | 0 | 21900 | 25847.0812064965215 | 3500 | 4130.8120649651975 | 0 | 0 |  |  | 2000 | 2052.884615384615384615384615384615384615 |  | 0 | 27400 | 14314.9827770837073384615384615384615385 | 32030.7778868463343846153846153846153846 | 67 | 0 | 24 |  |  |  |  | 162 | 162 | 282 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT RELATED TO THE CONTROLLER OR CONTROL ROOM. | [12 empty] | YES | 3 | 0 | NO |  |  | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | INCORRECT OPERATION | INCORRECT EQUIPMENT | [222 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | JOHN TOUMEH | COMPLIANCE ENGINEER | jtoumeh@ugi.com | 7176754606 |  |  |  |  | KELLY BEAVER | VP ENGINEERING AND OPERATIONS SUPPORT | 610-796-3601 | kbeaver@ugi.com | ~THIS IS A SUPPLEMENTAL REPORT BEING SUBMITTED. THE TIME THE INCIDENT OCCURED IN QUESTION A.4 HAS BEEN UPDATED TO THE TIME AND DATE THE STOPPER FITTING FAILED. ALSO, QUESTION A.6 WAS CHANGED TO ORIGINAL NRC REPORT NUMBER AND NOT THE UPDATED NUMBER RECEIVED WHEN UGI PROVIDED AN UPDATE. ~ BASED ON QUESTIONS RAISED BY PHMSA, A SUPPLEMENTAL REPORT IS BEING FILED. UGI EMPLOYEES WERE PERFORMING A STOPPING OPERATION ON A HIGH PRESSURE GAS MAIN USING AN EXISTING BOTTOM OUT FITTING. THE STOPPING OPERATION WAS BEING PERFORMED TO ABANDON A SECTION OF MAIN THAT WAS REPLACED. A BOTTOM OUT STOPPER FITTING WAS USED TO STOP THE FLOW OF GAS FROM THE BOTTOM OF STOPPER FITTING. AFTER PERFORMING THE STOPPING OPERATION, AND OBSERVING A 30 MINUTE WAIT PERIOD TO ENSURE PROPER STOP OFF, A 3 FOOT SECTION OF THE 10" MAIN WAS REMOVED. WHILE PREPARING TO WELD ON A 10" CAP, GAS WAS DETECTED BYPASSING THE STOPPER. AN EMPLOYEE TRIED TO TIGHTEN THE STOPPER, AND THE STOPPER DISLODGED RESULTING IN A RELEASE OF GAS. LATER THE EMPLOYEE COMPLAINED OF SHOULDER PAIN AND WAS TAKEN TO THE EMERGENCY ROOM. HE WAS ADMITTED OVERNIGHT AND THEN RELEASED. AFTER REVIEW, IT WAS DETERMINED THAT UGI PROCEDURES AND THE MANUFACTURER INSTRUCTIONS WERE NOT FOLLOWED. THE STOPPER THAT WAS SELECTED WAS ONLY DESIGNED TO STOP FLOW FROM ABOVE THE STOPPER, AND SHOULD NOT HAVE BEEN USED TO STOP THE FLOW OF GAS COMING FROM BELOW THE STOPPER. UGI IS ISSUING A COMPANYWIDE ADVISORY TO PREVENT REOCCURRENCE OF A SIMILAR INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20180012 | 16821 | 2018-01-19 19:30 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2017-12-21 00:27 |  |  | 2017 | 1001 BENCH MARK ROAD | MCDONOUGH | HENRY | GA | 30252 | 33.4661 | -84.0483 | [9 empty] | 2017-12-21 14:00 | 1200257 |  | NATURAL GAS |  | 60428.16 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-12-21 00:30 |  |  |  | 2017-12-21 01:46 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | 4-INCH POSI-HOLD COUPLING | 2010 | [8 empty] | OTHER | 4-INCH POSI-HOLD COUPLING | [9 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 39415 | 46518.845011600931275 | 49995 | 59005.699767981442575 | 0 | 0 |  |  | 170332 | 174835.9711538461538461538461538461538462 |  | 0 | 259742 | 205438.6112395145534546153846153846153846 | 280360.5159334285276961538461538461538462 | 0 | 0 | 211 |  |  |  |  | 300 | 300 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | OTHER COMPRESSION TYPE FITTING | STYLE 700 POSI-HOLD |  |  | DRESSER |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | BASED ON AN INTERNAL LAB REVIEW, PROBABLE CAUSE WAS UNDERINFLATION OF POSIHOLD FITTING RESULTING IN REDUCED PIPE RESTRAINT. | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | RALPH MCCOLLUM | SR. COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R LONN | MANAGING DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@southernco.com | A 4-INCH HP STEEL MAIN WITH A BULL PLUG END CONNECTED BY A STYLE 700 POSI-HOLD COMPRESSION COUPLING SEPARATED FROM THE MAIN. AS A RESULT OF THE SEPARATION, GAS SERVICE TO 211 CUSTOMERS WAS INTERRUPTED TO MAKE REPAIRS TO THE MAIN. AT THIS POINT IT WAS DETERMINED THAT THE INCIDENT RESULTED IN A COST THAT EXCEEDED THE $50,000 THRESHOLD FOR REPORTING. THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME.
2025-03-31 10:13 | NO | NO | NO | 20180013 | 16767 | 2018-01-26 14:06 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2017-12-27 04:38 |  |  | 2017 | CONSUMERS ENERGY REGULATOR STATION 66079 | FLINT | GENESEE | MI | 48505 | 43.0517 | -83.6796 | [9 empty] | 2017-12-27 10:20 | 1200584 |  | NATURAL GAS |  | 11960 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-12-27 04:38 |  |  |  | 2017-12-27 08:09 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1978 | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | BLOWING RELIEF VALVE | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 660 | 778.9531322505801 | 550 | 649.12761020881675 | INCIDENT INVESTIGATION - (1/24/2018 OVERHAUL REGULATOR STATION INVESTIGATE) |  | 34385 | 35294.21875 |  | 0 | 35595 | 33240.68696345707667 | 36722.29949245939685 | 0 | 0 | 0 |  |  |  |  | 133 | 118 | 125 |  |  | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING TECHINICAL ANALYST LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON DECEMBER 27, 2017 AT APPROXIMATELY 04:38 HOURS CONSUMERS ENERGY GAS CONTROL RECEIVED A HIGH-HIGH ALARM AT IDAHO AND ST. JOHN REGULATOR STATION (REGULATOR STATION 66079). THE REGULATOR STATION IS LOCATED IN FLINT, MICHIGAN (GENESEE COUNTY) THE GAS CONTROLLER CONTACTED THE ROYAL OAK WORK MANAGEMENT CENTER (GAS DISPATCH) WHO NOTIFIED THE REGULATION FIELD LEADER AND THE GAS MECHANIC AT 04:48 AND 04:59 RESPECTIVELY. THE GAS MECHANIC (GM) ARRIVED ONSITE AT APPROXIMATELY 08:21. THE RESPONSE TIME WAS DELAYED DUE TO VEHICLE ISSUES RESULTING FROM THE EXTREME COLD WEATHER. THE EMPLOYEE CONTACTED THE GARAGE FOR ASSISTANCE. AN ACTION PLAN TO ADDRESS PROTOCOLS TO FOLLOW WHEN A SITUATION PROHIBITS AN EMPLOYEE FROM RESPONDING TO AN EMERGENCY IN A TIMELY MATTER IS BEING DEVELOPED AND SHOULD MINIMIZE REOCCURRING RESPONSE DELAYS. UPON ARRIVAL THE GM OBSERVED THE RELIEF VALVE BLOWING AT STATION 66079 AND IMMEDIATELY BEGAN TO ISOLATE EACH OF THE TWO REGULATION RUNS AND FOUND THEY WERE NOT THE CAUSE. THE GM CONTACTED GAS SYSTEM PLANNING WHO ADVISED THE GM TO CHECK THE REGULATION EQUIPMENT AT REGULATOR STATION 66044. REGULATOR STATION 66044 IS ON THE SAME HIGH PRESSURE LOOP TO THE SOUTH. WHILE EN-ROUTE TO REGULATOR STATION 66044 THE GM RECEIVED A CALL FROM PERSONNEL ONSITE AT REGULATOR STATION 66079 ADVISING THE BLOWING RELIEF RESET ITSELF AND WAS NO LONGER BLOWING. THE GM PERFORMED LOCK-OFF TEST AT BOTH STATIONS (66079 AND 66044) AND BOTH STATIONS PASSED LOCK-OFF TESTING. BOTH STATIONS WERE CHECKED AND FOUND TO BE OPERATING PROPERLY SO BOTH STATIONS WERE LEFT IN OPERATION DUE TO EXTREME COLD WEATHER CONDITIONS. ON JANUARY 24, 2018 AN INTERNAL EXAMINATION OF THE REGULATORS WAS CONDUCTED. GREASE AND OTHER DEBRIS PARTICLES WERE FOUND AND MAY HAVE BEEN A CONTRIBUTING FACTOR FOR THE ABNORMAL OPERATING CONDITION. AN APPARENT CAUSE WAS COMPLETED AND THE CAUSE IS UNDETERMINED. THE REGULATORS WERE CLEANED AND ONE DIAPHRAGM WAS REPLACED.
2025-03-31 10:13 | NO | YES | NO | 20180015 | 16812 | 2018-01-26 14:58 | SUPPLEMENTAL FINAL | 1640 | BOSTON GAS CO | 170 DATA DRIVE | WALTHAM | MA | 02451 | 2017-12-31 18:20 |  |  | 2017 | 340 HYDE PARK AVENUE | BOSTON | SUFFOLK | MA | 02130 | 42.2893 | -71.118 | [9 empty] | 2017-12-31 20:35 | 1200871 |  | NATURAL GAS |  | 31963 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 20 | 2017-12-31 18:20 |  |  |  | 2017-12-31 18:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 84 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1934 | [5 empty] | 10 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 520000 | 613720.6496519722 | 417922 | 493244.92566125293417 | 0 | 0 |  |  | 159643 | 163864.3293269230769230769230769230769231 |  | 0 | 1097565 | 610056.0404602445923863076923076923076923 | 1270829.90464014821109307692307692307692 | 0 | 0 | 3 |  |  |  |  | 9.9 | 15 | 22 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EVENT WAS NOT CAUSED BY CONTROLLER ACTION(S). | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | ,,,CIRCUMFERENTIAL BREAK FOUND UPON EXCAVATION OF MAIN. AT THE TIME, SEVERE COLD TEMPERATURE SNAP WAS UNDERWAY FOR SEVERAL DAYS. SUSPECTED THERMAL STRESS OR FROST HEAVE. | NO | [218 empty] | CORINNE D. BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE D. BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | 6317703549 | corinne.byrnes@nationalgrid.com | NE DISPATCH AND SCHEDULING RECEIVED SEVERAL LEAK NOTIFICATIONS STARTING AT 19:57 ON 12/31 FROM FIELD OPS. FURTHER INVESTIGATION SHOWED A CIRCUMFERENTIAL BREAK IN MAIN, WHICH RESULTED IN A FIRE. NATIONAL GRID EMPLOYEES WERE TRANSPORTED TO BRIGHAM AND WOMEN'S HOSPITAL, AND SUBSEQUENTLY NOT SENT FOR DRUG TESTING BECAUSE IMMEDIATE MEDICAL RESPONSE AND TREATMENT FOR THE INJURED EMPLOYEES WAS THE PRIORITY AT THAT TIME. PER THE REGULATIONS, A SUPERVISOR WRITTEN RECORD FORM, DOCUMENTING THE REASON FOR NOT TESTING, WAS COMPLETED AND SENT TO THE DRUG AND ALCOHOL PROGRAM MANAGEMENT TEAM. THE FIRE IN THE HOLE WAS EXTINGUISHED AT 13:30 ON 1/2/2018, WHILE AN 8" BYPASS WAS BUILT TO OFFSET THE FLOW AND PRESERVE CONTINUITY OF SERVICE. TWENTY (20) PEOPLE WERE EVACUATED FOR SAFETY REASONS FROM THE FOLLOWING NEARBY DWELLINGS: 340, 344-346, AND 348-350 HYDE PARK AVENUE (TOTAL 3 BUILDINGS/SERVICES). THE LEAK ON A 10" CI MAIN WAS TEMPORARILY REPAIRED USING AN 8" PL BYPASS. PERMANENT REPAIRS WERE COMPLETED BY 1/3/2018. PERMANENT REPAIR CONSISTED OF APPROXIMATELY 55 FEET OF REPLACEMENT PIPE USING CI/ST INSUL. COUPLINGS.
2025-03-31 10:13 | NO | YES | NO | 20180016 | 16770 | 2018-01-26 16:47 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2017-12-28 05:01 |  |  | 2017 | 41140 NONA COURT | HEMET | RIVERSIDE | CA | 92544-0000 | 33.7266 | -116.943 | [9 empty] | 2017-12-28 09:34 | 1200667 |  | NATURAL GAS |  | 11 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 12 | 2017-12-28 07:16 |  |  |  | 2017-12-28 07:16 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1984 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | FAILED ILLEGAL BYPASS | CLASS 3 LOCATION | 250000 | 295058.00464037125 | 1882 | 2221.19665893271477 | 200 | 236.046403712297 | 0 | 0 |  |  | 66 | 67.74519230769230769230769230769230769231 |  | 0 | 252148 | 123284.5609838479602447692307692307692308 | 297582.9928953239540776923076923076923077 | 0 | 0 | 7 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | THEFT OF TRANSPORTED COMMODITY | [156 empty] | MICHAEL BARRINGER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | mbarringer@semprautilities.com | 7144780745 |  |  |  |  | MICHAEL BARRINGER | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 7144780745 | mbarringer@semprautilities.com | ON DECEMBER 28TH, SOCALGAS RESPONDED TO A STRUCTURE FIRE AT A SINGLE-FAMILY HOME LOCATED AT 41140 NONA COURT IN THE CITY OF HEMET. UPON ARRIVAL CREWS FOUND THE IGNITED GAS BLOWING FROM THE RISER AND THE HOME ENGULFED IN FLAMES. THE GAS RELEASE WAS CONTROLLED BY PINCHING 2' PLASTIC MAIN. NO INJURIES OR FURTHER DAMAGE RESULTED FROM THIS INCIDENT. REPAIRS TO THE DAMAGED RISER WERE COMPLETED AND IT WAS LEFT CLAMPED AND PLUGGED AT THE SERVICE VALVE. INVESTIGATION OF THE INCIDENT SHOWED THAT THE METER FOR THIS CUSTOMER HAD BEEN REMOVED ON APRIL 15, 2014 DUE TO NON-PAYMENT. THE SERVICE VALVE WAS LEFT IN A LOCKED CLOSED POSITION. AT SOME POINT AFTER THE METER WAS REMOVED THE CUSTOMER TAMPERED WITH THE SERVICE VALVE AND INSTALLED A BYPASS AND REGULATOR TO SUPPLY GAS TO THE HOUSELINE. THIS INCIDENT WAS REPORTED DUE TO MEDIA COVERAGE DAMAGES IN EXCESS OF $50,000. THIS INCIDENT WAS ALSO REPORTED TO THE CPUC.
2025-03-31 10:13 | NO | YES | NO | 20180017 | 31243 | 2018-01-31 16:45 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-01-01 04:57 |  |  | 2018 | INTERSECTION OF COLGATE LANE AND O'CONNOR RD. | IRVING | DALLAS | TX | 75062 | 32.8511 | -96.9504 | [9 empty] | 2018-01-01 07:25 | 1200886 |  | NATURAL GAS |  | 465 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 5 | 2017-12-31 21:20 |  |  |  | 2017-12-31 22:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1972 | [5 empty] | 6 | PE2306 | NIPAK | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 254000 | 292954.652639216322 | 24672 | 28455.815708325768096 | 8756 | 10098.861962633772108 | 0 | 0 |  |  | 3128 | 3157.579196217494089834515366430260047281 |  | 0 | 290556 | 140222.167828545489675158392434988179669 | 334666.9095063933562938345153664302600473 | 0 | 0 | 1 |  |  |  |  | 36 | 36 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SCADA SYSTEM DID NOT DETECT THE INCIDENT DUE TO THE RELATIVELY SMALL DROP IN PRESSURE CAUSED BY THE INCIDENT | [12 empty] | YES | 3 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | OTHER COMPRESSION TYPE FITTING | COUPLING | OTHER | BOLTED | UNKNOWN |  | OTHER | MATERIALS JOINED: 1ST PLASTIC, 2ND PLASTIC | [22 empty] | YES | SEPARATION | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | KEN PARKS | OPERATIONS MANAGER | james.parks@atmosenergy.com | 817-375-7902 | 817-375-7979 |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT NO. 1200977 AT 7:55 PM ON 12-31-2017, ATMOS ENERGY RECEIVED A CALL FROM THE IRVING FIRE DEPARTMENT REPORTING THE SMELL OF NATURAL GAS ALONG O'CONNOR ROAD IN IRVING, TEXAS. A SERVICE TECHNICIAN WAS DISPATCHED AT 8:23 PM TO INVESTIGATE, AND PROCEEDED TO LOCATE AN UNDERGROUND GAS LEAK NEAR THE INTERSECTION OF COLGATE LANE AND O'CONNOR ROAD AT APPROXIMATELY 9:20 PM. A CONSTRUCTION CREW ARRIVED ONSITE AT APPROXIMATELY 10:00 PM. AFTER COMPLETING LINE LOCATES, THE CONSTRUCTION CREW BEGAN EXCAVATING ALONG A 6" POLY MAIN IN O'CONNOR ROAD TO PINPOINT AND REPAIR THE LEAK. THE CREW REQUESTED ASSISTANCE FROM THE IRVING FIRE DEPARTMENT, WHICH ARRIVED ONSITE AT APPROXIMATELY 3:15 AM ON 1-1-2018. THE CONSTRUCTION CREW CONTINUED WORKING TO ISOLATE AND REPAIR THE LEAK UNTIL APPROXIMATELY 5:00 AM WHEN THE RESIDENCE AT 3567 COLGATE LANE IGNITED. ALL OCCUPANTS WERE EVACUATED FROM THE RESIDENCE WITHOUT INJURY. ONCE THE FIRE WAS EXTINGUISHED, THE CONSTRUCTION CREW RESUMED WORK AND ELIMINATED THE LEAK AT APPROXIMATELY 6:30 AM BY "SQUEEZING OFF" APPROXIMATELY 80' OF THE POLY MAIN. WITH THE EXCEPTION OF THE RESIDENCE WHERE THE FIRE OCCURRED, GAS SERVICE IN THE AREA WAS NOT DISRUPTED. AT 7:06 AM, AN ATMOS ENERGY REPRESENTATIVE DETERMINED THAT THE CRITERIA FOR A REPORTABLE INCIDENT MAY HAVE BEEN REACHED AND A TELEPHONIC REPORT WAS MADE TO PHMSA (NRC 1200886) AT 7:25 AM AND THE TEXAS RAILROAD COMMISSION (TRRC 1693) AT 7:35 AM. AT APPROXIMATELY 11:25 AM THE LOCATION OF THE LEAK WAS EXPOSED AND IT WAS DETERMINED THAT THE 6" POLY MAIN HAD SEPARATED FROM ONE END OF A MECHANICAL, BOLTED FITTING THAT WAS USED TO JOIN THE MAIN. THE CREW COMPLETED REPAIRS BY FUSING A 5' SECTION OF 6" POLY TO REPLACE THE MECHANICAL BOLTED COUPLING AND PLACED THE 80' SECTION OF THE 6" POLY MAIN BACK IN SERVICE AT 4:00 PM.
2025-03-31 10:13 | NO | YES | YES | 20180018 | 31005 | 2018-02-05 11:46 | SUPPLEMENTAL | 12438 | MIDDLE TENNESSEE NATURAL GAS UTIL DIST | P.O. BOX 670, 1030 WEST BROAD ST | SMITHVILLE | TN | 37166 | 2018-01-08 20:25 |  |  | 2018 | 266 ROMA DRIVE | CROSSVILLE | CUMBERLAND | TN | 38555 | 35.9194 | -85.039 | [9 empty] | 2018-01-08 21:25 | 1201373 |  | NATURAL GAS |  | 2.86 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 3 | 2018-01-08 20:34 |  |  |  | 2018-01-08 20:40 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1976 | [5 empty] | 0.75 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | UNKNOWN | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | 200000 | 230672.9548340286 | 2500 | 2883.4119354253575 | 6500 | 7496.8710321059295 | 0 | 0 |  |  | 17 | 17.16075650118203309692671394799054373522 |  | 0 | 209017 | 99852.8962898355377683215130023640661939 | 241070.3985580610690330969267139479905437 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2016-09-29 | NO | [12 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | DRAINAGE | NO | [5 empty] | DATA NOT COLLECTED |  | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | MATT STENNETT | VICE PRESIDENT - ENGINEERING | mstennett@mtng.com | 615-597-0515 | 615-597-6331 |  |  |  | JAMES E. HODGES | EXECUTIVE VICE PRESIDENT AND C.E.O. | 615-597-4300 | jhodges@mtng.com | ON JANUARY 8, 2018, FIRE CONSUMED A PERSONAL RESIDENCE LOCATED AT 266 ROMA DRIVE, CROSSVILLE, TENNESSEE. AN EXPLOSION WAS REPORTED IN CONJUNCTION WITH THE FIRE. THERE WERE THREE (3) OCCUPANTS IN THE HOME AT THE TIME OF THE INCIDENT. ONE OCCUPANT RECEIVED INJURIES REQUIRING HOSPITALIZATION. AT APPROXIMATELY 8:34 P.M. (CST), MIDDLE TENNESSEE NATURAL GAS UTILITY DISTRICT (MTNGUD) RECEIVED A REPORT OF A FIRE AND EXPLOSION AT 266 ROMA DRIVE, CROSSVILLE, TENNESSEE. AT APPROXIMATELY 8:40 P.M. (CST) TWO MTNGUD SERVICE TECHNICIANS ARRIVED AT THE SCENE. THE FIRE DEPARTMENT AND OTHER EMERGENCY SERVICE PROVIDERS WERE ON THE SCENE. THE HOUSE WAS IN FLAMES. AT APPROXIMATELY AT 8:45 P.M. (CST), THE SERVICE TECHNICIANS CUT AND CAPPED THE THREE-QUARTER INCH (3/4") P.E. SERVICE LINE APPROXIMATELY THIRTY (30) FEET FROM THE HOUSE. A REMOTE METHANE LEAK DETECTION SURVEY WAS PERFORMED TO DETERMINE THE PRESENCE OF NATURAL GAS. THE SURVEY DETECTED A SLIGHT READING WHICH DISSIPATED FOLLOWING THE CAPPING OF THE SERVICE LINE. BEFORE THE SERVICE TECHNICIANS LEFT THE SCENE THEY REMOVED THE GAS METER AND REGULATOR WHICH WERE DAMAGED BEYOND USE IN THIS INCIDENT. MTNGUD TECHNICIANS DID NOT INVESTIGATE ANY PIPE DOWNSTREAM OF THE GAS METER. ON JANUARY 9, 2018, MTNGUD PERSONNEL CONDUCTED AN ODORANT TEST NEAR THE INCIDENT SITE. THE ODORANT WAS IN AN ACCEPTABLE RANGE. ON JANUARY 11, 2018, AN AIR TEST ON THE SERVICE LINE INDICATED A FAILURE OF THE SERVICE LINE. EXCAVATION UNDER A CONCRETE SLAB LED TO DISCOVERY OF A SERVICE LINE REPAIR BY USE OF A COMPRESSION COUPLING. THIS REPAIR LOCATION WAS DIRECTLY UNDERNEATH A FOUR-INCH PVC DRAIN PIPE. ONE END OF THE SERVICE LINE WAS DISCONNECTED FROM THE COUPLING. IT IS UNKNOWN IF THIS DISCONNECTION OCCURRED BEFORE OR DURING THE EXPLOSION. FURTHER INVESTIGATION REVEALED TWO (2) ADDITIONAL DAMAGED AREAS ON THE SERVICE LINE. IN 2006, AN EXCAVATOR HIT AND CUT THE LINE. THIS DAMAGE HAD BEEN REPAIRED BY USE OF A STAB FITTING. THIS REPAIR WAS INTACT. THE SIGHT OF A CROSSING OF THE SERVICE LINE WITH A CABLE TV LINE REVEALED THAT THE SERVICE LINE HAD BEEN STRUCK AND PULLED WITH FORCE LEAVING MARKS AND DISTORTION ON THE LINE. THE LINE REMAINED SERVICEABLE AT THIS DAMAGE LOCATION. AN MTNGUD SERVICE TECHNICIAN WAS ONSITE AT THIS METER ON 12/5/17 FOR A REGULAR ANNUAL PRESSURE CONFIRMATION AND THERE WERE NO INDICATIONS OF IRREGULARITIES OR ABNORMAL OPERATING CONDITIONS AT THAT TIME. WEATHER IN CROSSVILLE, TENNESSEE, PRIOR TO THIS INCIDENT WAS UNUSUALLY COLD WITH FREEZING AND THAWING OF THE GROUND IN THE VICINITY, WHICH MAY HAVE CONTRIBUTED TO THE COUPLING TO SERVICE LINE FAILURE. PREVIOUS EXCAVATION DAMAGE MAY ALSO HAVE COMPROMISED THE INTEGRITY OF THIS CONNECTION. THE SEPARATION OF THE COUPLING FROM THE SERVICE LINE WAS SO COMPLETE, IT RAISES ISSUES OF THE TIME AND CAUSE OF THE SEPARATION.
2025-03-31 10:13 | NO | YES | NO | 20180019 | 31922 | 2018-02-08 09:50 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2018-01-09 05:30 |  |  | 2018 | 765 ASHLEY ROAD | MONTECITO | SANTA BARBARA | CA | 93108 | 34.4461 | -119.6525 | [9 empty] | 2018-01-09 17:38 | 1201468 |  | NATURAL GAS |  | 327 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2018-01-09 05:30 |  |  |  | 2018-01-09 06:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1939 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | PIPE SEVERED DUE TO MUDSLIDE, HEAVY RAIN WEATHER, DEBRIS. | CLASS 3 LOCATION | 214956 | 247922.678396517258708 | 3733687 | 4306303.063576998707241 | 2155021 | 2485525.308996915738003 | 0 | 0 |  |  | 1962 | 1980.553191489361702127659574468085106383 |  | 0 | 6105626 | 2917485.88133271299883710638297872340426 | 7041731.60416192106565412765957446808511 | 0 | 0 | 6 |  |  |  |  | 44.5 | 45 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | MUDSLIDE |  |  |  | NO | [218 empty] | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | amatin@semprautilities.com | 9099190463 |  |  |  |  | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE MANAGER | 9093357915 | tbauer@semprautilities.com | SOCALGAS FOUND THE HOUSE AT 765 ASHLEY ROAD TO HAVE BEEN DEMOLISHED FROM A MUDSLIDE CAUSED BY EXTREME WEATHER CONDITIONS IN SANTA BARBARA COUNTY AND CONTROLLED THE GAS BY SHUTTING THE RISER OFF AT THIS LOCATION. HUNDREDS OF HOMES IN THE MONTECITO AREA WERE FOUND TO HAVE ALSO BEEN EITHER DESTROYED OR DAMAGED AS A RESULT OF THESE MUDSLIDES. AT THE REQUEST OF SANTA BARBARA COUNTY FIRE (SBCF) TO SUPPORT SAFETY IN THE COMMUNITY OF MONTECITO, SOCALGAS TEMPORARILY ISOLATED NATURAL GAS SERVICE TO SPECIFIC AREAS IDENTIFIED BY SBCF. THE MAJORITY OF THE MONTECITO AREA WAS IMPACTED BY THIS ACTION. THROUGHOUT THE WEEKS OF RESPONSE, SOCALGAS SAFELY ISOLATED THE AFFECTED AREAS, ASSESSED SYSTEM IMPACTS, INCLUDING TO THE DISTRIBUTION SYSTEM, MADE NECESSARY REPAIRS, AND ULTIMATELY RESTORED SERVICE TO OVER 3,000 INDIVIDUAL HOMES AND BUSINESSES AFTER REPAIRING AND READYING THE SYSTEM AS THE EVACUATION WAS GRADUALLY LIFTED. THIS INCIDENT WAS REPORTED TO THE DOT AND TO THE CPUC DUE TO THE POTENTIAL RELEASE OF GAS, THE DAMAGE COST EXCEEDING $50,000, AND MEDIA ATTENTION. AFTER CONSULTATION WITH SED, THIS SECOND INCIDENT IN THE MONTECITO AREA HAS BEEN REPORTED AND IS BEING TRACKED AS A SEPARATE INCIDENT FROM THE TRANSMISSION RELATED EVENTS (NRC #1201382) RESULTING FROM THE WEATHER CONDITIONS. THE TOTAL COST IN RESPONSE TO THIS EVENT IS PENDING AND WILL BE PROVIDED ONCE AVAILABLE. THE 48-HOUR NOTIFICATION WAS COMPLETED PER NRC #1201513. FOR ANY FURTHER QUESTIONS, PLEASE CONTACT IK SONG AT (818) 279-5388. UPDATE 8/27/2018: PRELIMINARY YTD TOTAL COST INFORMATION (NOT FINALIZED); SYSTEM RESTORATION TIME. UPDATE 1/7/2019: UPDATED YTD TOTAL COST INFORMATION (NOT FINALIZED). UPDATE 4/8/2019: UPDATED YTD TOTAL COST INFORMATION (FINALIZED) AND ESTIMATED GAS LOSS. NUMBER OF PEOPLE EVACUATED DUE TO INCIDENT IS UNKNOWN AS THE ENTIRE AREA WAS UNDER MANDATORY AND VOLUNTARY EVACUATION PROTOCOLS. FOR ANY FURTHER QUESTIONS, PLEASE CONTACT ALI MATIN AT (909) 919-0463.
2025-03-31 10:13 | NO | YES | YES | 20180020 | 34350 | 2018-02-09 17:11 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2018-01-11 23:15 |  |  | 2018 | 334-336 PARK STREET | LAWRENCE | ESSEX | MA | 01841 | 42.7158 | -71.1748 | [9 empty] | 2018-01-12 02:10 | 1201687 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | YES | 13 | 2018-01-12 00:02 |  |  |  | 2018-01-12 00:35 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | ABOVE AND BELOW SEE PART H |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | MAIN AND HOUSE PIPING | UNKNOWN | [8 empty] | OTHER | CAST IRON MAIN | [9 empty] | LEAK |  |  | OTHER | MAIN CRACK, HOUSE PIPE LEAKS | [5 empty] | CLASS 3 LOCATION | 252406 | 291116.189189189114058 | 4934 | 5690.701795755485562 | 520 | 599.74968256847436 | 40000 | 46134.59096680572 | CATEGORIZED AS CONTENT ON THE FIRE DEPARTMENTS REPORT |  | 0 | 0 |  | 0 | 297860 | 142284.47487756223848 | 343541.23163431879398 | 0 | 0 | 1 |  |  |  |  | 88 | 88 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | MEGGAN BIRMINGHAM | DIRECTOR SAFETY COMPLIANCE AND RISK MANAGEMENT | mbirmingham@nisource.com | [5 empty] | MEGGAN BIRMINGHAM | DIRECTOR SAFETY COMPLIANCE AND RISK MANAGEMENT | 508.468.9956 | mbirmingham@nisource.com | THE FIRE DEPARTMENT RECEIVED THEIR FIRST ALARM AT 23:15 ON 1/11/2018. THE FIRE DEPARTMENT NOTIFIED THE COMPANY OF A FIRE AT 00:02 ON 1/12/2018. THE COMPANY'S FIRST RESPONDER ARRIVED ON SITE AT 00:35. THE COMPANY WAS MADE AWARE OF A POTENTIAL EXPLOSION AT 01:35. FIRE DEPARTMENT SHUT OFF GAS AT METER VALVE PRIOR TO THE COMPANY ARRIVING ON SITE AND THUS THE MADE SAFE TIME IN 13A IS THE SAME AS THE ON SITE TIME IN 17B. THE SERVICE IMPACTED DURING THE INCIDENT WAS TIED TO A 99 PSIG COATED STEEL MAIN. THERE ALSO WAS A DUAL CAST IRON MAIN RUNNING UNDER THE STREET. THE FIRE MARSHALL'S INVESTIGATION FOUND THAT THE HOUSE PIPING IN THE BASEMENT HAD SEVERAL LEAKS. IN ADDITION, THERE WAS A PRE-EXISTING CRACK IN THE FOUNDATION OF THE BUILDING AND THE COMPANY FOUND A LEAK ON THE CAST IRON MAIN. THE FIRE MARSHALL (REPORT NUMBER 2018-117-55) WAS UNABLE TO DETERMINE WHETHER THE SOURCE OF THE NATURAL GAS THAT WAS INVOLVED IN THE FIRE AND EXPLOSION WAS LEAKING HOUSE PIPING OR GAS THAT MAY HAVE MIGRATED INTO THE BASEMENT FROM THE CAST IRON MAIN THROUGH THE CRACK IN THE FOUNDATION. THE FIRE MARSHALL ALSO COULD NOT DETERMINE THE CAUSE OF THE FIRE AND EXPLOSION. THE COMPANY WAS ALSO UNABLE TO DETERMINE THE SOURCE OF THE GAS INVOLVED IN THE INCIDENT. BECAUSE THE SOURCE OF THE GAS IS UNKNOWN, AN ESTIMATE OF THE VOLUME OF GAS RELEASED AND ITS ESTIMATED COST CANNOT BE DETERMINED AND THUS DEFAULT VALUES WERE UTILIZED BASED ON THE FIELD COMPLETION REQUIREMENT.
2025-03-31 10:13 | NO | YES | NO | 20180021 | 16798 | 2018-02-12 18:55 | ORIGINAL FINAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2018-01-13 16:14 |  |  | 2018 | 150 NW COLBERN ROAD | LEE'S SUMMIT | JACKSON | MO | 64086-5701 | 38.946 | -94.3869 | [9 empty] | 2018-01-15 14:07 | 1201975 |  | NATURAL GAS |  | 348.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-01-13 16:14 |  |  |  | 2018-01-13 16:50 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | IN CREEK UNDER WATER |  |  | YES | [6 empty] | YES | UNCASED | UNKNOWN | UNKNOWN |  | INVESTOR OWNED |  | MAIN |  | 1929 | [5 empty] | 10 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | LEAK NOT EXPOSED | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 234673 | 270663.571648829968239 | 500 | 576.6823870850715 | 0 | 0 |  |  | 1942 | 1960.364066193853427895981087470449172577 |  | 0 | 237115 | 114153.029896882548968728132387706855792 | 273200.6181021088931668959810874704491726 | 0 | 0 | 0 |  |  |  |  | 146 | 146 | 155 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF GAS RELEASED WAS NOT DETECTABLE BY THE SCADA SYSTEM AND THE CONTROLLER(S) TOOK NO ACTIONS THAT WOULD HAVE CONTRIBUTED TO OR CAUSE THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | NICOLE CHRISTIANER | MANAGER OF PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  |  |  |  | CRAIG HOEFERLIN | VP OF OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | A GAS LEAK WAS DISCOVERED ON A 10-INCH DISTRIBUTION MAIN WEST OF 150 NW COLBERN RD ON JANUARY 13, 2018 AT 4:14 PM. THE LEAK WAS UNDER A SMALL UNNAMED CREEK AND THE NATURAL GAS WAS ESCAPING UP THROUGH THE WATER AND INTO THE ATMOSPHERE. NO UNDERGROUND MIGRATION OCCURRED. STOPPER FITTINGS WERE INSTALLED ON EACH SIDE OF THE LEAK AND THE LEAKING MAIN WAS TAKEN OUT OF SERVICE ON JANUARY 18, 2018. THE WORK WAS DELAYED DUE TO EXTREME WEATHER CONDITIONS, BUT SPIRE EMPLOYEES WERE ONSITE MONITORING THE LEAK CONTINUOUSLY UNTIL THE PIPELINE WAS TAKEN OUT OF SERVICE. THE CAUSE WAS NOT ABLE TO BE DETERMINED DUE TO THE INACCESSIBILITY OF THE LEAKING PIPE, THEREFORE "UNKNOWN" WAS SELECTED IN THE REPORT. SPIRE DETERMINED THIS WOULD BE A REPORTABLE INCIDENT AT APPROXIMATELY 2:00 PM ON JANUARY 15, 2018 DUE TO THE REPAIR COSTS EXCEEDING $50,000. NRC INCIDENT REPORT UPDATED ON JANUARY 17, 2018 AT 8:18 A.M., REPORT NUMBER 1202099.
2025-03-31 10:13 | NO | YES | NO | 20180022 | 30794 | 2018-02-13 09:20 | SUPPLEMENTAL FINAL | 13299 | NEW JERSEY NATURAL GAS CO | 1415 WYCKOFF ROAD | WALL | NJ | 07719 | 2018-01-16 11:04 |  |  | 2018 | 360 CARTY AVENUE | FORT MONMOUTH | MONMOUTH | NJ | 07703 | 40.3191 | -74.0379 | [9 empty] | 2018-01-16 12:00 | 1202034 |  | NATURAL GAS |  | 68 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2018-01-16 11:22 |  |  |  | 2018-01-16 11:16 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1993 | [5 empty] | 1 | ASTM D2513 | PHILLIPS DRISCOPIPE, INC. | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 9.33 |  |  | 3408 | MECHANICAL PUNCTURE | 10 | 2.8 | [7 empty] | CLASS 3 LOCATION | 595000 | 686252.040631235085 | 4638 | 5349.305822601123234 | 491 | 566.302104117540213 | 0 | 0 |  |  | 652 | 658.16548463356973995271867612293144208 |  | 0 | 600781 | 287283.9225979515981923309692671394799054 | 692825.8140425873181869527186761229314421 | 0 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | TRENCHER | WATER | YES | 173411986 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | MOBEEN KHAN | DIRECTOR - SYSTEM ENHANCEMENT | mukhan@njng.com | 732-919-8035 | 732-919-0936 |  |  |  | MOBEEN KHAN | DIRECTOR - SYSTEM ENHANCEMENT | 732-919-8035 | mukhan@njng.com | ON JANUARY 16, 2018, A THIRD PARTY EXCAVATOR WAS OPERATING TRENCHING EQUIPMENT IN A ROADWAY TO INSTALL A WATER MAIN WHEN IT STRUCK THE GAS SERVICE LINE TO 360 CARTY AVENUE IN OCEANPORT, NEW JERSEY. THE INCIDENT OCCURRED IN AN AREA OF FORT MONMOUTH, A FORMER INSTALLATION OF THE US DEPARTMENT OF THE ARMY, WHICH WAS UNDERGOING REDEVELOPMENT ACTIVITIES. OCEANPORT POLICE CONTACTED NEW JERSEY NATURAL GAS ("NJNG") AT 11:04 A.M. TO REPORT A POTENTIALLY BROKEN MAIN OR SERVICE AT THIS LOCATION AND ADVISED THAT A VEHICLE WAS ON FIRE. NJNG PERSONNEL WERE DISPATCHED AT 11:05 A.M. AND ARRIVED ONSITE AT 11:16 A.M. WHERE POLICE AND FIRE PERSONNEL WERE ALREADY ONSITE. AT 11:22 A.M., NJNG PERSONNEL CONFIRMED THERE WAS A GAS LEAK AND IGNITION AS A RESULT OF DAMAGE TO THE ONE INCH PLASTIC SERVICE LINE CAUSED BY THE TRENCHER. THE IGNITION RESULTED IN THE TRENCHING MACHINE CATCHING FIRE WHICH ULTIMATELY DESTROYED THE MACHINE. THE AREA WAS MADE SAFE AT 12:49 P.M. BY SQUEEZING OFF THE 4 INCH PLASTIC MAIN. THE SERVICE TO 360 CARTY AVENUE, A VACANT STRUCTURE, WAS THEN RETIRED AT THE MAIN. THERE WERE NO OUTAGES AS A RESULT OF THE SHUTDOWN AND NO EVACUATIONS WERE NEEDED AS THE BUILDINGS IN THIS AREA WERE VACANT. AFTER RETIRING THE SERVICE LINE, GAS WAS REINTRODUCED TO THE MAIN AT 4:45 P.M. ON JANUARY 16, 2018. NO NEW SERVICE LINE WAS INSTALLED. THE SUBSEQUENT INVESTIGATION DETERMINED THE NATURAL GAS SERVICE LINE WAS PROPERLY MARKED OUT (NEW JERSEY ONE CALL TICKET NUMBER 173411986), THE MARKS WERE WITHIN TOLERANCE, AND THE SERVICE LINE HAD 23.5 INCHES DEPTH OF COVER. THE THIRD PARTY EXCAVATOR FAILED TO USE HAND TOOLS WHERE REQUIRED AND STRUCK THE SERVICE LINE WITH A MECHANIZED TRENCHER.
2025-03-31 10:13 | NO | NO | NO | 20180023 | 30116 | 2018-02-14 16:17 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2018-01-16 23:15 |  |  | 2018 | 413 GRANDVIEW DRIVE | ANDERSON | MADISON | IN | 46017-1208 | 40.1173 | -85.5998 | [9 empty] | 2018-01-17 08:37 | 1202105 |  | NATURAL GAS |  | 79 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 10 | 2018-01-17 04:40 |  |  |  | 2018-01-17 00:08 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 44 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.18 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 57000 | 65741.792127698151 | 9063 | 10452.944948304006009 | 970 | 1118.76383094503871 | 0 | 0 | NONE |  | 327 | 330.09219858156028368794326241134751773 |  | 0 | 67360 | 32326.2879493087514581843971631205673759 | 77643.5931055287560026879432624113475177 | 0 | 0 | 4 |  |  |  |  | 36 | 36 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2015-01-01 | NO | [12 empty] | NO | YES | CITY STREET | [12 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | SEWER (SANITARY/STORM) | NO | [5 empty] | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | JO COHORST | MANAGER GAS COMPLIANCE AND QMP | jcohorst@vectren.com | 812-491-5743 |  |  |  |  | NANCY CONDER | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | 812-491-4545 | nconder@vectren.com | VECTREN WAS CONTACTED BY CHESTERFIELD INDIANA FIRE DISPATCH REGARDING RESIDENTIAL FIRE AT 413 GRANDVIEW DRIVE, ANDERSON, INDIANA ON 1/16/18 AT 11:30 PM. UPON ARRIVAL, NATURAL GAS APPEARED TO BE FEEDING THE FIRE; NATURAL GAS READINGS WERE FOUND UNDERGROUND NEAR THE RESIDENTIAL STRUCTURE. A LEAK WAS FOUND ON A 2 INCH BARE STEEL NATURAL GAS DISTRIBUTION MAIN OPERATING AT APPROXIMATELY 36 PSIG. THE LEAK OCCURRED AT A PVC SEWER LATERAL WHICH CROSSED UNDERNEATH THE NATURAL GAS MAIN. THE MAIN EXHIBITED A BOW SHAPE PRIOR TO REPAIR. THE LEAK WAS REPAIRED WITH A LEAK CLAMP AND THE INSTALLATION OF A REINFORCING "PUMPKIN" SLEEVE. THIS MAIN IS INCLUDED IN A BARE STEEL REPLACEMENT PROJECT CURRENTLY SCHEDULED FOR 2019. INVESTIGATION INDICATED THAT NEGLIGENT INSTALLATION OF SEWER LINE BY A THIRD PARTY CONTRACTOR APPROXIMATELY 15 YEARS AGO DISPLACED THE NATURAL GAS MAIN DISTRESSING AND FATIGUING THE MATERIAL. PLEASE NOTE THAT THE ADDRESS, 413 GRANDVIEW DRIVE, ANDERSON, IN 46017, IS ALSO KNOWN AS 413 WESTERN DRIVE, ANDERSON, IN 46017, WITH "GRANDVIEW" AND "WESTERN" REFERRING TO THE EASTERN AND WESTERN SIDES OF THE SAME ROAD.
2025-03-31 10:13 | NO | YES | NO | 20180024 | 16803 | 2018-02-14 18:42 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2018-01-15 18:13 |  |  | 2018 | HAWK SPRINGS AND MESA PARK DR | LAS VEGAS | CLARK COUNTY | NV | 89135 | 36.0881 | -115.3233 | [9 empty] | 2018-01-15 22:04 | 1202010 |  | NATURAL GAS |  | 190 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-01-15 18:13 |  |  |  | 2018-01-15 17:52 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2005 | [5 empty] | 4 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 12278 | 14161.012697261015754 | 6659 | 7680.256031198982237 | 92783 | 107012.643841828377969 | 0 | 0 |  |  | 520 | 524.91725768321513002364066193853427896 |  | 0 | 112240 | 53853.0052800194590498345153664302600473 | 129378.829827971591090023640661938534279 | 2 | 0 | 1766 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 2005 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [7 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | ALYSE BAKER | COMPLIANCE SPECIALIST | alyse.baker@swgas.com | 702-365-2077 | 702-365-2205 |  |  |  | THOMAS CARDIN | DIRECTOR OF GAS OPERATIONS | 702-365-2028 | thomas.cardin@swgas.com | OPERATOR RESPONDED TO AN ODORS COMPLAINT RECEIVED AT 17:00 PDT LOCATED IN A CUL-DE-SAC NEAR 5454 BRISTOL BEND COURT IN LAS VEGAS, NV. A HAZARDOUS GRADE 1 LEAK WAS DISCOVERED ON A 4-INCH M8100 PIPE LOCATED NEAR THE INTERSECTION OF HAWK SPRINGS ROAD AND MESA PARK DRIVE IN LAS VEGAS, NV. THE FLOW OF GAS TO THE SECTION OF PIPE WAS TAKEN OUT OF SERVICE WHILE REPAIRS WERE COMPLETED WHICH RESULTED IN A SERVICE OUTAGE OF 1768 CUSTOMERS. BASED ON COMMUNICATIONS THAT THE PUBLIC UTILITIES COMMISSION OF NEVADA'S REGULATORY OPERATIONS STAFF HAD WITH THE PIPELINE AND HAZARDOUS MATERIALS SAFETY ADMINISTRATION'S ACCIDENT INVESTIGATION DIVISION, PART A - 4 "LOCAL TIME AND DATE OF THE INCIDENT" REFLECTS THE TIME OPERATOR PERSONNEL IDENTIFIED AND REPORTED A GRADE 1 LEAK ON THE PIPELINE. AT THAT TIME, NO INCIDENT REPORTING CRITERIA WAS MET. THE SHUTDOWN TIME REPORTED IN PART A, 13A (21:49) IS THE EARLIEST DATE AND TIME A REPORTING CRITERIA WAS MET. DUE TO THE SHUTDOWN OF THE PIPELINE, THE INCIDENT WAS ESTIMATED TO REACH PROPERTY DAMAGE OF $50,000 OR MORE. TELEPHONIC NOTIFICATION WAS MADE WITHIN ONE HOUR OF THE SHUTDOWN TIME. PART A, 6: SOUTHWEST GAS NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) TELEPHONICALLY OF THE INCIDENT ON JANUARY 15, 2018 AT 22:04 PDT. THE NRC ISSUED REPORT NUMBER 1202010 FOR THE INCIDENT. SOUTHWEST GAS PROVIDED A 48-HOUR UPDATE TELEPHONICALLY TO THE NRC ON JANUARY 17, 2018 AT 14:28 PDT. THE NRC ISSUED REPORT NUMBER 1202162 FOR THE UPDATED REPORT.
2025-03-31 10:13 | NO | NO | NO | 20180025 | 30066 | 2018-02-15 12:20 | SUPPLEMENTAL FINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-01-20 02:30 |  |  | 2018 | INTERSECTION OF NE 24TH AND FOLSOM | AMARILLO | POTTER | TX | 79110 | 35.2366 | -101.7243 | [9 empty] | 2018-01-20 04:45 | 1202383 |  | NATURAL GAS |  | 1059 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-01-20 02:30 |  |  |  | 2018-01-20 03:00 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | 2" CONNECTION FOR A BLOW DOWN VALVE WAS BROKEN WHEN VEHICLE STRUCK STATION. | CLASS 3 LOCATION | 5000 | 5766.823870850715 | 2644 | 3049.496462905858092 | 1784 | 2057.602757119535112 | 0 | 0 |  |  | 3442 | 3474.548463356973995271867612293144208038 |  | 0 | 12870 | 7717.813577107026337096926713947990543735 | 14348.471554233082199271867612293144208 | 0 | 0 | 0 |  |  |  |  | 200 | 200 | 215 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DUE TO 3RD PARTY DAMAGE AND THE PRESSURE ON THE SYSTEM REMAIN CONSTANT AT NORMAL OPERATING PRESSURE DURING THE INCIDENT TIME FRAME. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MIKE CULP | COMPLIANCE MANAGER | mike.culp@atmosenergy.com | 8062206849 | 8067984495 |  |  |  | MIKE CULP | COMPLIANCE MANAGER | 8062206849 | mike.culp@atmosenergy.com | ABOVE GROUND NATURAL GAS FACILITY WAS STRUCK BY A VEHICLE AFTER LEAVING THE ROADWAY AT AN INTERSECTION. SPEED AND ALCOHOL WERE FACTORS IN THE INCIDENT. THE ABOVE GROUND STATION WAS STRUCK AND A 2" BLOW DOWN VALVE WAS BROKEN. THE SETTING WAS VALVED OFF AND GAS FLOW BY-PASSED TO MAINTAIN PRESSURE ON THE SYSTEM DOWNSTREAM. THE SETTING IS REPAIRED AND THE BROKEN SECTION HAS BEEN TAKEN OUT OF SERVICE. THIS FACILITY IS LOCATED AT A T-INTERSECTION IN A RURAL AREA EAST OF AMARILLO. FLOOD LIGHTING TO HELP DRIVERS IDENTIFY THE STATION IS BEING ADDED TO THE LOCATION. THE COUNTY HAS BEEN ASKED TO ADD ROAD SIGNS NOTING THE DEAD END OF THE STREET. THE BROKEN SECTION OF THE FACILITY HAS BEEN REMOVED AND GAS FLOW REDIRECT THROUGH ANOTHER PART OF THE STATION THAT IS NOT IN THE DIRECT PATH OF TRAFFIC IF THEY EXIT THE DEAD END INTERSECTION. IT WAS ORIGINALLY THOUGHT THAT THE PERSON INJURED IN THE INCIDENT REQUIRED HOSPITALIZATION BUT IT WAS LATER DETERMINED THAT HE WAS TREATED AT THE HOSPITAL EMERGENCY ROOM AND RELEASED WHERE HE WAS ARRESTED ON CHARGES OF DUI.
2025-03-31 10:13 | NO | YES | YES | 20180026 | 30073 | 2018-02-16 09:36 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2018-01-20 08:15 |  |  | 2018 | 151 BAY 49TH STREET | BROOKLYN | KINGS | NY | 11214 | 40.5865 | -73.9868 | [9 empty] | 2018-01-20 15:46 | 1202427 |  | NATURAL GAS |  | 35 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 9 | 2018-01-20 08:45 |  |  |  | 2018-01-20 09:21 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1927 | [5 empty] | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 4 LOCATION | 75000 | 86502.358062760725 | 24000 | 27680.754580083432 | 7342 | 8468.004171957189906 | 0 | 0 |  |  | 216 | 218.042553191489361702127659574468085106 |  | 0 | 106558 | 51000.1162397582905240851063829787234043 | 122869.1593679928362677021276595744680851 | 0 | 0 | 1 |  |  |  |  | 0.3 | 0.31 | 0.43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT THE RESULT OF ANY OPERATION THAT THE CONTROL ROOM CAN PERFORM. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROST HEAVE | ,,, | NO | [218 empty] | CORINNE D. BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE D. BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | 6317703549 | corinne.byrnes@nationalgrid.com | ON THE MORNING OF SATURDAY, JANUARY 20, 2018, THE COMPANY RECEIVED NOTIFICATION OF A POTENTIAL GAS FIRE AT A TWO-STORY RESIDENTIAL BUILDING IN THE GRAVESEND SECTION OF BROOKLYN. FDNY RESPONDED TO THE INCIDENT AND EXTINGUISHED THE FIRE WITHIN MINUTES. ON ARRIVAL, CMS DETECTED ELEVATED GAS READINGS AT VARIOUS LOCATIONS IN AND AROUND THE PREMISES. AT APPROX.14:30, FIELD OPERATIONS SUBSEQUENTLY LOCATED AND REPAIRED A CRACK ON A SIX-INCH CAST IRON MAIN LOCATED IN FRONT OF THE BUILDING, THEREBY CONFIRMING THE DISCOVERY OF AN OUTSIDE LEAK POTENTIALLY CAUSING THE INCIDENT. APPARENT INCIDENT CAUSE IS FROST HEAVE. FOUR INDIVIDUALS REPORTEDLY SUSTAINED INJURIES IN THE FIRE. ONE WAS TAKEN TO THE HOSPITAL WITH BURNS TO HIS LEGS (NOTE: THE EXTENT OF ANY TREATMENT/HOSPITALIZATION IS NOT KNOWN AT THIS TIME), THE OTHERS WERE TREATED AT THE SCENE. THE BUILDING SUSTAINED MODERATE STRUCTURAL DAMAGE. THE FIRE MARSHAL HAS PUBLICLY INDICATED THE INCIDENT WAS CAUSED BY A GAS LEAK THAT IGNITED WHEN AN OCCUPANT TURNED ON A LIGHT SWITCH IN A SECOND FLOOR APARTMENT. AT THIS POINT, THE INCIDENT IS STILL UNDER INVESTIGATION. **PLEASE NOTE THAT FOR PART C QUESTION 2A, INSTALLATION DATE WAS A RANGE OF TIME BETWEEN 1913 AND 1927.
2025-03-31 10:13 | NO | YES | NO | 20180027 | 30260 | 2018-02-16 15:50 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2018-01-19 05:53 |  |  | 2018 | 1700 BROAD STREET | UTICA | ONEIDA | NY | 13501 | 43.0955 | -75.1975 | [9 empty] | 2018-01-23 10:45 | 1202624 |  | NATURAL GAS |  | 4863 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 15 | 2018-01-19 05:53 |  |  |  | 2018-01-19 07:15 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 42 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1971 | [5 empty] | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | UNKNOWN | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 250000 | 288341.19354253575 | 5800 | 6689.5156901868294 | 27400 | 31602.1948122619182 | 0 | 0 | QUESTION 2A IS PENDING EVALUATION BY CLAIMS ADJUSTER. |  | 13269 | 13394.4751773049645390070921985815602837 |  | 0 | 296469 | 147672.2264524985858269503546099290780142 | 340027.3792222894621390070921985815602837 | 7 | 0 | 0 |  |  |  |  | 23 | 23 | 24 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT THE RESULT OF ANY OPERATION THAT THE CONTROL ROOM CAN PERFORM. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | STAB |  |  |  | UNK |  | OTHER | MATERIALS JOINED: 1ST PLASTIC, 2ND PLASTIC | [22 empty] | YES | UNKNOWN AT THE PRESENT TIME. FITTING SUBMITTED TO THIRD PARTY LABORATORY FOR ANALYSIS. ALSO DO NOT KNOW CAUSE OF THE FITTING FAILURE (QUESTION 25) |  | YES |  |  |  | OTHER | UNKNOWN AT THIS TIME | NO | [86 empty] | CORINNE D. BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE D. BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | 6317703549 | corinne.byrnes@nationalgrid.com | 5/2/2018 SUPPLEMENTAL REPORT ISSUED TO REFLECT DATE AND TIME OF IGNITION, NOT IDENTIFICATION OF INCIDENT, AND BELOWGROUND FACILITY (ALTHOUGH THE INCIDENT OCCURRED ABOVEGROUND). AT 08:01 ON 1/19/2018 NATIONAL GRID WAS MADE AWARE OF A STRUCTURE AND PIPELINE FACILITY FIRE AT 1700 BROAD STREET. GAS WAS SHUT OFF AT 13:48 TO MAKE THE AREAS SAFE. THE SECTION OF PIPE WAS EXPOSED AND ISOLATED IN ORDER TO LOCATE LEAK AND DETERMINE THE LEAK CAUSE AT APPROX. 17:50 ON 1/19. NINE (9) PEOPLE FROM THREE (3) BUILDINGS WERE EVACUATED. A SMALL SECTION OF PIPE WAS INSTALLED 23:00 ON 1/19 TO RESTORE SERVICE VIA A ONE-WAY FEED. UPON AIR TEST, THE SOURCE OF THE LEAK WAS DETERMINED TO BE A PL-PL COMPRESSION COUPLING ON A 4" MAIN, AS DETERMINED ON 1/24. NRC WAS NOTIFIED ON 1/23 AT 10:45 BASED ON THE POSSIBILITY OF EXCEEDING THE $50,000 INCIDENT CRITERIA.
2025-03-31 10:13 | NO | YES | YES | 20180028 | 32182 | 2018-02-16 19:40 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2018-01-20 11:14 |  |  | 2018 | 4643 CLELAND AVENUE | LOS ANGELES | LOS ANGELES | CA | 90065 | 34.1112 | -118.2166 | [9 empty] | 2018-01-20 13:25 | 1202430 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 3 | 2018-01-20 11:14 |  |  |  | 2018-01-20 11:31 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  | 46 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1925 | [5 empty] | 3 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 36508 | 42107.041175403580644 | 360109 | 415337.035461636025587 | 18978 | 21888.556684200973854 | 0 | 0 |  |  | 0 | 0 |  | 0 | 415595 | 198525.20088880842846 | 479332.633321240580085 | 0 | 0 | 1 |  |  |  |  | 18 | 18 | 20 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | LOCALIZED |  |  | YES |  |  |  | YES | NO |  | YES | NO | [8 empty] | YES | COAL TAR | [21 empty] | 2017-02-15 | NO | [227 empty] | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | amatin@semprautilities.com | 909-919-0463 |  |  |  |  | TROY BAUER | PIPELINE SAFETY AND COMPLIANCE MANAGER | 909-335-7915 | tbauer@semprautilities.com | SOCALGAS RECEIVED REPORT OF A STRUCTURE FIRE AT 4643 CLELAND AVE IN LOS ANGELES ON 1/20/2018. THE COMPANY CREW RESPONDED AND FOUND UNDERGROUND INDICATIONS. AFTER FURTHER INVESTIGATION, THE CREW FOUND A LEAK, MADE THE REPAIRS, AND CONTINUED TO AERATE UNTIL ANY HAZARDOUS CONDITION HAD BEEN ELIMINATED. THE MAIN REPLACEMENT AS A PERMANENT REPAIR HAS BEEN COMPLETED. THE CAUSE OF THE LEAK WAS EXTERNAL CORROSION. THIS INCIDENT WAS REPORTED TO THE DOT AND TO THE CPUC DUE TO THE POTENTIAL INVOLVEMENT OF GAS ASSOCIATED TO AN INJURY AND THE DAMAGE COST EXCEEDING $50,000. THE 48-HOUR NOTIFICATION WAS COMPLETED PER NRC #1202558. FOR ANY FURTHER QUESTIONS, PLEASE CONTACT IK SONG AT (818) 279-5388. UPDATE (7/16/18): UPDATED THE TOTAL COST INFORMATION ON PART D OF THE REPORT. UPDATE (5/22/19): UPDATED THE APPARENT CAUSE ON PART G OF THE REPORT. FOR ANY FURTHER QUESTIONS, PLEASE CONTACT ALI MATIN AT (909) 919-0463.
2025-03-31 10:13 | NO | YES | NO | 20180029 | 30183 | 2018-02-23 18:19 | SUPPLEMENTAL FINAL | 13360 | ENTERGY NEW ORLEANS, LLC | 3700 TULANE AVENUE L-TUL-111 | NEW ORLEANS | LA | 70119 | 2018-01-26 08:25 |  |  | 2018 | 1505 BASIN STREET | NEW ORLEANS | ORLEANS | LA | 70116 | 29.9635 | -90.0715 | [9 empty] | 2018-01-26 12:43 | 1202904 |  | NATURAL GAS |  | 0.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2018-01-26 08:25 |  |  |  | 2018-01-26 08:57 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | SEAMLESS | SEAMLESS | 0.145 | [6 empty] | OTHER | [8 empty] | LIVE NATURAL GAS SERVICE LINE CUT IN TWO WITH RECIPROCATING SAW. | CLASS 3 LOCATION | 303086 | 349568.715944131961298 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 303086 | 144780.878106294328248 | 349568.715944131961298 | 1 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | READILY APPARENT KNOWLEDGE THAT CONTROLLERS OR CONTROL ROOM ISSUES DID NOT CONTRIBUTE TO THE INCIDENT. | [12 empty] | NO |  |  | YES | 2 | 1 | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | LEON T HINSON | SENIOR ENGINEER - REGULATORY COMPLIANCE | lhinson@entergy.com | 504-595-3722 | 504-593-3440 |  |  |  | MICHELLE P BOURG | DIRECTOR - GAS DISTRIBUTION BUSINESS | 504-593-3434 | mpivach@entergy.com | NOTE ALL TIMES CENTRAL STANDARD TIME (CST) AT APPROXIMATELY 8:30 AM 1/26/2018, ENTERGY GAS PERSONNEL WERE NOTIFIED BY AN ENTERGY CONTRACTOR FOREMAN WHOSE CREWS WERE PERFORMING METER CONVERSIONS AT 1505 BASIN STREET, AND BY NEW ORLEANS FIRE DEPARTMENT (NOFD) OF A HOUSE FIRE AT THE SAME ADDRESS IN THE TREMÉ NEIGHBORHOOD OF NEW ORLEANS. AFTER NOTIFICATION ENTERGY PERSONNEL ARRIVED ON SCENE BETWEEN 8:55 AM AND 9:15 AM. NOFD HAD ALREADY EVACUATED TWO INDIVIDUALS AND A DOG FROM INSIDE THE STRUCTURE. NO INJURIES WERE REPORTED BY THE CONTRACTORS OR THE PUBLIC. THE FIRE WAS FULLY INVOLVED WHEN ENTERGY PERSONNEL ARRIVED. NOFD HAD CONTROL OF THE SCENE AND RESTRICTED ACCESS TO THE STRUCTURE. IN THE INTERIM, ENTERGY PERSONNEL INTERVIEWED CONTRACTOR EMPLOYEES PERFORMING METER CONVERSIONS JUST PRIOR TO THE FIRE. BASED ON THE INTERVIEWS IT WAS SUSPECTED THAT THE CONTRACTOR EMPLOYEES AND NATURAL GAS WERE CONTRIBUTORS TO THE FIRE. PHMSA STATE PARTNER, DEPARTMENT OF NATURAL RESOURCES, OFFICE OF CONSERVATION, PIPELINE DIVISION (DNR PIPELINE DIVISION) WAS NOTIFIED TO THAT EFFECT. ENTERGY INFORMED ITS CONTRACTOR THE EMPLOYEES IN QUESTION MUST BE DRUG TESTED. BETWEEN 11:30 AM AND NOON, NOFD GRANTED ENTERGY PERSONNEL A SHORT WINDOW OF ACCESS TO ITS FACILITIES ONLY. PERSONNEL WERE ACCOMPANIED BY FIREMEN AS THEY PERFORMED THE INSPECTION. ENTERGY TURNED OFF GAS SERVICE VALVE, REMOVED THE METER HEADER THAT HAD BEEN CUT AND CONFIRMED THE FIRE WAS GAS RELATED. ONCE CONFIRMED, ENTERGY COMPLIANCE COORDINATOR WAS CONTACTED WHO SUBSEQUENTLY CONTACTED THE NATIONAL RESPONSE CENTER (NRC) REPORTING THE INCIDENT. THE NOTIFICATION WAS RECORDED BY NRC AT 12:43 PM. ENTERGY CONTRACTOR PERSONNEL KNOWINGLY USED AN UNAUTHORIZED TOOL WHILE PERFORMING A METER CONVERSION AT THE RESIDENCE. THE CONTRACT PERSONNEL DID NOT FOLLOW PROCEDURES WHILE PERFORMING THE TASK, ALTHOUGH HE WAS QUALIFIED TO PERFORM THE TASK. THE USE OF THIS UNAUTHORIZED TOOL INTRODUCED AN IGNITION SOURCE THAT ULTIMATELY IGNITED ESCAPING GAS. ENTERGY WAS UNABLE TO ESTIMATE THE AMOUNT OF GAS LOSS BECAUSE WATER SPRAYED ON THE FIRE STOPPED OFF THE LOW PRESSURE GAS FLOW.
2025-03-31 10:13 | NO | YES | NO | 20180030 | 31988 | 2018-03-01 17:15 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY | DALLAS | TX | 75240 | 2018-01-30 11:40 |  |  | 2018 | INTERSECTION OF COLLINS AND ROGERS | ARLINGTON | TARRANT | TX | 76014 | 32.7461 | -97.0976 | [9 empty] | 2018-01-30 12:39 | 1203193 |  | NATURAL GAS |  | 200 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2018-01-30 11:40 |  |  |  | 2018-01-30 11:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 42 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1996 | [5 empty] | 4 | PE 2406 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 150000 | 173004.71612552145 | 16916 | 19510.318519862138988 | 0 | 0 | 0 | 0 |  |  | 1078 | 1088.193853427895981087470449172576832151 |  | 0 | 167994 | 80740.5965903073488203877068557919621749 | 193603.2284988114849690874704491725768322 | 0 | 0 | 0 |  |  |  |  | 35 | 35 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DRILLING | POLE | NO | [7 empty] | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | LYNN MILLER | OPERATIONS SUPERVISOR | lynn.miller@atmosenergy.com | 469-261-2037 | 817-375-7979 |  |  |  | MARLO SUTTON | DIRECTOR REGULATORY AND COMPLIANCE | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT NO. 1203367 ON JANUARY 30, 2018 AT APPROX. 11:40, A THIRD PARTY CONTRACTOR DRILLING A HOLE FOR THE INSTALLATION OF A LIGHT POLE HIT A 4" POLY MAIN. THE CONTRACTOR DID NOT CALL IN FOR LOCATES. THE OPERATOR ABANDONED THE RIG WHILE RUNNING, WHICH IGNITED THE GAS AND BURNED THE UNIT. AT 14:30, THE MAIN WAS ISOLATED USING SQUEEZE TOOLS. THE LINE IS A DUAL FEED, SO IT WAS NOT NECESSARY TO SHUT DOWN THE LINE, AND NO CUSTOMERS WERE INTERRUPTED. THE MAIN WAS REPAIRED AT ON JANUARY 31, 2018, BY REPLACING 5 FEET OF 4" MAIN.
2025-03-31 10:13 | NO | YES | NO | 20180031 | 30061 | 2018-03-07 15:24 | SUPPLEMENTAL FINAL | 31632 | NORTHWESTERN CORPORATION | 3010 W. 69TH ST. | SIOUX FALLS | SD | 57108 | 2018-02-06 10:14 |  |  | 2018 | 507 N 2ND ST | ABERDEEN | BROWN | SD | 57401 | 45.471 | -98.4909 | [9 empty] | 2018-02-06 13:25 | 1203737 |  | NATURAL GAS |  | 5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2018-02-06 10:14 |  |  |  | 2018-02-06 10:23 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1956 | [8 empty] | STEEL |  |  |  | 0.156 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 85000 | 98036.005804462155 | 150 | 173.00471612552145 | 500 | 576.6823870850715 | 25000 | 28834.119354253575 | FIRE INVESTIGATION/RENTAL OF GROUND THAW BLANKET TO REMOVE FROST |  | 50 | 50.47281323877068557919621749408983451537 |  | 0 | 110700 | 52902.9890557414894009456264775413711584 | 127670.2850751650936355791962174940898345 | 0 | 0 | 2 |  |  |  |  | 23 | 23 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | STRUCTURAL MOVEMENT OF BUILDING WALL | [154 empty] | MELISSA BARUTH | DOT SUPERVISOR | melissa.baruth@northwestern.com | 6053537462 |  |  |  |  | MELISSA BARUTH | DOT SUPERVIOSR | 6053537462 | melissa.baruth@northwestern.com | EVENTS ON FEB 6 2018 NORTHWESTERN ORIGINALLY REPORTED TO THE NRC WITH THE NOTIFICATION TIME OF 8:58. THIS WAS AN ERROR IN REPORTING. THE TIME NORTHWESTERN RECEIVED THE FIRST NOTIFICATION FROM 911 WAS 10:14 CST. THIS TIME WAS RETRIEVED FROM OUR INCOMING CALL LONG AND VERIFIED TO BE ACCURATE. THE INCORRECT TIME OF 8:58 INCORRECTLY REPORTED REPRESENTED THE DATE/TIME STAMP IN CUSTOMER INFORMATION SYSTEM AND IS IN MST TIME ZONE. THE INCIDENT LOCATION IS IN CST TIME ZONE. IN ADDITION THE DATE/TIME STAMP WAS INCORRECTLY ATTACHED TO TWO CONSECUTIVE ORDERS BY THE CUSTOMER SERVICE REPRESENTATIVE. 10:14 CST NORTHWESTERN RECEIVED A CALL FROM 911 REQUESTING ASSISTANCE AT 207 N 2ND IN ABERDEEN SD. HOUSE WAS A VACANT PREMISE WITH NO ONE OCCUPYING THE STRUCTURE. 10:23 CST NORTHWESTERN ARRIVED ON SITE. 10:28 CST POWER SHUT OFF TO PREMISE AT THE POLE. 10:50 CST ADJACENT STRUCTURES CHECKED WITH FIRE DEPARTMENT 10:55 CST FIRE DEPARTMENT REQUESTED SERVICE LINE TO BE SHUT OFF 11:20 CST SERVICE WAS SQUEEZED OFF APPROXIMATELY 40 FT. FROM HOME DUE TO FIRE. 11:28 TO 12:00 CST SD PUC NOTIFIED. ODORMETER, LEAK SURVEY AND ADDITIONAL BAR HOLING COMPLETED. NO EVIDENCE OF ADDITIONAL GAS ISSUES FOUND. 12:00 TO 17:00 CST AREA MONITORED AND TECHNICIANS ON SITE TO ASSIST FIRE DEPARTMENT AS NEEDED. 13:25 CST NRC NOTIFIED. DUE TO HEAVY GROUND FROST A THAW BLANKET WAS APPLIED TO BE USE TO THAW THE GROUND TO COMPLETE THE FULL RETIREMENT OF THE SERVICE ON FEB 12 2018. FEB 7 2018 PREMISE HISTORICALLY A RENTAL HOME WITH NO OCCUPANTS AT THIS TIME. LAST KNOWN OCCUPANTS INTERVIEWED BY FIRE MARSHALL AND NORTHWESTERN REPRESENTATIVE. OCCUPANTS INDICATED NO NOTICEABLE GAS SMELL INSIDE THE HOME. OCCUPANTS' WASHER AND DRYER LOCATED IN THE BASEMENT ON THE WALL DIRECTLY ASSOCIATED WITH NATURAL GAS METER. OCCUPANTS DESCRIBED AN ISSUE WITH THE BASEMENT WALL CRACKING DUE TO WALL MOVEMENT AND CREATING A DRAFT IN THE HOME. LANDLORD SUPPLIED CAULKING TO OCCUPANTS TO FILL IN CRACKS CREATED BY BASEMENT WALL MOVEMENT. METER RETRIEVED AND OBTAINED BY NORTHWESTERN. PER FIRE MARSHALL REQUEST PRESSURE TEST ATTEMPTED FROM SQUEEZE POINT TO METER AND FAILED. SITE RELEASED BY FIRE MARSHALL TO HOME OWNER INSURANCE. FEB 9 2018 ATTEMPTED TO RETIRE SERVICE FROM SQUEEZE OFF POINT THE MAIN IN ALLEY AS THAW BLANKET HAD BEEN ON SINCE FEB 6 2018. INSUFFICIENT THAW. THAW BLANKET PUT BACK ON MAIN/SERVICE AREA. FEB 12 2018 SUFFICIENT THAW. SERVICE RETIRED AT THE MAIN. FEB 21 2018 COORDINATED INVESTIGATION WITH ALL CONCERNED PARTIES INCLUDING THE SD PUC TO DIG UP SERVICE PIPE FROM SQUEEZE OFF POINT TO METER. THAW BLANKETS PUT ON SERVICE THE WEEK PRIOR. EXCAVATED PARTIAL AREA. DUE TO UNFORESEEN CONCRETE PATIO INSUFFICIENT THAW AROUND METER AREA. REAPPLIED THE THAW BLANKET. FEB 23 2018 COORDINATED INVESTIGATION WITH ALL CONCERNED PARTIES INCLUDING THE SD PUC TO RESUME EXCAVATION. SERVICE AND RISER AREA FULLY EXCAVATED. FRACTURE FOUND AT THE RISER CONNECTION TO A 90 DEGREE ELBOW. DAMAGED RISER AND ELBOW REMOVED FROM THE GROUND. PRESSURE TEST FROM PIPE REMOVAL ELBOW TO SQUEEZE OFF POINT SUCCESSFUL. NO FURTHER DAMAGE. DUE TO THE FRACTURED SURFACE OF THE ELBOW AND PIPE, NORTHWESTERN AND OUTSIDE INVESTIGATION RETAINED BY NORTHWESTERN BELIEVE THE EVIDENCE SUPPORTS THE FRACTURE TO BE CAUSE BY AN OUTSIDE FORCE, LIKELY THE BASEMENT WALL MOVEMENT, CREATED THE FORCE ON THE PIPE TO CAUSE THE FRACTURE.
2025-03-31 10:13 | NO | NO | NO | 20180032 | 30323 | 2018-03-09 15:52 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2018-02-08 23:52 |  |  | 2018 | 200 FOX HOLLOW DRIVE | MAYFIELD HEIGHTS | CUYAHOGA | OH | 44124 | 41.5111 | -81.4502 | [9 empty] | 2018-02-09 04:02 | 1203924 |  | NATURAL GAS |  | 105 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 48 | 2018-02-08 23:52 |  |  |  | 2018-02-09 00:39 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1988 | [8 empty] | OTHER | SERVICE REGULATOR | [9 empty] | LEAK |  |  | OTHER | ICE ACCUMULATED AT VENT | [5 empty] | CLASS 3 LOCATION | 80000 | 92269.18193361144 | 5311 | 6125.520315617629473 | 370 | 426.74496644295291 | 0 | 0 |  |  | 273 | 275.581560283687943262411347517730496454 |  | 0 | 85954 | 41183.8087261186971051631205673758865248 | 99097.0287759557103262624113475177304965 | 0 | 0 | 36 |  |  |  |  | 31 | 31 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROZEN COMPONENTS | ,,, | NO | [218 empty] | JEFFERY BURDETTE | TECHNICAL SPECIALIST III | jeffery.l.burdette@dominionenergy.com | 330-754-5524 |  |  |  |  | JEFFERY BURDETTE | TECHNICAL SPECIALIST III | 330-754-5524 | jeffery.l.burdette@dominionenergy.com | DUE TO THAWING AND FREEZING TEMPERATURES, ICE ACCUMULATED AROUND THE SERVICE REGULATOR VENT FROM IMPROPERLY MAINTAINED GUTTERS ON THE APARTMENTS AT 200 FOX HOLLOW DRIVE, MAYFIELD HEIGHTS, OHIO. THE PROPERTY OWNERS STATED THAT THEY HAD BEEN AWARE OF THE DRAINAGE PROBLEM. THE ICE ACCUMULATION AROUND THE VENT CAUSED THE SERVICE REGULATOR TO INTRODUCE EXCESSIVE HOUSELINE PRESSURES TO THE DOWNSTREAM APPLIANCES WHICH RESULTED IN AN APARTMENT FIRE. THE RESULTING DAMAGES FROM THE FIRE, ALONG WITH THE WATER DAMAGES FROM THE EFFORTS TO EXTINGUISH THE FIRE, EXCEEDED THE $50,000 REPORTABLE INCIDENT THRESHOLD.
2025-03-31 10:13 | NO | YES | NO | 20180033 | 30047 | 2018-03-15 13:35 | ORIGINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2018-02-14 14:15 |  |  | 2018 | 381-383 WEST MAIN STREET | LITTLE FALLS | HERKIMER | NY | 13365 | 40.6733 | -73.5182 | [9 empty] | 2018-02-15 08:39 | 1204403 |  | NATURAL GAS |  | 63.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | YES | 7 | 2018-02-14 14:30 |  |  |  | 2018-02-14 14:21 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNKNOWN | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | INCIDENT IS UNDER INVESTIGATION AND CAUSE HAS NOT BEEN DETERMINED AS OF YET. | CLASS 3 LOCATION | 200000 | 230672.9548340286 | 0 | 0 | 7142 | 8237.331217123161306 | 0 | 0 |  |  | 153 | 154.446808510638297872340425531914893617 |  | 0 | 207295 | 99092.3475807666223708936170212765957447 | 239064.7328596623996038723404255319148936 | 0 | 0 | 3 |  |  |  |  | 19.64 | 22 | 24 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT THE RESULT OF AN OPERATION THAT THE CONTROL ROOM CAN PERFORM. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | CORINNE D. BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | 6317703549 | corinne.byrnes@nationalgrid.com | NATIONAL GRID DISPATCH RECEIVED NOTIFICATION FROM HERKIMER COUNTY 911 CENTER OF A POSSIBLE DISTURBANCE AT THE RESIDENCE OF 383-387 W. MAIN ST. LITTLE FALLS, NY 13365. THREE PREMISES WERE DAMAGED AS A RESULT OF THIS INCIDENT: 381-383, 389, AND 399 W. MAIN STREET. SEVEN CUSTOMERS HAVE HAD THEIR GAS SERVICE SHUT OFF FOR SAFETY REASONS. NO REPORTED INJURIES AT THE PRESENT TIME. INVESTIGATIONS BY NATIONAL GRID AND LOCAL AUTHORITIES ARE ONGOING. CAUSE OF THE INCIDENT AND, IF GAS-RELATED, LOCATION OF GAS FAULT REMAINS UNDETERMINED. NOTE: UNDER PART D, ESTIMATED COST OF PRIVATE AND NON-OPERATOR DAMAGE VALVES WERE DETERMINED FROM INTERNET SOURCES. THIS IS A PRELIMINARY ASSESSMENT AND SUBJECT TO REVISION VIA SUPPLEMENTAL REPORT.
2025-03-31 10:13 | NO | YES | YES | 20180034 | 35120 | 2018-03-23 17:03 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-02-23 06:38 | CENTRAL | NO | 2018 | 3534 ESPANOLA DR. | DALLAS | DALLAS | TX | 75220 | 32.8681 | -96.8597 |  | YES | [7 empty] | 2018-02-23 07:34 | 1205026 | 1205177 | NATURAL GAS |  | 1.14 | 0.04 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2018-02-23 06:38 | OTHER | A FIRE DID NOT OCCUR, AND WE ARE UNABLE TO ACCURATELY ESTIMATE VOLUME OF GAS CONSUMED BY THE FIRE. | 1 | YES | 42 | 2018-02-23 06:42 | YES | OPERATOR | 2018-02-23 06:42 | 2018-02-23 06:42 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1946 | UNKNOWN |  |  |  |  | 2 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.15 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 199000 | 229519.590059858457 | 13835 | 15956.801650643928405 | 1353 | 1560.502539452203479 | 0 | 0 |  | 7.19 | 8 | 8.07565011820330969267139479905437352246 | 0 | 0 | 214196 | 102322.7430775056888161513002364066193853 | 247044.9699000727921936926713947990543735 | 0 | 0 | 42 | 4 | 0 | 42 | 0 | 25 | 25 | 55 | 192.619(A)(2) | 1946-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 5 |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ABNORMAL CHANGES IN PRESSURE | [12 empty] | YES | 31 | 0 | YES | 12 | 0 | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2017-03-07 | NO | [12 empty] | NO | YES | OTHER | [12 empty] | MUNICIPALITY | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | NO | [5 empty] | DATA NOT COLLECTED |  | MISCELLANEOUS ROOT CAUSES | PREVIOUS DAMAGE | [170 empty] | BILL BROOKS | DIRECTOR REGULATORY AND COMPLIANCE | bill.brooks@atmosenergy.com | 806-787-9422 |  | TOMMY LOONEY | tommy.looney@atmosenergy.com | 469-261-7387 | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON 2/23/2018, A NATURAL GAS EXPLOSION OCCURRED AT 3534 ESPANOLA DRIVE, DALLAS, TEXAS AT 6:38 A.M. MULTIPLE 911 CALLS CAME INTO THE DALLAS FIRE-RESCUE DISPATCH CENTER REPORTING THE EXPLOSION. FIVE FAMILY MEMBERS WERE IN THE HOUSE AT THE TIME OF THE ACCIDENT. ONE RESIDENT'S INJURIES WERE FATAL. THE OTHER FOUR RESIDENTS SUSTAINED NON-LIFE-THREATENING INJURIES. AT THE TIME OF THE EXPLOSION, ATMOS PERSONNEL WERE IN THE AREA WORKING TO REPAIR A NON-HAZARDOUS LEAK IN THE 3500 BLOCK OF ESPANOLA. AN ATMOS OPERATIONS SUPERVISOR HEARD THE EXPLOSION AND TOOK IMMEDIATE ACTION TO PROTECT LIVES AND MAKE THE AREA SAFE. HE DIRECTED HIS CREW TO START EVACUATING A TWO-BLOCK AREA, NORTH AND SOUTH OF THE ACCIDENT HOUSE. FIREFIGHTERS AND ATMOS CREWS WENT DOOR-TO-DOOR ADVISING RESIDENTS TO EVACUATE AND TO REFRAIN FROM STARTING CARS OR SWITCHING ON LIGHTS. THE EVACUATION WAS COMPLETED IN 12-15 MINUTES WITH THE ASSISTANCE OF DALLAS FIRE-RESCUE. THE ATMOS ONSITE OPERATIONS SUPERVISOR, WORKING WITH THE OPERATIONS MANAGER AND THE DIRECTOR OF OPERATIONS, COORDINATED THE SHUT-DOWN OF THE MAIN LINE IN THE ALLEY BEHIND 3534 ESPANOLA. THE NATIONAL TRANSPORTATION SAFETY BOARD (NTSB) ARRIVED ONSITE ON 2/25/2018. ATMOS ENERGY, THE TEXAS RAILROAD COMMISSION (RRC), PIPELINE & HAZARDOUS MATERIALS SAFETY ADMINISTRATION (PHMSA), AND DALLAS FIRE - RESCUE ASSISTED WITH THE NTSB'S INVESTIGATION. THE PROBABLE CAUSE OF THE EXPLOSION AT 3534 ESPANOLA DRIVE WAS THE IGNITION OF AN ACCUMULATION OF NATURAL GAS THAT LEAKED FROM THE GAS MAIN THAT WAS DAMAGED DURING A SEWER REPLACEMENT PROJECT 23 YEARS EARLIER. POST-ACCIDENT EXCAVATION CONFIRMED THE 2" MAIN WAS CRACKED IN THE AREA IT HAD BEEN GOUGED, BENT, AND DENTED BY MECHANIZED EQUIPMENT. THE THIRD-PARTY DAMAGE WAS NEVER REPORTED TO ATMOS.
2025-03-31 10:13 | NO | YES | NO | 20180036 | 30966 | 2018-03-27 13:13 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2018-02-25 00:12 |  |  | 2018 | 613 FLEMING FALLS RD. | MANSFIELD | RICHLAND | OH | 44905-1430 | 40.7852 | -82.4916 | [9 empty] | 2018-02-25 02:17 | 1205179 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 9 | 2018-02-25 00:33 |  |  |  | 2018-02-25 01:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNKNOWN | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNKNOWN PLEASE SEE NARRATIVE | CLASS 3 LOCATION | 54000 | 62281.697805187722 | 1200 | 1384.0377290041716 | 322000 | 371383.457282786046 | 15000 | 17300.471612552145 | LABORATORY GAS ANALYSIS |  | 0 | 0 |  | 0 | 392200 | 187349.6644295303496 | 452349.6644295300846 | 0 | 0 | 2 |  |  |  |  | 76 | 76 | 86 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | ROB SMITH | MANAGER OF COMPLIANCE | rrsmith@nisource.com | 6148182110 | 6148182151 |  |  |  | ROB SMITH | MANAGER OF COMPLIANCE | 6148182110 | rrsmith@nisource.com | ON FEBRUARY 25, 2018, RICHLAND COUNTY 911 REPORTED A FIRE AND POSSIBLE EXPLOSION AT 613 FLEMING FALLS ROAD IN MANSFIELD, OHIO AT 12:33 AM TO COLUMBIA GAS OF OHIO, INC ("COLUMBIA"). COLUMBIA'S SERVICE TECHNICIAN WAS DISPATCHED AT 12:42 AM AND ARRIVED ON SITE AT 01:15 AM AND FOUND THAT GAS HAD BEEN SHUT OFF AT THE METER VALVE BY THE FIRE DEPARTMENT. ADDITIONAL COLUMBIA RESOURCES ARRIVED ON SITE AT 1:50 AM TO ASSIST IN THE RESPONSE TO THE INCIDENT. COLUMBIA EMPLOYEES SET UP A PERIMETER AND EVACUATED THE NEIGHBORING HOME AT 605 FLEMING FALLS WHERE NATURAL GAS READINGS WERE DISCOVERED IN THE BASEMENT. COLUMBIA VERIFIED THAT THE SYSTEM PRESSURE WAS WITHIN THE MAOP ESTABLISHED FOR THAT SYSTEM AND THAT ODORANT WAS COMPLIANT WITH STATE AND FEDERAL REQUIREMENTS. ELECTRIC METERS WERE REMOVED TO ELIMINATE SOURCES OF IGNITION AND COLUMBIA BEGAN TO SEARCH FOR LEAKAGE AND ENSURE SAFETY. THE NIGHT OF THE INCIDENT THERE WAS A TREMENDOUS AMOUNT OF RAIN THAT CAUSED THE SANITARY LIFT PUMPS TO FAIL AND MAY HAVE POTENTIALLY PUSHED A SLUG OF SEWER GAS INTO THE BASEMENT VIA FLOOR DRAINS THAT WERE FOUND TO BE TIED DIRECTLY TO THE SANITARY SEWER FOR 605 AND 613 FLEMING FALLS RD. THE EXPLOSION THAT OCCURRED APPEARS TO BE A LOW LEVEL EXPLOSION. COLUMBIA LOCATED AND REPAIRED A TOTAL OF FOUR LEAKS OF WHICH WE BELIEVE TO BE NON-CAUSAL. THE CLOSEST BEING APPROXIMATELY 290' AWAY AND THE FURTHEST BEING APPROXIMATELY 1300' AWAY FROM THE INCIDENT. THE SURFACE LEVEL OF THE SOUTH SIDE OF THE STREET IS APPROXIMATELY 12' LOWER THAN THE SURFACE LEVEL OF THE STREET IN FRONT OF THE INCIDENT SITE. COLUMBIA CREATED A TEMPORARY BYPASS TO KEEP CUSTOMERS IN SERVICE, ABANDONING APPROXIMATELY 775' OF BARE STEEL HIGH PRESSURE MAINLINE ON THE SOUTH SIDE OF THE STREET. COLUMBIA PRESSURE TESTED THE BARE STEEL MAIN ON THE SOUTH SIDE OF THE STREET ALONG WITH THE SERVICES (WITH NO DROP IN PRESSURE AT 76 PSIG) AND RAN A CAMERA INSIDE THEM TO ENSURE ALL SERVICE TEES WERE ACCOUNTED FOR AND TO LOOK FOR ANOMALIES. COLUMBIA TESTED APPROXIMATELY 448' OF HIGH DENSITY POLY ETHYLENE (HDPE) MAIN LINE AND 6 SERVICES ON THE NORTH SIDE OF THE STREET AND IT SUCCESSFULLY PASSED SEVERAL PRESSURE TESTS AT 76 PSIG (OPERATING PRESSURE), 15 INCHES WATER COLUMN AND 150 PSIG. IN ADDITION COLUMBIA TESTED APPROXIMATELY 1,175' OF HDPE MAIN LINE AND SERVICE ON THE STREET BEHIND INCIDENT SITE. AT 613 FLEMING FALLS RD., COLUMBIA PRESSURE TESTED THE SERVICE LINE AND CHECKED THE SERVICE REGULATOR FOR LOCK UP AND FLOW WITHOUT ISSUE AND NO LEAKAGE DETECTED. THE SERVICE LINE AT THE NEIGHBORING HOME (637 FLEMING FALLS RD) WAS ALSO TESTED AND FOUND TO BE LEAK FREE. COLUMBIA DID EXPLORATORY EXCAVATION AROUND THE AREA TO ENSURE CONDUITS DID NOT EXIST THAT COULD CONVEY MIGRATING GAS. COLUMBIA ALSO RAN A CAMERA IN THE SANITARY MAIN AND SEWER LATERALS TO ENSURE THAT A CROSS BORE DID NOT EXIST. UN-COLLAPSED STORM SEWERS WERE VIDEOED AS WELL TO ENSURE A CROSS BORE DID NOT EXIST. COLUMBIA WORKED WITH THE PUCO, STATE FIRE MARSHALL, A THIRD-PARTY CAUSE AND ORIGIN SPECIALIST, AND A GEOLOGIST TO DETERMINE A CAUSE. LABORATORY GAS ANALYSES AND OUR GEOLOGIST'S INTERPRETATION INDICATE THAT THE STRAY GAS SAMPLES HAD A COMPARABLE ISOTOPIC COMPOSITION AND MOLECULAR PROFILE, AND IS SIMILAR IN ORIGIN TO COLUMBIA'S PIPELINE GAS, HOWEVER, NATURALLY OCCURRING METHANE CONTAINING SIMILAR MOLECULAR AND ISOTOPIC PROFILE CANNOT BE COMPLETELY RULED OUT AS A POTENTIAL SOURCE. THE GEOLOGIST THEORIZES THAT GROUND WATER, IN COMBINATION WITH THE ABUNDANCE OF RAIN WATER, LIKELY CREATED CONDITIONS FAVORABLE FOR GAS MIGRATION TOWARD THE STRUCTURES AT 605 AND 613 FLEMING FALLS RD. COLUMBIA HAS DETERMINED THAT THE CAUSE OF THIS INCIDENT CANNOT BE FULLY ASCERTAINED. PLEASE CONSIDER THIS REPORT A FINAL REPORT. NOTE: UPDATED LATITUDE AND LONGITUDE 9-21-18
2025-03-31 10:13 | NO | NO | NO | 20180037 | 30178 | 2018-03-29 09:25 | SUPPLEMENTAL FINAL | 14330 | ORANGE & ROCKLAND UTILITY INC | ONE BLUE HILL PLAZA | PEARL RIVER | NY | 10965 | 2018-02-27 15:51 |  |  | 2018 | 21 THAMSEN DRIVE | STONY POINT | ROCKLAND | NY | 10980 | 41.2408 | -73.9868 | [9 empty] | 2018-02-28 08:12 | 1205411 |  | NATURAL GAS |  | 7.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2018-02-27 15:51 |  |  |  | 2018-02-27 16:03 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2014 | [8 empty] | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | MOTOR VEHICLE STRUCK THE METER SET, UNKNOWN INITIAL FAILURE"POSSIBLY CRUSHED", METER EVENTUALLY MELTED. | CLASS 2 LOCATION | 75000 | 86502.358062760725 | 600 | 692.0188645020858 | 3086 | 3559.283693089061298 | 0 | 0 |  |  | 28 | 28.26477541371158392434988179669030732861 |  | 0 | 78714 | 37613.5909762397279605295508274231678487 | 90781.9253957655836819243498817966903073 | 0 | 0 | 1 |  |  |  |  | 60 | 60 | 80 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DONALD HIGGINS | SECTION MANAGER GAS EMERGENCY RESPONSE | higginsd@oru.com | 845-577-3014 | 845-577-3166 |  |  |  | DONALD HIGGINS | SECTION MANAGER GAS EMERGENCY RESPONSE | 845-577-3014 | higginsd@oru.com | ON 2/27/18 AT APPROXIMATELY 1551 HOURS THE ROCKLAND COUNTY 911 CENTER NOTIFIED ORANGE & ROCKLAND UILITIES OF A MOTOR VEHICLE INTO A BUILDING, POSSIBLE GAS METER INVOLVED AT 21 THAMSEN DRIVE, STONY POINT, NY. O&R EMERGENCY RESPONSE ARRIVED AT 1603 HOURS, AT THAT TIME IT WAS VERIFIED THAT A VEHICLE OPERATED BY THE HOMEOWNER HELEN LAVELLE HAD BEEN DRIVEN INTO THE GAS METER SET AND THE HOUSE . UPON ARRIVAL THE VEHICLE, GAS METER SET AND THE HOUSE WERE ALL ON FIRE. AT 1613 HOURS THE RISER VALVE "WINGCOCK" ON THE GAS SERVICE RISER WAS SHUT OFF TO 21 THAMSEN AND THE FIRE WAS SUBSEQUENTLY EXTINGUISHED. THE 3/4 INCH GAS SERVICE TO THE HOUSE WAS RETIRED THAT EVENING. THERE WERE NO INJURIES OR EVACUATIONS ASSOCIATED WITH THE EVENT. PRELIMINARY ESTIMATES INDICATE DAMAGE IN EXCESS OF $50,000.00
2025-03-31 10:13 | NO | NO | NO | 20180038 | 30136 | 2018-04-01 22:02 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2018-03-02 16:04 |  |  | 2018 | 3400 OLD ALABAMA ROAD | JOHNS CREEK | FULTON | GA | 30022 | 34.0229 | -84.2617 | [9 empty] | 2018-03-02 18:00 | 1205665 |  | NATURAL GAS |  | 1926.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-03-02 16:08 |  |  |  | 2018-03-02 16:55 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 54 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1974 | [5 empty] | 6 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 43569 | 50250.949845818960367 | 21932 | 25295.596227099576276 | 0 | 0 |  |  | 3275 | 3305.969267139479905437352245862884160757 |  | 0 | 68776 | 34347.3287705097891299385342789598108747 | 78852.5153400580165484373522458628841608 | 2 | 0 | 2 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TRAFFIC SIGNAL | YES | 2138300576 |  |  | CONTRACT LOCATOR | YES | YES | 9 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICHARD R LONN | DIRECTOR COMPLIANCE AND PRM | (404) 584-3552 | rlonn@southernco.com | A 6-INCH STEEL MAIN WAS RUPTURED BY A CONTRACT CREW WHILE DIRECTIONAL DRILLING TO INSTALL A TRAFFIC SIGNAL CONDUIT. ONCE THE INCIDENT WAS MADE SAFE IT WAS IDENTIFIED THAT REPAIRS TO THE AFFECTED PIPELINE WOULD EXCEED THE $50,000 THRESHOLD FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. NOTIFICATION TO THE ONE-CALL CENTER WAS MADE WHERE THE MAIN WAS CORRECTLY LOCATED, HOWEVER, THE EXCAVATOR FAILED TO VERIFY LOCATION BY TEST-HOLE (POT-HOLING).
2025-03-31 10:13 | NO | NO | NO | 20180039 | 30152 | 2018-04-03 12:24 | SUPPLEMENTAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2018-03-05 14:45 |  |  | 2018 | 747 TIMMONS BLVD | RAPID CITY | PENNINGTON | SD | 57703 | 44.0776 | -103.1501 | [9 empty] | 2018-03-05 15:30 | 1205947 |  | NATURAL GAS |  | 38.65 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2018-03-05 14:45 |  |  |  | 2018-03-05 15:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2005 | [8 empty] | OTHER | REGULATOR BODY AND ASSOCIATED PIPING | [9 empty] | LEAK |  |  | OTHER | OTHER OUTSIDE FORCES | [5 empty] | CLASS 3 LOCATION | 45500 | 52478.0972247415065 | 2386 | 2751.928351169961198 | 4390 | 5063.27135860692777 | 0 | 0 |  |  | 173 | 174.635933806146572104018912529550827423 |  | 0 | 52449 | 25133.223776253783163271867612293144208 | 60467.9328683245420401040189125295508274 | 1 | 0 | 0 |  |  |  |  | 50 | 50 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JOSH SANDERS | MANAGER OF STANDARDS AND COMPLIANCE | josh.sanders@mdu.com | 701-222-7773 |  |  |  |  | JOSH SANDERS | MANAGER OF STANDARDS AND COMPLIANCE | 701-222-7773 | josh.sanders@mdu.com | ON 3/5/2018 AT 14:45 MST A TRAILER HAULING A CAR DETACHED FROM A PICKUP TRUCK HITCH LEFT THE ROAD WAY AND CROSSED THROUGH ROAD DITCH, ACROSS ROW BERM AND CRASHED INTO A GROCERY STORE LOCATED AT 747 TIMMONS BLVD. THE DETACHED TRAILER STRUCK THE BUILDING'S PAD MOUNTED ELECTRICAL TRANSFORMER AND SURROUNDING FENCE. THE FLYING DEBRIS FROM THE ACCIDENT DAMAGED THE ABOVE GROUND GAS METER SET RESULTING IN GAS RELEASE AND IGNITION OF A FIRE AT THE METER LOCATION ON THE SIDE OF THE BUILDING. AT APPROXIMATELY 15:00 MDU SERVICE TECHNICIAN ARRIVED ON SCENE THE SAME TIME AS RAPID CITY FIRE DEPARTMENT. MDU CONSTRUCTION PERSONNEL ALONG WITH MDU SUPERVISORS ARRIVED BETWEEN 15:15 AND 15:30. LOCAL SUPERVISION INFORMED MDU GENERAL OFFICE OF THE ACCIDENT AND IT WAS DECIDED THAT DUE TO THE RELEASE AND DAMAGE RESULTING IN POSSIBLY MORE THAN $50,000 OF DAMAGE THAT A REPORT WAS MADE TO NRC AT 15:30. GAS RELEASE WAS CONTROLLED AT 16:05 WHEN THE 4" MDPE MAIN THAT PROVIDED THE FEED TO THE STORE'S SERVICE LINE WAS SQUEEZED OFF. A FOLLOW UP REPORT WAS SUBMITTED TO THE NRC ON MARCH 6, 2018 AT 11:44. THE FOLLOW UP REPORT NUMBER IS 1206023. A NEW METER SET WAS CONSTRUCTED AND INSTALLED PRIOR TO SERVICE BEING COMPLETELY RESTORED TWO DAYS AFTER THE ACCIDENT ON 3/7/2018 AT 15:06 WHEN THE BUILDING'S NON-JURISDICTIONAL APPLIANCE PIPING DOWNSTREAM OF THE METER HAD BEEN REPAIRED AND INSPECTED BY THE LOCAL JURISDICTION. THIS EVENT RESULTED IN NO INJURIES OR FATALITIES, AND ONLY THE AFFECTED GROCERY STORE WAS TAKEN OUT OF SERVICE AS A RESULT OF THE ACCIDENT.
2025-03-31 10:13 | NO | YES | YES | 20180041 | 31608 | 2018-04-09 10:38 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2018-03-10 11:03 |  |  | 2018 | 2101 BEL AIR AVE | SAN JOSE | SANTA CLARA | CA | 95128 | 37.3314 | -121.9374 | [9 empty] | 2018-03-10 22:57 | 1206479 |  | NATURAL GAS |  | 459.08 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 1 | 2018-03-10 11:03 |  |  |  | 2018-03-10 11:22 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1951 | [5 empty] | 0.5 | UNKNOWN | UNKNOWN | COPPER | [10 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 594675 | 685877.197079629788525 | 15586 | 17976.343370215848798 | 26249 | 30274.671957192083607 | 0 | 0 |  |  | 1962 | 1980.553191489361702127659574468085106383 |  | 0 | 638472 | 305886.0157422882947651063829787234042553 | 736108.7655985270826321276595744680851064 | 0 | 0 | 1 |  |  |  |  | 57 | 57 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE IS NO SCADA AT THIS SITE, GAS CONTROL WAS NOTIFIED BY GAS DISPATCH. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | INTERNAL CORROSION | CORROSION | INTERNAL | CORROSION | INTERNAL | INTERNAL CORROSION | [32 empty] | GENERAL CORROSION | [5 empty] | YES | COPPER SULFIDATION DUE TO NORMAL SULFUR CONTENT IN NATURAL GAS |  | YES | [5 empty] | YES | AT COPPER SERVICE DOWNSTREAM OF TRANSITION FITTING BETWEEN STEEL TO COPPER | NO | NO | 2018-01-01 | NO | [227 empty] | ENZA BARBATO | PROGRAM MANAGER | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | MANAGER OF GAS OPS COMPLIANCE AND RISK | 925-786-0267 | gsr8@pge.com | ON MARCH 10, 2018 AT APPROXIMATELY 1103 HOURS, PG&E WAS NOTIFIED OF A STRUCTURE FIRE AT 2101 BEL AIR AVE IN SAN JOSE. THE GAS SERVICE REPRESENTATIVE (GSR) ARRIVED ON-SITE AT 1122 HOURS. PER THE FIRE DEPARTMENT, WITNESSES REPORTED AN EXPLOSION FOLLOWED BY A STRUCTURE FIRE. IT WAS REPORTED THAT THE FIRE MAY HAVE STARTED WHEN A CUSTOMER STRUCK A MATCH IN THE BATHROOM. AN INJURY WAS REPORTED AS MINOR BURNS. IT WAS LATER DETERMINED THAT THE INJURY NECESSITATED AN IN-PATIENT HOSPITALIZATION. ONCE THE FIRE WAS PUT OUT, THE GSR REQUESTED FOR LEAK SURVEY DUE TO RESIDUAL READS IN THE AREA. LEAK SURVEY DETECTED GAS NEXT DOOR (2109 BEL AIR AVE) AND AT THE STREET LOCATION. THE NEXT DOOR HOUSE'S GAS WAS SHUT OFF AND THE HOME WAS EVACUATED DURING THE INVESTIGATION. AT 1653 HOURS, THE INCIDENT WAS REPORTED TO THE CPUC DUE TO MEDIA AND SUSPECTED INVOLVEMENT OF NATURAL GAS IN THE VICINITY OF PG&E FACILITIES PG&E CREWS INVESTIGATED AND IDENTIFIED A LEAK AT THE STEEL TO COPPER TRANSITION FITTING FOR 2108 BEL AIR AVE. THE CREW ISOLATED THE LEAK AND STOPPED THE FLOW OF GAS BY 2051 HOURS. MEDIA, POLICE AND FIRE DEPARTMENT WERE REPORTED ON-SITE. AT 2245 HOURS, IT WAS DETERMINED THAT THERE WAS GAS MIGRATION TOWARD THE HOUSE IN THE AREA WHERE THE EXPLOSION OCCURRED. AT 2257 HOURS, THE INCIDENT WAS REPORTED TO THE DOT (#1206479) DUE TO AN UNINTENTIONAL RELEASE OF GAS AND ESTIMATED PROPERTY DAMAGES EXCEEDING $50K. ON 3/11/18 BY 1330 HOURS, THE CREW COMPLETED REPAIRS BY REPLACING THE ENTIRE SERVICE AT 2108 BEL AIR AVE. FOUR CUSTOMER'S GAS SERVICE WAS IMPACTED AS A RESULT OF THE INCIDENT. GAS SERVICE WAS RESTORED TO THE CUSTOMERS THAT WERE ABLE TO RECEIVE SERVICE.
2025-03-31 10:13 | NO | YES | YES | 20180042 | 35601 | 2018-04-12 16:42 | SUPPLEMENTAL FINAL | 20170 | UNION UTILITY DEPT, CITY OF | 101 SHARPE AVE. P.O. BOX 987 | UNION | SC | 29379 | 2018-04-11 01:30 | EASTERN | NO | 2018 | 101 TOSCHES CREEK CIRCLE | UNION | UNION | SC | 29379 | 34.7187 | -81.6379 |  |  |  | YES | [5 empty] | 2018-04-11 13:30 | 1209064 |  | NATURAL GAS |  | 2 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2018-04-11 01:35 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1.9 | NO | 15 | 2018-04-11 01:35 |  |  |  | 2018-04-11 01:50 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1996 |  | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | STEEL |  | OTHER | THREAD JOINT ABOVE GROUND | 0.128 | [6 empty] | LEAK |  |  | OTHER | VANDALISM-CRACK IN RISER | [5 empty] | CLASS 1 LOCATION | 5000 | 5766.823870850715 | 2842 | 3277.862688191546406 | 812 | 936.532196626156116 | 0 | 0 |  | 24 | 48 | 48.45390070921985815602836879432624113475 | 0 | 0 | 8702 | 4178.744153406587064907801418439716312057 | 10029.6726563776373801560283687943262411 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 30 | 60 | 192.619(A)(2) | 1996-07-31 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA DID NOT DETECT CHANGE IN GAS PRESSURE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [156 empty] | JOE F. NICHOLS | CITY ADMINISTRATOR | jnichols@cityofunion.org | [5 empty] | JOE F. NICHOLS | CITY ADMINISTRATOR | 864-429-1700 | jnichols@cityofunion.org | APRIL 11, 2018 AT 1:30 AM 911 DISPATCH CALLED WATER PLANT FOR FIRE AT DAYS INN AT TOSCHES CREEK CIRCLE, UNION, SC. AT 1:35AM PATRICK RUSSELL, GAS STANDBY PERSONNEL ARRIVED AT SCENE AND FOUND FIRE AT GAS METER. FIRE DEPARTMENT WAS ALREADY ON THE SCENE. FIRE WAS CONTAINED AT 1:40 AM AND FIRE EXTINGUISHED AROUND 1:55 AM. ADDITIONAL GAS EMPLOYEES WERE DISPATCHED AT 1:41 AM TO ASSIST (MAXIE SANDERS, BRYAN WEST, CHAD FERRELL, AND DUSTIN AUSTIN). 15 DAYS INN OCCUPANTS WERE EVACUATED APPROXIMATELY AT 1:40 AM. GAS RISER WAS BENT BACK AND GAS FLOW WAS RESTRICTED AND COMPLETELY RESTRICTED AT 2:15AM. JOHNNY EUSTACE WITH SC ORS WAS NOTIFIED BY PHONE OF INCIDENT AT APPROXIMATELY 2:30AM. AT THIS TIME WE WERE NOT AWARE OF ANY MEDICAL ATTENTION FOR INJURIES. DAYS INN OCCUPANTS WERE ALLOWED TO RETURN APPROXIMATELY AT 3:00AM. GAS PERSONNEL NOTICED THAT PSO HAD A SUSPECT ON THE SCENE IN PATROL CAR IN HANDCUFFS. AT APPROXIMATELY 4:30AM GAS PERSONNEL REVIEWED SECURITY VIDEO AT DAYS INN THAT SHOWS A PERSON INTENTIONALLY KICKING GAS METER UNTIL GAS RISER CRACKED RELEASING GAS AT BROKEN THREADS. GAS METER, RISER, REGULATOR, AND PIPING WERE REPLACED AND GAS SERVICE TO BUILDING WAS RESTORED AT 5:15AM. GAS PERSONNEL WAS NOTIFIED THAT SUSPECT WAS LATER TAKEN TO AUGUSTA BURN CENTER AND ORS ADVISED NRC REPORTING WAS REQUIRED. REPORT WAS FILED AT 1:30PM 04-11-2018
2025-03-31 10:13 | NO | YES | NO | 20180043 | 31394 | 2018-04-19 13:51 | SUPPLEMENTAL FINAL | 18308 | NV ENERGY | PO BOX 10100 | RENO WASHOE | NV | 89520 | 2018-03-22 20:17 |  |  | 2018 | 624 EUREKA AVENUE | RENO | WASHOE | NV | 89512 | 39.5349 | -119.8049 | [9 empty] | 2018-03-22 22:49 | 1207485 |  | NATURAL GAS |  | 54 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 30 | 2018-03-22 20:25 |  |  |  | 2018-03-22 21:02 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 20 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2018 | [5 empty] | 0.75 | ASTM A197 & ASTM A53 | UNKNOWN | OTHER | BLACK IRON | [9 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 322526 | 371990.127153999541218 | 20 | 23.06729548340286 | 25646 | 29579.192998367487378 | 4500 | 5190.1414837656435 | COMPENSATION FOR EVACUEES |  | 261 | 263.46808510638297872340425531914893617 |  | 0 | 352953 | 168720.8469304662270049361702127659574468 | 407045.9970167224579347234042553191489362 | 0 | 0 | 1 |  |  |  |  | 37 | 37 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | NATURAL GAS | YES | 802900026 |  |  | CONTRACT LOCATOR | YES | YES | 14 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | JAY WIGGINS | MANAGER GAS OPS AND COMPLIANCE | jwiggins@nvenergy.com | 775-834-7850 |  |  |  |  | JAY WIGGINS | MANAGER GAS OPS AND COMPLIANCE | 775-834-7850 | jwiggins@nvenergy.com | ON MARCH 22, 2018 AT 20:17, THE RENO FIRE DEPARTMENT WAS NOTIFIED OF A BUILDING FIRE AT 624 EUREKA AVENUE IN RENO, NEVADA. AT 20:25 NV ENERGY (NVE) WAS CONTACTED BY THE CITY OF RENO PUBLIC SAFETY DISPATCH NOTIFYING OF A "WORKING FIRE" AT 624 EUREKA AVENUE IN RENO, NEVADA. NVE GAS DISPATCH SENDS GAS SERVICEMEN TO INVESTIGATE. AT 20:51 THE CITY OF RENO PUBLIC SAFETY DISPATCH CONTACTED NVE AGAIN TO REPORT THAT THERE WAS AN EXPLOSION AT THIS LOCATION, POSSIBLY FROM THE FURNACE. AT 21:02 THE FIRST NVE PERSONNEL ARRIVE AT THE SITE AND FOUND THE HOME AT 624 EUREKA AVE DAMAGED BY WHAT APPEARED TO BE A GAS EXPLOSION WITH INDICATIONS OF UNDERGROUND GAS READINGS. RENO FIRE DEPARTMENT AND NVE PERSONNEL EVACUATE THE NEIGHBORHOOD AND MONITOR GAS CONCENTRATIONS WHILE OTHER NVE PERSONNEL EXPOSE THE SERVICE TEE AND SECURE THE GAS LEAK. THE LEAK OCCURRED AT THE THREADED JOINT BETWEEN A 3/4" BLACK IRON PIPE NIPPLE AND A 3/4" BLACK IRON 90 DEGREE ELBOW AT THE SERVICE TEE CONNECTION TO 614 EUREKA AVENUE. BASED UPON THE RENO FIRE DEPARTMENT INCIDENT REPORT, NATURAL GAS LEAKING FROM THE SERVICE TEE APPEARS TO HAVE TRAVELED THROUGH A SERVICE TRENCH INTO THE BASEMENT OF 624 EUREKA. THE LEAKING GAS WAS IGNITED IN THE BASEMENT BY THE FURNACE, EXPLODED, AND DAMAGED THE HOME. TWO INDIVIDUALS WERE IN THE RESIDENCE AT THE TIME OF THE EXPLOSION BUT NO INJURIES WERE SUSTAINED. THE CAUSE OF THE FAILURE IS STILL UNDER INVESTIGATION AND A SUPPLEMENTAL REPORT WILL BE FILED WHEN THE CAUSE IS DETERMINED. AT 22:36 THE NVE DUTY SUPERVISOR ON SCENE DETERMINED THAT THE PROPERTY DAMAGE COSTS WOULD EXCEED $50,000. THE INITIAL NOTIFICATION TO THE NATIONAL RESPONSE CENTER (NRC) WAS MADE AT 22:49 AND WAS GIVEN NRC INCIDENT REPORT # 1207485. NVE PROVIDED AN UPDATE TO THE NRC ON MARCH 23, 2018 AT 15:44 AND WAS GIVEN NRC INCIDENT REPORT # 1207546. SUPPLEMENTAL UPDATE: FURTHER ANALYSIS HAS DETERMINED THAT THE PIPE-TO-ELBOW JOINT FAILED DUE TO OVERLOAD FROM AN EXTERNAL BENDING LOAD AND NOT DUE TO A MATERIAL OR MANUFACTURING DEFECT ASSOCIATED WITH THE PIPES OR FITTINGS. THE EXTERNAL BENDING LOAD AT THE FAILED PIPE-TO-ELBOW JOINT OCCURRED AS A RESULT OF LOADING IMPARTED TO THIS JOINT DURING COMPACTION AROUND THE TEMPORARY SERVICE CONNECTION. NV ENERGY'S CONTRACTOR WAS PERFORMING BACKFILL AND COMPACTION ACTIVITIES ON THIS TEMPORARY SERVICE CONNECTION ONE DAY PRIOR TO THE INCIDENT OCCURRING. FINAL UPDATE: ANALYSIS HAS CONCLUDED AND THE INCIDENT WAS CAUSED BY A LEAK FROM A CRACK IN THE BLACK IRON PIPE USED FOR THE TEMPORARY SERVICE CONNECTION FOR THE NEIGHBORING PROPERTY 614 EUREKA AVENUE. THE GAS MIGRATED INTO THE BASEMENT OF THE INCIDENT HOUSE WHERE IT FOUND AN IGNITION SOURCE, MOST LIKELY THE HOUSE FURNACE. THE DIRECT CAUSE OF THE CRACK IN THE PIPE WAS MECHANICAL OVERLOADING OF THE HORIZONTAL SECTION OF THE TEMPORARY SERVICE CONNECTION. THE MECHANICAL OVERLOADING WAS LIKELY CAUSED DURING COMPACTION OF SAND AROUND THE TEMPORARY SERVICE CONNECTION, DUE TO INSUFFICIENT COVER (SAND ABOVE THE PIPE) DURING COMPACTION.
2025-03-31 10:13 | NO | YES | NO | 20180045 | 31451 | 2018-04-26 13:26 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2018-03-28 14:53 |  |  | 2018 | 56 SOUTH MCDONNELL RD | SOUTH SAN FRANCISCO | SAN MATEO | CA | 94030 | 37.6133 | -122.3924 | [9 empty] | 2018-04-17 10:18 | 1209558 |  | NATURAL GAS |  | 531 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 1 | 2018-03-28 14:53 |  |  |  | 2018-03-28 15:10 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1996 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 99000 | 114183.112642844157 | 11000 | 12687.012515871573 | 0 | 0 |  |  | 1593 | 1608.06382978723404255319148936170212766 |  | 0 | 111593 | 54033.3540258808417021276595744680851064 | 128478.1889885029640425531914893617021277 | 1 | 0 | 0 |  |  |  |  | 46 | 46 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO SCADA AT THIS LOCATION. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE BUSINESS | [10 empty] | UNKNOWN/OTHER | BACKHOE/TRACKHOE | UNKNOWN/OTHER | YES | 805201511 | 811 |  | UTILITY OWNER | YES | YES | 11 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ENZA BARBATO | REGULATORY COMPLIANCE | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | MANAGER OF REGULATORY COMPLIANCE | 925-786-0267 | gsr8@pge.com | ON WEDNESDAY, MARCH 28, 2018 AT 1453 HOURS, PG&E WAS NOTIFIED OF A THIRD PARTY DIG IN AT 56 SOUTH MCDONNELL RD, IN THE CITY OF SOUTH SAN FRANCISCO. A THIRD PARTY CONTRACTOR, TEICHERT CONSTRUCTION, STRUCK A 6' STEEL MAIN WITH A BACKHOE. THERE WAS A VALID USA TICKET NUMBER (X805201511) AND THE GAS LINE WAS LOCATED & DAY-LIGHTED, BUT THE EXCAVATOR MISTAKENLY BELIEVED IT TO BE AN ABANDONED WATER MAIN AND HAD INSTRUCTED THE EXCAVATION CREW TO REMOVE IT. WHILE EXCAVATING TO REMOVE THE GAS MAIN STUB, THE STUB WAS DAMAGED CAUSING AN UNINTENTIONAL RELEASE OF GAS. THE REPAIR CREW ARRIVED ON-SITE AT 1510 HOURS AND STOPPED THE FLOW OF GAS BY CLOSING THE 3 VALVES BY 1638 HOURS. THE CREW DEACTIVATED 29 FEET OF 6" STEEL MAIN AND WELDED ON (2) 6" DEAD END CAPS. ON 3/29/18, THE CREW INSTALLED 40' OF 6" STEEL MAIN AND TIED IT BACK INTO SERVICE. POLICE AND FIRE DEPARTMENT WERE REPORTED ON SITE. SERVICE WAS IMPACTED TO 1 CUSTOMER. THERE WERE NO INJURIES, NO FATALITIES, AND NO IGNITION ASSOCIATED WITH THIS INCIDENT. THIS INCIDENT IS BEING REPORTED DUE TO THE UNINTENTIONAL RELEASE OF GAS AND PRESENCE OF CHANNEL 7 MEDIA HELICOPTER OBSERVED AT 1657 HOURS. ON 4/17/18 AT 1003 HOURS, PG&E DETERMINED THAT THE ESTIMATED REPAIR COSTS EXCEEDED THE >50K CRITERIA AND REPORTED THE INCIDENT TO THE DOT ON 4/17/18 AT 1016 HOURS (DOT REPORT NUMBER 1209558). A 48 HOUR UPDATE WAS REPORTED TO THE DOT ON 4/18/18 AT 0748 HOURS (DOT REPORT NUMBER 1209623).
2025-03-31 10:13 | NO | YES | NO | 20180046 | 30969 | 2018-04-27 15:48 | SUPPLEMENTAL FINAL | 11800 | ATMOS ENERGY CORPORATION - LOUISIANA | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-03-28 12:08 |  |  | 2018 | 13505 US HWY 90 | BOUTTE | ST CHARLES | LA | 70039 | 29.9006 | -90.3881 | [9 empty] | 2018-03-28 13:55 | 1207899 |  | NATURAL GAS |  | 9.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 5 | 2018-03-28 11:07 |  |  |  | 2018-03-28 11:50 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 1.3 | 4.1 | [7 empty] | CLASS 3 LOCATION | 450000 | 519014.14837656435 | 1500 | 1730.0471612552145 | 5500 | 6343.5062579357865 | 0 | 0 |  |  | 4547 | 4589.997635933806146572104018912529550827 |  | 0 | 461547 | 222549.9345604352329739952718676122931442 | 531677.6994316891571465721040189125295508 | 1 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 5 | 0 | YES | 5 | 1 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | BORING | NATURAL GAS | YES | 180147050 | LOUISIANA 811 |  | CONTRACT LOCATOR | NO | YES | 1 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO UNLOCATABLE FACILITY | [170 empty] | DANIEL WAGUESPACK | COMPLIANCE MANAGER | daniel.waguespack@atmosenergy.com | 504 849 4363 |  |  |  |  | DANIEL WAGUESPACK | COMPLIANCE MANAGER | 504 849 4363 | daniel.waguespack@atmosenergy.com | ON MARCH 28, 2018 AN ATMOS ENERGY CONTRACTOR, WAS INSTALLING A NEW SERVICE LINE BY DIRECTIONAL BORE WHEN IT STRUCK AN EXISTING 1" POLYETHYLENE (PE) PIPELINE SERVING A DOMINO'S PIZZA RESTAURANT LOCATED AT 13505 US HIGHWAY 90, BOUTTE, LA. THE CONTRACTOR HAD BEEN UNABLE TO LOCATE THE EXISTING 1" SERVICE LINE DUE TO A TRACER WIRE THAT WAS MISSING OR BROKEN. THE DAMAGE OCCURRED AT 11:07 AM UNDERNEATH A PAVED PARKING LOT ADJACENT TO THE RESTAURANT. ALL OCCUPANTS OF THE RESTAURANT WERE PROMPTLY EVACUATED. AN ATMOS ENERGY CREW WAS WORKING TO SQUEEZE OFF THE DAMAGED PIPELINE WHEN A FLASH OCCURRED IN THE FRONT PORTION OF THE RESTAURANT AT APPROXIMATELY 12:08 PM. THERE WERE NO INJURIES. THE DAMAGED SERVICE LINE WAS ISOLATED AND GAS WAS SHUT OFF AT 12:18 PM.
2025-03-31 10:13 | NO | NO | NO | 20180047 | 30387 | 2018-05-02 11:05 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2018-04-06 11:27 |  |  | 2018 | 32ND ST AND 113TH WEST AVENUE | SAND SPRINGS | TULSA | OK | 74063 | 36.1176 | -96.1191 | [9 empty] | 2018-04-07 08:10 | 1208724 |  | NATURAL GAS |  | 5292 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-04-06 11:27 |  |  |  | 2018-04-06 11:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1952 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.33 | [6 empty] | MECHANICAL PUNCTURE | 3 | 2 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 4731 | 5456.568746598946533 | 16818 | 19397.288771993464974 | 0 | 0 |  |  | 20918 | 21115.8061465721040189125295508274231678 |  | 0 | 42467 | 29827.0793574525627996122931442080378251 | 45969.6636651645155259125295508274231678 | 1 | 0 | 19 |  |  |  |  | 40 | 40 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | DEVELOPER | UNKNOWN/OTHER | ROAD WORK | NO | [5 empty] | YES | 5 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RYAN OWENS | ENGINEER | ryan.owen@onegas.com | 4054642196 |  |  |  |  | SEAN BLAIR | DIRECTOR OF ENGINEERING | 4055302560 | sean.blair@onegas.com | A&A ASPHALT DAMAGED ONG'S 8" STEEL MAIN WHILE GRADING THE SURFACE DURING ROAD CONSTRUCTION. SERVICE WAS RESTORED THE NEXT DAY. AMENDMENT MADE FROM THE REPORT SUBMITTED ON 05/02/18.
2025-03-31 10:13 | NO | NO | NO | 20180048 | 31452 | 2018-05-04 15:03 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2018-04-05 09:55 |  |  | 2018 | 101 PANORAMIC WAY | BERKELEY | ALAMEDA | CA | 94704 | 37.8692 | -122.2488 | [9 empty] | 2018-04-05 11:44 | 1208561 |  | NATURAL GAS |  | 83.67 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-04-05 09:55 |  |  |  | 2018-04-05 10:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 3 | TR-418 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.304 |  | 418 | MECHANICAL PUNCTURE | 3.7 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 42500 | 49018.0029022310775 | 36500 | 42097.8142572102195 | 0 | 0 |  |  | 252 | 254.382978723404255319148936170212765957 |  | 0 | 79252 | 37972.7579299991422127659574468085106383 | 91370.200138164701255319148936170212766 | 0 | 0 | 220 |  |  |  |  | 20 | 20 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | MUNICIPALITY | UNKNOWN/OTHER | UNKNOWN/OTHER | YES | 735500270 | 811 |  | UTILITY OWNER | YES | YES | 11 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | ENZA BARBATO | REGULATORY COMPLIANCE | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | REGULATORY COMPLIANCE MANAGER | 925-786-0267 | gsr8@pge.com | ON THURSDAY 4/5/18 AT APPROXIMATELY 0955 HOURS, PG&E WAS NOTIFIED OF A DIG-IN AT 101 PANORAMIC WAY, BERKELEY. EBMUD STRUCK AND DAMAGED A 3" PLASTIC MAIN . ALTHOUGH EBMUD HAD A VALID USA TICKET (W735500270) TO PERFORM EXCAVATION AT THE JOBSITE, THE FACILITY WHICH WAS STRUCK AND DAMAGED WAS NOT PROPERLY MARKED PURSUANT TO THE USA TICKET . AN EMERGENCY SHUTDOWN ZONE WAS UTILIZED TO ISOLATE THE GAS IN THE DISTRIBUTION SYSTEM. PG&E ARRIVED ON SITE AT 1035 HOURS. M&C PERSONNEL STOPPED THE FLOW OF GAS AT 1111 HOURS BY USING A SHUT-OFF VALVE. REPAIR CREWS REPLACED 4' OF 3" PLASTIC. THE FIRE DEPARTMENT WAS REPORTED ON SITE. THERE WAS APPROXIMATELY 220 CUSTOMER IMPACTED. ALL BUT 29 CGI CUSTOMERS HAVE BEEN RESTORED BY 4/5/18 AT 2300 HOURS. THERE WERE NO INJURIES, FATALITIES OR IGNITION ASSOCIATED WITH THIS INCIDENT. THIS INCIDENT WAS REPORTED TO THE DOT (#1208561) AND THE CPUC AS IT IS DEEMED A SIGNIFICANT EVENT IN THE JUDGMENT OF THE OPERATOR DUE TO THE LARGE NUMBER OF AFFECTED CUSTOMERS. A 48 HOUR UPDATE WAS CALLED INTO THE DOT ON 4/6/18 AT 1434 HOURS (#1208690).
2025-03-31 10:13 | NO | NO | NO | 20180049 | 36313 | 2018-05-07 16:55 | SUPPLEMENTAL FINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-04-09 14:05 | CENTRAL | YES | 2018 | #30 VISTA CREST COURT | ODESSA | ECTOR | TX | 79762 | 31.8833 | -102.3017 | [5 empty] | YES |  |  |  | 2018-04-09 16:15 | 1208894 |  | NATURAL GAS |  | 42 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2018-04-09 13:52 | ALLOWED TO BURN OUT |  | 42 | YES | 1 | 2018-04-09 13:52 | NO |  |  | 2018-04-09 14:13 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 30 | NO | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2005 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.75 | UNKNOWN | DRISCO PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.7 | 0.7 | [7 empty] | CLASS 2 LOCATION | 3312 | 3819.944132051513616 | 1800 | 2076.0565935062574 | 1200 | 1384.0377290041716 | 0 | 0 |  | 4.7619 | 200 | 201.891252955082742316784869976359338061 | 0 | 0 | 6512 | 3201.93481901150281978250591016548463357 | 7481.929707517025358316784869976359338061 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 35 | 35 | 60 | 192.619(A)(2) | 2005-06-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 580928120 | LONE STAR 811 |  | CONTRACT LOCATOR | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | MIKE CULP | COMPLIANCE MANAGER | mike.culp@atmosenergy.com | 8062206849 |  | MIKE CULP | mike.culp@atmosenergy.com | 8062206849 | MIKE CULP | COMPLIANCE MANAGER | 8062206849 | mike.culp@atmosenergy.com | AT&T CONTRACTOR INSTALLING PHONE CABLE BY DIRECTIONAL BORE HIT A GAS SERVICE LINE UNDER A CONCRETE DRIVEWAY. THE GAS MAIN IN THE AREA WAS MARKED BUT THE SERVICE LINE THAT WAS DAMAGED WAS NOT MARKED BY THE ATMOS LOCATE CONTRACTOR. GAS MIGRATED INTO THE ADJACENT HOUSE AND AT APPROXIMATELY 14:40 CAUSED A SMALL EXPLOSION INSIDE THE HOUSE IN THE GARAGE AREA. ONE PERSON WAS IN THE HOUSE BUT WAS NOT INJURED. DAMAGE TO SOME SHEET ROCK WALLS AND CEILINGS OCCURRED. HEATH CONSULTANTS, THE ATMOS ENERGY LOCATE CONTRACTOR COMPLETED AN INVESTIGATION OF THE INCIDENT AND FOUND THAT SOME SERVICE LINES IN THE AREA REQUESTED TO BE LOCATED WERE NOT MARKED. THEY FOUND THEIR TECHNICIAN DID NOT FOLLOW THEIR COMPANY PROCEDURES AND TERMINATED HIS EMPLOYMENT. THIS EMPLOYEE WAS NOT DRUG AND ALCOHOL TESTED AS THE COMPLETED WORK HAPPENED OVER A WEEK BEFORE THE INCIDENT. HEATH HAS COMPLETED A SAFETY REVIEW WITH THEIR EMPLOYEES SERVING THE ATMOS WTX DIVISION WHICH INCLUDED A REVIEW OF THERE PROCEDURES. THEY ALSO COMMITTED TO ADDING THIS TO THEIR SAFETY MEETING TOPICS. THE NRC NUMBER FOR THE 48 HOUR RESPONSE IS 1209053. NOTE: DATE OF MOST RECENT SURVEY WAS ON 12/01/2017, THIS DATE ENTRY CONVERTS TO 0012 ON THE PHMSA SITE, REPORTED TO TANYA DAVIS ON 6/21/2017. PDF COPY OF ACTUAL REPAIR COST BY STAR INSURANCE CLAIM SERVICE WAS EMAILED ON 5-25-2018 TO THE FOLLOWING INDIVIDUALS: BRIAN E. PIERZINA, P.E. SR. ACCIDENT INVESTIGATOR ACCIDENT INVESTIGATION DIVISION US DOT/PHMSA STEPHANIE WEIDMAN; TEXAS RAILROAD COMMISSION ACCIDENT COORDINATOR SENT EMAIL ON 6-21-2017 PDF COPY OF UPDATED REPORT TO LARRY SNELSON AND TO RRC SAFETY ADDRESS SAFETY@RRC.TEXAS.GOV UPDATED SUBPART G3 QUESTION 1. DATE OF MOST RECENT LEAK SURVEY CONDUCTED ON 12-2-2017
2025-03-31 10:13 | NO | YES | YES | 20180050 | 31172 | 2018-05-07 18:08 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5420 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-04-07 13:00 |  |  | 2018 | 433 MYRTLE DR. | HURST | TARRANT | TX | 76053 | 32.8157 | -97.1777 | [9 empty] | 2018-04-07 15:41 | 1208763 |  | NATURAL GAS |  | 47.9 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | YES | 3 | 2018-04-07 13:18 |  |  |  | 2018-04-07 14:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | A VEHICLE STRUCK THE METER AND RISER, AND BECAME LODGED ON TOP OF THE METER. THE METER SET WAS BROKEN AND GAS ESCAPED RESULTING IN A FIRE. THE FIRE BURNED FOR 2 HOURS, MELTING THE METER, REGULATOR AND RISER. DUE TO THE DAMAGE AND THE AMOUNT OF TIME THE METER SET WAS UNDER FIRE, THERE IS NO WAY TO DETERMINE IF THE SOURCE OF THE ESCAPING GAS WAS AT THE RISER BELOW GROUND OR A BROKEN REGULATOR. | CLASS 3 LOCATION | 223128 | 257347.975331035667304 | 3156 | 3640.019227280971308 | 100 | 115.3364774170143 | 0 | 0 |  |  | 298 | 300.817966903073286052009456264775413712 |  | 0 | 226682 | 108419.443105250130709635933806146572104 | 261404.1490026367261980520094562647754137 | 0 | 0 | 1 |  |  |  |  | 37 | 37 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE CAUSED BY 3RD PARTY | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DAVID DRAPER | OPERATIONS SUPERVISOR | david.draper@atmosenergy.com | 214-415-0482 | 817-685-1295 |  |  |  | MARLO SUTTON | DIRECTOR REGULATORY AND COMPLIANCE | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT NO. 1208878 ON SATURDAY, APRIL 7, 2018, AT APPROXIMATELY 1300 HOURS, A VEHICLE LEFT THE ROADWAY AND STRUCK THE HOUSE AT 433 MYRTLE DR. IN HURST, TX, DAMAGING THE METER SET LOCATED ON THE HOUSE WHICH CAUSED THE UNCONTROLLED ESCAPE OF NATURAL GAS. AS THE METER WAS LOCATED DIRECTLY ON THE HOUSE AND THUS SIGNIFICANTLY AWAY FROM ANY ROADWAY, THIS WAS NOT "VEHICULAR DAMAGE THAT MAY BE ANTICIPATED" AS DESCRIBED IN SECTION 192.353. THE HOUSE IGNITED, CAUSING EXTENSIVE DAMAGE. AT 1318 HOURS, THE INITIAL CALL WAS MADE TO ATMOS ENERGY TO REPORT A GAS LEAK/FIRE. AT 1334 HOURS AN ATMOS ENERGY TECHNICIAN WAS ENROUTE, AND ARRIVED ONSITE AT 1400 HOURS. THE TECHNICIAN IMMEDIATELY BEGAN AN INVESTIGATION TO MAKE SURE THE AREA WAS SAFE AND THE RELEASE OF GAS WAS LOCALIZED TO THE DAMAGED PIPE. THERE WERE THREE PEOPLE IN THE HOUSE WHEN THE GAS IGNITED AND ALL WERE TAKEN TO THE HOSPITAL. ONE PERSON WAS TREATED AND RELEASED AND THE OTHER TWO WERE ADMITTED AND TREATED FOR BURNS. AT 1530 HOURS, AFTER EXPOSING THE PROPERTY STOP, THE CONSTRUCTION CREW WAS ABLE TO SHUT THE VALVE AND ELIMINATE THE SOURCE OF GAS, CAUSING THE FIRE TO SUBSIDE.
2025-03-31 10:13 | NO | YES | NO | 20180051 | 30491 | 2018-05-10 12:48 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2018-04-10 08:35 |  |  | 2018 | 12445 HIGHWAY 50 | SALIDA | CHAFFEE | CO | 81201 | 38.5215 | -106.1062 | [9 empty] | 2018-04-10 11:23 | 1208951 |  | NATURAL GAS |  | 85 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2018-04-10 08:35 |  |  |  | 2018-04-10 08:35 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 40 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1 | UNKNOWN | UNKNOWN | STEEL |  | FURNACE BUTT WELDED | FURNACE BUTT WELD | 0.166 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 0.6 | 0.1 |  | CLASS 2 LOCATION | 0 | 0 | 9774 | 11272.987302738977682 | 15068 | 17378.900417195714724 | 300000 | 346009.4322510429 | OUTAGE RESTORATION |  | 261 | 263.46808510638297872340425531914893617 |  | 0 | 325103 | 155417.2055373952932049361702127659574468 | 374924.7880560839753847234042553191489362 | 456 | 0 | 3461 |  |  |  |  | 493 | 505 | 550 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EMPLOYEE WAS ON SITE AT TIME OF INCIDENT. CONTROLLER MERELY CONFIRMED AND MONITORED CONDITIONS. | [12 empty] | YES | 1 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | OTHER | BRITTLE FRACTURE | [36 empty] | YES | DYNAMIC LOADING |  | YES |  |  |  | OTHER | UNEXPECTED BRITTLE FAILURE UNDER NORMAL SERVICE CONDIITONS | NO | [86 empty] | MIKE NOONE | SENIOR ENGINEER | michael.j.noone@xcelenergy.com | 303-571-3610 |  |  |  |  | MARK NOLAN | PRINCIPAL ENGINEER | 303-571-3931 | mark.nolan@xcelenergy.com | ON 4/10/18 DURING THE ANNUAL VALVE INSPECTION OF HFV-40247 THE OPERATOR FOUND NATURAL GAS READINGS IN THE VALVE BOX. DURING REPAIR EFFORTS THE THREADED SERVICE PIPE FAILED AT THE INLET TO THE VALVE. BASED ON METALLURGICAL AND FAILURE ANALYSIS BY THIRD PARTY LABORATORY, THE FAILURE SURFACE EXHIBITS SIGNS CONSISTENT WITH A BRITTLE FRACTURE. DYNAMIC LOADING IS SUSPECTED AS A POSSIBLE CAUSE, BUT IS NOT CONCLUSIVE. HOWEVER, BASED ON PRELIMINARY INVESTIGATION THE FAILURE IS NOT BELIEVED TO BE A RESULT OF DIRECT CONTACT WITH EXCAVATION EQUIPMENT. INSTALLATION STRESS MAY BE A CONTRIBUTING FACTOR, AS THE CONNECTION FAILED WHEN SOIL WAS REMOVED FROM AROUND THE VALVE AND SERVICE LINE AND COULD HAVE RESULTED IN SUDDEN MOVEMENT.
2025-03-31 10:13 | NO | YES | NO | 20180052 | 31422 | 2018-05-10 20:04 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2018-04-10 12:11 |  |  | 2018 | INTERSECTION OF TOPANGA CYN BLVD & POEMA PL | CHATSWORTH | LOS ANGELES | CA | 90290 | 34.2785 | -118.6044 | [9 empty] | 2018-04-12 10:30 | 1209161 |  | NATURAL GAS |  | 193 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-04-10 12:11 |  |  |  | 2018-04-10 12:31 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 40 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1987 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 4 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 221696 | 255696.356974424022528 | 200 | 230.6729548340286 | 0 | 0 |  |  | 1158 | 1168.950354609929078014184397163120567376 |  | 0 | 223054 | 107078.6477172589677819007092198581560284 | 257095.9802838679802060141843971631205674 | 0 | 0 | 429 |  |  |  |  | 40 | 40 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 18086013 | DIGALERT |  | UTILITY OWNER | YES | YES | 26 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | BRYON WALSH | PIPELINE SAFETY AND COMPLIANCE ADVISOR | bwalsh@semprautilities.com | 619-992-1473 |  |  |  |  | BRYON WALSH | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 619-992-1473 | bwalsh@semprautilities.com | ON APRIL 10, 2018, A THIRD-PARTY CONTRACTOR STRUCK A 6-INCH GAS STEEL DISTRIBUTION LINE WHILE PERFORMING TRENCHING FOR A NEW SEWER LINE. THIS RESULTED IN AN ESCAPE OF GAS. CREW RESPONDED AND WAS ABLE TO CONTROL THE GAS THROUGH CLOSING A VALVE. THERE WERE NO INJURIES THAT RESULTED FROM THIS INCIDENT. INVESTIGATION SHOWED THAT PRIOR TO THE INCIDENT, THE THIRD-PARTY CONTRACTOR HAD A USA TICKET AND THE LINE WAS PROPERLY MARKED BY THE UTILITY OWNER. AT THE TIME OF THE INCIDENT, THE THIRD-PARTY CONTRACTOR DID HAVE A VALID USA TICKET FOR THE EXCAVATION ACTIVITIES PERFORMED. IN ADDITION, THE THIRD-PARTY CONTRACTOR FAILED TO POT HOLE THE FACILITIES BY HAND. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO ESTIMATED DAMAGE AMOUNT EXCEEDING $50,000. ON 05/23/2018, CHANGED THE NOTIFICATION TIME (PART A) TO THE NRC FROM 1330 TO 1030. FOR ANY FURTHER QUESTIONS, CONTACT BRYON WALSH-(619) 992-1473. FINAL REPORT BOX CHECKED
2025-03-31 10:13 | NO | YES | YES | 20180053 | 32422 | 2018-05-15 17:57 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-04-15 17:30 |  |  | 2018 | INTERSECTION OF DITTO AVE. AND DUGAN ST. | ARLINGTON | TARRANT | TX | 76014 | 32.734 | -97.0963 | [9 empty] | 2018-04-15 18:59 | 1209422 |  | NATURAL GAS |  | 46 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2018-04-15 15:26 |  |  |  | 2018-04-15 16:02 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 29 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1981 | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 150000 | 173004.71612552145 | 13143 | 15158.673226918189449 | 7010 | 8085.08706693270243 | 0 | 0 |  |  | 286 | 288.704491725768321513002364066193853428 |  | 0 | 170439 | 81547.301734048835353408983451536643026 | 196537.1809110981102005130023640661938534 | 0 | 0 | 14 |  |  |  |  | 24 | 24 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE BY 3RD PARTY | [12 empty] | YES | 4 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | IGNITION SOURCE INTRODUCED INTO HAZARDOUS ENVIRONMENT |  |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | LYNN MILLER | OPERATIONS SUPERVISOR | lynn.miller@atmosenergy.com | 469-261-2037 | 817-375-7979 |  |  |  | MARLO SUTTON | DIRECTOR REGULATORY AND COMPLIANCE | 214-206-2033 | marlo.sutton@atmosenergy.com | 48 HR. NRC REPORT NO. 1209590 AT 3:26 PM ON APRIL 15, 2018, ATMOS ENERGY RECEIVED A CALL FROM THE ARLINGTON FIRE DEPARTMENT REPORTING THAT A GAS MAIN HAD BEEN STRUCK AT THE INTERSECTION OF DITTO AND DUGAN IN ARLINGTON, TX. AN ATMOS ENERGY SERVICE TECHNICIAN ARRIVED AT 4:02 PM AND DETERMINED THAT A GAS MAIN AND A WATER LINE HAD BEEN DAMAGED DURING A CITY PROJECT TO EXCAVATE THE WATER LINE. THE EXCAVATED TRENCH WAS FILLING WITH WATER, AND THE GAS LINE WAS LEAKING UNDERNEATH THE WATER. AN ATMOS ENERGY CONSTRUCTION CREW ARRIVED AT 4:20 PM TO REPAIR THE GAS LEAK AND, AFTER FIRST CONFIRMING NO GAS WAS PRESENT IN THE ATMOSPHERE, BEGAN PUMPING WATER FROM THE TRENCH USING GASOLINE-FIRED WATER PUMPS PROVIDED BY THE CITY. AFTER SOME TIME, AN ACCIDENTAL IGNITION OCCURRED. BECAUSE THIS ACTION LED TO THE CIRCUMSTANCE THAT MADE THIS A REPORTABLE INCIDENT, THE CAUSE OF THIS INCIDENT IS LISTED AS "INCORRECT OPERATIONS." AT APPROXIMATELY 5:30 PM, THE GAS IGNITED OVER THE TRENCH DAMAGING A BACKHOE THAT WAS ADJACENT TO THE TRENCH. A FLASH OCCURRED INJURING A CITY EMPLOYEE AND TWO FIRE FIGHTERS. THE INJURY OF ONE OF THE FIRE FIGHTERS RESULTED IN HOSPITALIZATION; THEREFORE, ATMOS ENERGY REPORTED THIS AS AN INCIDENT. ATMOS ENERGY CREWS ELIMINATED THE GAS LEAK AT 9:40 PM AND THE GAS MAIN WAS REPAIRED AND PLACED BACK INTO SERVICE ON APRIL 17, 2018 AT 5:00 PM.
2025-03-31 10:13 | NO | YES | NO | 20180055 | 30982 | 2018-05-17 14:03 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2018-04-17 17:23 |  |  | 2018 | 2312 EASTWAY ROAD | DECATUR | DEKALB | GA | 30033 | 33.7953 | -84.2947 | [9 empty] | 2018-04-18 11:00 | 1209624 |  | NATURAL GAS |  | 1825 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-04-17 17:23 |  |  |  | 2018-04-17 18:03 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2003 | [5 empty] | 2 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | OTHER | [8 empty] | 1-1/2" HOLE IN 2" PE CAUSED BY WATER LEAK (100 PSIG) | CLASS 3 LOCATION | 32875 | 37916.866950843451125 | 490165 | 565339.044531108143595 | 19786 | 22820.475421730449398 | 0 | 0 | PIPE REPLACEMENT |  | 7092 | 7159.06382978723404255319148936170212766 |  | 0 | 549918 | 265924.6157708474482701276595744680851064 | 633235.4507334692781605531914893617021277 | 0 | 0 | 130 |  |  |  |  | 40.5 | 40.5 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | WATER LEAKAGE FROM ADJACENT 100 PSIG WATER MAIN ABRADED AN APPROXIMATE 1-1/2" HOLE IN A 2" PE GAS MAIN. | [154 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | ADDITIONAL NRC REPORT NUMBER (1209884) OBTAINED FROM NRC FOR THIS INCIDENT ON 04/20/18 @ 18:41. WATER LEAKAGE FROM ADJACENT 8" CAST IRON WATER MAIN WITH A WATER PRESSURE OF 100 PSIG ABRADED AN APPROXIMATE 1-1/2" HOLE IN A 2" PE GAS MAIN. WATER INFILTRATED THE GAS SYSTEM RESULTING IN THE LOSS OF GAS SERVICE TO 130 RESIDENTIAL CUSTOMERS. DUE TO ISSUES WITH THE WATER IN THE SYSTEM AND THE HARDSHIP OF EVACUATING THE WATER FROM THE SYSTEM, 2,521' OF 2" PE PLASTIC PIPE AND 1,618' OF 4" PE PLASTIC PIPE WAS REPLACED. ONCE THE INCIDENT WAS MADE SAFE IT WAS IDENTIFIED THAT REPAIRS TO THE AFFECTED PIPELINE WOULD EXCEED THE $50,000 THRESHOLD FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME.
2025-03-31 10:13 | NO | YES | NO | 20180056 | 35992 | 2018-05-17 14:17 | SUPPLEMENTAL FINAL | 11824 | LOUISVILLE GAS & ELECTRIC CO | 820 WEST BROADWAY, PO BOX 32030 | LOUISVILLE | KY | 40202 | 2018-04-17 12:04 | EASTERN | NO | 2018 | INTERSECTION OF HURSTBOURNE LANE AND TAYLORSVILLE ROAD | LOUISVILLE | JEFFERSON COUNTY | KY | 40214 | 38.2158 | -85.5912 | [6 empty] | YES |  |  | 2018-04-19 14:39 | 1209754 |  | NATURAL GAS |  | 1940 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2018-04-17 12:00 |  |  |  | 2018-04-17 13:06 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 108 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 511394 | 589823.825321966109342 | 0 | 0 |  | 3.8332 | 7436 | 7506.316784869976359338061465721040189125 | 0 | 0 | 518830 | 251231.1213413901338766335697399527186761 | 597330.1421068360857013380614657210401891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1962-09-18 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WAS NO CONTROL ROOM OR SCADA INVOLVEMENT WITH THE INCIDENT OR RESPONSE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | STATE | AUGER | POLE | YES | 1804171010 |  |  | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | JOE RYAN | DIRECTOR GAS ASSET INTEGRITY MGMT AND COMPLIANCE | joe.ryan@lge-ku.com | 502-376-5944 |  |  |  |  | J. GREGORY CORNETT | DIRECTOR LEGAL SERVICES ASSOCIATE GENERAL COUNSEL | 502-627-2756 | greg.cornett@lge-ku.com | ON APRIL 17, 2018, LG&E WAS NOTIFIED AT 12:04AM OF THIRD PARTY DAMAGE TO AN 8" STEEL DISTRIBUTION MAIN AT THE INTERSECTION OF HURSTBOURNE LANE AND TAYLORSVILLE ROAD (NW CORNER) IN JEFFERSON COUNTY, KENTUCKY. THE PIPELINE WAS DAMAGED BY AN AUGER BEING USED BY THAT THIRD PARTY TO PREPARE TO POUR A FOUNDATION FOR A UTILITY POLE (NOT AN LG&E POLE). A PERIMETER WAS ESTABLISHED AND GAS SAFELY VENTED UNTIL IT WAS SHUT OFF AT APPROXIMATELY 11:00 AM ON APRIL 18, 2018. NO INJURIES OCCURRED AND NO CUSTOMERS LOST SERVICE.
2025-03-31 10:13 | NO | YES | YES | 20180057 | 32902 | 2018-05-22 09:28 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-04-21 23:58 |  |  | 2018 | 900 N. O'NEAL ST. | CALDWELL | BURLESON | TX | 77836 | 30.5265 | -96.7103 | [9 empty] | 2018-04-22 10:23 | 1209969 |  | NATURAL GAS |  | 70 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 3 | 2018-04-22 08:10 |  |  |  | 2018-04-22 08:45 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 155000 | 178771.539996372165 | 3380 | 3898.37293669508334 | 1910 | 2202.92671866497313 | 0 | 0 |  |  | 435 | 439.113475177304964539007092198581560284 |  | 0 | 160725 | 76974.991271437140968226950354609929078 | 185311.9531269095264345390070921985815603 | 0 | 0 | 1 |  |  |  |  | 33 | 33 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT COULD NOT BE SEEN BY CONTROLLERS | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | NUT FOLLOWER |  | COUPLING |  | UNKNOWN |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND PLASTIC | [22 empty] | YES | SEPARATION | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | DARYL TALLEY | OPERATIONS SUPERVISOR | daryl.talley@atmosenergy.com | 979-774-2502 | 979-774-2521 |  |  |  | MARLO SUTTON | DIRECTOR REGULATORY AND COMPLIANCE | 214-206-2033 | marlo.sutton@atmosenergy.com | ON APRIL 22, 2018 AT 08:10 ATMOS ENERGY RECEIVED NOTICE OF AN INCIDENT THAT HAD OCCURRED AT 900 N. O'NEAL STREET IN CALDWELL TEXAS AT 23:58 THE PREVIOUS DAY (APRIL 21). ATMOS ENERGY REPRESENTATIVES ARRIVED ON SITE AT 08:45 ON APRIL 22 AND DISCOVERED INDICATIONS OF NATURAL GAS PRESENT UNDER O'NEAL STREET AND IN THE SEWER. THE RESIDENTS OF 901 AND 904 O'NEAL STREET WERE EVACUATED AS A PRECAUTION WHILE ATMOS ENERGY COMPLETED ITS INVESTIGATION ALONG WITH REPRESENTATIVES FROM THE TEXAS RAILROAD COMMISSION. AT APPROXIMATELY 13:30 ATMOS ENERGY CREWS IDENTIFIED A LEAK NEAR THE LOCATION WHERE THE SERVICE LINE FOR 901 O'NEAL TAPPED INTO THE GAS MAIN. THE LEAK WAS ELIMINATED, THE SERVICE LINE TO 901 O'NEAL WAS REPLACED, AND GAS SERVICE WAS RESTORED BY 20:00 ON APRIL 22. IN THE COURSE OF THE COMPANY'S INVESTIGATION, A THIRD PARTY CONDUCTED AN EXAMINATION AND TESTING OF THE FACILITIES. THE RESULTS OF THE EXAMINATION AND TESTING WERE CONSISTENT WITH OTHER INFORMATION, WHICH INDICATED THAT THE SOURCE OF THE FUGITIVE NATURAL GAS WAS ASSOCIATED WITH THE INTERIOR DRESSER FITTING OF THE 900 COUPLING ASSEMBLY.
2025-03-31 10:13 | NO | YES | YES | 20180058 | 33073 | 2018-05-23 14:00 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2018-04-23 15:45 |  |  | 2018 | 13210 HOLLOWAY ROAD | LOST HILLS | KERN | CA | 93249 | 35.7078 | -119.8242 | [9 empty] | 2018-04-23 18:08 | 1210125 |  | NATURAL GAS |  | 0.87 |  | NO | [5 empty] | 0 | YES | 0 | 3 | 0 | 0 | 0 | 3 | YES |  |  |  |  | NO | 0 | 2018-04-23 15:45 |  |  |  | 2018-04-23 15:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2018 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | LEAK |  |  | OTHER | UNDER INVESTIGATION | [5 empty] | CLASS 1 LOCATION | 0 | 0 | 0 | 0 | 60000 | 69201.88645020858 | 0 | 0 |  |  | 5 | 5.04728132387706855791962174940898345154 |  | 0 | 60005 | 28666.0149404009405200945626477541371158 | 69206.9337315324570685579196217494089835 | 0 | 1 | 0 |  |  |  |  | 390 | 390 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | YES | 3 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | INADEQUATE PROCEDURE | YES |  |  |  |  | OTHER MAINTENANCE | NO | [50 empty] | BRYON WALSH | PIPELINE SAFETY AND COMPLIANCE ADVISOR | bwalsh@semprautilites.com | 619-992-1473 |  |  |  |  | BRYON WALSH | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 619-992-1473 | bwalsh@semprautilites.com | AT APPROXIMATELY 3:50 PM, ON MONDAY 04-23-2018, THREE CONTRACTORS WORKING ON AN ABOVE GROUND METER SET WERE INJURED WHEN NATURAL GAS WAS BRIEFLY IGNITED. THE INCIDENT SITE WAS AT 13210 HOLLOWAY ROAD, LOST HILLS. ALL THREE CONTRACTORS WERE WEARING FULL-FACE AIR MASK RESPIRATOR SUITS WHEN THE INCIDENT OCCURRED. THEY WERE ALL TRANSPORTED TO A LOCAL HOSPITAL WITH BURN INJURIES. THE CAUSE OF THE INCIDENT IS STILL UNDER INVESTIGATION. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO A RELEASE OF GAS AND INJURIES NECESSITATING HOSPITALIZATION. UPDATE 05/24/2018: UPDATED COSTS OF EMERGENCY RESPONSE TO 60K. UPDATE 01/23/2019: INVESTIGATION IS ON-GOING. UPDATE 04/30/2019: VALVE INSPECTION AND TESTING OCCURRED ON APRIL 18, 2018. IT REVEALED THAT THE VALVE CONTAINED RUST AND/OR OTHER PARTICULATE MATTER AND WAS PARTIALLY OPEN. THE VALVE COULD NOT BE EITHER OPENED OR CLOSED FROM THAT POSITION USING A TORQUE WRENCH SET AT VALVE MANUFACTURER'S SPECIFICATION, WHICH APPEARED TO BE DUE TO THE PRESENCE OF THE PARTICULATES. ROOT CAUSE TBD. UPDATE 9/12/2019: THE TECHNICAL ROOT CAUSE ANALYSIS IS COMPLETE. PRELIMINARY INVESTIGATION SHOWED THE STRUCTURE BUILT AROUND THE FACILITY WAS THE CAUSAL FACTOR OF THE INCIDENT. THE INCIDENT EVALUATION PROCESS IS STILL ON-GOING. UPDATE 12/13/19: SOCALGAS ALLOWED A FILTER SEPARATOR WITH LEAKING VALVES, TO BE TURNED OVER TO A CONTRACTOR WHO ALTERED THE JOB BY INSTALLING A TENT OVER THE FILTER SEPARATOR. FOR ANY FURTHER QUESTIONS, CONTACT BRYON WALSH AT (619) 992 1473.
2025-03-31 10:13 | NO | NO | NO | 20180059 | 31057 | 2018-05-25 09:26 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2018-04-27 14:56 |  |  | 2018 | 58 BOBOLINK STREET | ROCHESTER HILLS | OAKLAND | MI | 48309 | 42.6377 | -83.1858 | [9 empty] | 2018-04-27 16:38 | 1210519 |  | NATURAL GAS |  | 3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2018-04-27 14:56 |  |  |  | 2018-04-27 14:56 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | 1969 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 55000 | 63435.062579357865 | 800 | 922.6918193361144 | 3850 | 4440.45438055505055 | 0 | 0 |  |  | 10 | 10.09456264775413711583924349881796690307 |  | 0 | 59660 | 28503.4927866607372401891252955082742317 | 68808.3033418967840871158392434988179669 | 0 | 0 | 1 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS IMMEDIATELY IDENTIFIED BY THE OPERATOR EMPLOYEE WORKING ONSITE | [12 empty] | YES | 1 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE EMPLOYEE WAS PERFORMING AN ROUTINE METER EXCHANGE. WHILE ATTEMPTING TO REMOVING THE EXISTING METER USING WRENCHING TOOLS, THE RISER SNAPPED CAUSING GAS TO BE RELEASED FROM THE RISER. | [154 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmking1967@gmail.com | 989-280-2963 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING TECHINICAL ANALYST LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON FRIDAY, APRIL 27, 2018 AT APPROXIMATELY 14:46 A CONSUMERS ENERGY GAS SERVICE WORKER ARRIVED AT 58 BOBOLINK STREET, ROCHESTER HILLS, MI TO PERFORM A ROUTINE METER EXCHANGE. WHILE ATTEMPTING TO REMOVE THE EXISTING METER USING WRENCHING TOOLS, THE GSW HEARD HISSING AND NOTICED THE RISER HAD BEEN COMPROMISED AND GAS WAS ESCAPING. THE EMPLOYEE RETURNED TO HIS VEHICLE AND NOTIFIED GAS DISPATCH A DISTRIBUTION CREW WAS NEEDED. HE ALSO NOTIFIED HIS FIELD LEADER. UPON RETURN TO THE METER LOCATION THE GSW OBSERVED FIRE AT THE RESIDENCE. HE IMMEDIATELY EVACUATED THE RESIDENTS FROM A NEIGHBORING HOME AND ADVISED DISPATCH THE ESCAPING GAS HAD IGNITED AND FIRE PERSONNEL WAS NEEDED ONSITE. THE GAS DISTRIBUTION CREW ARRIVED AT APPROXIMATELY 15:31, EXCAVATED A REMOTE HOLE NEAR THE DISTRIBUTION PIPELINE AND SQUEEZED THE 1/2" STEEL SERVICE LINE STOPPING THE BLOWING GAS AT APPROXIMATELY 16:25. A ROOT CAUSE ANALYSIS TEAM HAS BEEN ASSEMBLED TO INVESTIGATE THE FAILURE, IDENTIFY A ROOT CAUSE(S) AND DEVELOP COUNTERMEASURE(S) TO MINIMIZE RE-OCCURRENCE. THE INVESTIGATION WAS COMPLETED AND THE ROOT CAUSE WAS DETERMINED TO BE THE CORROSIVE CONDITION OF THE METER AND THE EMPLOYEE'S FAILURE TO RECOGNIZE THE METER CONDITION AND TAKE ADEQUATE PRECAUTIONS TO ELIMINATE THE POTENTIAL FOR A GAS RELEASE. COUNTERMEASURES TO MINIMIZE FUTURE OCCURRENCE INCLUDE A GAS SERVICE MANUAL REVISION REQUIRING EMPLOYEES TO INSPECT THE RISER CONDITION BEFORE REPLACING THE GAS METER AND ACTIONS TO BE TAKEN WHEN ATMOSPHERIC CORROSION IS IDENTIFIED TO AVOID DAMAGE THAT MAY RESULT IN A RELEASE OF GAS.
2025-03-31 10:13 | NO | YES | YES | 20180060 | 30463 | 2018-05-30 10:52 | SUPPLEMENTAL FINAL | 2492 | CLEVELAND GAS DEPT | 201 N BROADWAY/PO DRAWER 190 | CLEVELAND | OK | 74020 | 2018-04-26 15:40 |  |  | 2018 | 501 N. BROADWAY | CLEVELAND | PAWNEE | OK | 74020 | 36.3132 | -96.4632 | [9 empty] | 2018-04-26 21:08 | 1210439 |  | NATURAL GAS |  | 67.5 |  | NO | [5 empty] | 0 | YES | 2 | 0 | 0 | 0 | 0 | 2 | YES |  |  |  |  | NO | 50 | 2018-04-26 08:00 |  |  |  | 2018-04-26 08:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 84 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | CODED | UNKNOWN | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | 0 | 0 | 1000 | 1153.364774170143 | 500 | 576.6823870850715 | 0 | 0 | TOTAL COST OF REPAIRS AND EMERGENCY PERSONNEL. |  | 270 | 272.553191489361702127659574468085106383 |  | 0 | 1770 | 968.661307316170085106382978723404255319 | 2002.600352744576202127659574468085106383 | 1 | 0 | 1 |  |  |  |  | 20 | 20 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | FAILURE TO FOLLOW PROCEDURE FOR PROPER CLASSIFICATION OF LEAK AND INADEQUATE REPAIR PROCEDURES. | YES |  | YES |  |  | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | CLINTON E. STOUT | CHEIF OF POLICE | cstout@cityofclevelandok.com | 918-358-3506 | 918-358-3600 |  |  |  | ELZIE SMITH | CITY MANAGER | 918-358-3506 | elziesmith@hotmail.com | THE CITY OF CLEVELAND RECEIVED NOTIFICATION FROM A PUBLIC SOURCE OF THE LEAK ON 25 APRIL 18. THE LEAK WAS LOCATED BY OPERATOR ON 25 APRIL 18 AT APPROX. 1600HRS. LEAK WAS DEEMED AS A CLASS 2 LEAK BY THE OPERATOR ON 25 APRIL 18. NO CGI READINGS WERE TAKEN OR MIGRATION STUDY DONE TO PROPERLY CLASSIFY THE LEAK. PERSONNEL RESPONDED ON 26 APRIL 18 AT APPROX. 1300HRS TO BEGIN REPAIR OPERATIONS. NO CGI READINGS WERE BEING TAKEN DURING THE REPAIR OPERATIONS OF THE PIPELINE. THE LEAK WAS EXCAVATED BY A QUALIFIED PERSONNEL MEMBER. AFTER THE STEEL PIPELINE AND LEAK WAS EXPOSED FOUR QUALIFIED PERSONNEL MEMBERS BEGAN THE REPAIR PROCESS. PERSONNEL MEMBERS 1 & 2 WERE CLEANING THE COATING ON THE PIPELINE TO PREPARE FOR A REPAIR CLAMP. PERSONNEL MEMBER 3 WAS SUPERVISING THE REPAIR PROCESS. PERSONNEL MEMBER 4 WAS USING A STEEL FILE TO PREPARE THE STEEL PIPELINE FOR CATHODIC ANODE INSTALLATION. THE INITIAL ATTEMPT TO TIGHTEN CLAMP WAS UNSUCCESSFUL TO SEAL THE LEAK. TORQUE WRENCH WAS NOT USED IN THE INSTALLATION OF CLAMP. PERSONNEL MEMBER 3 THEN CHANGED POSITIONS WITH PERSONNEL MEMBER 1. WHILE MOVING CLAMP IN AN ATTEMPT TO SEAL THE LEAK, IGNITION OF GAS OCCURRED. UNKNOWN SOURCE CAUSED THE IGNITION OF THE GAS. PERSONNEL MEMBER 2 HAD CELL PHONE ON HIS PERSON NEAR THE SOURCE OF LEAK. PERSONNEL MEMBER 4 HAD TWO CELL PHONES NEAR THE SOURCE OF LEAK. PERSONNEL MEMBER 2,3,4 WERE TRANSPORTED TO HOSPITAL FOR BURN INJURIES. PERSONNEL MEMBERS 2 WAS TREATED AND RELEASED SHORTLY BEFORE MIDNIGHT ON 26 APRIL 18. PERSONNEL MEMBERS 3 AND 4 SPENT SEVERAL DAYS IN BURN UNIT AT TULSA HOSPITAL. PERSONNEL MEMBER 5 WHO ARRIVED AFTER IGNITION OF GAS WAS SENT AND CHECKED AT LOCAL HOSPITAL FOR GENERAL SICKNESS. IT IS APPARENT THE PROPER PROCEDURE FOR LEAK CLASSIFICATIONS WAS NOT FOLLOWED AND THAT REPAIR PROCEDURES ARE INADEQUATE. THE CITY OF MANNFORD WAS CALLED IN TO ASSIST WITH THE LEAK REPAIR. THE CITY OF MANNFORD HAS PREPARED A WRITTEN STATEMENT OF THEIR ACTIONS TAKEN IN THE REPAIR OF THE PIPELINE. THE STATEMENT IS AVAILABLE UPON REQUEST.
2025-03-31 10:13 | NO | NO | NO | 20180061 | 30647 | 2018-06-07 14:34 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2018-05-03 08:12 |  |  | 2018 | 648 COUNTY STREET | TAUNTON | BRISTOL | MA | 02780 | 41.8849 | -71.067 | [9 empty] | 2018-05-03 10:58 | 1211050 |  | NATURAL GAS |  | 345.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 9 | 2018-05-03 08:12 |  |  |  | 2018-05-03 08:18 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 14 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2018 | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 50178 | 57873.537638309435454 | 0 | 0 | 0 | 0 |  |  | 1435 | 1448.569739952718676122931442080378250591 |  | 0 | 51613 | 25309.4954045863845711394799054373522459 | 59322.1073782621541301229314420803782506 | 100 | 0 | 597 |  |  |  |  | 74 | 75 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | STATE | BACKHOE/TRACKHOE | ROAD WORK | YES | 20181304314 |  |  | UTILITY OWNER | YES | YES | 7 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | KATHERINE SILVER | SR OPERATIONS COMPLIANCE SPECIALIST | ksilver@nisource.com | 508-864-1836 |  |  |  |  | MEGGAN BIRMINGHAM | MANAGER OPERATIONS COMPLIANCE | 508-468-9956 | mbirmingham@nisource.com | LARGE SCALE OUTAGE AS A RESULT OF A 3RD PARTY DAMAGE, MDR CONSTRUCTION PERFORMING A MASS DOT JOB (REBUILDING THE INTERSECTION OF COUNTY ST AND HART ST TAUNTON). 3RD PARTY EXCAVATION DAMAGE DUE TO NOT HAND DIGGING WITHIN THE TOLERANCE ZONE PRIOR TO UTILIZING MECHANICAL MEANS TO DIG.
2025-03-31 10:13 | NO | NO | NO | 20180062 | 31054 | 2018-06-11 06:43 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2018-05-12 04:03 |  |  | 2018 | 46359 HULING STREET | SHELBY TOWNSHIP | MACOMB | MI | 48317 | 42.6345 | -83.0872 | [9 empty] | 2018-05-12 10:05 | 1211945 |  | NATURAL GAS |  | 4.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2018-05-12 04:03 |  |  |  | 2018-05-12 04:46 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2007 | [8 empty] | OTHER | ALUMINUM | [9 empty] | LEAK |  |  | OTHER | 3/8" HOLE (LIGHTNING STRIKE) | [5 empty] | CLASS 3 LOCATION | 50000 | 57668.23870850715 | 800 | 922.6918193361144 | 504 | 581.295846181752072 | 0 | 0 |  |  | 13 | 13.122931442080378250591016548463356974 |  | 0 | 51317 | 24519.5009890656236242458628841607565012 | 59185.349305467096850250591016548463357 | 0 | 0 | 1 |  |  |  |  | 53 | 53 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO INVESTIGATION WAS REQUIRED FOR THIS EVENT | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  | ,,, | YES |  |  |  | YES | LIGHTNING/THUNDER STORM | [213 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING TECHINICAL ANALYST LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON SATURDAY, MAY 12, 2018 AT APPROXIMATELY 04:03 CONSUMERS ENERGY RECEIVED NOTICE FROM 911 OF A GAS RELATED STRUCTURE FIRE AT 46359 HULING, SHELBY TOWNSHIP (MACOMB COUNTY) MICHIGAN. WHEN THE GAS SERVICE WORKER (GSW) ARRIVED ONSITE AT APPROXIMATELY 04:46 THE GAS WAS SHUT-OFF AT THE LOCKWING AND THE EMPLOYEE WAS INFORMED BY FIRE PERSONNEL THE SUSPECTED CAUSE WAS A LIGHTNING STRIKE TO THE METER RESULTING IN A GAS RELEASE AND SUBSEQUENT IGNITION. THE PLASTIC DIALS WERE MELTED OFF THE SPRAGUE175RM METER AND A HOLE APPROXIMATELY 3/8" HAD FORMED IN THE REGULATOR CONE. THE DAMAGED METER WAS REMOVED AND TRANSPORTED TO THE CONSUMERS ENERGY LABORATORY SERVICES FOR FURTHER EXAMINATION (RESULTS PENDING). A STRIKENET REPORT REQUEST WAS ALSO SUBMITTED WHICH CONFIRMED 5 CLOUD-TO-GROUND LIGHTNING STRIKES DETECTED WITHIN 1 MILE OF THE PROPERTY AND THE LIKELY CAUSE OF THE RELEASE AND IGNITION. AN INVESTIGATION OF THE SURROUNDING AREAS WAS CONDUCTED, WHICH INCLUDED A LEAK SURVEY TO ENSURE NO ADDITIONAL NATURAL GAS FACILITIES WERE COMPROMISED AS A RESULT OF THE INCLEMENT WEATHER. CONSUMERS ENERGY LABORATORY SERVICES REPORT WAS COMPLETED ON JULY 6, 2018 A SUMMARY HAS BEEN INCLUDED BELOW: A HOLE AND DISTORTED SURFACE APPEARANCE WAS NOTED ON THE HOUSING. MICROSTRUCTURAL CROSS-SECTION IN THE AREA OF THE HOLE AND AWAY FROM THE HOLE INDICATED THE AFFECTED AREA HAD BEEN THERMALLY AFFECTED. THE CAUSE OF THE METER FAILURE WAS NOT DETERMINED.
2025-03-31 10:13 | NO | YES | NO | 20180063 | 30711 | 2018-06-13 14:30 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 40 SYLVAN ROAD | WALTHAM | MA | 02451 | 2018-05-14 15:53 |  |  | 2018 | 99 MESEROLE AVENUE | BROOKLYN | KINGS | NY | 11206 | 40.727 | -73.9534 | [9 empty] | 2018-05-14 21:24 | 1212155 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-05-14 15:53 |  |  |  | 2018-05-14 16:23 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1994 | [5 empty] | 8 | UNKNOWN | PHILLIPS DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 3408 | OTHER | [8 empty] | MULTIPLE SERVICE OUTAGES (117) RESULTING FROM WATER INFILTRATION INTO A LOW PRESSURE MAIN. | CLASS 4 LOCATION | 0 | 0 | 392379 | 452556.116724106540197 | 147621 | 170260.861327770679803 | 0 | 0 |  |  | 0 | 0 |  | 0 | 540000 | 257952.11318701272 | 622816.97805187722 | 0 | 0 | 518 |  |  |  |  | 0.33 | 0.33 | 0.43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EVENT OCCURRED ON LOW PRESSURE DISTRIBUTION SYSTEM AND WAS DUE TO WATER INTRUSION. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE NOT RELATED TO EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | PREVIOUS MECHANICAL DAMAGE | [112 empty] | PREVIOUS MECHANICAL DAMAGE NOT RELATED TO EXCAVATION | [7 empty] | 2018-03-02 | NO | [159 empty] | CORINNE D. BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE D BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | 6317703549 | corinne.byrnes@nationalgrid.com | SUPPLEMENTAL REPORT CREATED 7/26/2018 TO CORRECT LONGITUDE/LATITUDE COORDINATES. DISPATCH RECEIVED FIFTEEN CUSTOMER COMPLAINTS OF NO GAS AT 151 GUERNSEY ST, STARTING AT 15:53 ON 5/14/2018. IT WAS LATER DETERMINED THAT A BROKEN WATER SERVICE IN FRONT OF 99 MESEROLE AVENUE CAUSED WATER EROSION AND SAND ABRASION/INTRUSION INTO A 8" PLASTIC LOW PRESSURE MAIN FEEDING A 6" LOW PRESSURE STEEL MAIN. THIS OUTAGE IMPACTED 518 CUSTOMERS FEED BY 117 SERVICES AT GUERNSEY STREET AND 1025 LORIMER STREET. A TEMPORARY SLEEVE REPAIR WAS MADE ON 5/15/2018 AT 10:00 AND CREWS ARE REPLACING APPROX. 30 FEET OF THE DAMAGED MAIN ON 6/5/2018. TIMELINE: 5/14/2018 15:53 - COMPANY WAS NOTIFIED OF NO GAS CONDITION AT 151 GUERNSEY ST. (NO. CUSTOMERS IMPACTED UNKNOWN AT THIS TIME) FIFTEEN CUSTOMER NOTIFICATIONS FOLLOWED. 16:23 - NATIONAL GRID FIRST RESPONDER ARRIVED ON SITE. MULTIPLE CREWS DISPATCHED. 23:35 - DISPATCH WAS NOTIFIED THAT 117 SERVICES WERE IMPACTED.
2025-03-31 10:13 | NO | YES | NO | 20180064 | 30513 | 2018-06-19 15:09 | ORIGINAL | 4483 | ENSTAR NATURAL GAS CO | 3000 SPENARD ROAD | ANCHORAGE | AK | 99503 | 2018-05-30 15:27 |  |  | 2018 | 2300 S. RUTH ST | WASILLA | MATANUSKA-SUSITNA BOROUGH | AK | 99654 | 61.5562 | -149.4435 | [9 empty] | 2018-05-30 16:07 | 1213713 |  | NATURAL GAS |  | 500 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2018-05-30 15:27 |  |  |  | 2018-05-30 15:50 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1996 | [5 empty] | 2 | ASTM D2513 | DRISCO | PLASTIC |  |  |  |  | OTHER | HDPE | 11 |  |  |  | MECHANICAL PUNCTURE | 2 | 6 | [7 empty] | CLASS 3 LOCATION | 370000 | 426744.96644295291 | 78 | 89.962452385271154 | 11153 | 12863.477326319604879 | 0 | 0 |  |  | 985 | 994.314420803782505910165484633569739953 |  | 0 | 382216 | 183029.6917625180525666288416075650118203 | 440692.72064246156853891016548463356974 | 0 | 0 | 17 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | OTHER | [12 empty] | CONTRACTOR | DRILLING | WATER | NO | [5 empty] | YES | 4 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | RUSTY ALLEN | COMPLIANCE ENGINEER | rusty.allen@enstarnaturalgas.com | 907-334-7765 |  |  |  |  | STEVE COOPER | DIRECTOR OF OPERATIONS | 907-334-7730 | steve.cooper@enstarnaturalgas.com | E & D WATER WELLS WAS DRILLING A NEW WATER WELL FOR RESIDENTIAL DEVELOPMENT WITHOUT A LOCATE. DURING THE DRILLING THEY RUPTURED A 2 INCH HDPE MAIN THAT OPERATES AT 60 PSIG. THE NATURAL GAS RELEASED FROM THE DAMAGE IGNITED AND CONSUMED THE DRILL RIG. ONE INDIVIDUAL WAS TREATED AND RELEASED WITH MINOR BURNS FROM THE LOCAL HOSPITAL. EMERGENCY RESPONSE WAS REQUIRED BY ENSTAR NATURAL GAS AND THE WASILLA FIRE DEPARTMENT. EXCAVATION WAS REQUIRED TO SECURE THE 2 INCH MAIN FOR REPAIRS. THE DAMAGE REQUIRED 17 RESIDENTIAL RELIGHTS AND THE REPLACEMENT OF 50 FEET OF 2 INCH HDPE MAIN. THE ESTIMATED TOTAL COST OF THE DRILL RIG IS $370,000 AND IS A TOTAL LOSS TO THE CONTRACTOR.
2025-03-31 10:13 | NO | NO | NO | 20180065 | 30518 | 2018-06-20 11:32 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2018-05-25 17:02 |  |  | 2018 | 2211 RUBY DRIVE | AUGUSTA | RICHMOND | GA | 30906 | 33.4221 | -82.0287 | [9 empty] | 2018-05-26 20:20 | 1213366 |  | NATURAL GAS |  | 15.39 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2018-05-25 17:08 |  |  |  | 2018-05-25 17:31 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1960 | [8 empty] | OTHER | METER SET PIPING | [9 empty] | LEAK |  |  | OTHER | METER AND METER SET PIPING WAS | [5 empty] | CLASS 3 LOCATION | 54000 | 62281.697805187722 | 570 | 657.41792127698151 | 217 | 250.280155994921031 | 0 | 0 |  |  | 43 | 43.40661938534278959810874704491725768322 |  | 0 | 54830 | 26211.3063035190187888132387706855791962 | 63232.8025018449673305981087470449172577 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A RESIDENTIAL METER SET WAS DAMAGED BY A HOMEOWNER ON A RIDING LAWNMOWER WHILE CUTTING GRASS. THE ESCAPING GAS IGNITED CAUSING DAMAGE TO THE LAWNMOWER AND HOUSE. ONCE THE INCIDENT WAS MADE SAFE AND COST ASSOCIATED WITH THE INCIDENT WERE IDENTIFIED IT WAS DETERMINED THAT THE DAMAGES WOULD EXCEED THE $50,000 THRESHOLD FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME.
2025-03-31 10:13 | NO | YES | NO | 20180066 | 30789 | 2018-06-28 20:55 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2018-05-29 18:04 |  |  | 2018 | 44600 FIVE MILE ROAD | NORTHVILLE | WAYNE | MI | 48168 | 42.3958 | -83.484 | [9 empty] | 2018-05-29 23:03 | 1213615 |  | NATURAL GAS |  | 30552 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-05-29 18:04 |  |  |  | 2018-05-29 18:37 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1970 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  |  |  | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 4 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 18856 | 21747.846181752216408 | 4325 | 4988.302648285868475 | 0 | 0 |  |  | 87073 | 87896.3853427895981087470449172576832151 |  | 0 | 110254 | 92382.6135926730759467706855791962174941 | 114632.5341728276829917470449172576832151 | 23 | 0 | 0 |  |  |  |  | 309 | 309 | 340 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 73550774 |  |  | CONTRACT LOCATOR | NO | YES | 18 | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmking1967@gmail.com | 989-280-2963 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING TECHINICAL ANALYST LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON MAY 29, 2018 AT APPROXIMATELY 18:04 A THIRD PARTY CONTRACTOR INSTALLING EDGE DRAIN MADE CONTACT WITH A 1" HIGH PRESSURE NATURAL GAS SERVICE LINE PULLING THE SERVICE TEE OFF AN 8" STEEL (HIGH PRESSURE) PIPELINE CAUSING GAS TO BE RELEASED. THE PIPELINE IS LOCATED ON FIVE MILE ROAD, NORTHVILLE, MICHIGAN (WAYNE COUNTY). THE CONTRACTOR RECOGNIZED CONTACT HAD BEEN MADE WITH THE PIPELINE, EXITED THE EQUIPMENT AND IMMEDIATELY NOTIFIED CONSUMERS ENERGY OF THE DAMAGE. NO IGNITION, INJURIES OR FATALITIES OCCURRED AS A RESULT OF THE DAMAGE. CONSUMERS PERSONNEL ARRIVED ONSITE AT APPROXIMATELY 18:37 AND BEGAN MONITORING SURROUNDING LOCATIONS TO ENSURE GAS WAS NOT MIGRATING. A PORTION OF THE ROAD WAS CLOSED AND THE DAMAGED LOCATION AND SURROUNDING BUILDINGS WERE CONTINUOUSLY MONITORED UNTIL THE PIPELINE WAS ISOLATED AND THE GAS WAS SHUT-OFF. ON MAY 30, 2018 AT APPROXIMATELY 13:25 THE DAMAGED SECTION OF PIPELINE WAS ISOLATED BY UTILIZING A MUELLER CONTROL FITTING WEST OF THE DAMAGE AND CLOSING THE VALVE TO THE EAST OF THE DAMAGE LOCATION. APPROXIMATELY 3' OF 8" PIPE WAS CUT-OUT AND REPLACED, A NEW SERVICE TEE WAS INSTALLED AND APPROXIMATELY 11' OF SERVICE LINE REPLACE TO REPAIR THE DAMAGE AND RESUME NORMAL OPERATIONS.
2025-03-31 10:13 | NO | YES | YES | 20180068 | 31254 | 2018-07-10 11:52 | SUPPLEMENTAL FINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2018-06-09 13:55 |  |  | 2018 | 1500 RIVERSIDE AVE | BALTIMORE | BALTIMORE CITY IS NOT WITHIN BALTIMORE COUNTY | MD | 21230 | 39.2727 | -76.6083 | [9 empty] | 2018-06-16 15:21 | 1215480 |  | NATURAL GAS |  | 0.01 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | YES | 0 | 2018-06-16 13:55 |  |  |  | 2018-06-16 13:55 |  | NO | PUBLIC PROPERTY | UNDERGROUND | OTHER | PUBLIC WORKS MANHOLE - NON-UTILITY STRUT |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1903 | [5 empty] | 12 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 5000 | 5766.823870850715 | 500 | 576.6823870850715 | 0 | 0 | EMERGENCY RESPONSE PERSONNEL. |  | 10 | 10.09456264775413711583924349881796690307 |  | 0 | 5510 | 2636.628103185295040189125295508274231678 | 6353.600820583540637115839243498817966903 | 0 | 0 | 0 |  |  |  |  | 5.95 | 5.95 | 10 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | CAST IRON JOINT FAILURE | [11 empty] | YES | CAST IRON JOINT LEAK |  | YES |  |  |  | OTHER | CAST IRON JOINT | NO | [86 empty] | STEVE TROCH | MANAGER - GAS ENGINEERING AND ASSET PERFORMANCE | steve.troch@bge.com | 4104709560 | 4104709549 |  |  |  | STEVE TROCH | MANAGER - GAS ENGINEERING AND ASSET PERFORMANCE | 4104709560 | steve.troch@bge.com | ON 6/9/2018 A BGE CONTRACTOR PAVING CREW WAS INSTALLING THERMOPLASTIC MARKER TRAFFIC LINES ON A BALTIMORE CITY STREET SURFACE USING A HEAT TORCH (IN ORDER FOR THE THERMOPLASTIC LINES TO ADHERE TO THE SURFACE). WHEN PERFORMING THIS FUNCTION NEAR A BALTIMORE CITY MANHOLE, AN IGNITION OCCURRED WHICH CAUSED THE MANHOLE LID TO RAISE AND STRIKE THE CONTRACTOR EMPLOYEE, RESULTING IN AN INJURY REQUIRING AN OVERNIGHT HOSPITAL STAY. THE EXACT COMPOSITION OF THE IGNITION SOURCE (IN THE MANHOLE) WAS LATER CONFIRMED AS NATURAL GAS, BUT THE SOURCE OF THE GAS WAS UNDETERMINED AT THE TIME OF THE INITIAL EMERGENCY RESPONSE. FOLLOWING CONTINUING GAS LEAK AREA SURVEYS, A GAS MAIN LEAK WAS IDENTIFIED AND A CAST IRON JOINT WAS SUBSEQUENTLY REPAIRED. THE APPARENT GAS LEVELS IN THE SUBJECT MANHOLE WERE REDUCED. THUS THE SOURCE AT THE TIME OF IGNITION WAS UNDETERMINED BUT BY JUNE 16, THE CORRELATION OF THE REPAIR AND THE GAS LEVELS MEASURED IN THE MANHOLE WAS THE BASIS FOR THE NRC NOTICE DETERMINATION.
2025-03-31 10:13 | NO | YES | YES | 20180069 | 32496 | 2018-07-16 17:45 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2018-06-14 15:20 |  |  | 2018 | 3735 W. 56TH ST. | TULSA | TULSA | OK | 74132 | 36.082 | -96.0357 | [9 empty] | 2018-06-14 16:45 | 1215296 |  | NATURAL GAS |  | 43.09 |  | NO | [5 empty] | 0 | YES | 3 | 0 | 1 | 0 | 0 | 4 | YES |  |  |  |  | YES | 2 | 2018-06-14 13:30 |  |  |  | 2018-06-14 14:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1970 | [5 empty] | 2 | ALDY-A | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | UNKNOWN | MECHANICAL PUNCTURE | 1.5 | 1.5 | [7 empty] | CLASS 3 LOCATION | 1000 | 1153.364774170143 | 9100 | 10495.6194449483013 | 15000 | 17300.471612552145 | 0 | 0 |  |  | 150 | 151.418439716312056737588652482269503546 |  | 0 | 25250 | 12130.0672941969624028368794326241134752 | 29100.8742713869013567375886524822695035 | 0 | 0 | 53 |  |  |  |  | 20 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 6 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  | YES | [6 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | UNKNOWN/OTHER | YES | 18060808170456 |  |  | CONTRACT LOCATOR | UNKNOWN/OTHER | YES | 3 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | SETH SLIFER | SR. COMPLIANCE SPECIALIST | seth.slifer@onegas.com | 450-248-7018 |  |  |  |  | MEGHAN BOOKER | DIRECTOR OF ENGINEERING | 405-530-2501 | meghan.booker@onegas.com | A THIRD-PARTY EXCAVATOR HIRED BY THE TULSA HOUSING AUTHORITY (THA) HIT ONG'S 2" MAIN. ONG RESPONDED TO NOTIFICATION OF THE LINE HIT BY THE TULSA FIRE DEPARTMENT. WHILE EXCAVATING TO SQUEEZE OFF THE LINE TO STOP THE FLOW OF GAS, ONG STRUCK AN UNMARKED, LIVE ELECTRICAL CONDUIT RESULTING IN AN IMMEDIATE IGNITION. THA HAD FAILED TO REGISTER AND MARK THE PRIVATE ELECTRICAL LINE THA HAD INSTALLED JUST A FEW INCHES BELOW GROUND.
2025-03-31 10:13 | NO | YES | NO | 20180070 | 31684 | 2018-07-19 15:57 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2018-06-19 17:00 |  |  | 2018 | WALTON BOULEVARD & E. OAKLAND | ROCHESTER HILLS | OAKLAND | MI | 48309 | 42.6802 | -83.2074 | [9 empty] | 2018-06-19 23:30 | 1215824 |  | NATURAL GAS |  | 11125 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-06-19 17:00 |  |  |  | 2018-06-19 17:53 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 240 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2018 | [5 empty] | 8 | API5L | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.784 |  | 2406 | MECHANICAL PUNCTURE | 0.5 | 25.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 70845 | 81710.127426083780835 | 604 | 696.632323598766372 | 0 | 0 |  |  | 30149 | 30434.0969267139479905437352245862884161 |  | 0 | 101598 | 62283.7299113336081981938534278959810875 | 112840.8566763964951975437352245862884161 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | STORM DRAIN/CULVERT | YES | 81380462 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | SENIOR ENGINEERING TECHINICAL ANALYST LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON JUNE 19, 2018 AT APPROXIMATELY 17:00 A THIRD PARTY CONTRACTOR INSTALLING STEEL SHEET PILING FOR SHORING, DAMAGED AN 8" PLASTIC (MEDIUM PRESSURE) PIPELINE CAUSING GAS TO BE RELEASED. THE PIPELINE IS LOCATED ON WALTON BOULEVARD, ROCHESTER HILLS, MICHIGAN (OAKLAND COUNTY). THE CONTRACTOR RECOGNIZED CONTACT HAD BEEN MADE WITH THE PIPELINE, EXITED THE EQUIPMENT AND IMMEDIATELY NOTIFIED CONSUMERS ENERGY OF THE DAMAGE. NO IGNITION, INJURIES OR FATALITIES OCCURRED AS A RESULT OF THE DAMAGE. CONSUMERS PERSONNEL ARRIVED ONSITE AT APPROXIMATELY 17:53 AND BEGAN MONITORING SURROUND LOCATIONS TO ENSURE GAS WAS NOT MIGRATING. A PORTION OF THE ROAD WAS CLOSED AND THE DAMAGE AND SURROUNDING LOCATIONS WERE CONTINUOUSLY MONITORED UNTIL THE PIPELINE WAS ISOLATED AND THE GAS WAS SHUT-OFF . ON JUNE 20, 2018 AT APPROXIMATELY 04:56 THE DAMAGED SECTION OF PIPELINE WAS ISOLATED BY SQUEEZING THE 8" PLASTIC PIPELINE IN TWO REMOTE LOCATIONS AND INSTALLING PLASTIC CAPS AT EACH END. PERMANENT REPAIR TO THE PIPELINE SEGMENT WAS DELAYED UNTIL THE CULVERT WORK WAS COMPLETED. ON NOVEMBER 15, 2018 APPROXIMATE 500 FEET OF 8" PLASTIC PIPELINE WAS INSTALL REPAIRING THE DAMAGE SEGMENT AND NORMAL OPERATIONS WERE RESUMED.
2025-03-31 10:13 | NO | NO | NO | 20180071 | 30671 | 2018-07-20 10:27 | ORIGINAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2018-06-22 00:40 |  |  | 2018 | 408 SOUTH 2ND STREET | BROOKLYN | KINGS | NY | 11211 | 40.7091 | -73.9512 | [9 empty] | 2018-06-22 07:16 | 1216080 |  | NATURAL GAS |  | 247.2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2018-06-22 00:40 |  |  |  | 2018-06-21 14:56 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 8 | 0.5 |  | CLASS 4 LOCATION | 0 | 0 | 0 | 0 | 40000 | 46134.59096680572 | 0 | 0 |  |  | 1296 | 1308.255319148936170212765957446808510638 |  | 0 | 41296 | 20317.7767057361668085106382978723404255 | 47442.8462859546561702127659574468085106 | 0 | 0 | 0 |  |  |  |  | 0.28 | 0.29 | 0.43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT WAS NOT CAUSED BY EVENTS UNDER THE CONTROL OF THE CONTROL ROOM. | [12 empty] | YES | 3 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | APPARENT CAUSE OF THE INCIDENT WAS WATER INFILTRATION INTO A PARTIALLY EXCAVATED OPENING OVER A 6" GAS MAIN WHICH CAUSED THE CAST IRON MAIN TO BE UNDERMINED, CRACK, AND GO ON FIRE. CONTRIBUTING FACTOR WAS THE PROXIMITY OF AN EXPOSED UNDERGROUND COMMUNICATIONS WIRE (60 V AC). | [154 empty] | CORINNE D. BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE D BYRNES | PRIN PROGRAM MANAGER FEDERAL PROGRAMS | 6317703549 | corinne.byrnes@nationalgrid.com | AT APPROX. 14:56 ON THURSDAY, JUNE 21, CUSTOMER AND METER SERVICES (CMS) WAS RESPONDING TO AN OUTSIDE LEAK INVESTIGATION AT 408 SOUTH 2ND STREET. AFTER SIGNIFICANT INVESTIGATION AT SEVERAL ADDRESSES IN THE PROXIMITY OF THIS LOCATION, FIELD PERSONNEL OBTAINED A GAS READING OF 90% AT A SEWER MANHOLE AT 10 TEN EYCK STREET, AS CALLED IN TO OUR DISPATCH CENTER. AFTER CONTINUED TESTING, THE LEAK LOCATION WAS NARROWED DOWN TO 408 SOUTH 2ND STREET. EMPLOYEES WERE HAND-DIGGING OVER A 6" CI MAIN (INTERSECTING A 16" CI MAIN TEE FITTING). THE WORKERS HAD EXCAVATED A 5' X 3' OPENING, WHICH STARTED TO GIVE WAY DUE TO WATER INFILTRATION, AND A FIRE ENSUED (6/22 AT 00:40). THREE EMPLOYEES WERE TREATED FOR BURNS: (2 ON SCENE) AND ONE TRANSPORTED VIA EMS TO LOCAL HOSPITAL FOR OBSERVATION AND RELEASED THE SAME DAY. AT 01:26 ON FRIDAY JUNE 22, DETERMINED THAT A WATER MAIN BREAK HAD OCCURRED IN THE AREA, AND UNDERMINED THE EXCAVATION, WHICH POTENTIALLY CAUSED DAMAGE TO THE 6" GAS MAIN. WATER MAIN RELEASE WAS CONTROLLED BETWEEN 03:27 AND 04:30 ON JUNE 22. GAS MAIN WAS SHUT DOWN AT 11:00 ON JUNE 22 AND RESTARTED AT 15:00. APPARENT CAUSE OF THE INCIDENT WAS WATER INFILTRATION WHICH CAUSED THE LOW PRESSURE CAST IRON MAIN TO BE UNDERMINED, RUPTURE AND THEN SET ON FIRE. CONTRIBUTING FACTOR WAS THE PROXIMITY OF AN EXPOSED UNDERGROUND COMMUNICATIONS WIRE (60 V AC). SIZE OF DAMAGED AREA IS APPROX. 1/2 X 8" CRACK, WHICH RESULTED IN THE RELEASE OF APPROX. 247.2 MCF.
2025-03-31 10:13 | NO | YES | NO | 20180072 | 30762 | 2018-08-07 14:15 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2017-05-18 10:21 |  |  | 2017 | INTERNATIONAL SERVICE RD. @ CROSSOVER #1 | GRAPEVINE | TARRANT | TX | 75261 | 32.902 | -97.0415 | [9 empty] | 2017-05-18 14:46 | 1178694 |  | NATURAL GAS |  | 2082 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2017-05-18 10:21 |  |  |  | 2017-05-18 10:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 77 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1971 | [5 empty] | 10 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 0.5 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 80811 | 95375.729651972164335 | 0 | 0 | 0 | 0 |  |  | 12504 | 12834.6346153846153846153846153846153846 |  | 0 | 93315 | 51374.5552364804638354615384615384615385 | 108210.3642673567797196153846153846153846 | 4 | 0 | 0 |  |  |  |  | 220 | 220 | 275 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT COULD NOT BE SEEN BY CONTROLLERS | [12 empty] | NO |  |  | YES | 3 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | OTHER | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 1762927668 | TEXAS811 |  | CONTRACT LOCATOR | YES | YES | 16 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | SHED BELCHER | COMPLIANCE SUPERVISOR | shed.belcher@atmosenergy.com | 940-380-7454 |  |  |  |  | MARLO SUTTON | DIRECTOR REGULATORY AND COMPLIANCE | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT NUMBER 1178842 AT APPROXIMATELY 10:21AM ON MAY 18, 2017, A DISTRIBUTION MAIN WAS HIT AT CROSSOVER #1 AT INTERNATIONAL SERVICE ROAD AT DFW AIRPORT BY AN ATMOS CONTRACTOR WHO WAS WORKING ON A PIPE REPLACEMENT PROJECT. IN ORDER TO MAKE REPAIRS IT WAS DETERMINED THAT THE LINE NEEDED TO BE SHUT DOWN; CNG WAS UTILIZED TO PROVIDE UNINTERRUPTED GAS SERVICE TO AFFECTED CUSTOMERS. THE REPAIRS WERE COMPLETED AT 3:00 AM ON MAY 19, 2017 AND BY 7:30 AM THE PIPE WAS BACK IN SERVICE AND CNG NO LONGER UTILIZED. THIS WAS ORIGINALLY REPORTED TELEPHONICALLY TO THE NATIONAL RESPONSE CENTER (NRC) AND THE TEXAS RAILROAD COMMISSION (TRRC). DURING THE INVESTIGATION WE EVALUATED THE ESTIMATED DAMAGES WOULD NOT EXCEED THE REPORTING CRITERIA AND WE RETRACTED THE TELEPHONIC REPORT AS WELL AS SENT A NOTIFICATION LETTER TO THE TRRC INFORMING THEM OF THE RETRACTION. IN A MAY 30, 2018 MEETING WITH A TRRC PIPELINE SAFETY INSPECTOR, IT CAME TO OUR ATTENTION THAT THE TOTAL ESTIMATED DAMAGES MAY HAVE EXCEEDED THE $50,000 THRESHOLD REQUIRING US TO REPORT THIS INCIDENT. WE HAVE FINALIZED OUR DAMAGE ESTIMATE WHICH IS INCLUDED IN THIS REPORT. PART OF ATMOS ENERGY'S CONTINUAL EDUCATION AND OUTREACH EFFORTS INVOLVE MAKING CONTACT WITH EXCAVATORS WHO HAVE CHALLENGES RELATED TO CHAPTER 18 RULES AND REGULATIONS. THIS EXCAVATOR IS INCLUDED IN OUR PUBLIC LIAISON OUTREACH MEETINGS, AND WE HAVE FURTHER REACHED OUT TO THIS EXCAVATOR TO COMMUNICATE THE IMPORTANCE OF SAFE DIGGING AND LINE LOCATING PRACTICES.
2025-03-31 10:13 | NO | YES | YES | 20180073 | 31423 | 2018-08-09 14:37 | SUPPLEMENTAL | 22763 | WISCONSIN GAS LLC DBA WE ENERGIES | 231 W. MICHIGAN STREET | MILWAUKEE | WI | 53203 | 2018-07-10 19:04 |  |  | 2018 | INTERSECTION OF MAIN AND BRISTOL | SUN PRAIRIE | DANE | WI | 53590-2223 | 43.1833 | -89.2137 | [9 empty] | 2018-07-10 21:44 | 1217955 |  | NATURAL GAS |  | 600 |  | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES | 0 | 0 | 1 | 0 | 0 | 1 | YES |  |  |  |  | YES | 650 | 2018-07-10 18:25 |  |  |  | 2018-07-10 19:02 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 31 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1991 | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2.3 | 0.8 | [7 empty] | CLASS 3 LOCATION | 20000000 | 23067295.48340286 | 200000 | 230672.9548340286 | 300000 | 346009.4322510429 | 0 | 0 |  |  | 3500 | 3533.096926713947990543735224586288416076 |  | 0 | 20503500 | 9795894.84064959636406619385342789598109 | 23647510.96741464544799054373522458628842 | 100 | 5 | 500 |  |  |  |  | 54 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT CAUSED BY THIRD PARTY EXCAVATION DAMAGE. SCADA POINT DID NOT GO INTO ALARM AS A RESULT OF THE DAMAGE. | [12 empty] | YES | 3 | 0 | YES | 2 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | NO | [5 empty] | YES | 398 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CHRISTOPHER GIGOT | SR. ENGINEER | christopher.gigot@we-energies.com | (414) 221-5347 |  |  |  |  | TIM STROMMEN | MANAGER GAS CODE COMPLIANCE | (414) 221-5173 | tim.strommen@we-energies.com | ON TUESDAY JULY 10, 2018 AT 6:25PM, WE ENERGIES WAS NOTIFIED BY THE SUN PRAIRIE FIRE DEPARTMENT THAT NATURAL GAS FACILITIES HAD BEEN STRUCK NEAR THE INTERSECTION OF BRISTOL AND MAIN STREET IN SUN PRAIRIE, WISCONSIN. AT 6:38PM, WE ENERGIES DISPATCHED A FIRST RESPONDER WHO ARRIVED ON SITE AT 7:02 PM. UPON ARRIVAL, THE WE ENERGIES RESPONDER RECOGNIZED THE SIGNIFICANCE OF THE SITUATION BY THE LOCAL FIRST RESPONDER EVACUATIONS UNDERWAY. THE WE ENERGIES RESPONDER IMMEDIATELY CONTACTED GAS DISPATCH AND ASKED FOR ASSISTANCE. AT 7:04 PM, THE BUILDING AT 100 W. MAIN STREET EXPLODED, WHICH CAUSED MULTIPLE BUILDINGS IN THE VICINITY TO CATCH FIRE AND SUSTAIN SIGNIFICANT DAMAGE. AT 7:06PM, THE WE ENERGIES EMPLOYEE ON SITE NOTIFIED GAS DISPATCH OF THE EXPLOSION AND REQUESTED ADDITIONAL ASSISTANCE. AS A RESULT OF THE EXPLOSION, SEVEN LOCAL EMERGENCY RESPONDERS AND ONE WE ENERGIES EMPLOYEE WERE INJURED. TWO FIRE FIGHTERS AND A WE ENERGIES EMPLOYEE WERE TRANSPORTED TO A NEARBY HOSPITAL. WE ENERGIES WAS LATER INFORMED THAT ONE OF THE FIREFIGHTERS WHO WAS TRANSPORTED TO THE HOSPITAL HAD PASSED AWAY. THE OTHER FIREFIGHTER TRANSPORTED TO THE HOSPITAL REQUIRED INPATIENT, OVERNIGHT HOSPITALIZATION AND THE WE ENERGIES EMPLOYEE TRANSPORTED TO THE HOSPITAL DID NOT REQUIRE INPATIENT, OVERNIGHT HOSPITALIZATION (UPDATED 1/2/19). DUE TO THE EXTENT OF THE DAMAGE, TWELVE VALVES IN THE INCIDENT AREA NEEDED TO BE CLOSED TO STOP THE FLOW OF GAS. AT 8:06PM, WE ENERGIES PERSONAL BEGAN CLOSING THE EMERGENCY VALVES TO STOP THE FLOW OF GAS. AT 1:12 AM JULY 11, 2018 IT WAS REPORTED THAT THE ALL VALVES HAD BEEN SHUT, GAS STOPPED BLOWING, AND THE FIRE WAS OUT, RESULTING IN APPROXIMATELY 600 CUSTOMERS OUT OF SERVICE. ON JULY 10, AT 9:44PM, WE ENERGIES MADE A TELEPHONIC NOTIFICATION TO THE NATIONAL RESPONSE CENTER TO REPORT A NATURAL GAS INCIDENT PER 49 CFR PART 191.3 DUE TO ESTIMATED PROPERTY DAMAGE OF MORE THAN $50,000 AND PERSONAL INJURY NECESSITATING IN-PATIENT HOSPITALIZATION. WE ENERGIES ALSO INFORMED WISCONSIN PUBLIC SERVICE COMMISSION PIPELINE SAFETY MANAGER OF THE INCIDENT. RESTORATION OF GAS SERVICES BEGAN THE MORNING OF JULY 11, 2018 AND THE MAJORITY OF CUSTOMERS WERE RESTORED WITHIN 24 HOURS. FURTHER RESTORATION CONTINUED FOR SEVERAL DAYS AS PREMISES WERE MADE SAFE AND ACCESSIBLE. UPON INVESTIGATION, IT WAS DETERMINED THAT A THIRD PARTY EXCAVATOR INSTALLING TELECOMMUNICATIONS FACILITIES WITH HORIZONTAL DIRECTIONAL DRILLING EQUIPMENT HAD DAMAGED A 2" PE GAS MAIN. THE DAMAGED MAIN RELEASED GAS WHICH MIGRATED BELOW GRADE, INTO NEARBY BUILDINGS, AND WAS IGNITED BY AN UNKNOWN SOURCE. ONE-CALL CENTER RECORDS DO NOT INDICATE THAT THE THIRD PARTY EXCAVATOR HAD MADE A REQUEST TO LOCATE BURIED FACILITIES IN THE BORING PATH PRIOR TO CONSTRUCTION ACTIVITIES. ADDITIONALLY, AT THE DAMAGED GAS LINE LOCATION, FACILITIES HAD NOT BEEN EXPOSED BY THE EXCAVATOR TO ENSURE THAT PROPER CLEARANCES WERE MAINTAINED BETWEEN THE BORING EQUIPMENT AND WE ENERGIES FACILITIES.
2025-03-31 10:13 | NO | YES | YES | 20180074 | 32921 | 2018-08-15 11:16 | SUPPLEMENTAL FINAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2018-07-16 10:23 |  |  | 2018 | 1106 PASEO BOULVARD | KANSAS CITY | JACKSON | MO | 64106 | 39.1001 | -94.5641 | [9 empty] | 2018-07-16 13:06 | 1218524 |  | NATURAL GAS |  | 0.58 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2018-07-16 10:32 |  |  |  | 2018-07-16 10:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1983 | [5 empty] | 2 | 3408 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | GAS ESCAPING FROM A PLASTIC INLINE SERVICE TEE DUE TO IMPROPERLY STOPPING FLOW OF GAS. | CLASS 3 LOCATION | 0 | 0 | 2566 | 2959.534010520586938 | 500 | 576.6823870850715 | 0 | 0 |  |  | 3 | 3.02836879432624113475177304964539007092 |  | 0 | 3069 | 1467.396194423755200056737588652482269504 | 3539.244766399984679134751773049645390071 | 0 | 0 | 3 |  |  |  |  | 1.1 | 1.1 | 2.2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | FAILURE TO FOLLOW PROPER PROCEDURE WHILE PERFORMING A SERVICE LINE REPLACEMENT. |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY | nicole.christianer@spireenergy.com | 314-349-2929 |  |  |  |  | CRAIG HOEFERLIN | VP OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | A COMPANY CONTRACTOR WAS ABANDONING A STEEL SERVICE LINE TO 1106 PASEO BOULEVARD, KANSAS CITY, MO. THE 2-INCH STEEL SERVICE LINE WAS CONNECTED TO A 3-INCH PLASTIC MAIN WITH A PLASTIC INLINE TEE AND A TRANSITION FITTING TO THE STEEL SERVICE. WHILE IN THE PROCESS OF ABANDONING THE STEEL SERVICE LINE, THE CREW MEMBER CUT THE PLASTIC PIPE BETWEEN THE OUTLET OF THE INLINE SERVICE TEE AND THE TRANSITION FITTING WITHOUT STOPPING THE FLOW OF GAS. THE CREW MEMBER THEN ATTEMPTED TO CUT THE EXISTING STEEL SERVICE LINE WITH AN ELECTRIC RECIPROCATING SAW IN A LIVE GAS CONDITION. THE NATURAL GAS IGNITED INJURING TWO CREW MEMBERS. THE CREW MEMBERS DID NOT FOLLOW THE PROCEDURES OUTLINED IN THE COMPANY STANDARD "PREVENTION OF ACCIDENTAL IGNITION." THE TWO CREW MEMBERS WERE TAKEN TO THE HOSPITAL AND ONE OF THE CREW MEMBERS REQUIRED INPATIENT HOSPITALIZATION, THE OTHER WAS TREATED AND RELEASED. THE CONTRACTOR MANAGEMENT VERBALLY REQUESTED THAT THE HOSPITAL PERFORM A DRUG AND ALCOHOL TEST FOR THE TWO CREW MEMBERS TAKEN TO THE HOSPITAL. HOWEVER, THE HOSPITAL ONLY PERFORMED AN ALCOHOL TEST. NRC INCIDENT REPORT WAS UPDATED ON JULY 18, 2018 AT 10:12 A.M., REPORT NUMBER 1218726.
2025-03-31 10:13 | NO | YES | NO | 20180075 | 31230 | 2018-08-20 01:30 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD N.E. SUITE 20 | ALBUQUERQUE | NM | 87109 | 2018-07-19 15:58 |  |  | 2018 | INTERSECTION OF LOS ALAMITOS HEIGHTS RD & LOBO CANYON RD | GRANTS | CIBOLA | NM | 87020 | 35.175 | -107.8156 | [9 empty] | 2018-07-19 18:16 | 1218911 |  | NATURAL GAS |  | 138.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2018-07-19 11:45 |  |  |  | 2018-07-19 11:59 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1978 | [5 empty] | 4 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 3 LOCATION | 280299 | 323286.992835116912757 | 31843 | 36726.594503899863549 | 500 | 576.6823870850715 | 0 | 0 | TOTAL LOSS OF BORE MACHINE |  | 264 | 266.496453900709219858156028368794326241 |  | 0 | 312906 | 149592.1999542024999169929078014184397163 | 360856.7661800025570258581560283687943262 | 0 | 0 | 96 |  |  |  |  | 49 | 49 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 4 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | CREWS WERE MAKING REPAIRS TO 4" STEEL LINE AFTER CONTRACTORS BORE MACHINE STABILIZER. WHILE MAKING REPAIRS AN IGNITION OCCURRED UNDER BORE MACHINE THAT ENGULFED THE MACHINE RESULTING IN TOTAL LOSS. CAUSE OF IGNITION IS UNKNOWN. |  |  |  | YES | CREWS WERE MAKING REPAIRS TO 4" STEEL LINE AFTER CONTRACTORS BORE MACHINE STABILIZER. WHILE MAKING REPAIRS AN IGNITION OCCURRED UNDER BORE MACHINE THAT ENGULFED THE MACHINE RESULTING IN TOTAL LOSS. CAUSE OF IGNITION IS UNKNOWN. | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ANDREA MARTINEZ | PIPELINE SAFETY MANAGEMENT SYSTEMS MANAGER | andrea.martinez@nmgco.com | 505-697-3518 |  |  |  |  | TOM BULLARD | VP ENG-GAS MGMT-TECH SERVICES | 505-697-3599 | tom.bullard@nmgco.com | ON JULY 19, 2018, AT 11:45 NMGC CREWS WERE CALLED OUT TO A 3RD PARTY DAMAGE AT THE INTERSECTION OF LOS ALAMITOS HEIGHTS ROAD AND LOBO CANYON RD. A 4" STEEL GAS MAIN WAS PUNCTURED BY BORE MACHINE STABILIZER. WHILE MAKING REPAIRS AN IGNITION OCCURRED UNDER BORE MACHINE THAT ENGULFED THE MACHINE AND WAS A TOTAL LOSS APPROXIMATE COST OF CONTRACTOR BORE MACHINE IS $280,299 AND $31,843.00 IN OPERATORS PROPERTY DAMAGE AND REPAIR COSTS. COST OF TOTAL LOSS OF BORE MACHINE CAUSED REPORTABLE INCIDENT. INVESTIGATION IS COMPLETE, HOWEVER, CAUSE OF IGNITION IS UNKNOWN.
2025-03-31 10:13 | NO | YES | NO | 20180076 | 33006 | 2018-08-20 18:19 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-07-21 14:45 |  |  | 2018 | 365 W. NORTHWEST HWY & LAS COLINAS | IRVING | DALLAS | TX | 75039 | 32.8792 | -96.9412 | [9 empty] | 2018-07-21 19:18 | 1219129 |  | NATURAL GAS |  | 36.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-07-21 14:55 |  |  |  | 2018-07-21 16:29 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 358 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2018 | [5 empty] | 6 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY | HFW | 0.28 | [6 empty] | MECHANICAL PUNCTURE | 0.2 | 0.2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 167075 | 192698.419644476641725 | 2881 | 3322.843914384181983 | 0 | 0 |  |  | 214 | 216.023640661938534278959810874704491726 |  | 0 | 170170 | 81385.9629390922336680472813238770685579 | 196237.2871995227622422789598108747044917 | 0 | 0 | 0 |  |  |  |  | 305 | 305 | 500 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | NOTIFICATION FROM 2ND PARTY CONTRACTOR |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 9 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | NATURAL GAS | YES | 1870250110 | TEXAS811 |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | BRUCE MISERENDINO | OPERATIONS SUPERVISOR | bruce.miserindino@atmosenergy.com | 214-206-2387 |  |  |  |  | MARLO SUTTON | DIRECTOR REGULATORY AND COMPLIANCE | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT NUMBER 1219291 AT 2:55 PM ON JULY 21, 2018, A SECOND PARTY CONTRACTOR WORKING ON A REPLACEMENT PROJECT FOR ATMOS ENERGY DAMAGED A 6-INCH STEEL HIGH PRESSURE GAS LINE WHILE DIRECTIONAL DRILLING. THE LINE WAS LOCATED PRIOR TO EXCAVATION, HOWEVER, THE CONTRACTOR FAILED TO POT-HOLE AND IDENTIFY THE EXACT LOCATION OF THE GAS LINE. THE ACCESS ROAD IN FRONT OF NORTHWEST HWY AND AN ADJACENT PARKING LOT WERE BLOCKED OFF TO VEHICULAR TRAFFIC. AN ATMOS SERVICE TECH ARRIVED AT 4:29 PM AND VERIFIED THE RELEASE OF GAS. THE LEAK WAS ELIMINATED AT 6:32 PM BY CLOSING AN ABOVE-GROUND VALVE. THE DAMAGED SECTION OF THE PIPE WAS REPLACED AND PLACED BACK IN SERVICE ON OCTOBER 26, 2018.
2025-03-31 10:13 | NO | NO | NO | 20180077 | 31458 | 2018-08-22 15:44 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2018-07-22 08:31 |  |  | 2018 | 8000 FOOTHILLS BLVD | ROSEVILLE | PLACER | CA | 95747 | 38.7856 | -121.3187 | [9 empty] | 2018-07-24 11:34 | 1219376 |  | NATURAL GAS |  | 837 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-07-22 08:31 |  |  |  | 2018-07-22 08:53 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1998 | [5 empty] | 4 | ASTM D2513 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | RUPTURE |  |  |  |  | LONGITUDINAL |  | 4 | 12 |  | CLASS 3 LOCATION | 0 | 0 | 50000 | 57668.23870850715 | 0 | 0 | 0 | 0 | COSTS FOR THIS EVENT ARE STILL BEING EVALUATED, BUT ARE ESTIMATED TO BE >$50K |  | 2500 | 2523.640661938534278959810874704491725768 |  | 0 | 52500 | 26218.9702911536600472813238770685579196 | 60191.8793704456842789598108747044917258 | 1 | 0 | 0 |  |  |  |  | 480 | 45 | 60 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | ENZA BARBATO | REGULATORY COMPLIANCE | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | REGULATORY COMPLIANCE MANAGER | 925-328-5776 | gsr8@pge.com | ON JULY 22, 2018 AT 0831 HOURS, PG&E WAS NOTIFIED OF A SERVICE LINE RUPTURE AT A PARKING LOT AT 9100 FOOTHILLS BLVD IN ROSEVILLE. THE ACTUAL SERVICE LINE THAT RUPTURED WAS 8000 FOOTHILLS BLVD. PG&E'S GAS SERVICE REPRESENTATIVE ARRIVED ON-SITE AT 0853 HOURS. PG&E'S CREW STOPPED THE FLOW OF GAS BY SHUTTING IN THE STATION AT 1033 HOURS. THE AREA WAS UNCOVERED AND DETERMINED THAT THE 4" PLASTIC SERVICE HAD RUPTURED FROM A POTENTIAL MAOP EXCEEDANCE. THERE WAS NO PRESSURE MONITORING/RECORDING ON THIS LINE, THEREFORE THE EXACT PRESSURE REACHED AT THE TIME OF THE RUPTURE IS UNKNOWN. THE CAUSE OF THE OVERPRESSURE EVENT WAS A MALFUNCTION OF THE CONTROL EQUIPMENT. ONE CUSTOMER'S GAS SERVICE WAS IMPACTED. THE CUSTOMER'S GAS SERVICE WAS RESTORED USING COMPRESSED NATURAL GAS (CNG) PORTABLE TANKS ON 7/23/18 AT 0700 HOURS. THE RUPTURED SERVICE PIPE IS PLANNED TO BE DEACTIVATED, AND A NEW SERVICE IS TO BE INSTALLED FROM AN EXISTING DISTRIBUTION MAIN. CONSTRUCTION IS PENDING. THERE WERE NO INJURIES, FATALITIES OR IGNITION ASSOCIATED WITH THIS INCIDENT. FIRE DEPARTMENT WAS REPORTED ON-SITE. THIS INCIDENT WAS REPORTED TO THE CPUC DUE TO A MAOP EXCEEDANCE EVENT, WHICH WAS DETERMINED ON 7/22/18 AT 1748 HOURS. ON 7/24/18 AT 1120 HOURS, IT WAS DETERMINED THAT REPAIR COSTS WOULD EXCEED $50K. ON 7/24/18 AT 1134 HOURS, THIS INCIDENT WAS REPORTED TO THE DOT DUE TO THE $50K CRITERIA. GAS EQUIPMENT AFFECTED
2025-03-31 10:13 | YES | NO | NO | 20180078 | 30847 | 2018-08-23 20:26 | ORIGINAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2018-07-26 09:00 |  |  | 2018 | 4245 WAYSHARA AVE. | REDDING | SHASTA | CA | 96001 | 40.5799 | -122.4279 | [9 empty] | 2018-07-28 10:50 | 1219782 |  | NATURAL GAS |  | 740 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 614 | 2018-07-28 10:10 |  |  |  | 2018-07-27 01:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1971 | [8 empty] | PLASTIC |  |  |  |  | UNKNOWN |  |  |  | UNKNOWN |  | LEAK |  |  | OTHER | FOUND 4 METERS MELTED | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 229000 | 264120.533284962747 | 810000 | 934225.46707781583 | 0 | 0 | COSTS ARE FOR THE EMERGENCY RESPONSE FOR THE ENTIRE SHASTA COUNTY. |  | 2220 | 2240.992907801418439716312056737588652482 |  | 0 | 1041220 | 498392.0229811423229219858156028368794326 | 1200586.99327057999543971631205673758865 | 0 | 0 | 614 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DUE TO A WILDFIRE BEYOND OPERATORS CONTROL. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | ENZA BARBATO | REGULATORY COMPLIANCE | e1bo@pge.com | 925-357-7889 |  |  |  |  | SUSIE RICHMOND | REGULATORY COMPLIANCE MANAGER | 925-786-0267 | gsr8@pge.com | ON JULY 26, 2018 AT 0900 HOURS (OPERATIONAL AT 1400 HOURS), THE NORTH VALLEY OPERATIONS EMERGENCY CENTER (OEC) WAS ACTIVATED TO SUPPORT THE CARR FIRE IN REDDING. DURING THE NIGHT OF JULY 25-26, THE FIRE INCREASED IN SIZE. GAS EMERGENCY CENTER (GEC) WAS ACTIVATED TO SUPPORT THE EVENT. AS OF 7/27/18 AT 1300 HOURS, 468 GAS CUSTOMERS WERE PROACTIVELY SHUT IN. DURING THE NIGHT OF JULY 27-28, CREWS CONTINUED TO ASSESS ADDITIONAL AREAS. AS OF 7/28/18 AT 0600 HOURS, THE CREW SHUT-IN AN ADDITIONAL 71 GAS CUSTOMER SERVICES AND CUT-OFF 17 GAS SERVICES. AS OF 7/29/18 AT 1500 HOURS, ALL KNOWN PRESSURIZED RISERS WITHOUT A HOME HAVE BEEN CUT-OFF. PG&E CREWS CUT OFF RISERS WITHOUT HOMES IN THE DEPRESSURIZED ZONES. RESTORATION AND SUBSEQUENT RELIGHTS WERE COMPLETED FOR HOMES THAT WERE ABLE TO BE RESTORED BY 8/5/18. 32 REMAINING CUSTOMERS WERE LEFT A SERVICE REPORT ADVISING THEM TO CALL THE CONTACT CENTER TO BE RESTORED AT THEIR CONVENIENCE. THERE WERE APPROXIMATELY 614 CUSTOMERS WHO HAD THEIR GAS SERVICE IMPACTED. AS THE EVACUATION COVERED A VAST AREA OF SHASTA-TRINITY COUNTY AND THE EVACUATION TOTAL IS UNDETERMINED AT THE TIME OF THIS REPORT. THERE WERE NO REPORTED INJURIES OR FATALITIES INVOLVING NATURAL GAS. PG&E REPORTED THIS INCIDENT TO THE DOT AND CPUC DUE TO THE UNINTENTIONAL RELEASE OF GAS AND ESTIMATED REPAIR COSTS GREATER THAN $50K. THIS WAS DETERMINED ON 7/28/18 AT 1010 HOURS. AN UPDATE WAS PROVIDED TO THE DOT (1219914) ON 7/30/18 AT 0922 HOURS.
2025-03-31 10:13 | NO | YES | YES | 20180079 | 32257 | 2018-08-24 08:48 | SUPPLEMENTAL FINAL | 2412 | CITIZENS GAS UTIL DIST | 12519 SCOTT HWY PO BOX 320 | HELENWOOD | TN | 37755 | 2018-07-25 21:30 |  |  | 2018 | UNKNOWN | JELLICO | CAMPBELL | TN | 37762 | 36.5761 | -84.1992 | [9 empty] | 2018-07-26 09:20 | 1219541 |  | NATURAL GAS |  | 382 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | NO | 0 | 2018-07-25 22:30 |  |  |  | 2018-07-25 23:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | OTHER | CONSUMER OWNED UTILITY DISTRICT | OTHER | BLOW-OFF PIPE FOR DRIP GAS | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 3.1 | 1 |  | CLASS 1 LOCATION | 0 | 0 | 600 | 692.0188645020858 | 600 | 692.0188645020858 | 0 | 0 |  |  | 1200 | 1211.347517730496453900709219858156028369 |  | 0 | 2400 | 1693.794294079886422695035460992907801418 | 2595.385246734668053900709219858156028369 | 0 | 0 | 0 |  |  |  |  | 180 | 180 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | CHRIS PIERCE |  | cpierce@citizensgas.org | 423-539-0391 | 423-569-5303 |  |  |  | GREG BELL | GENERAL MANAGER | 423-569-4457 | citgasgb@highland.net | UPDATE FOR SUPPLEMENTAL REPORT: NO NEW INFORMATION HAS BECOME AVAILABLE TO US FOR THIS REPORT. AT THIS TIME WE HAVE STILL BEEN UNABLE TO VERIFY THE DETAILS OF WHAT HAPPENED AND THE ACTUAL INJURIES THAT MAY HAVE OCCURRED DURING THIS EVENT. OUR EMPLOYEES WERE TOLD THAT ONE OR MORE INDIVIDUALS WERE TAKEN TO THE LOCAL EMERGENCY ROOM AND THEN FLOWN OUT TO A TRAUMA CENTER FOR BURN INJURIES. ORIGINAL DESCRIPTION: PLEASE NOTE THAT MOST INFORMATION, OTHER THAN INCURRED DAMAGE IS HERESAY. LOCAL POLICE DEPARTMENTS WERE CONTACTED IN ORDER TO GATHER MORE INFORMATION AND CONFIRM ANY INFORMATION WE HAD, HOWEVER NO POLICE REPORTS WERE FILED AND THEY HAD NO ADDITIONAL OR CONFIRMING INFORMATION. ON THE EVENING OF JULY 25TH, TWO INDIVIDUALS WERE APPARENTLY TRESPASSING ON PRIVATE PROPERTY AND ON CITIZENS GAS UTILITY DISTRICT RIGHT-OF-WAY. THE INDIVIDUALS WERE RIDING IN A SIDE BY SIDE UTV AND IT APPEARS AS IF THEY STRUCK A 1" PIPE THAT HAD PREVIOUSLY BEEN USED TO EXPEL DRIP GAS FROM THE PIPELINE. WHEN OUR CREW ARRIVED THEY FOUND THE SIDE BY SIDE HAD BEEN ON FIRE AND THE INDIVIDUALS IN QUESTION HAD LEFT THE SCENE WITH ANOTHER THIRD PARTY AND BEEN TAKEN TO THE LOCAL HOSPITAL. WE ARE UNCERTAIN OF THE EXTENT OF INJURIES TO THE INDIVIDUALS INVOLVED IN THE INCIDENT. NOTHING ELSE IN THE AREA APPEARED TO HAVE BEEN ON FIRE. THE 1" LINE HAD BEEN BROKEN BELOW AN INSTALLED SHUT OFF VALVE, BUT THE PIPELINE HAD ALMOST BLOWN DOWN BY THE TIME OUR CREW ARRIVED DUE TO THE PLACEMENT OF A CHECK VALVE IN THE MAIN LINE AND A VALVE BEING SHUT OFF AT THE GAS SOURCE AT A NEARBY COMPRESSOR STATION THAT IS OPERATED BY ANOTHER ENTITY.
2025-03-31 10:13 | NO | NO | NO | 20180080 | 30975 | 2018-08-25 07:03 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2018-07-26 19:55 |  |  | 2018 | W.150TH & PURITAS AVE. | CLEVELAND | CUYAHOGA | OH | 44135 | 41.4336 | -81.8012 | [9 empty] | 2018-07-27 10:41 | 1219656 |  | NATURAL GAS |  | 4774 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-07-26 19:55 |  |  |  | 2018-07-26 20:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1968 | [5 empty] | 8 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 968 | 1116.457101396698424 | 1187 | 1369.043986939959741 | 0 | 0 |  |  | 21532 | 21735.6122931442080378250591016548463357 |  | 0 | 23687 | 21136.1339552461222752245862884160756501 | 24221.1133814808662028250591016548463357 | 0 | 0 | 0 |  |  |  |  | 81 | 81 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | OTHER COMPRESSION TYPE FITTING | STYLE 38 COMPRESSION |  |  | DRESSER |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | INADEQUATE SUPPORT | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | JEFFERY BURDETTE | TECHNICAL SPECIALIST III | jeffery.l.burdette@dominionenergy.com | 330-754-5524 |  |  |  |  | JEFFERY BURDETTE | TECHNICAL SPECIALIST III | 330-754-5524 | jeffery.l.burdette@dominionenergy.com | THE 1968 STEEL 8" SYSTEM IS BEING REPLACED WITH 8" HD PLASTIC. DUE TO ONGOING REPLACEMENT WORK BEING PERFORMED, THE LINE HAD NOT YET BEEN BACKFILLED IN THE FAILED AREA. AN EXISTING 8" STEEL TO STEEL STYLE 38 DRESSER COUPLING PULLED APART. THE EXISTING COUPLING APPEARS TO HAVE SEPARATED DUE TO LACK OF SUPPORT.
2025-03-31 10:13 | NO | YES | YES | 20180081 | 30886 | 2018-09-02 16:24 | ORIGINAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2018-05-12 05:00 |  |  | 2018 | 4695 W JEFFERSON | TRENTON | WAYNE COUNTY | MI | 48183 | 42.1221 | -83.1798 | [9 empty] | 2018-08-03 10:33 | 1220406 |  | NATURAL GAS |  | 13 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO |  |  |  |  | NO | 0 | 2018-05-12 05:00 |  |  |  | 2018-05-12 05:28 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | HIGH-HEAD EXTENSION EQUIPMENT | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 77258 | 89106.655722836907894 | 19693 | 22713.212497732626099 | 0 | 0 |  |  | 37 | 37.34988179669030732860520094562647754137 |  | 0 | 96988 | 46346.9866155603349166997635933806146572 | 111857.2181023662243003286052009456264775 | 0 | 3 | 0 |  |  |  |  | 145 | 145 | 150 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | FRENAE F. SMITH | MANAGER | frenae.smith@dteenergy.com | 313-389-7762 | 313-389-7755 |  |  |  | FRENAE F. SMITH | MANAGER | 313-460-1681 | frenae.smith@dteenergy.com | DTE GAS RECEIVED A CALL FROM TRENTON FIRE DEPARTMENT OF A VEHICLE HIT OF A GAS LINE AT 6:12AM. DTE GAS WAS ONSITE AT 6:51PM. ONCE DTE GAS FIRST RESPONDERS WERE ON SEEN IT WAS CONFIRMED THAT A DRIVER HAD HIT THE HIGH-HEAD EXTENSION AT THE LOCATION. THERE WAS A LEAK AS A RESULT OF THE INCIDENT. THE DRIVER WAS TAKEN TO THE HOSPITAL AND DRUG & ALCOHOL TESTING WAS PERFORMED. RESULT. THIS LEAK IMPACTED 3 BUSINESSES. THE MPSC WAS CONTACTED AT 11:33AM ONCE IT WAS REALIZED THAT THE REPAIR WAS GOING TO BE APPROXIMATELY $10,000. GAS WAS OFF AT 15:03PM ON 5/12/18 WITH A RELEASE OF GAS OF 13 MCF. ON AUGUST 3RD, 2018, THE REPAIR COST REPORT WAS RECEIVED AND WAS $96,988. THE NRC WAS CONTACTED AT ON 8/3/18 AT 10:33AM TO REPORT THE INCIDENT BASED ON COST TO THE OPERATOR.
2025-03-31 10:13 | NO | YES | NO | 20180082 | 32163 | 2018-09-06 13:01 | SUPPLEMENTAL FINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2018-05-12 04:35 |  |  | 2018 | 13004 S 29TH STREET | BELLEVUE | SARPY | NE | 68123 | 41.1153 | -95.9549 | [9 empty] | 2018-08-08 11:07 | 1220893 |  | NATURAL GAS |  | 4 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 6 | 2018-05-12 04:35 |  |  |  | 2018-05-12 05:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 52 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1977 | [5 empty] | 0.625 | UNKNOWN | X-TRUBE | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | LIGHTNING STRIKE | CLASS 3 LOCATION | 100000 | 115336.4774170143 | 2500 | 2883.4119354253575 | 3000 | 3460.094322510429 | 0 | 0 |  |  | 12 | 12.11347517730496453900709219858156028369 |  | 0 | 105512 | 50407.405564925239248226950354609929078 | 121692.0971501273914645390070921985815603 | 0 | 0 | 1 |  |  |  |  | 60 | 60 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  | ,,, | NO | [218 empty] | MICHAEL CONRAD | SENIOR CLAIMS INVESTIGATOR | mike_conrad@mudnebr.com | 4025047165 | 4025045165 |  |  |  | MICHAEL CONRAD | SENIOR CLAIMS INVESTIGATOR | 4025047165 | mike_conrad@mudnebr.com | ON SATURDAY MAY 12, 2018 LIGHTNING STRUCK THE RESIDENCE LOCATED AT 13004 S 29TH STREET, BELLEVUE, SARPY COUNTY, NEBRASKA DURING A SEVERE WEATHER STORM. IT WAS THE REASONABLE BELIEF OF THE OPERATOR BASED ON THE INFORMATION AVAILABLE AT THE TIME OF THE INCIDENT UP UNTIL AUGUST 8, 2018 THAT THE LIGHTNING STRIKE CAUSED A FIRE INSIDE OF THE HOUSE FOLLOWED BY A SECONDARY IGNITION AT THE METER SET. BECAUSE THIS WAS BELIEVED TO BE A SECONDARY IGNITION EVENT, IT WAS NOT REPORTED TO THE NRC BECAUSE THE DAMAGE TO THE OPERATORS FACILITIES DID NOT EXCEED $50,000. THE OPERATOR RECEIVED ADDITIONAL INFORMATION ON AUGUST 8, 2018 FROM THE NEBRASKA STATE FIRE MARSHAL THAT INDICATED THAT IGNITION AT THE METER SET LIKELY OCCURRED CONCURRENTLY WITH THE FIRE THAT OCCURRED INSIDE OF THE HOUSE AS A RESULT OF THE LIGHTNING STRIKE. BASED ON THAT INFORMATION, THE OPERATOR PROMPTLY REPORTED THE INCIDENT AT 11:07 AM THAT DAY. THE 48-HOUR FOLLOW-UP REPORT WAS SUBMITTED AT APPROXIMATELY 10:00 AM ON AUGUST 10, 2018 (NRC #1221114). ON OCTOBER 24, 2018 THE GAS SERVICE WAS RESTORED TO THE RESIDENCE. THERE IS NO FURTHER WORK NEEDED AT THIS LOCATION AND THIS MATTER IS NOW FINAL.
2025-03-31 10:13 | NO | YES | NO | 20180083 | 31878 | 2018-09-07 13:10 | SUPPLEMENTAL FINAL | 31467 | UGI CENTRAL PENN GAS, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2018-08-09 11:08 |  |  | 2018 | 304 TOMBS RUN ROAD | JERSEY SHORE | LYCOMING | PA | 17740 | 41.2573 | -77.271 | [9 empty] | 2018-08-09 15:22 | 1221035 |  | NATURAL GAS |  | 15992 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 3 | 2018-08-09 11:05 |  |  |  | 2018-08-09 11:34 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1961 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.156 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 1 LOCATION | 0 | 0 | 15500 | 17877.1539996372165 | 187000 | 215679.212769816741 | 0 | 0 |  |  | 37263 | 37615.3687943262411347517730496453900709 |  | 0 | 239763 | 131528.4608848460820567375886524822695035 | 271171.7355637801986347517730496453900709 | 0 | 0 | 1 |  |  |  |  | 326 | 327 | 350 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY EXCAVATION DAMAGE AND EMERGENCY RESPONSE WAS PROMPTLY HANDLED BY UGI'S CONTACT CENTER AND DISPATCH. CONTROLLER ACTION AND CONTROL ROOM ISSUES DID NOT CREATE THE INCIDENT NOR IMPACT EMERGENCY RESPONSE. | [12 empty] | NO |  |  | YES | 2 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | COUNTY ROAD |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 20181062791 |  |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | FRANK BENNETT | DIRECTROR ENGINEERING AND TECHNICAL SERVICES | fbennett@ugi.com | 6107963567 |  |  |  |  | KELLY BEAVER | VP ENGINEERING AND OPERATIONS SUPPORT | 6107963601 | kbeaver@ugi.com | **THIS A SUPPLEMENTARY REPORT TO UPDATE THE TOTAL DAMAGE AND REPAIR COST IN PART D.2. A TYPO WAS ALSO FOUND IN THE 1-CALL TICKET NUMBER FOR THE WORK IN PART G3.9, THE REPORT INCORRECTLY STATED 2014062791 WHEN IT SHOULD HAVE BEEN 2018062791. THIS SUPPLEMENTARY REPORT WILL BE THE LAST REPORT FILED FOR THIS EVENT. ** A CONTRACTOR WAS INSTALLING A NEW GAS PIPELINE TO REPLACE AN EXISTING GAS PIPELINE. THE CONTRACTOR HIT A SERVICE LINE, AND PULLED THE SERVICE TAP OFF THE EXISTING MAIN. THREE HOUSES IN THE VICINITY OF THE LINE HIT WERE EVACUATED AND ELECTRIC POWER WAS SHUT OFF. VALVES COULD HAVE BEEN CLOSED TO PROMPTLY ISOLATE THE LEAK, AND IF THIS WAS DONE, THE INCIDENT REPORTING CRITERIA WOULD NOT HAVE BEEN MET. CLOSING VALVES WOULD HAVE RESULTED IN LOSS OF GAS SERVICE TO OVER 2000 CUSTOMERS INCLUDING 2 HOSPITALS. UGI MADE THE DECISION TO ALLOW THE GAS TO VENT TO A SAFE AREA WHILE A TEMPORARY BYPASS WAS INSTALLED. THE NRC WAS CALLED WHEN GAS LOSS CALCULATIONS INDICATED THAT OVER 3000 MCF WOULD BE VENTED. THE COST OF INSTALLING THE BYPASS ALSO EXCEEDED $50,000.
2025-03-31 10:13 | NO | YES | NO | 20180084 | 33027 | 2018-09-13 18:54 | SUPPLEMENTAL FINAL | 31191 | ENERGY WEST MONTANA | NO. 1 FIRST AVENUE SOUTH P.O. BOX 2229 | GREAT FALLS | MT | 59403-2229 | 2018-08-26 03:39 |  |  | 2018 | 4601 WILLOWDALE LANE | GREAT FALLS | CASCADE | MT | 59404 | 47.4636 | -111.3172 | [9 empty] | 2018-08-26 13:52 | 1222758 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2018-08-26 06:27 |  |  |  | 2018-08-26 03:55 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  | 60 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1980 | [5 empty] | 1 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 700000 | 807355.3419191001 | 900 | 1038.0282967531287 | 7100 | 8188.8898966080153 | 0 | 0 |  |  | 0 | 0 |  | 0 | 708000 | 338203.881734083344 | 816582.260112461244 | 0 | 0 | 2 |  |  |  |  | 230 | 60 | 60 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | SOCKET, HEAT FUSION |  | 1980 | ALDYL-A | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [13 empty] | YES | TENSILE STRESS, & EXTERNAL AND INTERNAL PRESSURE |  |  |  | YES |  |  |  | NO | [86 empty] | IRA SHAULIS | SAFETY DIRECTOR | ishaulis@egas.net | 4068680748 |  |  |  |  | IRA SHAULIS | SAFETY DIRECTOR | 4068680748 | ishaulis@egas.net | THE 1" CTS, SDR 11.5, ALDYL-A PIPE AND 1" SOCKET FUSION COUPLING WERE DIRECTLY UNDER THE FOOTING AND FOUNDATION OF 4601 WILLOWDALE LANE. THERE APPEARED TO BE EXTERNAL DAMAGE TO THE 1" COUPLING AND THE 1" CTS PIPING APPEARS TO HAVE BEEN LOWERED IN PLACE BY THE HOME BUILDER. THE 1" CTS PIPING WAS A DEAD END SERVICE STUB AND WAS UNKNOWINGLY OPERATING AT 230 PSI DUE TO A PREVIOUS UPRATE OF A 10" STEEL PIPELINE. THE 1" CTS, SDR 11.5, ALDYL-A PIPE AND 1" SOCKET FUSION COUPLING WERE SUBJECT TO A SHOCKWAVE CREATED BY THE HOME EXPLOSION. THE 1" CTS, SDR 11.5, ALDYL-A PIPE AND 1" SOCKET FUSION COUPLING IS BEING SENT TO AN INDEPENDENT LAB FOR A FORENSIC INVESTIGATION AND TESTING. 4/12/2019: LAB TESTING RESULTS WERE RECEIVED FROM TWO THIRD PARTY CONSULTANTS. RESULTS INDICATED THAT THE 1" COUPLING FAILED DUE TO SLOW CRACK GROWTH PROPAGATION AS A RESULT OF MULTIPLE STRESSES BEING APPLIED TO THE FITTING. PER THE REPORTS, THE CRACK GROWTH AND LEAK POINT ON THE COUPLING WAS CONSISTENT WITH A TENSILE LOAD ON THE COUPLING. THE PHENOMENA OF A BRITTLE CRACK WHICH STARTS IN THE LOCATION WHERE THE HEAT FUSION JOINED TUBING TERMINATES ON THE INTERIOR OF A SOCKET FUSION HAS BEEN DOCUMENTED PREVIOUSLY IN INDUSTRY. THE CRACK FORMED BY THE NOTCH GEOMETRY CREATED BY THE INSERTED TUBING AND ITS POINT OF HEAT FUSION JOINING TO THE SOCKET WHICH, WHEN UNDER GAS PRESSURE, CAN CREATE A STRESS RISER. THE NOTCH GEOMETRY MAY HAVE BEEN CONTRIBUTED BY THE SOCKET FUSION TOOLS AVAILABLE AT THE TIME OF INSTALLATION. THE FAILURE IS ALSO CONSISTENT WITH INDUSTRY KNOWLEDGE OF ALDYL-A PIPE AND FITTINGS MANUFACTURED PRIOR TO 1984 AND SUSCEPTIBILITY TO INNER WALL CRACKING. THE COUPLING WAS 10" UNDER THE FOUNDATION OF THE GARAGE AND APPEARED TO BE LOWERED IN PLACE DURING THE CONSTRUCTION OF THE STRUCTURE. LOWERING WOULD HAVE CAUSED TENSILE STRESS ON THE PIPE AND COUPLING. NO EXTERNAL DAMAGES WERE SEEN ON THE PIPE OR COUPLING FROM CONSTRUCTION OF THE GARAGE STRUCTURE. AGAIN PER THE REPORTS, THE INTERNAL PRESSURE IN THE PIPE MAY HAVE ACCELERATED THE FAILURE IN THE COUPLING BUT COULD NOT BE DETERMINED AS THE SOLE ROOT CAUSE OF THE FAILURE. THE TIME TO FAILURE FROM CRACKING COULD NOT BE ESTIMATED OR DETERMINED IN EITHER REPORT. 11/19/2019 - SUBMITTED AS FINAL REPORT WITHOUT FURTHER CHANGES AT THIS TIME.
2025-03-31 10:13 | NO | YES | YES | 20180085 | 33377 | 2018-09-17 11:26 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2018-08-17 12:15 |  |  | 2018 | 23 E. DAME AVENUE | HOMERVILLE | CLINCH | GA | 31634 | 31.0369 | -82.7469 | [9 empty] | 2018-08-17 15:26 | 1221854 |  | NATURAL GAS |  | 31.8 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES |  |  |  |  | YES | 125 | 2018-08-17 10:09 |  |  |  | 2018-08-17 10:54 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 50 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1989 | [5 empty] | 2 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 88500 | 102072.7825140576555 | 16565 | 19105.487484128418795 | 200 | 230.6729548340286 | 0 | 0 |  |  | 230 | 232.174940898345153664302600472813238771 |  | 0 | 105495 | 50498.7183667317579443498817966903073286 | 121641.1178939184480486643026004728132388 | 0 | 0 | 0 |  |  |  |  | 43 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 8088262005 |  |  | CONTRACT LOCATOR | NO |  |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | 404-584-4910 | rslagle@southernco.com | AN EXCAVATOR (LGM SERVICES LLC.) INSTALLING FIBER OPTIC COMMUNICATIONS CONDUIT BY DIRECTIONAL DRILLING STRUCK AN ATLANTA GAS LIGHT COMPANY 2-INCH PE 45 PSIG NATURAL GAS MAIN DURING A BORE. AN ADJACENT SEWER MAIN WAS ALSO DAMAGED. THE DISTANCE BETWEEN THE DAMAGE TO THE GAS MAIN AND THE DAMAGE TO THE SEWER MAIN WAS APPROXIMATELY 4 FT., 6 IN. GAS LEAKING FROM THE 2-INCH GAS MAIN ENTERED UNDERGROUND SEWER FACILITIES THROUGH THE DAMAGED PORTION OF THE SEWER MAIN AND THEN TRAVELED TO THE SEWER LATERAL FOR THE COFFEE SHOP LOCATED AT 23 E. DAME AVE., HOMERVILLE, GA. AN INSPECTION OF THE COFFEE SHOP REVEALED AN IMPROPERLY PLACED P-TRAP, WHICH IS THE LIKELY PATH OF ENTRANCE OF THE NATURAL GAS INTO THE COFFEE SHOP. THE GAS THAT ENTERED THE COFFEE SHOP THROUGH THE LATERAL WAS THEN IGNITED BY AN UNKNOWN IGNITION SOURCE. THERE ARE NO GAS FACILITIES GOING TO THE COFFEE SHOP. THREE (3) INDIVIDUALS IN THE STRUCTURE WERE INJURED RESULTING IN HOSPITALIZATION. IN ADDITION TO THE DAMAGE TO THE COFFEE SHOP STRUCTURE ITSELF, TWO PARKED VEHICLES WERE DAMAGED. LOCATES WERE REQUESTED BY THE EXCAVATOR IN THE GENERAL AREA OF THEIR WORK. HOWEVER, THE EXCAVATOR WAS DIRECTIONAL DRILLING OUTSIDE OF THE SCOPE OF THOSE LOCATE REQUEST(S). THERE WAS NO LOCATE REQUEST MADE FOR THE AREA WHERE THE DAMAGE TO THE GAS MAIN OCCURRED. IT APPEARED THAT THERE WAS NO INDICATION THAT THE EXCAVATOR HAD WHITE LINED THE AREA OF THE DRILL PATH OR WHERE THE DAMAGE TO THE GAS MAIN OCCURRED, BUT THE EXCAVATOR HAD PLACED WHITE FLAGS IN OTHER NEARBY AREAS. ADDITIONAL NRC REPORT NUMBER 1222363 WAS CREATED FOR THE SAME EVENT AFTER A 48 HOUR SUPPLEMENTAL CALL WAS PLACED WITH THE NRC.
2025-03-31 10:13 | NO | YES | YES | 20180086 | 31449 | 2018-09-21 16:55 | SUPPLEMENTAL FINAL | 15329 | PEOPLES GAS LIGHT & COKE CO | 200 E RANDOLPH STREET | CHICAGO | IL | 60601 | 2018-08-24 12:39 |  |  | 2018 | 2037 N MILWAUKEE AVE | CHICAGO | COOK | IL | 60647 | 41.9181 | -87.6892 | [9 empty] | 2018-08-24 14:22 | 1222593 |  | NATURAL GAS |  | 75.9 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2018-08-24 12:39 |  |  |  | 2018-08-24 13:03 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 40 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2012 | [5 empty] | 2 | UNKNOWN | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | UNKNOWN | OTHER | [8 empty] | IT IS CURRENTLY UNKNOWN IF THE INITIAL DAMAGE TO THE THE GAS MAIN WITH A SHOVEL, TORCH, OR BUCKET ON A TRENCHER. THE SIZE OF THE INITIAL DAMAGE IS UNKNOWN SINCE THE PIPE MELTED DURING THE FIRE. | CLASS 4 LOCATION | 10000 | 11533.64774170143 | 0 | 0 | 7421 | 8559.119989116631203 | 0 | 0 |  |  | 279 | 281.638297872340425531914893617021276596 |  | 0 | 17700 | 8582.35369976574404927659574468085106383 | 20374.4060286904016285319148936170212766 | 0 | 0 | 11 |  |  |  |  | 22 | 22 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY A THIRD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | OTHER | [12 empty] | DEVELOPER | UNKNOWN/OTHER | BUILDING CONSTRUCTION | YES | 600505057 | 811 CHICAGO |  | CONTRACT LOCATOR | YES | YES | 8 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | SHAWN BARTELS | PRINCIPAL ENGINEER | shawn.bartels@peoplesgasdlivery.com | (312)240-5421 |  |  |  |  | THOMAS WEBB | COMPLIANCE MANAGER | (312)240-4650 | thomas.webb@peoplesgasdelivery.com | ON FRIDAY, 08/24/2018, WHILE EXCAVATING FOR A NEW COMMERCIAL BUILDING, TAYLOR EXCAVATING IGNITED A 2" MP YELLOW PLASTIC GAS MAIN CAUSING INJURY TO 2 OF THEIR WORKERS. PGL RECEIVED NOTICE OF THE INCIDENT AT 12:39PM AND ARRIVED ON SITE AT 1:03PM. THE GAS WAS ISOLATED BY PGL CREWS AT 1:10PM. TO THE BEST OF OUR KNOWLEDGE, THESE TWO WORKERS WERE SENT TO THE HOSPITAL. ONE OF THE WORKERS WAS RELEASED AFTER RECEIVING CARE AND THE OTHER REMAINED OVERNIGHT. THE LOCATION OF THE DAMAGED GAS MAIN IS 3' EAST OF THE WEST SIDE OF N. CAMPBELL AVE. AND IN THE PUBLIC RIGHT OF WAY. TAYLOR EXCAVATING HAD ONLY REQUESTED PRIVATE PROPERTY DIG TICKETS AND DID NOT HAVE THE RIGHT TO DIG IN THE PUBLIC RIGHT OF WAY. PGL HAD CUT OFF THE ONLY GAS SERVICE HEADING INTO THIS EXCAVATION SITE ON 04/24/2018, AND PGL NO LONGER HAD ANY LIVE GAS FACILITIES IN THE SCOPE OF TAYLOR EXCAVATING'S PROJECT. USIC HAD MADE CONTACT WITH SEVERAL WORKERS ON SITE WHILE COMPLETING THE LOCATE AND HAD CLEARED THE DIG TICKETS AS EXCAVATION SITE CLEAR. THESE TWO WORKERS, PLUS A THIRD WORKER, WERE SAID TO HAVE BEEN DIGGING WITH SHOVELS AROUND A CAISSON CLOSE TO THE DAMAGED GAS MAIN. MULTIPLE TAYLOR EXCAVATING EMPLOYEES STATED THAT THEY HAD NOT SMELLED GAS AT ANY TIME PRIOR TO THE IGNITION. TAYLOR EXCAVATING STATED THEY HAD 3 EMPLOYEES DIGGING WITH SHOVELS AROUND THE CAISSON WHICH IS NEAR THE GAS MAIN WHEN THE FIRE ERUPTED. THE OWNER AND FOREMAN ON SITE STATED THAT THERE WERE SEVERAL METAL SHAVINGS IN THEIR EXCAVATION AND MAYBE THEY HIT ONE OF THOSE OR THE CAISSON AND CAUSED A SPARK. THEY STATED THAT THEY WERE DIGGING AROUND THE CAISSON AND MOVING THE EARTH TOWARDS A TRENCHER THAT WAS REMOVING THE SPOIL. THE TRENCHER WAS SAID TO HAVE BEEN APPROXIMATELY 15 FEET SOUTH AND 5 FEET WEST OF THE DAMAGED GAS MAIN. OTHER WORKERS WHOM HAD SPOKEN WITH A PGL EMPLOYEE SAID THAT THE FIRE STARTED WHEN THEY STRUCK A TORCH THEY WERE GOING TO USE TO CUT THE CAISSON. IT IS CURRENTLY UNKNOWN IF TAYLOR EXCAVATING DAMAGED THE GAS MAIN WITH A SHOVEL, TORCH, OR THE BUCKET ON THE TRENCHER.
2025-03-31 10:13 | NO | YES | YES | 20180087 | 31008 | 2018-09-25 17:47 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2018-08-30 01:57 |  |  | 2018 | 671 12TH AVE | COLUMBUS | PLATTE | NE | 68601 | 41.4228 | -97.3418 | [9 empty] | 2018-08-31 09:37 | 1223265 |  | NATURAL GAS |  | 6 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES |  |  |  |  | NO | 1 | 2018-08-30 02:10 |  |  |  | 2018-08-30 02:30 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 75000 | 86502.358062760725 | 225 | 259.507074188282175 | 1500 | 1730.0471612552145 | 0 | 0 |  |  | 36 | 36.34042553191489361702127659574468085106 |  | 0 | 76761 | 36684.313103264653044680851063829787234 | 88528.2527237361365686170212765957446809 | 0 | 0 | 1 |  |  |  |  | 8 | 8 | 10 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | BILL STEPHENS | MGR CODES AND STANDARDS | bill.stephens@blackhillscorp.com | 3035663509 |  |  |  |  | BILL STEPHENS | MGR CODES AND STANDARDS | 3035663509 | bill.stephens@blackhillscorp.com | ON 8-30-2018 AT 1:57 A.M., A PICKUP TRUCK WAS TRAVELING EAST ON 7TH STREET IN COLUMBUS NEBRASKA TOWARD A TEE INTERSECTION AT 12TH AVENUE. THE PICKUP TRUCK FAILED TO STOP AT A STOP SIGN AND CONTINUED ACROSS 12TH STREET, JUMPING THE CURB, ACROSS THE FRONT LAWN OF A RESIDENCE AT 671 12TH AVE, AND IMPACTED THE HOUSE AT SAME ADDRESS AS WELL AS THE NATURAL GAS METER SERVING THE HOME. THE IMPACT OF THE TRUCK BUSTED THROUGH THE OUTER WALL OF THE RESIDENCE AND THE GAS METER AT THE STRUCTURE. THIS IMPACT TO THE GAS METER ALLOWED BLOWING NATURAL GAS AND WAS IGNITED, CATCHING THE RESIDENCE AND VEHICLE ON FIRE. LOCAL POLICE AND FIRE DEPARTMENT RESPONDED AND THE OCCUPANTS FROM THE VEHICLE WERE REMOVED FROM THE VEHICLE AND TRANSPORTED TO THE HOSPITAL FOR BURN INJURIES. THE FIRE WAS EXTINGUISHED AND THE BLOWING GAS FROM THE METER WAS PINCHED OFF BELOW GROUND TO STOP THE FLOW OF NATURAL GAS BY BLACK HILLS ENERGY TECHNICIAN AND FIRE DEPARTMENT PERSONNEL. THE GAS SERVICE TO THE RESIDENCE WAS ABANDONED UNTIL REPAIRS TO THE STRUCTURE HAVE BEEN COMPLETED.
2025-03-31 10:13 | NO | NO | NO | 20180088 | 31120 | 2018-09-28 16:06 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2018-08-31 09:15 |  |  | 2018 | REDHAWK PARKWAY AND EL CHIMISAL ROAD | TEMECULA | RIVERSIDE | CA | 92592 | 33.4702 | -117.0762 | [9 empty] | 2018-08-31 16:47 | 1223342 |  | NATURAL GAS |  | 4265 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-08-31 09:15 |  |  |  | 2018-08-31 09:50 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2000 | [5 empty] | 4 | PLASTIC | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.333 |  | UNKNOWN | MECHANICAL PUNCTURE | 4 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 37303 | 43023.966170868844329 | 200 | 230.6729548340286 | 0 | 0 |  |  | 25590 | 25831.985815602836879432624113475177305 |  | 0 | 63093 | 41810.8735516181752479716312056737588652 | 69086.624941305709808432624113475177305 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | TRAFFIC SIGNAL | YES | 181561918 | NA |  | UTILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | BRYON WALSH | PIPELINE SAFETY AND COMPLIANCE ADVISOR | bwalsh@semprautilities.com | 619-992-1473 |  |  |  |  | BRYON WALSH | PIPELINE SAFET AND COMPLIANCE ADVISOR | 619-992-1473 | bwalsh@semprautilities.com | ON 08/31/2018 AT APPROXIMATELY 09:15, A THIRD-PARTY CONTRACTOR WAS TRENCHING FOR ELECTRICAL CONDUIT INSTALLATION FOR TRAFFIC LIGHTS AT THE INTERSECTION OF REDHAWK PARKWAY AND EL CHIMISAL ROAD, TEMECULA. THIS RESULTED IN AN ESCAPE OF GAS. CREWS RESPONDED AND CONTROLLED THE GAS. NO FURTHER DAMAGES OR INJURIES RESULTED FROM THIS INCIDENT. INVESTIGATION REVEALED THAT THE THIRD-PARTY CONTRACTOR HAD A VALID USA TICKET AND THE LINES WERE MARKED CORRECTLY. THE CONTRACTOR HAD DAY- LIGHTED THE 4 INCH GAS MAIN PREVIOUSLY ABOUT 6 FEET AWAY FROM THE DAMAGE LOCATION. WHILE CONTINUING TO TRENCH, THE CONTRACTOR FAILED TO USE CAUTION WHEN DIGGING BY THE GAS LINE. THIS INCIDENT WAS REPORTED TO DOT AND CPUC BASED ON AN ESTIMATED GAS RELEASE OF 3 MMCF. TOTAL GAS LOSS FOR THE INCIDENT WAS 4.265 MMCF. FOR ANY FURTHER QUESTIONS, CONTACT BRYON WALSH AT (619) 992-1473.
2025-03-31 10:13 | NO | YES | YES | 20180089 | 33416 | 2018-09-28 17:12 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2018-08-28 12:52 |  |  | 2018 | 100 POTOMAC PLACE | WINCHESTER | FREDERICK COUNTY | VA | 22602 | 39.1726 | -78.1273 | [9 empty] | 2018-08-28 15:07 | 1222963 |  | NATURAL GAS |  | 36.89 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2018-08-28 13:00 |  |  |  | 2018-08-28 13:09 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | IN OR SPANNING AN OPEN DITCH |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1967 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.3 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 471 | 543.234808634137353 | 6665 | 7687.176219844003095 | 2542 | 2931.853255940503506 | ADMIN & OVERHEAD |  | 115 | 116.087470449172576832151300236406619385 |  | 0 | 9793 | 4730.462802085253266174940898345153664303 | 11278.3517548678165308321513002364066194 | 0 | 0 | 2 |  |  |  |  | 53 | 53 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: THE CONTROL ROOM OPERATIONS WERE NOT A CONTRIBUTING CAUSE OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | 3RD PARTY DAMAGE BY CHOP SAW. | [154 empty] | RICHARD FITZPATRICK | SUPERVISOR - PIPELINE SAFETY | richardfitzpatrick@washgas.com | 7037505921 |  |  |  |  | STEPHEN PRICE | AVP SAFETY QUALITY SYSTEM PROTECTION | 703-750-4586 | sprice@washgas.com | FUOG INTERBUILD WORKING FOR FREDERICK COUNTY INSTALLING SEWER USED A CHOP SAW TO CUT THROUGH 2" STEEL GAS MAIN CAUSING IGNITION. FUOG INTERBUILD WAS WORKING OUTSIDE THE AREA OF ITS ONE CALL TICKET, DUG WHEN NO MARKS OR FLAGS WERE PRESENT, AND DID NOT CALL FOR A RE-MARK WHEN THE GAS MAIN WAS EXPOSED. VIRGINIA STATE CORPORATION COMMISSION HAS CONCLUDED THEIR INVESTIGATION OF THE INCIDENT AT 100 POTOMAC PLACE WINCHESTER, VA. VA SCC HAS DETERMINED THAT NO PROBABLE VIOLATIONS OF THE VIRGINIA DAMAGE PREVENTION ACT AND COMMISSION RULES FOR ENFORCEMENT OF THE DAMAGE PREVENTION ACT WERE COMMITTED BY WASHINGTON GAS. THE DIVISION'S DAMAGE PREVENTION STAFF ALSO PERFORMED THEIR INVESTIGATION AND HAD DETERMINED THAT NO POTENTIAL NON-COMPLIANCES WITH THE COMMISSION'S PIPELINE SAFETY STANDARDS EXIST AS TO WASHINGTON GAS. WITH STAFFS FINDINGS OF NO NON-COMPLIANCE ISSUES, WASHINGTON GAS RESPECTFULLY CLOSES THIS REPORT.
2025-03-31 10:13 | NO | NO | NO | 20180090 | 31058 | 2018-10-05 17:51 | SUPPLEMENTAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2017-01-18 15:21 |  |  | 2017 | 221 N. 16TH AVE. | YAKIMA | YAKIMA | WA | 98902 | 46.6016 | -120.5304 | [9 empty] | 2018-10-05 09:02 | 1226616 |  | NATURAL GAS |  | 239.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2017-01-18 15:21 |  |  |  | 2017-01-18 15:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 39381 | 46478.717122969840785 | 18307 | 21606.507563805105895 | 15299 | 18056.369651972159015 | OVERHEAD RATE APPLIED |  | 1763 | 1809.617788461538461538461538461538461538 |  | 0 | 74750 | 37351.2672762359512951538461538461538462 | 87951.2121272086441565384615384615384615 | 0 | 0 | 3 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | FROST HEAVE |  | NO | [218 empty] | CHRIS GRISSOM | MANAGER QUALITY CONTROL | christopher.grissom@cngc.com | [5 empty] | CHRIS GRISSOM | MANAGER QUALITY CONTROL | 541-706-6292 | christopher.grissom@cngc.com | CNGC PERSONNEL RESPONDED TO AN ODOR CALL ON 1/18/17. CNGC PERSONNEL PERFORMED AN INVESTIGATION PER COMPANY PROCEDURE, CHECKING CNGC FACILITIES/PIPELINE AND STRUCTURE FOUNDATIONS IN THE VICINITY OF THE ODOR CALL. NO IMMEDIATE HAZARDS, OR GAS LEAKS WERE FOUND. ON 1/19/17 CNGC PERSONNEL CONTINUED TO INVESTIGATE THE GAS ODOR, AND EXTENDED THE INVESTIGATION TO INCLUDE ADDITIONAL CNGC FACILITATES/PIPELINE AND STRUCTURE FOUNDATIONS. AGAIN, NO IMMEDIATE HAZARDS, OR GAS LEAKS WERE FOUND. ON 1/20/17, CNGC PERSONNEL CONTINUED TO INVESTIGATE THE GAS ODOR, AND THROUGH EXPLORATORY EXCAVATION, DETECTED NATURAL GAS IN AN IRRIGATION LINE. CNGC PERSONNEL MONITORED THE IRRIGATION LINE AND UTILIZED THE DIRECTION OF GAS MIGRATION IN THE LINE TO AID IN PIN-POINTING THE LOCATION OF THE GAS LEAK. ON 1/21/17, CNGC PERSONNEL WERE ABLE TO PINPOINT THE LEAK TO A 2" DISTRIBUTION PIPELINE IN THE ROADWAY. CNGC PERSONNEL EXCAVATED THE PIPELINE AND STOPPED THE FLOW OF GAS IN THE PIPELINE. ONCE THE FLOW WAS STOPPED IN THE PIPELINE, THE AFFECTED SEGMENT OF PIPELINE WAS REPLACED. THE LEAK CAUSE WAS DETERMINED TO BE A CRACK IN THE PIPELINE RESULTING FROM NATURAL FORCES (FROST HEAVE). CNGC PERSONNEL CONTINUED TO WORK THROUGH THE WEEKEND (OVERTIME PAY IS A CONTRIBUTING FACTOR TO THE INCIDENT BEING REPORTABLE) TO COMPLETE THE PIPELINE REPAIR (1/21/17), RESTORE SERVICE TO AFFECTED CUSTOMERS (1/21/17), AND RESTORE THE AFFECTED ROADWAY (1/22/17). THE ROOT CAUSE OF THE INCIDENT WAS A NATURAL FORCE LEAK WITH A TOTAL REPAIR COST OF $72,986.99, INCLUSIVE OF OPERATOR LABOR (STANDARD AND OVERTIME), MATERIALS, CONTRACTOR LABOR, PERMITS, SURFACE RESTORATION AND OVERHEAD. NO INJURIES, HOSPITALIZATIONS, EXPLOSIONS OR IGNITIONS WERE OBSERVED.
2025-03-31 10:13 | NO | NO | NO | 20180091 | 31387 | 2018-10-05 19:06 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 5241 SPRING MOUNTAIN ROAD | LAS VEGAS | NV | 89103 | 2018-06-14 07:05 |  |  | 2018 | 99 CONVENTION CENTER DRIVE | LAS VEGAS | CLARK COUNTY | NV | 89109 | 36.1323 | -115.1635 | [9 empty] | 2018-06-20 12:35 | 1215896 |  | NATURAL GAS |  | 30 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 3 | 2018-06-14 07:42 |  |  |  | 2018-06-14 07:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 40 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1955 | [5 empty] | 4 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.135 | [6 empty] | LEAK |  |  | OTHER | SEE PART H FOR INFORMATION | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 5598 | 6456.536005804460514 | 72745 | 83901.520497007052535 | 0 | 0 |  |  | 68 | 68.6430260047281323877068557919621749409 |  | 0 | 78411 | 37487.0958613190095972860520094562647754 | 90426.6995288162411813877068557919621749 | 16 | 0 | 0 |  |  |  |  | 33 | 33 | 33 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | PRESSURIZED WATER LINE LEAK. SEE PART H FOR ADDITIONAL INFORMATION. | [154 empty] | ALYSE BAKER | COMPLIANCE SPECIALIST | alyse.baker@swgas.com | 702-365-2077 | 702-365-2205 |  |  |  | ANTHONY HILLS | DIRECTOR OF OPERATIONS | 702-365-2049 | anthony.hills@swgas.com | OPERATOR WAS NOTIFIED ON JUNE 14, 2018 AT 07:05 PDT BY LAS VEGAS VALLEY WATER DISTRICT, OF A LEAK ON FACILITY DUE TO AN ADJACENT LEAKING WATER LINE. A HAZARDOUS GRADE 1 LEAK WAS DISCOVERED ON A 4-INCH STEEL PIPE LOCATED AT 99 CONVENTION CENTER DRIVE IN LAS VEGAS, NV. THE FLOW OF GAS TO THE SECTION OF PIPE WAS TAKEN OUT OF SERVICE WHILE REPAIRS WERE COMPLETED WHICH RESULTED IN A SERVICE OUTAGE OF 16 COMMERCIAL CUSTOMERS. FROM THE START OF THE INCIDENT UNTIL ITS CONCLUSION, THE OPERATOR SHARED INFORMATION AND KEPT THE PUBLIC UTILITIES COMMISSION OF NEVADA (PUCN) INFORMED AS EVENTS WERE TAKING PLACE. AFTER THE INCIDENT, THE OPERATOR AND THE PUCN WERE IN COMMUNICATION CONCERNING THE ROOT CAUSE AND THE POST-INCIDENT SUMMARY. PART A, 4: BASED ON COMMUNICATIONS THAT THE PUBLIC UTILITIES COMMISSION OF NEVADA'S REGULATORY OPERATIONS STAFF HAD WITH THE PIPELINE AND HAZARDOUS MATERIALS SAFETY ADMINISTRATION'S ACCIDENT INVESTIGATION DIVISION, "LOCAL TIME AND DATE OF THE INCIDENT" REFLECTS THE TIME OPERATOR PERSONNEL WAS NOTIFIED BY LAS VEGAS VALLEY WATER DISTRICT OF A POSSIBLE LEAK ON THE PIPELINE. AT THAT TIME, NO INCIDENT REPORTING CRITERIA HAD BEEN MET. PART A, 6: SOUTHWEST GAS NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) TELEPHONICALLY OF THE INCIDENT ON JUNE 20, 2018 AT 12:35 PDT, DUE TO INCREASING COSTS ASSOCIATED WITH DEWATERING AND PURGING ACTIVITIES, THAT WOULD POSSIBLY MEET THE $50,000 REPORTABLE CRITERIA. THE NRC ISSUED REPORT NUMBER 1215896 FOR THE INCIDENT. SOUTHWEST GAS PROVIDED A 48-HOUR UPDATE TELEPHONICALLY TO THE NRC ON JUNE 22, 2018 AT 11:47 PDT AND ADVISED THAT THE INCIDENT DID NOT MEET $50,000 DAMAGE CRITERIA. AN EMAIL WAS ALSO SENT TO PETER.KATCHMAR@DOT.GOV ADVISING THE SAME. THE NRC ISSUED REPORT NUMBER 1216106 FOR THE FOLLOW UP REPORT. ON SEPTEMBER 13, 2018, OPERATOR DETERMINED THAT ESTIMATED COST OF EMERGENCY RESPONSE HAD INCREASED OVER 20 PERCENT, MEETING THE $50,000 REPORTABLE DAMAGE CRITERIA LARGELY DUE TO COMPANY PERSONNEL OVERTIME LABOR LOADINGS. BASED UPON THIS INFORMATION, THE PUCN WAS ADVISED OF THE UPDATED COST AND OPERATOR WAS DIRECTED TO SUBMIT THE WRITTEN REPORT BY OCTOBER 13, 2018. PART C, 5 AND G4: GAS PIPE WALL WAS ERODED-THROUGH BY WATER JETTING FROM AN ADJACENT LEAKING WATER PIPELINE. THE LEAKING STREAM OF PRESSURIZED WATER MIXED WITH SOIL AND SAND TO CREATE AN EROSIVE SLURRY THAT CONTINUALLY IMPINGED UPON THE STEEL GAS PIPE WALL RESULTING IN THE LEAK. SUPPLEMENTAL: PART A, 13A: CORRECTED LOCAL TIME & DATE OF SHUTDOWN FROM 10:19 TO 09:32.
2025-03-31 10:13 | NO | YES | YES | 20180092 | 35384 | 2018-10-13 13:31 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2018-09-13 16:18 | EASTERN | NO | 2018 | 85 ANDOVER ST | LAWRENCE | ESSEX | MA | 01843 | 42.697 | -71.1753 | YES | YES |  | YES | [5 empty] | 2018-09-13 17:05 | 1224542 |  | NATURAL GAS |  | 678 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 25 | 25 | YES | 2018-09-13 16:18 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 0 | 2018-09-13 16:29 | YES | OPERATOR | 2018-09-13 16:29 | 2018-09-13 16:32 |  | NO | PUBLIC PROPERTY | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 24 | NO | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1961 | [8 empty] | OTHER | MULTIPLE PIPE MATERIAL AND SIZES | [9 empty] | OTHER | [8 empty] | OVERPRESSURIZATION | CLASS 3 LOCATION | 575000000 | 663184745.147832225 | 261000000 | 301028206.058407323 | 16500000 | 19030518.7738073595 | 734000000 | 846569744.240884962 | CLAIMS AND OTHER MITIGATION. | 3.05 | 2068 | 2087.555555555555555555555555555555555556 | 0 | 0 | 1586502068 | 757855685.872584593111111111111111111111 | 1829815301.776487425055555555555555555556 | 784 | 0 | 7249 | 25 | 0 | 7249 | 784 | 6 | 0.38 | 0.5 | 192.623 | 1961-01-01 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  | YES |  |  | YES | YES | [7 empty] | YES | 3 | 0 | YES | 4 | 0 | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [222 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED |  |  |  |  | YES | INADVERTENT OVERPRESSURIZATION. THE NTSB'S INVESTIGATION WAS COMPLETED ON SEPTEMBER 24, 2019. | DECOMMISSIONING | YES | NO, BUT THEY WERE PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | KATHERINE M SILVER | OPERATIONS COMPLIANCE SUPERVISOR | katherine.silver@eversource.com | 5088641836 |  |  |  |  | KATHERINE M SILVER | OPERATIONS COMPLIANCE SUPERVISOR | 5088641836 | katherine.silver@eversource.com | ON SEPTEMBER 13, 2018, COLUMBIA GAS OF MASSACHUSETTS EXPERIENCED AN OVERPRESSURIZATION OF ITS LOW-PRESSURE GAS DISTRIBUTION SYSTEM IN LAWRENCE, ANDOVER, AND NORTH ANDOVER, MASSACHUSETTS. THIS INCIDENT WAS INVESTIGATED BY THE NATIONAL TRANSPORTATION SAFETY BOARD, WHICH ISSUED ITS REPORT ON SEPTEMBER 24, 2019. THAT REPORT, WHICH IS AVAILABLE TO THE PUBLIC, INCLUDES A NARRATIVE DESCRIPTION OF THE INCIDENT AND ITS PROBABLE CAUSE. PART A #5A -LOCATION IS ADDRESS OF THE FIRST PRIORITY CALL. MULTIPLE LOCATIONS ARE ASSOCIATED WITH THIS INCIDENT. PART A 12F - SOURCE OF INJURIES (25) WERE FROM PRESS RELEASES FROM MEDIA. PART A #13A - ALL VALVES WERE SHUT DOWN AT 19:24 ON 9/13/2018, BUT THERE WAS SOME BLEED THROUGH OF GAS UNTIL 6:26 ON 9/14/2018. PART A #16 - NUMBER OF CUSTOMERS EVACUATED IS UNKNOWN, DUE TO EVACUATIONS BEING COMPLETED BY MULTIPLE SOURCES INCLUDING BUT NOT LIMITED TO POLICE, FIRE, SELF/PUBLIC, OPERATOR, MAYOR OF LAWRENCE AND MEDIA. PART D #3B- INDUSTRIAL CUSTOMERS ARE INCLUDED IN OUR COMMERCIAL ACCOUNTS. PART E #1 - THE HIGHEST PRESSURE RECORDED WAS A 6.0, WHICH IS THE UPPER LIMIT OF THE RECORDING EQUIPMENT. 5.6.21- UPDATED PART A7 AND PART D. - COST OF GAS RELEASED, A13 -A15: TIMES ARE ESTIMATED AS THERE WERE MULTIPLE EMERGENCY RESPONDERS. A21C: VOLUME OF GAS LOST IN FIRE IS UNKNOWN, MULTIPLE FIRES. REQUIRED TO PUT IN A NUMBER. D6-7: BUILDINGS EVACUATED, AFFECTED IS BASED ON NUMBER OF CUSTOMERS AFFECTED. TOTAL EVACUATION NUMBER IS UNKNOWN. E3B: DEFAULTED DATE TO THE REGULATOR STATION INSTALL YEAR. THIS WAS A LOW PRESSURE SYSTEM WITH PIPE INSTALLED OVER MANY DECADES. THE SYSTEM WAS OPERATING AT PRESSURES CONSISTENT WITH 192.623.
2025-03-31 10:13 | NO | NO | NO | 20180093 | 31141 | 2018-10-13 20:25 | SUPPLEMENTAL FINAL | 18684 | SUBURBAN PROPANE | 2440 DAIRY ROAD | LANCASTER | PA | 17601 | 2018-09-14 14:00 |  |  | 2018 | 117 N OREGON ST | YREKA | SISKIYOU | CA | 96097 | 41.7324 | -122.6383 | [9 empty] | 2018-09-14 17:48 | 1224652 |  | PROPANE GAS |  | 85 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 125 | 2018-09-14 14:21 |  |  |  | 2018-09-14 14:25 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1966 | [5 empty] | 2 | ASTM A53 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 4500 | 5190.1414837656435 | 5000 | 5766.823870850715 | 0 | 0 |  |  | 10000 | 10094.5626477541371158392434988179669031 |  | 0 | 19500 | 13876.1079014184861891252955082742316785 | 21051.5280023704956158392434988179669031 | 0 | 0 | 1 |  |  |  |  | 5 | 5 | 7 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 819200562 | USA NORTH 811 |  | UTILITY OWNER | YES | YES | 21 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JOHN MINCHEW | AREA SAFETY MANAGER | jminchew@suburbanpropane.com | 678-641-8658 | 315-254-2809 |  |  |  | CATHERINE QUINLIVAN | DIRECTOR ENVIRONMENTAL SAFETY AND ENGINEERING | 717-579-6028 | cquinlivan@suburbanpropane.com | THIRD-PARTY CONTRACTOR WAS EXCAVATING ROADWAY IN AREA OF MARKED GAS DISTRIBUTION LINE(S). CONTRACTOR FAILED TO USE HAND TOOLS TO INVESTIGATE SPECIFIC GAS DISTRIBUTION LINE(S) LOCATION WHILE EXCAVATING. BACKHOE STRUCK SERVICE FEEDER AND MAIN, CRACKING THE TEE CONNECTION ON THE MAIN AND RELEASING GAS FROM THE DISTRIBUTION SYSTEM. DAMAGED SECTION OF GAS DISTRIBUTION LINE WAS ISOLATED BY KEY VALVES (APPROXIMATELY ONE MILE OF DISTRIBUTION SYSTEM). REPAIRS WERE MADE, ISOLATED SECTION TESTED, AND SERVICE REINSTATED AFTER SUCCESSFUL LEAK TESTING.
2025-03-31 10:13 | NO | YES | YES | 20180095 | 31851 | 2018-10-15 11:30 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2018-09-18 14:00 |  |  | 2018 | 314 CONTINENTAL DRIVE | GREENVILLE | GREENVILLE | SC | 29615 | 34.8651 | -82.308 | [9 empty] | 2018-09-18 18:03 | 1225007 |  | NATURAL GAS |  | 0.01 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2018-09-18 14:20 |  |  |  | 2018-09-18 14:45 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 2 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1972 | [5 empty] | 0.625 | UNKNOWN | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | UNKNOWN | OTHER | [8 empty] | CONTRACTOR DAMAGED THE GAS LINE WITH A TORCH. | CLASS 3 LOCATION | 0 | 0 | 2406 | 2774.995646653364058 | 0 | 0 | 0 | 0 |  |  | 25 | 25.23640661938534278959810874704491725768 |  | 0 | 2431 | 1172.665124641992608472813238770685579196 | 2800.232053272749400789598108747044917258 | 0 | 0 | 12 |  |  |  |  | 70 | 70 | 70 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | CONTRACTOR DAMAGED GAS LINE WITH TORCH. | [154 empty] | CHRISTOPHER RANSOME | PIPELINE SAFETY AND COMP ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | A THIRD-PARTY CONTRACTOR DAMAGED A SERVICE LINE WITH A TORCH AT 314 CONTINENTAL DRIVE IN GREENVILLE, SC. THE CONTRACTOR RECEIVED BURNS TO HIS LEGS AND WAS TRANSPORTED TO THE HOSPITAL WHICH REQUIRED AN OVERNIGHT STAY AT THE BURN UNIT. THE INCIDENT RESULTED IN A LOSS OF 12 CUSTOMERS.
2025-03-31 10:13 | NO | YES | NO | 20180096 | 31091 | 2018-10-18 12:40 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 5241 SPRING MOUNTAIN ROAD | LAS VEGAS | NV | 89103 | 2018-09-20 09:40 |  |  | 2018 | BUCKSKIN AVENUE AND SHADY TIMBER STREET | LAS VEGAS | CLARK COUNTY | NV | 89129 | 36.2219 | -115.3237 | [9 empty] | 2018-09-20 11:43 | 1225212 |  | NATURAL GAS |  | 9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 11 | 2018-09-20 09:40 |  |  |  | 2018-09-20 09:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 96 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1998 | [5 empty] | 2 | ASTM D2513 | PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 400 | 461.3459096680572 | 105 | 121.103301287865015 | 120603 | 139099.251859241756229 | 0 | 0 |  |  | 20 | 20.18912529550827423167848699763593380615 |  | 0 | 121128 | 57870.6474633994726243782505910165484634 | 139701.8901954931867182316784869976359338 | 48 | 0 | 1674 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | NATURAL FORCE DAMAGE | TEMPERATURE | [56 empty] | TEMPERATURE |  |  |  | THERMAL STRESS |  | NO | [218 empty] | YVONNE BRODEUR | SPECIALIST DIVISION COMPLAINCE | yvonne.brodeur@swgas.com | 702-365-2149 | 702-365-2205 |  |  |  | ANTHONY HILLS | DIRECTOR OF GAS OPERATIONS | 702-365-2049 | anthony.hills@swagas.com | WHILE CONDUCTING A SPECIAL LEAK PATROL ON M7000/8000 PIPE, A COMPANY CONTRACTOR FROM HEATH CONSULTANTS DISCOVERED A HAZARDOUS GRADE 1 LEAK ON A 2-INCH M8000 PIPE AT THE 2"X1" CONTINENTAL TAPPING SADDLE NEAR THE INTERSECTION OF BUCKSKIN AVENUE AND SHADY TIMBER STREET IN LAS VEGAS, NEVADA. THE FLOW OF GAS TO THE SECTION OF PIPE WAS TAKEN OUT OF SERVICE WHILE REPAIRS WERE COMPLETED WHICH RESULTED IN A SERVICE OUTAGE OF 1,722 CUSTOMERS. G2 - NATURAL FORCE DAMAGE: THE COMPANY COMPLETED IT'S INVESTIGATION INTO THE FAILURE AND DETERMINED THE APPARENT CAUSE OF THE LEAK TO BE "NATURAL FORCE DAMAGE", WITH A SUB-CAUSE OF "TEMPERATURE - THERMAL STRESS". THE TAPPED HOLE IN THE PIPE WAS AXIALLY DISPLACED APPROXIMATELY ONE INCH WITH RESPECT TO THE TAPPING TEE'S ORIGINAL POSITION. THE MOVEMENT OF THE PIPE, LIKELY DUE TO THERMAL CONTRACTION, RESULTED IN THE DISPLACEMENT OF THE SADDLE-TO-PIPE O-RING, BREAKING THE GAS-TIGHT SEAL RESULTING IN A LEAK. BASED ON COMMUNICATIONS THAT THE PUBLIC UTILITES COMMISSION OF NEVADA'S REGULATORY OPERATIONS STAFF HAD WITH THE PIPELINE AND HAZARDOUS MATERIALS SAFETY ADMINISTRATION'S ACCIDENT INVESTIGATION DIVISION, PART A, 4 "LOCAL TIME AND DATE OF THE INCIDENT" REFLECTS THE TIME OPERATOR PERSONNEL IDENTIFIED AND REPORTED A GRADE 1 LEAK ON THE PIPELINE. AT THE TIME, NO INCIDENT REPORTING CRITERIA WAS MET. THE SHUTDOWN TIME REPORTED IN PART A, 13A (11:23 PDT) IS THE EARLIEST DATE AND TIME A REPORTING CRITERIA WAS MET. DUE TO THE SHUTDOWN OF THE PIPELINE, THE INCIDENT WAS ESTIMATED TO REACH PROPERTY DAMAGE OF $50,000 OR MORE. TELEPHONIC NOTIFICATIONS WERE MADE WITHIN ONE HOUR OF THE SHUTDOWN TIME. PART A, 6: SOUTHWEST GAS NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) TELEPHONICALLY OF THE INCIDENT ON SEPTEMBER 20, 2018 AT 11:43 PDT. THE NRC ISSUED REPORT NUMBER 1225212 FOR THE INCIDENT. SOUTHWEST GAS PROVIDED A 48-HOUR UPDATE TELEPHONICALLY TO THE NRC ON SEPTEMBER 21, 2018 AT 15:48 PDT. THE NRC ISSUED REPORT NUMBER 1225343 FOR THE UPDATED REPORT.
2025-03-31 10:13 | NO | YES | YES | 20180099 | 32042 | 2018-11-02 14:46 | SUPPLEMENTAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY | CANONSBURG | PA | 15317 | 2018-10-03 02:18 |  |  | 2018 | TIMBERIDGE DRIVE AND CLIFTON ROAD | BETHEL PARK | ALLEGHENY | PA | 15102 | 40.2934 | -80.0317 | [9 empty] | 2018-10-03 05:34 | 1226351 |  | NATURAL GAS |  | 139.8 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 2 | 2018-10-03 02:21 |  |  |  | 2018-10-03 02:53 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 84 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2010 | [5 empty] | 4 | UNKNOWN | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | MECHANICAL PUNCTURE | 4 | 3 | [7 empty] | CLASS 3 LOCATION | 2000 | 2306.729548340286 | 100 | 115.3364774170143 | 14344 | 16543.864320696531192 | 10000 | 11533.64774170143 | COST OF REPAIR TO TRACK HOE FOR EXCAVATOR |  | 555 | 560.248226950354609929078014184397163121 |  | 0 | 26999 | 13150.2729319352295224964539007092198582 | 31059.8263151056161019290780141843971631 | 0 | 0 | 23 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THEY WERE NOT A CONTRIBUTOR TO THE ISSUE HERE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 20182320939 |  |  | UTILITY OWNER | YES | YES | 11 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RICK BURKE | OPERATIONS COMPLIANCE MANAGER | rburke@nisource.com | 724-416-6332 | 724-416-6385 |  |  |  | MIKE TICE | OPERATIONS CENTER MANAGER | 724-773-5365 | mtice@nisource.com | ON OCTOBER 3, 2018 AT APPROXIMATELY 2:18 AM, AN EMPLOYEE OF GOLDEN TRIANGLE CONSTRUCTION DUG INTO AN ACCURATELY MARKED 4-INCH MEDIUM PRESSURE PLASTIC GAS MAIN CAUSING DAMAGE TO THE PIPELINE. UPON STRIKING THE PIPELINE AN UNKNOWN IGNITION SOURCE CAUSED THE ESCAPING GAS TO IGNITE. THE GOLDEN TRIANGLE EMPLOYEE WAS BURNED BY THE FIRE AND WAS ADMITTED TO THE HOSPITAL FOR TREATMENT OF HIS INJURIES. THE GAS WAS SHUT DOWN AT 4:05 AM AND SERVICE WAS RESTORED AT 3:25 PM ON OCTOBER 3, 2018.
2025-03-31 10:13 | NO | YES | NO | 20180100 | 31962 | 2018-11-07 15:56 | SUPPLEMENTAL FINAL | 6720 | ATMOS ENERGY CORPORATION - COLORADO/KANSAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-10-07 17:50 |  |  | 2018 | 142ND AND GIBBS RD. | Not Within a Municipality | LEAVENWORTH | KS | 66012 | 39.0581 | -94.9095 | [9 empty] | 2018-10-08 11:28 | 1226857 |  | NATURAL GAS |  | 75 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2018-10-07 18:12 |  |  |  | 2018-10-07 18:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1976 | [5 empty] | 4 | ASTM D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 9.33 |  |  | 3306 | LEAK |  |  | OTHER | UNDER INVESTIGATION | [5 empty] | CLASS 2 LOCATION | 100000 | 115336.4774170143 | 10000 | 11533.64774170143 | 10000 | 11533.64774170143 | 0 | 0 |  |  | 300 | 302.836879432624113475177304964539007092 |  | 0 | 120300 | 57602.8336633077912056737588652482269504 | 138706.6097798497841134751773049645390071 | 4 | 0 | 30 |  |  |  |  | 58 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [56 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | SUBSIDENCE |  |  |  |  | NO | [218 empty] | DOUGLAS L SHATAS | COMPLIANCE MANAGER | doug.shatas@atmosenergy.com | 816-863-0951 |  |  |  |  | DOUGLAS L SHATAS | COMPLIANCE MANAGER | 816-863-0951 | doug.shatas@atmosenergy.com | AT 18:12 ON 10/7/2018 ATMOS ENERGY WAS NOTIFIED OF AN INCIDENT AT 15721 142ND ST BONNER SPRINGS, KS. AN OPERATIONS SUPERVISOR ARRIVED ON THE SCENE AT 18:30, FOLLOWED BY A CONSTRUCTION CREW. UPON ARRIVAL, ATMOS ENERGY PERSONNEL CLOSED THE VALVE ON THE MAIN TO THE EAST AND PINCHED THE PLASTIC TO THE WEST TO STOP THE FLOW OF GAS AND ELIMINATE THE SAFETY HAZARD. THE FIRE DEPARTMENT ARRIVED ON THE SCENE AT 19:06. NO INJURIES OCCURRED AS A RESULT OF THIS INCIDENT. A NEARBY STRUCTURE CONTAINING A WATER PUMP STATION WAS DAMAGED. APPROXIMATELY 34 CUSTOMERS WERE OUT OF SERVICE FOR APPROXIMATELY 24 HOURS FOLLOWING THE INCIDENT. ATMOS ENERGY'S INVESTIGATION DETERMINED THE CAUSE OF THE INCIDENT WAS EXCESSIVE STRESS PUT ON THE PIPE FROM SOIL SUBSIDENCE.
2025-03-31 10:13 | NO | NO | NO | 20180101 | 31513 | 2018-11-09 16:04 | SUPPLEMENTAL FINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2018-10-15 18:02 |  |  | 2018 | 202 & HOPPER | ELKHORN | DOUGLAS | NE | 68022 | 41.2891 | -96.2291 | [9 empty] | 2018-10-15 19:54 | 1227562 |  | NATURAL GAS |  | 7.97 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2018-10-15 18:02 |  |  |  | 2018-10-15 18:23 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | MUNICIPALLY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 4 | UNKNOWN | DUPONT COMPANY | OTHER | ALDYL-A | [9 empty] | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 8000 | 9226.918193361144 | 3000 | 3460.094322510429 | 0 | 0 |  |  | 5124 | 5172.453900709219858156028368794326241135 |  | 0 | 16124 | 10039.4027784746089929078014184397163121 | 17859.4664165807928581560283687943262411 | 0 | 0 | 1 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS TRANSMISSION LINE WAS DAMAGED BY A PRIVATE CONTRACTOR. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 18288160 |  |  | UTILITY OWNER | YES | YES | 3 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | TYSON ROBARDS | CLAIMS ADJUSTER | tyson_robards@mudnebr.com | 402.504.7108 | 402.504.5108 |  |  |  | TYSON ROBARDS | CLAIMS ADJUSTER | 402.504.7108 | tyson_robards@mudnebr.com | ON MONDAY, OCTOBER 15, 2018 AT 18:02 METROPOLITAN UTILITIES DISTRICT (DISTRICT') RECEIVED NOTICE OF A 4 INCH GAS MAIN WHICH WAS STRUCK ON 202ND AND HOPPER ST. THE OMAHA FIRE DEPARTMENT HAD THE SCENE BLOCKED OFF DUE TO BLOWING GAS FROM THE STRUCK GAS MAIN. THE FIRE CAPTAIN TOLD US A CONTRACTOR HIT A GAS MAIN WHILE DIRECTIONAL BORING AND THE CORNER HOMES (20203 HOPPER & 3404 N 202ND ST.) WERE EVACUATED FOR SAFETY PRECAUTIONS. THE STRIKE WAS THE RESULT OF TWO FACTORS: THE LOCATE MARKS WERE OFF BECAUSE OF INACCURATE RECORDS THAT THE OPERATOR INHERITED FROM THE PREVIOUS OPERATOR OF THAT PORTION OF ITS GAS SYSTEM AND THE EXCAVATOR FAILED TO EXPOSE THE MAIN THROUGH HAND DIGGING PRIOR TO BORING AS THEY HAD AGREED TO DURING PREVIOUS CONVERSATIONS WITH THE OPERATOR. AT 19:49 THE DISTRICT'S A-REP COORDINATOR ADVISED ME TO NOTIFY THE NEBRASKA STATE FIRE MARSHAL. THE DECISION WAS MADE AT THIS TIME TO OVER REPORT THAN TO UNDER REPORT. NRC TELEPHONIC REPORT NUMBER 1227562 WAS MADE AT 18:54. A 48-HOUR TELEPHONIC FOLLOW-UP REPORT WAS SUBMITTED ON 10/17/18 AT APPROXIMATELY 17:45.
2025-03-31 10:13 | NO | YES | YES | 20180103 | 31232 | 2018-11-14 15:27 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2018-11-10 18:28 |  |  | 2018 | 2075 RIPLEY STREET | LAKE STATION | LAKE | IN | 46405 | 41.5797 | -87.2387 | [9 empty] | 2018-11-10 18:16 | 1230058 |  | NATURAL GAS |  | 0.01 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2018-11-10 14:26 |  |  |  | 2018-11-10 14:39 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 500 | 576.6823870850715 | 100 | 115.3364774170143 | 0 | 0 |  |  | 1 | 1.00945626477541371158392434988179669031 |  | 0 | 601 | 287.547265243252904018912529550827423168 | 693.02832076686121371158392434988179669 | 0 | 0 | 0 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | [197 empty] | NON-THREADED CONNECTION FAILURE | [14 empty] | GASKET | [68 empty] | LUKE E. SELKING | MANAGER PIPELINE SAFETY AND COMPLIANCE | leselking@nisource.com | 260-439-1290 |  |  |  |  | LUKE E. SELKING | MANAGER PIPELINE SAFETY AND COMPLIANCE | 260-439-1290 | leselking@nisource.com | REGULATOR STATION LOCATED ADJACENT TO FACILITY WHERE PERSON INVOLVED RESIDED. MAIN REGULATOR STATION WAS INSIDE FENCED AREA WITH THE EXCEPTION OF BLOW OFF VALVES LOCATED OUTSIDE THE FENCED AREA. RESIDENT FROM ASSISTED LIVING FACILITY WAS REPORTED TO BE SMOKING ON OR NEAR GAS VALVE WHEN IGNITION OCCURRED. RESIDENT WAS INJURED FROM FIRE AND TRANSPORTED TO HOSPITAL. PRIMARY LEAK WAS DETERMINED TO BE LOCATED ON THE VALVE FLANGE. LEAK WAS REPAIRED BY RETIREMENT 11-12-2018.
2025-03-31 10:13 | NO | YES | NO | 20180104 | 31637 | 2018-11-19 15:26 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2018-10-25 13:25 |  |  | 2018 | LASALLE STREET EXIT OFF I-77 | CHARLOTTE | MECKLENBURG | NC | 28216 | 35.261 | -80.8411 | [9 empty] | 2018-10-26 10:30 | 1228583 |  | NATURAL GAS |  | 182.2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-10-25 13:30 |  |  |  | 2018-10-25 14:05 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 14 | X42 0.250 WALL | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 5 | 0.25 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 221312 | 255253.464901142687616 | 8633 | 9956.998095410844519 | 0 | 0 | 0 |  | 4062 | 4100.411347517730496453900709219858156028 |  | 0 | 234007 | 113635.3403206863307848226950354609929078 | 269310.874344071262631453900709219858156 | 2 | 0 | 0 |  |  |  |  | 148 | 148 | 150 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE DAMAGE WAS DONE BY A THIRD-PARTY | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY | 2018-03-07 | NO |  |  | NO | [9 empty] | NO | YES | INTERSTATE HIGHWAY | [12 empty] | CONTRACTOR | AUGER | BUILDING CONSTRUCTION | NO | [5 empty] | YES | 46 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CHRISTOPHER RANSOME | PIPELINE SAFETY AND COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | PIPELINE SAFETY MANAGER | 704-731-4618 | farris.berry@duke-energy.com | CONTRACTOR FOR STATE DOT PROJECT WAS USING AUGER EQUIPMENT TO EXCAVATE PYLONS FOR CONCRETE SOUND BARRIERS BESIDE THE INTERSTATE INTERCHANGE IN CHARLOTTE, NC NEAR THE INTERSECTION OF I-77 AND I-85 NEAR LASALLE STREET. THE CONTRACTOR DID NOT HAVE AN ACTIVE 811 LOCATE TICKET FOR THIS WORK AND SUBSEQUENTLY DAMAGED THE EXISTING 14" CASED PIPELINE THAT CROSSES UNDERNEATH THE I-77 INTERCHANGE. THE INITIAL TELEPHONIC REPORT TO THE NATIONAL RESPONSE CENTER WAS MADE ON 10/26/2018 WHEN IT WAS DETERMINED THIS INCIDENT WOULD EXCEED THE $50,000 REPORTING THRESHOLD.
2025-03-31 10:13 | NO | NO | NO | 20180106 | 31565 | 2018-11-21 12:27 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2018-10-23 16:37 |  |  | 2018 | 130 SAGINAW STREET | BEAVERTON | GLADWIN | MI | 48612 | 43.8814 | -84.488 | [9 empty] | 2018-10-23 19:05 | 1228340 |  | NATURAL GAS |  | 14 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2018-10-23 16:37 |  |  |  | 2018-10-23 17:06 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1974 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 50000 | 57668.23870850715 | 600 | 692.0188645020858 | 704 | 811.968801015780672 | 500 | 576.6823870850715 | REPAIR SERVICE AND METER REPLACE |  | 40 | 40.37825059101654846335697399527186761229 |  | 0 | 51844 | 24783.5583042703044327565011820330969267 | 59789.2870117011045204633569739952718676 | 1 | 0 | 0 |  |  |  |  | 28 | 28 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON OCTOBER 13, 2018 AT APPROXIMATELY 16:37 HOURS, CONSUMERS ENERGY WAS NOTIFIED OF A GAS RELEASE AND IGNITION AT 130 SAGINAW STREET, (GLADWIN COUNTY)BEAVERTON, MICHIGAN. A SUMMARY OF THE GLADWIN COUNTY SHERIFF ACCIDENT REPORT IS A DPW EMPLOYEE RETURNED TO THE BUILDING TO PICK UP A RADIO AND PRESSED THE GAS PEDAL INSTEAD OF THE BRAKE WHICH CAUSED THE VEHICLE TO HIT THE FRONT (SOUTH) SIDE OF THE BUILDING AND DAMAGE THE GAS METER (A THREADED NIPPLE LOCATED ABOVE THE LOCKWING). THE GAS RELEASE IGNITED AND THE BUILDING CAUGHT FIRE. A CONSUMERS ENERGY FIRST RESPONDER ARRIVED ONSITE AT APPROXIMATELY 17:06 HOURS, THE GAS TO THE DAMAGED METER HAD BEEN TURN OFF AT THE LOCKWING BY FIRE PERSONNEL PRIOR TO ARRIVAL. A CONSUMERS ENERGY DISTRIBUTION CREW WAS NOTIFIED AND THE SERVICE LINE WAS CUT BACK AND PLUGGED UNTIL REPAIRS TO THE BUILDING ARE COMPLETE AND SERVICE RESTORED. THERE WERE NO FATALITIES OR INJURIES ASSOCIATED TO THE DAMAGE AND SUBSEQUENT IGNITION. A CAUSAL ANALYSIS INVESTIGATION WAS CONDUCTED TO IDENTIFY THE ROOT CAUSE, COUNTERMEASURES TO MINIMIZE FUTURE OCCURRENCES HAVE BEEN IDENTIFIED AND AN IMPLEMENTATION SCHEDULE IS BEING DEVELOPED.
2025-03-31 10:13 | NO | YES | YES | 20180107 | 32706 | 2018-11-21 16:08 | SUPPLEMENTAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2018-10-27 13:25 |  |  | 2018 | 2301 BENDRIDGE TRAIL | AUSTIN | TRAVIS | TX | 78744 | 30.1848 | -97.7597 | [9 empty] | 2018-10-28 18:40 | 1228800 |  | NATURAL GAS |  | 0 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 2 | 2018-10-27 13:25 |  |  |  | 2018-10-27 14:34 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 43 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | SERVICE TEE | 1972 | [8 empty] | STEEL |  | OTHER | WELDED | 0.14 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 500000 | 576682.3870850715 | 20000 | 23067.29548340286 | 20000 | 23067.29548340286 | 0 | 0 | UNKNOWN AT THIS TIME. |  | 0 | 0 |  | 0 | 540000 | 257952.11318701272 | 622816.97805187722 | 0 | 0 | 5 |  |  |  |  | 49 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | [14 empty] | NO | YES | CITY STREET | [12 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO | [5 empty] | YES | 288 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | FAILURE APPEARS TO BE CAUSED BY UNREPORTED THIRD PARTY EXCAVATION DAMAGE. | [169 empty] | DEAN LAFLAMME | DIRECTOR OF ENGINEERING | dean.laflamme@onegas.com | 512-370-8213 |  |  |  |  | DEAN LAFLAMME | DIRECTOR OF ENGINEERING | 512-370-8213 | dean.laflamme@onegas.com | ON 10/27/18 AT 13:25, TEXAS GAS SERVICE WAS NOTIFIED BY THE AUSTIN FIRE DEPARTMENT THAT THERE WAS AN EXPLOSION OF THE HOME AT 2301 BENDRIDGE TRAIL IN AUSTIN, TEXAS. ON 10/28/2018, IT WAS DETERMINED THAT A JURISDICTIONAL PIPELINE FAILURE WAS INVOLVED IN THE INCIDENT. INVESTIGATION IDENTIFIED DEFORMATION OF THE SERVICE LINE, WHICH APPEARS TO HAVE RESULTED FROM UNREPORTED THIRD-PARTY EXCAVATION DAMAGE. A LABORATORY EXAMINATION HAS BEEN CONDUCTED AT THE FAILURE LOCATIONS ON THE SERVICE TEE AT THE GAS MAIN AS WELL AS THE LOCATION WHERE THE SERVICE LINE WAS DEFORMED. THESE EXAMINATIONS WERE CONDUCTED BY A THIRD-PARTY EXPERT AND WERE OBSERVED BY TEXAS RAILROAD COMMISSION STAFF AND AUSTIN FIRE DEPARTMENT INVESTIGATOR. FURTHER TESTS AND EXAMINATIONS ARE UNDER WAY. THIS REPORT WILL BE SUPPLEMENTED WHEN THE INVESTIGATION IS COMPLETE. SUPPLEMENTAL INFORMATION BELOW ON THE THIRD-PARTY REPORT. THIRD-PARTY EXPERT BAKER RISK REPORTS THAT AN INSPECTION OF THE 6606/6608 STONLEIGH SERVICE LINE OCCURRED ON JUNE 24, 2019 AT BAKER RISK. THE INSPECTION CONFIRMS PRIOR OBSERVATIONS THAT THE DAMAGE TO THE SERVICE LINE WAS CAUSED BY EXTERNAL FORCES THAT DAMAGED THE WRAP AND BENT THE PIPE. THE FIELD WRAP ON THE TEE IN THE MIDDLE OF THE SERVICE LINE WAS COMPARABLE TO THE FIELD WRAP ON THE TEE AT THE MAIN. BOTH OF THESE WRAPS WERE INTACT WHEN THE EVIDENCE WAS RECOVERED. OBSERVATIONS OF THE TEES FOLLOWING REMOVAL OF THE WRAPS DURING EVIDENCE INSPECTIONS SHOWED THAT THE TEES WERE WELL PROTECTED BY THE WRAPS AND DID NOT EXHIBIT CORROSION. THE SERVICE LINE BEING DISPLACED TO THE WEST CAUSED CRACKS IN TWO LOCATIONS ON THE TEE AT THE GAS MAIN. THE TWO CRACKS ON THE TEE AT THE MAIN WERE STRESS-INDUCED FAILURES AND NOT CAUSED BY CORROSION OR WELD QUALITY OR CONDITION.
2025-03-31 10:13 | NO | NO | NO | 20180108 | 31227 | 2018-11-26 12:39 | ORIGINAL FINAL | 2572 | COLQUITT GAS SYSTEM, CITY OF | 154 WEST STREET | COLQUITT | GA | 39837 | 2018-10-11 12:00 |  |  | 2018 | 303 VIRGINIA STREET. | COLQUITT | MILLER | GA | 39837 | 31.1711 | -84.7406 | [9 empty] | 2018-10-11 12:00 | 1227200 |  | NATURAL GAS |  | 124 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-10-10 23:32 |  |  |  | 2018-10-10 23:35 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | BROKEN LINES DUE TO HURRICANE MICHAEL | 24 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 1 | ASTM D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 2406 | OTHER | [8 empty] | TREES UPROOTING SERVICE DUE TO HURRICANE MICHAEL. | CLASS 3 LOCATION | 0 | 0 | 2500 | 2883.4119354253575 | 4000 | 4613.459096680572 | 0 | 0 |  |  | 1600 | 1615.130023640661938534278959810874704492 |  | 0 | 8100 | 4599.068974729408430260047281323877068558 | 9112.001055746591438534278959810874704492 | 36 | 2 | 55 |  |  |  |  | 21 | 21 | 21 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS FORM IS SET UP FOR LARGER OPERATORS AND NOT FOR SMALL MUNICIPAL OWNED SYSTEMS. SMALL SYSTEM TYPICALLY DO NOT HAVE CONTROLLERS OR CONTROL ROOM MANAGEMENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [56 empty] | HIGH WINDS | [5 empty] | YES | YES | [217 empty] | SAM YARLEY | COMPLIANCE ANALYST | syarley@gasauthority.com | 2293763027 |  |  |  |  | EMANUEL HAIRE | GAS SUPERINTENDENT | 2297581000 | ehaire@colquittga.org | HURRICANE MICHAEL CAUSED NATURAL FORCE DAMAGE TO CITY OF COLQUITT'S DISTRIBUTION GAS SYSTEM. CITY OF COLQUITT DECIDED TO SHUT OFF THE DISTRIBUTION GAS SYSTEM DUE TO TREE DAMAGE AND THE RELEASE OF NATURAL GAS.
2025-03-31 10:13 | NO | YES | NO | 20180109 | 31828 | 2018-11-26 14:49 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2018-10-31 14:10 |  |  | 2018 | 11500 BALD HILL RD SE | YELM | THURSTON | WA | 98597 | 46.9201 | -122.5683 | [9 empty] | 2018-11-08 15:50 | 1229902 |  | NATURAL GAS |  | 311.51 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-10-31 14:10 |  |  |  | 2018-10-31 14:14 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 63 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1995 | [5 empty] | 2 | MPE | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 104637 | 120684.629874841253091 | 19669 | 22685.531743152542667 | 0 | 0 |  |  | 3203 | 3233.288416075650118203309692671394799054 |  | 0 | 127509 | 62370.6021649237883805768321513002364066 | 146603.4500340694458762033096926713947991 | 0 | 0 | 0 |  |  |  |  | 53.4 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE DAMAGE WAS CAUSED BY A THIRD PARTY CONTRACTOR. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | CABLE TV | YES | 18438667 |  |  | CONTRACT LOCATOR | NO |  |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | LEE MAXWELL | SR. REGULATORY COMPLIANCE ANALYST | lee.maxwell@pse.com | 425-4623575 |  |  |  |  | CHERYL MCGRATH | MANAGER COMPLIANCE PROGRAMS | 4254623207 | cheryl.mcgrath@pse.com | PUGET SOUND ENERGY (PSE) RESPONDED TO A BROKEN 2" PE GAS DISTRIBUTION MAIN IN YELM WA ON OCTOBER 31ST 2018. PSE WAS ONSITE AT 14:14 AND FOUND THAT THE LEAK WAS UNDER HARD SURFACE IN A BUSY INTERSECTION. THE SITUATION WAS CONTROLLED WHEN THE LEAK WAS UNCOVERED AND THE MAIN SQUEEZED AT 18:18. DUE TO NO CUSTOMERS DOWNSTREAM OF THE BREAK THE LINE WAS NOT BYPASSED, PSE CONTRACTOR INFRASOURCE COMPLETED THE FINAL REPAIR BY REPLACING 6' OF 2" PE MAIN AND THE LINE WAS PURGED BACK INTO SERVICE AT 20:00. THE FINAL REPAIR IS ESTIMATED AT $128,000.00. THE DAMAGE WAS CAUSED WHEN A TELECOMMUNICATIONS CONTRACTOR HIT THE MAIN WITH A DIRECTIONAL DRILL. THE TELECOMMUNICATIONS CONTRACTOR HAD AN ACTIVE LOCATE TICKET, BUT THE MAIN WAS NOT MARKED IN THE LOCATION WHERE THE PIPELINE WAS HIT. PSE FINDS THAT THE DAMAGE WAS A RESULT OF INACCURATE LOCATES BY THE LOCATING COMPANY ELM UTILITY SERVICES.
2025-03-31 10:13 | NO | NO | NO | 20180111 | 32107 | 2018-11-30 18:05 | SUPPLEMENTAL FINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2018-10-30 17:54 |  |  | 2018 | 4011 HARRISON STREET | BELLEVUE | SARPY | NE | 68147 | 41.1907 | -95.9741 | [9 empty] | 2018-10-31 14:07 | 1229049 |  | NATURAL GAS |  | 57.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2018-10-30 17:54 |  |  |  | 2018-10-30 18:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | INSIDE METER/REGULATOR SET |  | 1960 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 2.067 | [6 empty] | OTHER | [8 empty] | GAS SERVICE RISER AND METERS WERE DAMAGED AS A RESULT OF VEHICLE ACCIDENT | CLASS 3 LOCATION | 69400 | 80043.5153274079242 | 3000 | 3460.094322510429 | 1100 | 1268.7012515871573 | 0 | 0 |  |  | 179 | 180.692671394799054373522458628841607565 |  | 0 | 73679 | 35277.300039579804619385342789598108747 | 84953.0035729003095543735224586288416076 | 4 | 0 | 0 |  |  |  |  | 10 | 10 | 10 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE DAMAGES WERE A RESULT OF A VEHICLE ACCIDENT | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MICHAEL CONRAD | SENIOR CLAIMS INVESTIGATOR | mike_conrad@mudnebr.com | 4025047165 | 4025045165 |  |  |  | MICHAEL CONRAD | SENIOR CLAIMS INVESTIGATOR | 4025047165 | mike_conrad@mudnebr.com | ON TUESDAY OCTOBER 30 2018 AT 17:54 METROPOLITAN UTILITIES DISTRICT (DISTRICT) RECEIVED A NOTIFICATION THAT THERE WAS A GAS FILLED STRUCTURE AT 4011 HARRISON STREET BELLEVUE NE.. THERE WAS A UNKNOWN VEHICLE THAT DROVE THROUGH THE DOORWAY ON THE EAST END OF THE BUILDING AND STRUCK THE GAS METER SET AND METERS. THE VEHICLE PROCEEDED TO BACK OUT OF THE STRUCTURE AND DROVE AWAY FROM THE SCENE. THE STRUCTURE HOUSED FOUR SMALL BUSINESSES AND THE TWO EMPLOYEES TO ONE OF THE BUSINESSES WERE EVACUATED BY THE BELLEVUE FIRE DEPT. AS A RESULT OF THE GAS FILLED STRUCTURE. THE TRANSMISSION LINE TO THE STRUCTURE WAS SHUT OFF AT 19:19. THE STRUCTURE WAS THEN SECURED DUE TO THE DAMAGES. FOLLOWING DISCUSSIONS WITH THE NEBRASKA STATE FIRE MARSHAL'S OFFICE IT WAS DETERMINED THAT DUE EXTENT THE DAMAGES THAT WERE SUSTAINED AND THE OVERALL ESTIMATED REPAIR COSTS LIKELY WOULD EXCEED $50,000, THIS INCIDENT WAS A REPORTABLE INCIDENT TO THE NRC. ON WEDNESDAY OCTOBER 31 2018 THE NRC TELEPHONIC REPORT (#1229049) WAS MADE AT 14:07. ON THURSDAY NOVEMBER 1 2018 THE 48 HR. FOLLOW UP TELEPHONIC REPORT (#1229165) WAS MADE AT 13:32. TO DATE THERE HAS BEEN NO INFORMATION FORTHCOMING FROM BELLEVUE POLICE DEPT.., STATE FIRE MARSHAL, OR THIS DISTRICT'S INVESTIGATION THAT IDENTIFIES THE RESPONSIBLE PARTY FOR THIS INCIDENT. MAY 9, 2019: TO DATE THERE HAS BEEN NO FURTHER INFORMATION FORTHCOMING FROM ALL INVESTIGATING AGENCIES THAT IDENTIFIES THE RESPONSIBLE PARTY. THEREFORE THIS DISTRICT CONSIDERS THIS MATTER AND FILE FINALIZED.
2025-03-31 10:13 | YES | NO | NO | 20180112 | 34099 | 2018-12-05 11:11 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2018-11-08 08:55 |  |  | 2018 | 6674 PENTZ RD. | PARADISE | BUTTE | CA | 95969 | 39.7787 | -121.5761 | [9 empty] | 2018-11-08 15:31 | 1229905 |  | NATURAL GAS |  | 1224 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2018-11-08 10:02 |  |  |  | 2018-11-08 08:55 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1967 | [5 empty] | 0.75 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | GAS RELEASED DUE TO FIRE. | CLASS 3 LOCATION | 0 | 0 | 178000000 | 205298929.802285454 | 133000000 | 153397514.964629019 | 0 | 0 |  |  | 5532 | 5584.31205673758865248226950354609929078 |  | 0 | 311005532 | 148566475.447382384879432624113475177305 | 358702029.078971210588652482269503546099 | 691 | 0 | 11216 |  |  |  |  | 53 | 53 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | ENZA BARBATO | PROGRAM MANAGER | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | MANAGER OF GAS OPERATIONS COMPLIANCE AND RISK | 925-328-5776 | gsr8@pge.com | ON THURSDAY, NOVEMBER 8, 2018, AT APPROXIMATELY 0855 HOURS ON PG&E WAS ADVISED OF MANDATORY FIRE EVACUATIONS IN THE TOWN OF PARADISE AND A REQUEST TO SHUT OFF GAS TO A MOBILE HOME PARK LOCATED AT 6674 PENTZ RD, PARADISE. PG&E RECEIVED A LO-LO ALARM AT 1002 HOURS AND IS USING THIS AS THE BEST INDICATOR THAT THE ASSET WAS DAMAGED AT THAT TIME. BY 1035 HOURS, PG&E CREW HAD SHUT IN INLET FIRE VALVE V-302 AT SKYWAY & NEAL, PARADISE (REG. STATION P002). THE OEC WAS ACTIVATED AT APPROXIMATELY 0953 HOURS. THE GEC WAS ACTIVATED TO SUPPORT THE EVENT AT 1103 HOURS. THE CALFIRE INVESTIGATION REPORT STATES THAT THE CAMP FIRE WAS CAUSED BY ELECTRICAL TRANSMISSION LINES OWNED AND OPERATED BY PACIFIC GAS AND ELECTRICITY (PG&E). APPROXIMATELY 12,000 CUSTOMERS WERE PROACTIVELY SHUT IN. APPROXIMATELY 1,500 METERS WERE UNDAMAGED AND 10,500 METERS WERE DAMAGED. SERVICE CUT-OFFS AND RESTORATION PLANS ARE ONGOING.THERE WERE NO REPORTS OF INJURIES OR FATALITIES ASSOCIATED WITH PG&E GAS FACILITIES. MULTIPLE MEDIA OUTLETS, POLICE, FIRE DEPARTMENT WERE REPORTED ON SITE. THE NUMBERS PROVIDED HEREIN FOR DAMAGE COST CALCULATIONS ARE FOR ESTIMATION PURPOSES ONLY AND ARE THE BEST ESTIMATE AT THE TIME OF COMPLETING THIS REPORT . THIS INCIDENT WAS REPORTED TO THE DOT AT 1531 HOURS (NRC #1229905) AND CPUC AT 1537 HOURS. A 48 HOUR UPDATE WAS PROVIDED TO DOT ON FRIDAY, NOVEMBER 9, 2018 AT APPROXIMATELY 1222 HOURS (NRC #1229973). PG&E CONFIRMED THE RELEASE OF GAS FROM VARIOUS RESIDENTIAL SERVICE RISERS AND ESTIMATED THAT PROPERTY DAMAGE WILL EXCEED $50,000 AT APPROXIMATELY 1500 HOURS.
2025-03-31 10:13 | NO | NO | NO | 20180113 | 31841 | 2018-12-10 16:24 | SUPPLEMENTAL FINAL | 13299 | NEW JERSEY NATURAL GAS CO | 1415 WYCKOFF ROAD | WALL | NJ | 07719 | 2018-11-12 08:04 |  |  | 2018 | 527 2ND STREET | LAKEWOOD | OCEAN | NJ | 08701 | 40.0919 | -74.22 | [9 empty] | 2018-11-12 09:50 | 1230131 |  | NATURAL GAS |  | 133 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 100 | 2018-11-12 08:04 |  |  |  | 2018-11-12 08:22 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 42 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1996 | [5 empty] | 2 | ASTM D2513 | PHILLIPS DRISCOPIPE, INC. | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 4 | 7.5 | [7 empty] | CLASS 3 LOCATION | 50000 | 57668.23870850715 | 16244 | 18735.257391619802892 | 4647 | 5359.686105568654521 | 0 | 0 | EXPECTING NON-OPERATOR PRIVATE PROPERTY DAMAGE COST TO BE MORE THAN $50,000 |  | 1275 | 1287.056737588652482269503546099290780142 |  | 0 | 72166 | 35054.460718250763612113475177304964539 | 83050.2389432842598952695035460992907801 | 0 | 0 | 8 |  |  |  |  | 46 | 46 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | NO | [5 empty] | YES | 9 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | MOBEEN KHAN | DIRECTOR - SYSTEM ENHANCEMENT | mukhan@njng.com | 732-919-8035 | 732-919-0936 |  |  |  | MOBEEN KHAN | DIRECTOR - SYSTEM ENHANCEMENT | 732-919-8035 | mukhan@njng.com | ON NOVEMBER 12, 2018, AN EXCAVATOR USING A TRACKHOE STRUCK A NEW JERSEY NATURAL GAS ("NJNG") 2 INCH GAS MAIN (THE "PIPE") AT 527 2ND STREET, LAKEWOOD, OCEAN COUNTY, NEW JERSEY. THE EXCAVATOR, V ROSE EXCAVATING, LLC, WAS WORKING WITHOUT A VALID MARKOUT TICKET AT THE TIME OF THE INCIDENT. INCIDENT SUMMARY: THE PIPE, A 60 PSIG MAXIMUM ALLOWABLE OPERATING PRESSURE ("MAOP") HIGH DENSITY POLYETHYLENE ("HDPE") PERFORMANCE DRISCOPIPE 8000, WAS INSTALLED IN NOVEMBER 1996. AT THE TIME OF THE INCIDENT, THE PIPE WAS OPERATING AT APPROXIMATELY 46 PSIG. THE PIPE RUNS BEHIND EIGHT TOWNHOUSE RESIDENCES WITH ENTRANCES THAT FACE PRIVATE WAY AND 2ND STREET IN LAKEWOOD. THE MACHINE OPERATOR STRUCK THE PIPE WITH THE TRACKHOE BUCKET COMPLETELY SEVERING IT CIRCUMFERENTIALLY. UPON STRIKING THE PIPE, THE MACHINE OPERATOR LEFT THE TRACKHOE RUNNING AND FLED THE SCENE. THE ESCAPING NATURAL GAS IGNITED APPROXIMATELY TEN MINUTES AFTER THE PIPE WAS DAMAGED BY THE EXCAVATOR. NJNG RECEIVED AN INITIAL CALL FROM THE EXCAVATION COMPANY'S OWNER, VICTOR ROSE, AT 8:04 A.M. ON NOVEMBER 12, 2018 REPORTING DAMAGE TO A NATURAL GAS FACILITY. NJNG DISPATCHED PERSONNEL AT 8:09 A.M. WHO ARRIVED ON-SITE AT 8:22 A.M. NJNG'S TECHNICIAN TURNED OFF A 2" PLASTIC VALVE STOPPING THE FLOW OF GAS TO THE DAMAGED MAIN AND 8 METERS AT 8:50 A.M. POLICE AND FIRE DEPARTMENTS ALSO RESPONDED TO THE SCENE, BLOCKED TRAFFIC ON NEARBY STREETS (2ND STREET, 3RD STREET, FOREST AVENUE, PRIVATE WAY, NORTH LAKE DRIVE AND 1ST STREET) AND ENSURED THE PUBLIC WERE EVACUATED AWAY FROM THE SCENE DURING POLICE AND FIRE RESPONSE ACTIVITIES. AT 8:56 A.M., NJNG'S DIRECTOR OF SYSTEM ENHANCEMENT NOTIFIED THE NEW JERSEY BOARD OF PUBLIC UTILITIES' BUREAU OF PIPELINE SAFETY AND BUREAU OF ONE CALL OF THE EXCAVATION DAMAGE, GAS IGNITION AND SUBSEQUENT FIRE VIA EMAIL. NJNG SYSTEM ENHANCEMENT PERSONNEL NOTIFIED THE NATIONAL RESPONSE CENTER OF THE INCIDENT AT 9:50 A.M. AND WERE ASSIGNED REPORT NUMBER 1230131. THE EXCAVATOR: VICTOR ROSE WHO INDICATED HE WAS THE OWNER OF V ROSE EXCAVATING, LLC, 990 CEDAR BRIDGE AVENUE, BRICK, NEW JERSEY CALLED FOR A MARKOUT ON SEPTEMBER 1, 2018, FOR 527 2ND STREET TO INSTALL A STORM SEWER. THE MARKOUT TICKET NUMBER 182440105 EXPIRED ON NOVEMBER 8, 2018, FOUR DAYS PRIOR TO THE DAMAGE. THE EXCAVATOR DID NOT HAVE A VALID MARKOUT TICKET AT THE TIME OF THE INCIDENT. DAMAGE: THREE TOWNHOMES SUSTAINED FIRE DAMAGE: I) 527 2ND STREET; II) 525 2ND STREET; AND III) 207 PRIVATE WAY. THE DAMAGE INCLUDES BURNS TO THE STRUCTURE, SIDING, DECKS, INTERIOR DAMAGE AND OTHER SMOKE AND/OR WATER DAMAGE WHICH AT THIS TIME IS EXPECTED TO TOTAL MORE THAN $50,000.00. THE TRACKHOE SUSTAINED SOME SCORCHING DAMAGE BUT WAS CAPABLE OF DRIVING OFF THE PROPERTY AFTER THE AREA WAS MADE SAFE. THERE WERE NO FATALITIES OR INJURIES REQUIRING IN-PATIENT HOSPITALIZATION. RESTORATION OF GAS SERVICE: IN ORDER TO RESTORE GAS SERVICE TO THE AFFECTED DISTRIBUTION MAIN AND SERVICES FOLLOWING THE INCIDENT, APPROXIMATELY FIVE FEET OF NEW 2" HDPE MAIN WAS INSTALLED TO REPLACE THE DAMAGED MAIN. THE REPAIRED GAS MAIN WAS PUT BACK INTO SERVICE AT 5:30 P.M. ON NOVEMBER 12, 2018. AN UNDISTURBED PORTION OF THE PREVIOUSLY INSTALLED MAIN WAS MEASURED AT A DEPTH OF 3 FEET 6 INCHES. FOUR OF THE EIGHT AFFECTED METERS HAD THE GAS SERVICE RESTORED AFTER REPAIRS WERE COMPLETED. THE GAS SERVICE LINE TO 527 2ND STREET WAS RETIRED. GAS SERVICE WAS LEFT OFF TO THREE METERS AT END OF DAY. ONE OF THE THREE METERS HAS SINCE BEEN TURNED BACK ON. METERS AT 527 2ND STREET AND 207 PRIVATE WAY REMAIN OFF DUE TO THE FIRE DAMAGE TO THE STRUCTURES.
2025-03-31 10:13 | NO | YES | YES | 20180114 | 31326 | 2018-12-14 10:14 | ORIGINAL FINAL | 18124 | SAVANNAH PUBLIC UTILITY DEPT | 140 MAIN STREET | SAVANNAH | TN | 38372 | 2018-11-16 14:00 |  |  | 2018 | 2315 PICKWICK STREET | SAVANNAH | HARDIN | TN | 38372 | 35.1952 | -88.2434 | [9 empty] | 2018-11-16 16:35 | 1230610 |  | NATURAL GAS |  | 1000 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | YES | 0 | 2018-11-16 14:00 |  |  |  | 2018-11-16 14:07 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 2018 | [5 empty] | 2 | ASTM D2513 3408 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | OTHER | [8 empty] | GAS CONTRACTOR MARTIN CONTRACTING INC. WAS PURGING NATURAL GAS UNDERGROUND WITH A 2.0 PE LINE AND A 2.0 PE VALVE | CLASS 1 LOCATION | 0 | 0 | 0 | 0 | 2000 | 2306.729548340286 | 0 | 0 |  |  | 500 | 504.728132387706855791962174940898345154 |  | 0 | 2500 | 1422.281270274988009456264775413711583924 | 2811.457680727992855791962174940898345154 | 0 | 0 | 0 |  |  |  |  | 41 | 40 | 52 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 1 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | TDOT NATURAL GAS RELOCATION PROJECT PRIME CONTRACTOR DELTA CONTRACTING CO, AND SUB-CONTRACTOR MARTIN CONTRACTING INC. WAS PURGING NATURAL GAS UNDERGROUND IN AN EXCAVATION PIT, AND PROPER PROCEDURES WERE NOT IN PLACE FOR PURGING OPERATIONS AND PERSONNEL OPERATOR QUALIFICATIONS WERE NOT PROPERLY FOLLOWED. | YES | YES | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | VIRGIL MORRIS | DIRECTOR OF UTILITIES | directorsud@yahoo.com | 731-925-4216 | 731-925-2967 |  |  |  | VIRGIL MORRIS | DIRECTOR OF UTILITIES | 731-925-4216 | directorsud@yahoo.com | DURING A TDOT HIGHWAY WIDENING ROAD PROJECT, PRIME CONTRACTOR DELTA CONTRACTING CO. AND SUB-CONTRACTOR MARTIN CONTRACTING INC. WAS RELOCATING A NATURAL GAS MAIN AND MARTIN CONTRACTING INC. WAS PURGING A 6" STEEL MAIN THRU A 2" STEEL TO 2" PE TRANSITION PIPE WITH A 2" PE VALVE UNDERGROUND WHEN THE PURGING LOCATION IGNITED AT THE PURGING LOCATION, AND THE FIRE INJURED A CITY OF SAVANNAH UTILITY EMPLOYEE. UPON THE INJURY THE NATURAL GAS WAS TURNED OFF AT THE 6" STEEL VALVE APPROXIMATELY .08 MILES TO THE SOUTH ON PICKWICK STREET, HIGHWAY 128 SOUTH TO STOP THE FLOW OF NATURAL GAS. CITY OF SAVANNAH FIRE DEPARTMENT EXTINGUISHED THE REMAINING FIRE AFTER THE NATURAL GAS WAS TURNED OFF.
2025-03-31 10:13 | NO | YES | YES | 20180115 | 34307 | 2018-12-14 11:37 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2018-11-16 17:30 |  |  | 2018 | 13962 E. LINVALE PLACE | AURORA | ARAPAHOE | CO | 80014-3620 | 39.6667 | -104.8264 | [9 empty] | 2018-11-16 19:26 | 1230632 |  | NATURAL GAS |  | 6 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 1 | 0 | 1 | 2 | YES |  |  |  |  | YES | 230 | 2018-11-16 16:16 |  |  |  | 2018-11-16 16:52 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1979 | [5 empty] | 1.25 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 10 |  |  | 2306 | MECHANICAL PUNCTURE | 1.3 | 0.8 | [7 empty] | CLASS 3 LOCATION | 900000 | 1038028.2967531287 | 24000 | 27680.754580083432 | 11000 | 12687.012515871573 | 0 | 0 |  |  | 18 | 18.17021276595744680851063829787234042553 |  | 0 | 935018 | 446656.115602965877872340425531914893617 | 1078414.23406184966244680851063829787234 | 0 | 0 | 43 |  |  |  |  | 53 | 53 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | NO | [5 empty] | YES | 25 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | DUANE PURCELL | GAS DISTRIBUTION ENGINEER | duane.purcell@xcelenergy.com | 970-244-2715 |  |  |  |  | MARK NOLAN | PRINCIPAL ENGINEER | 3035713931 | mark.nolan@xcelenergy.com | A THIRD PARTY EXCAVATOR DAMAGED THE PE MAIN DURING DIRECTIONAL BORING ACTIVITIES. NO LOCATE REQUEST WAS RECEIVED FOR THE EXCAVATION. THE LEAKING GAS APPEARS TO HAVE ENTERED AN ADJACENT RESIDENTIAL STRUCTURE AND EXPLODED, AND THIS CAUSED THE FATALITY, INJURIES, AND PROPERTY DAMAGE. NOTE: RESPONSE C5 IS FOR THE LARGEST HOLE SIZE, BUT THERE WERE TWO SMALLER HOLES IN THE DAMAGED MAIN. NOTE: RESPONSE G3-3 IS "NO." HOWEVER THE COMPANY HAD RECEIVED PRIOR LOCATE REQUESTS FOR THE LARGE PROJECT, BUT NOT FOR THE AREA OF THE DAMAGE CAUSING THE INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20180116 | 31417 | 2018-12-17 12:34 | SUPPLEMENTAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2018-11-19 12:18 |  |  | 2018 | 1618 S ALSTON AVENUE | DURHAM | DURHAM | NC | 27707 | 35.097 | -78.0894 | [9 empty] | 2018-11-19 15:13 | 1230829 |  | NATURAL GAS |  | 2424 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-11-19 12:09 |  |  |  | 2018-11-19 12:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | YES | [6 empty] | YES | UNCASED | THIRD FORK CREEK | 1 |  | INVESTOR OWNED |  | MAIN |  | 2005 | [5 empty] | 4 | API 5L | UNKNOWN | STEEL |  | OTHER | ELECTRIC RESISTANCE WELD | 0.337 | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1620 | 1868.45093415563166 | 28003 | 32297.673771086514429 | 30114 | 34732.426809359686302 | CONTRACTOR TO INSTALL MAIN FOR PERMANENT REPAIR. |  | 10448 | 10546.7990543735224586288416075650118203 |  | 0 | 70185 | 38292.1202961493777055981087470449172577 | 79445.3505689753548496288416075650118203 | 0 | 0 | 0 |  |  |  |  | 60 | 60 | 66 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CAUSE OF INCIDENT WAS CLEARLY EXCAVATOR DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 183132209 | NC 811 |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | TUCKER BULLOCK | MANAGER - DISTRIBUTION OPERATIONS | tbullock@scana.com | 919-598-7417 | 803-933-8273 |  |  |  | SCOTT SWINDLER | GENERAL MANAGER - OPERATIONS AND MAINTENANCE | 704-810-3230 | mswindler@scana.com | AT 12:09PM, PSNC ENERGY'S CENTRAL DISPATCH RECEIVED A CALL FROM DURHAM COUNTY 911 OF A DAMAGED GAS LINE ON S ALSTON AVE, DURHAM, NC. PSNC ENERGY FIRST RESPONDER ARRIVED ON SCENE AT 12:15PM. FIRE DEPARTMENT WAS ON SCENE WHEN PSNC ENERGY FIRST RESPONDER ARRIVED. FRED SMITH COMPANY WAS DOING ROAD WORK FOR NCDOT AT A CREEK CROSSING. ROAD AT CREEK CROSSING HAD BEEN CLOSED FOR SEVERAL MONTHS. WHILE DIGGING IN THE CREEK, FRED SMITH COMPANY'S EXCAVATION EQUIPMENT HIT THE 4" STEEL NATURAL GAS MAIN AND CAUSED GAS TO ESCAPE. GAS LINE LOCATING MARKS WERE VISIBLE AND ACCURATE ON THE JOB SITE. GENERAL MANAGER - OPERATIONS AND MAINTENANCE NOTIFIED NCUC PIPELINE SAFETY DIRECTOR BY PHONE AT 2:58PM DUE TO PROJECTED REPAIR COSTS GREATER THAN $50,000. NATIONAL RESPONSE CENTER (REPORT ID 1230829) WAS NOTIFIED AT 3:13PM DUE TO PROJECTED REPAIR COSTS GREATER THAN $50,000. PSNC ENERGY CREWS RAN APPROXIMATELY 530 FEET OF ABOVE GROUND TEMPORARY 2 INCH PLASTIC MAIN ON RIDDLE RD AS A BYPASS TO MAINTAIN SERVICE TO NATURAL GAS CUSTOMERS. AT 9:07PM THIS BYPASS WAS TIED IN. PSNC ENERGY CREWS STOPPED GAS BLOWING BY CLOSING A VALVE INSTALLED ON ONE SIDE OF THE CREEK AND INSTALLING A STOPPER FITTING ON THE OTHER SIDE. GAS STOPPED BLOWING AT 11:15PM. NATURAL GAS SERVICE CONTINUED TO 2 RESIDENTIAL CUSTOMERS AT 1618 AND 1622 ALSTON AVE DOWNSTREAM OF THE STOPPER FITTING BY RUNNING AN ABOVE GROUND TEMPORARY SERVICE LINE. ON 11/20/2018 AND 11/21/2018, PSNC ENERGY CONTRACTOR INSTALLED APPROXIMATELY 530 FT OF 4 INCH UNDERGROUND PLASTIC MAIN ALONG RIDDLE RD AS A PERMANENT FIX TO THE DAMAGED LINE. THE GAS MAIN AT THE CREEK CROSSING WILL BE ABANDONED UNTIL AFTER ROAD WORK IS COMPLETE. ALSO ON THESE DATES PSNC ENERGY CREWS INSTALLED 250 FEET OF 2" PLASTIC MAIN AND A NEW SERVICE LINE AS A PERMANENT REPAIR TO SERVE NATURAL GAS TO 1618 AND 1622 ALSTON AVE.
2025-03-31 10:13 | NO | YES | NO | 20180118 | 31729 | 2018-12-18 13:25 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2018-11-19 11:34 |  |  | 2018 | 25900 NORTHWESTERN HIGHWAY | SOUTHFIELD | OAKLAND | MI | 48075 | 42.4793 | -83.2502 | [9 empty] | 2018-11-19 16:44 | 1230843 |  | NATURAL GAS |  | 5441 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-11-19 11:34 |  |  |  | 2018-11-19 12:09 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 9 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1963 | [5 empty] | 8 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 1 | 2 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 70959 | 81841.611010339177137 | 49 | 56.514873934337007 | 0 | 0 |  |  | 17738 | 17905.7352245862884160756501182033096927 |  | 0 | 88746 | 50483.6009337911648314704491725768321513 | 99803.8611088598025600756501182033096927 | 1 | 0 | 0 |  |  |  |  | 279 | 305 | 320 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | ROAD WORK | YES | 81340893 |  |  | CONTRACT LOCATOR | YES | YES | 3 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | THE PIPELINE DEPTH WAS INSUFFICIENT TO AVOID DAMAGE FROM THE SAW CUT OPERATION | [169 empty] | CARMELLA KING | SENIOR TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON NOVEMBER 19, 2018 AT APPROXIMATELY 11:34 HOURS A THIRD PARTY CONTRACTOR SAW CUTTING THE ROAD DAMAGED AN 8" STEEL (HIGH PRESSURE) PIPELINE CAUSING GAS TO BE RELEASED. THE PIPELINE DEPTH WHEN THE DAMAGE OCCURRED WAS APPROXIMATELY 9". THE DAMAGE PORTION OF THE PIPELINE WAS APPROXIMATELY .25" X 1.75". THE PIPELINE IS LOCATED ON NORTHWESTERN HIGHWAY AND CIVIC CENTER DRIVE, SOUTHFIELD, MICHIGAN (OAKLAND COUNTY) THE CONTRACTOR RECOGNIZED CONTACT HAD BEEN MADE WITH THE PIPELINE, SHUT-OFF THE EQUIPMENT AND CONTACTED CONSUMERS ENERGY OF THE DAMAGE. NO IGNITION, INJURIES OR FATALITIES OCCURRED AS A RESULT OF THE DAMAGE. CONSUMERS ENERGY PERSONNEL ARRIVE ONSITE AT APPROXIMATELY 12:09 HOURS AND BEGAN MONITORING SURROUNDING LOCATIONS TO ENSURE GAS WAS NOT MIGRATING. A PORTION OF THE ROAD WAS CLOSED TO ENSURE THE SAFETY OF MOTORIST. ON NOVEMBER 20, 2018 AT APPROXIMATELY 20:35 HOURS THE DAMAGED SECTION OF PIPELINE WAS ISOLATED UTILIZING MUELLER CONTROL FITTING TO THE NORTH AND SOUTH OF THE DAMAGE LOCATION. A WELDED SPLIT SLEEVE WAS INSTALLED TO PERMANENTLY REPAIR THE DAMAGE AND NORMAL OPERATIONS RESUMED AT APPROXIMATELY 23:40. ONE CUSTOMER WAS IMPACTED BY THE PIPELINE DAMAGE AND THE SERVICE WAS RESTORE IMMEDIATELY FOLLOWING THE REPAIR.
2025-03-31 10:13 | NO | YES | NO | 20180119 | 32138 | 2018-12-18 14:55 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2018-11-18 17:08 |  |  | 2018 | 1452 EAST WOODBURY ROAD | PASADENA | LOS ANGELES | CA | 91104-0000 | 34.1769 | -118.1207 | [9 empty] | 2018-11-18 19:27 | 1230766 |  | NATURAL GAS |  | 0.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 4 | 2018-11-18 17:08 |  |  |  | 2018-11-18 17:08 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 33 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1976 | [5 empty] | 0.5 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 7 |  |  | 2306 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 200000 | 230672.9548340286 | 11721 | 13518.588518048246103 | 2060 | 2375.93143479049458 | 0 | 0 |  |  | 5 | 5.04728132387706855791962174940898345154 |  | 0 | 213786 | 102125.5221959787240280945626477541371158 | 246572.5220681912177515579196217494089835 | 0 | 0 | 4 |  |  |  |  | 23 | 23 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | SOCKET, HEAT FUSION |  | 1976 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) |  |  |  |  | YES | [11 empty] | YES |  |  |  | OTHER | FUSION JOINT UNDER PRESSURE FROM PIPE BEND,POSSIBLY CAUSED BY DRAIN WORK IN 2015 | YES | 1976 | [85 empty] | ALEXANDER HUGHES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | ahughes@semprautilities.com | 9496972539 |  |  |  |  | ALEXANDER HUGHES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 9496972539 | ahughes@semprautilities.com | ON 11/18/2018, LOS ANGELES COUNTY FIRE DEPARTMENT REPORTED AN EXPLOSION AT 1452 E WOODBURY RD IN PASADENA. SOCALGAS CREWS RESPONDED AND FOUND GAS INDICATIONS AT THE FOUNDATION. PER FIRE DEPARTMENT ON SCENE, A NEARBY ELECTRICAL OUTLET WAS A POTENTIAL SOURCE OF IGNITION. SOCALGAS CREW LOCATED A LEAK ON THE 1/2INCH PLASTIC ALDYL-A GAS SERVICE TO 1452 E WOODBURY RD AND ABANDONED THE SERVICE. THE 2 GAS METERS (1452 & 1454) WERE REMOVED AND LEFT OFF, PENDING STRUCTURAL REPAIRS. THE 2 NEIGHBORING METERS (1442 & 1460) WERE TURNED OFF ON 11/18/2018 FOR SAFETY AND RESTORED AT 00:46 ON 11/19/2018. NO OTHER LEAKS WERE FOUND IN THE VICINITY. THERE WERE NO INJURIES NOR FATALITIES. THIS INCIDENT WAS REPORTED TO DOT DUE TO GAS RELEASE AND ASSOCIATED DAMAGES OVER $50,000. UPDATE 5-16-2019 - ON 4/26/19 THE ANALYSIS SUMMARY FROM THE EXPONENT LAB TESTING, THAT TRANSPIRED ON 3/29/19, WAS SENT TO THE CPUC. NO ADDITIONAL INFORMATION NEEDED, PER CPUC, AS EMAILED ON 5/9/19.
2025-03-31 10:13 | NO | NO | NO | 20180120 | 31397 | 2018-12-19 12:10 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2018-11-19 14:04 |  |  | 2018 | 104 SOMERSET DR | NOVATO | MARIN | CA | 94945 | 38.1206 | -122.5797 | [9 empty] | 2018-11-19 23:22 | 1230868 |  | NATURAL GAS |  | 1330 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 16 | 2018-11-19 14:04 |  |  |  | 2018-11-19 14:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 49 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1990 | [5 empty] | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | UNKNOWN |  |  |  | UNKNOWN |  | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 3 LOCATION | 50000 | 57668.23870850715 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4000 | 4037.825059101654846335697399527186761229 |  | 0 | 54000 | 27619.6795110118160756501182033096926714 | 61706.0637676088048463356973995271867612 | 1 | 0 | 15 |  |  |  |  | 50 | 50 | 56 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DRILLING | TELECOMMUNICATIONS | YES | 831002460 | N/A |  | UTILITY OWNER | YES | YES | 21 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | ENZA BARBATO | PROGRAM MANAGER | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | MANAGER OF GAS OPERATIONS COMPLIANCE AND RISK | 925-328-5776 | gsr8@pge.com | ON MONDAY, NOVEMBER 19, 2018 AT 14:04 HOURS, PG&E WAS NOTIFIED OF A THIRD PARTY DIG IN AT 104 SOMERSET DR, IN THE CITY OF NOVATO. A THIRD PARTY CONTRACTOR, FIBERCO, STRUCK A 4" DISTRIBUTION PLASTIC MAIN WHILE DIRECTIONAL BORING CAUSING A GAS RELEASE. THERE WAS A VALID USA TICKET (X831002460) AND THE LOCATOR FAILED TO MARK THE 4" PLASTIC GAS MAIN. THE REPAIR CREW ARRIVED ON-SITE AT 14:20 HOURS AND STOPPED THE FLOW OF GAS BY CLOSING TWO VALVES AND SQUEEZING A 6" STEEL MAIN BY 19:15 HOURS. SERVICE WAS IMPACTED TO 16 GAS CUSTOMERS. REPAIRS WERE COMPLETED ON 11/20/18 AT 15:30 HOURS. FIRE DEPARTMENT WAS REPORTED ONSITE. THERE WERE NO POLICE, INJURIES, FATALITIES, MEDIA OR IGNITION ASSOCIATED WITH THIS INCIDENT. THE INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO THE ESTIMATED PROPERTY DAMAGE EXCEEDING $50,000 WHICH WAS DETERMINED AT APPROXIMATELY 23:00 HOURS ON NOVEMBER 19, 2018.
2025-03-31 10:13 | NO | NO | NO | 20180121 | 31957 | 2018-12-20 16:36 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-11-20 16:30 |  |  | 2018 | 5250 FRYE RD. | IRVING | DALLAS | TX | 75061 | 32.8209 | -97.0265 | [9 empty] | 2018-11-20 15:49 | 1230923 |  | NATURAL GAS |  | 416.06 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-11-20 13:10 |  |  |  | 2018-11-20 13:57 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | DISTRIBUTION/TRANSMISSION LINE | 1979 | [8 empty] | STEEL |  | OTHER | STRAIGHT SEAM | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 0.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 45000 | 51901.414837656435 | 8793 | 10141.536459278067399 | 0 | 0 |  |  | 2158 | 2178.406619385342789598108747044917257683 |  | 0 | 55951 | 27711.4833396155175968132387706855791962 | 64221.3579163198451885981087470449172577 | 0 | 0 | 0 |  |  |  |  | 285 | 300 | 325 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SITE DEVELOPMENT | NO | [7 empty] | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | RICHARD VALLE | OPERATIONS SUPERVISOR | richard.valle@atmosenergy.com | 469-261-2140 |  |  |  |  | ERIK REYNOLDS | DIRECTOR REGULATORY AND COMPLIANCE | 214-206-2726 | erik.reynolds@atmosenergy.com | ADDITIONAL NRC REPORT NO. 1231039 ON NOVEMBER 20, 2018, A 3RD PARTY CONTRACTOR WAS MOVING DIRT OFF OF ATMOS ENERGY'S ROW TO USE AS FILL DIRT FOR A CONCRETE PROJECT NEARBY. ATMOS ENERGY HAD RECEIVED A LOCATE TICKET FROM A DIFFERENT CONTRACTOR THAT INCLUDED THE AREA WHERE THE DAMAGE OCCURRED AND THE SCOPE OF THE TICKET WAS MARKED PROPERLY. HOWEVER, THE CONTRACTOR THAT CAUSED THE DAMAGE DID NOT REQUEST A LOCATE FOR THE EXCAVATION THAT RESULTED IN THIS INCIDENT. THIS ROW CONTAINS A HIGH PRESSURE DISTRIBUTION 16 INCH PIPELINE WITH OPERATING PRESSURE OF APPROX. 300 POUNDS. THE CONTRACTOR'S EMPLOYEE OPERATING THE BOBCAT SKID STEER WITHIN THE MARKED TOLERANCE ZONE HIT THE ATMOS ENERGY C-16 PIPELINE WITH THE BUCKET TOOTH AND DAMAGED THE LINE, WHICH RESULTED IN AN INDENTION IN THE PIPE WITH A SMALL CRACK WITHIN THE INDENTION WHERE GAS WAS RELEASED. THE CONTRACTOR NOTIFIED ATMOS ENERGY OF THE INCIDENT AT 13:10, AND ATMOS CREWS ARRIVED AT THE SITE AT 13:57. A PERMANENT REPAIR WAS MADE ON NOVEMBER 29 BY INSTALLING 5' OF 16" STEEL PIPE.
2025-03-31 10:13 | NO | YES | YES | 20180122 | 31475 | 2018-12-21 10:44 | SUPPLEMENTAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2018-11-24 16:30 |  |  | 2018 | 743 TRUMBULL AVE. | LAWRENCE TWP. | MERCER | NJ | 08648 | 40.2482 | -74.736 | [9 empty] | 2018-11-26 16:59 | 1231342 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 10 | 2018-11-24 16:30 |  |  |  | 2018-11-24 16:37 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | 2018 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | HOMEOWNER INDUCED LEAK | [5 empty] | CLASS 4 LOCATION | 300000 | 346009.4322510429 | 0 | 0 | 152 | 175.311445673861736 | 3000 | 3460.094322510429 | NONE NOTED |  | 50 | 50.47281323877068557919621749408983451537 |  | 0 | 303202 | 144859.0958941235683369456264775413711584 | 349695.3108324659614215791962174940898345 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | HOMEOWNER INDUCED RELEASE OF GAS | [47 empty] | ROGER GUNNELS | PRINCIPLE REGULATORY SPECIALIST QAQC | roger.gunnels@pseg.com | 973-213-2474 |  |  |  |  | CHRISTOPHER LAROSSA | MANAGER REGULATORY POLICY AND PROCEDURE | 973-896-7617 | christopher.larossa@pseg.com | ON SATURDAY, NOVEMBER 24, 2018, AT APPROXIMATELY 4:30 PM BURLINGTON DISPATCH RECEIVED A CALL FROM THE LAWRENCE FIRE DEPARTMENT TO REPORT A HOUSE EXPLOSION AT 749 TRUMBULL AVENUE IN LAWRENCE. PSE&G PERSONNEL WERE PROMPTLY DISPATCHED TO THE SCENE. UPON ARRIVAL THE ACTUAL LOCATION WAS VERIFIED AS 743 TRUMBULL AVENUE. GAS WAS SHUT OFF AT CURB VALVE FOR 743 TRUMBULL AVENUE AND THE ADJACENT HOMES, 741 AND 745. AFTER THE EXPLOSION THE HOUSE WAS FULLY ENGULFED IN FLAMES AND SUSTAINED SEVERE DAMAGE. THE TWO ADJACENT HOUSES SUSTAINED MINOR FIRE DAMAGE. THERE WERE TWO INJURIES, ONE REQUIRING INPATIENT HOSPITALIZATION. INITIAL REPORTS FROM THE POLICE DEPARTMENT INDICATED THAT THE HOMEOWNER MAY HAVE BEEN WORKING ON THE HEATING SYSTEM AT THE TIME OF THE INCIDENT. SUBSEQUENT ONSITE INVESTIGATION DETERMINED THAT A PLUG ON THE SERVICE TEE INSIDE THE BASEMENT HAD BEEN MECHANICALLY REMOVED AND THE OPEN SERVICE TEE WAS THE SOURCE OF THE GAS LEAK. THE SERVICE WAS PRESSURE TESTED ON 11/25/18 AT 10PSI FOR 5 MINUTES AND SHOWED NO SIGNS OF LEAKAGE. THE SERVICE WAS PRESSURE TESTED AGAIN ON 12/3/18 AT 55 PSI FOR 5 MINUTES AND SHOWED NO SIGNS OF LEAKAGE. THE INVESTIGATION IS ONGOING WITH NO UPDATES AT THIS TIME.
2025-03-31 10:13 | NO | YES | YES | 20180123 | 32262 | 2018-12-23 19:46 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2018-11-24 08:34 |  |  | 2018 | 493 LEMAR AVENUE | OXNARD | VENTURA | CA | 93036-0000 | 34.2421 | -119.158 | [9 empty] | 2018-11-26 08:14 | 1231360 |  | NATURAL GAS |  | 139 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES |  |  |  |  | YES | 12 | 2018-11-24 17:41 |  |  |  | 2018-11-24 08:51 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 34 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | [5 empty] | 2 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 500000 | 576682.3870850715 | 38963 | 44938.551695991281709 | 200 | 230.6729548340286 | 0 | 0 |  |  | 834 | 841.886524822695035460992907801418439716 |  | 0 | 539997 | 258331.081737813985035773049645390070922 | 622693.4982607195053444609929078014184397 | 0 | 0 | 1 |  |  |  |  | 45 | 45 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [9 empty] | YES |  |  |  | OTHER | AXIAL CRACK ON UNDERSIDE OF MAIN WITH TREE ROUTE IN VICINITY | NO | [86 empty] | ALEXANDER HUGHES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | ahughes@semprautilities.com | 9496972539 |  |  |  |  | KHOA LE | SR PIPELINE SAFETY AND COMPLIANCE ADVISOR | 6268934536 | kle2@semprautilities.com | ON SATURDAY, NOVEMBER 24, 2018, SOCALGAS WAS NOTIFIED BY VENTURA COUNTY FIRE DEPARTMENT (VENTURA COUNTY FIRE) OF A STRUCTURE FIRE AND EXPLOSION AT 493 LEMAR AVE, OXNARD. THE CAUSE OF THE INCIDENT IS UNKNOWN; INITIAL INFORMATION PROVIDED BY VENTURA COUNTY FIRE SUGGESTED POSSIBLE PROPANE INVOLVEMENT. THERE WERE THREE INJURIES THAT WERE TRANSPORTED TO LOCAL HOSPITAL AS A RESULT OF THIS INCIDENT. DAMAGES ASSOCIATED WITH THIS INCIDENT EXCEEDS $50,000. ALTHOUGH THE GAS METER ASSEMBLY (MSA) DID NOT SUSTAIN DAMAGE FROM THE FIRE, VENTURA COUNTY FIRE REQUESTED THE SERVICE BE ABANDONED DUE TO EXTENSIVE PROPERTY DAMAGE AND THE POTENTIAL OF THE WEAKENED STRUCTURE FALLING ONTO THE MSA. LATER ON NOVEMBER 24, 2018, ONCE THE AREA AROUND THE INCIDENT WAS SAFE AND ACCESSIBLE, A SOCALGAS CREW BEGAN ABANDONING THE SERVICE. IN THE PROCESS, THE CREW FOUND A SMALL LEAK AT THE SERVICE-TO-MAIN-CONNECTION (SMC), WHICH IS LOCATED ACROSS THE STREET (CORTEZ STREET). THE CREW THEN PROCEEDED TO CONDUCT LEAK SURVEY AND BAR HOLE SURVEY OF THE GENERAL AREA. THROUGH THESE ACTIVITIES, THE CREW LOCATED A SECOND LEAK ON A 2-INCH PLASTIC MAIN INSTALLED UNDER LEMAR AVENUE. THE CREW ISOLATED APPROXIMATELY 100 FEET OF THE MAIN TO CUT-OFF SUPPLY TO THAT PORTION OF THE MAIN. ON MONDAY, NOVEMBER 26, 2018, PIPELINE SAFETY, COMPLIANCE AND EMERGENCY MANAGEMENT DEPARTMENT FROM SOCALGAS BECAME AWARE THAT NATURAL GAS INDICATIONS WERE IDENTIFIED NEAR THE INCIDENT. ALTHOUGH THE INCIDENT REMAINS UNDER INVESTIGATION AND NO CAUSE HAS BEEN DETERMINED, A PIPELINE SAFETY, COMPLIANCE AND EMERGENCY MANAGEMENT REPRESENTATIVE NOTIFIED THE DEPARTMENT OF TRANSPORTATION AND REPORTED THE INCIDENT TO THE CPUC. INVESTIGATION INTO THE CAUSE OF THE INCIDENT IS ONGOING. TENTATIVELY, SOCALGAS IS COORDINATING WITH VARIOUS PARTIES INVOLVED TO CONDUCT A PRESSURE TEST OF THE HOUSELINE ON JANUARY 11, 2019, AND AN INSPECTION OF THE SOCALGAS COMPONENTS ON JANUARY 18, 2019. FOR ANY FURTHER QUESTIONS, CONTACT KHOA LE AT (626) 893-4536 UPDATE 2/21/19: ON 1-11-2019, A SITE INSPECTION WAS CONDUCTED AT THE ADDRESS IN QUESTION. HA NGUYEN FROM CPUC WAS PRESENT. EXPERTS REPRESENTING THE HOME INSURANCE AND SOCALGAS WERE PRESENT. A PRESSURE TEST OF THE HOUSELINE WAS CONDUCTED. DURING THE TEST, A BREACH WAS FOUND NEAR THE WALL FURNACE AT THE HOUSELINE. A CRACK ON A NIPPLE AND ELBOW OF THE HOUSELINE WAS FOUND. EXPERTS REMOVED THAT PART OF THE HOUSELINE AND RETESTED THE REMAINING HOUSELINE. A COUPLE OF OTHER LEAKS WERE FOUND: ONE AT THE METER SET ASSEMBLY AT A UNION FITTING. ANOTHER LEAK WAS FOUND AT A LINE VALVE LOCATED IN THE GARAGE. AFTER THE RETEST OF HOUSELINE TEST, WE DISCUSSED THE NEXT PHASE OF INSPECTING THE MAIN LINE SET FOR 1-18-2019. ON 1-18-2019, ANOTHER SITE INSPECTION WAS CONDUCTED TO EXAMINE THE GAS MAIN PIPE. ESI HOSTED THE SITE INSPECTION IN IRVINE. ALL EXPERTS WERE PRESENT, INCLUDING DURGA SHRESTHA FROM THE CPUC. PHOTOS WERE TAKEN BY ALL PARTIES, INCLUDING DIGITALLY MAGNIFIED IMAGES OF THE PIPE SURFACE. DISCUSSION OF FUTURE TESTING WERE PENDING. ON 2-14-2019, ANOTHER SITE INSPECTION WAS CONDUCTED TO EXAMINE THE HOUSE'S CONCRETE FOUNDATION. ALL EXPERTS WERE PRESENT, INCLUDING HA NGUYEN FROM THE CPUC. ARRANGEMENTS HAVE BEEN MADE TO PERFORM ADDITIONAL TESTING ON THE PIPE ON 3/26/19; CPUC IS AWARE. 06-05-2019 UPDATE: - THE SECTION OF MAIN WAS INSPECTED ON 3/26/2019 AT A 3RD PARTY LABORATORY (VOLLMER GRAY LABORATORIES IN SIGNAL HILLS, CA). SAMPLE WAS VISUALLY INSPECTED, PRESSURE TESTED AND BEND BACK TESTED. THE IDENTIFIED LEAK CAUSE WAS EXCESSIVE STRESS, OTHER THAN PRESSURE (POINT LOAD), IN THE VICINITY OF UNDERGROUND TREE ROOTS. AFTER PERFORMING INVESTIGATIONS, SOCALGAS CONCLUDES THAT THE CAUSE OF THE EXPLOSION IS UNDETERMINED.
2025-03-31 10:13 | NO | YES | NO | 20180124 | 31410 | 2018-12-24 14:08 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2018-11-25 18:17 |  |  | 2018 | 2465 BROADWAY | NEW YORK | NEW YORK | NY | 10025 | 40.792 | -73.9744 | [9 empty] | 2018-11-25 22:26 | 1231251 |  | NATURAL GAS |  | 6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 50 | 2018-11-25 16:44 |  |  |  | 2018-11-25 17:17 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 37 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2015 | [5 empty] | 6 | PE | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | OTHER | ELECTRIC BURNOUT CAUSED LEAK | [5 empty] | CLASS 4 LOCATION | 250000 | 288341.19354253575 | 5000 | 5766.823870850715 | 38400 | 44289.2073281334912 | 500 | 576.6823870850715 | MATERIALS |  | 14 | 14.1323877068557919621749408983451536643 |  | 0 | 293914 | 140405.8993335761546562647754137115839243 | 338988.0395163118834919621749408983451537 | 4 | 0 | 534 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | OSCAR LEON | GAS EMERGENCY RESPONSE CENTER-OPERATIONS MANAGER | leono@coned.com | 718-319-2310 | 718-824-2219 |  |  |  | NICKOLAS HELLEN | GAS EMERGENCY RESPONSE CENTER-DEPARTMENT MANAGER | 718-319-2350 | hellenn@coned.com | ON NOVEMBER 25, 2018, AT 16:44, CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) RECEIVED A REPORT FROM THE FIRE DEPARTMENT OF THE CITY OF NEW YORK (FDNY) OF AN ELECTRICAL FIRE AT 2465 BROADWAY IN MANHATTAN. THE FDNY REPORTED THAT THE FIRE WAS PRODUCING ELEVATED LEVELS OF CARBON MONOXIDE (CO) AND THAT ONSITE FDNY PERSONNEL HAD DETECTED CO IN FRONT OF THE BUILDING, WHICH CONTAINS A LARGE EQUINOX GYM. AT 16:45, CON EDISON'S GERC DISPATCHED A MECHANIC TO THE LOCATION FROM ITS GAS DISTRIBUTION SERVICES (GDS) DEPARTMENT. PRIOR TO THE GDS MECHANIC'S ARRIVAL, THE FDNY EVACUATED AN UNKNOWN NUMBER OF OCCUPANTS FROM BUILDINGS ALONG THE WEST SIDE OF BROADWAY BETWEEN WEST 91ST AND WEST 92ND STREETS DUE TO THE CO CONDITION. THE CON EDISON GDS MECHANIC ARRIVED ON LOCATION AT 17:17 AND BEGAN TO INVESTIGATE. AT 17:34, THE GDS MECHANIC REPORTED A 50% NATURAL GAS READING FIVE FEET FROM THE FOUNDATION WALL OF THE BUILDING AT 2465 BROADWAY. THERE WAS NO ACCESS INTO THE BUILDING AT THAT TIME DUE TO THE CO CONDITION. A MULTIPLE RESOURCE RESPONSE EVENT (CODE MURRE) WAS THEN INITIATED BY CON EDISON DUE TO THE COMBINED INVOLVEMENT OF BOTH ELECTRIC AND GAS. ADDITIONAL CON EDISON GAS EMERGENCY RESPONDERS WERE THEN DISPATCHED TO THE LOCATION. AT 18:17, THE GDS MECHANIC REPORTED THAT AN EXPLOSION OCCURRED INSIDE THE EQUINOX GYM, SHATTERING THE BUILDING'S WINDOWS. THE GERC THEN DISPATCHED ADDITIONAL CON EDISON GAS PERSONNEL TO THE LOCATION TO PROVIDE ASSISTANCE. AT 18:34, ONSITE GDS PERSONNEL REPORTED HAVING NO ACCESS TO THE CURB VALVE ON THE GAS SERVICE LINE SUPPLYING 2465 BROADWAY DUE TO UNSAFE CONDITIONS IN THE SIDEWALK AREA RELATED TO AN APPARENT UNDERGROUND ELECTRIC CABLE BURNOUT. BY 20:39, CON EDISON PERSONNEL CLOSED THREE LOW-PRESSURE MAIN VALVES TO ISOLATE THE AREA, WHICH INTERRUPTED GAS SERVICE TO NINE BUILDINGS AND 538 CUSTOMERS. IN ADDITION, CON EDISON ELECTRIC OPERATIONS PERSONNEL DE-ENERGIZED THE ELECTRIC SUPPLY ON THE WEST SIDE OF BROADWAY BETWEEN WEST 91ST AND WEST 92ND STREETS, AND CONFIRMED THAT AN UNDERGROUND ELECTRIC CABLE BURNOUT HAD OCCURRED IN THE AREA IN FRONT OF 2465 BROADWAY.AT 21:47, CON EDISON PERSONNEL REPORTED, PER THE ONSITE FDNY BATTALION CHIEF,THAT A SUSPECTED NATURAL GAS IGNITION HAD OCCURRED INSIDE OF THE EQUINOX GYM. THE FDNY ALSO REPORTED DETECTING 3.5 PERCENT NATURAL GAS-IN-AIR (70 PERCENT OF THE LOWER EXPLOSIVE LIMIT) INSIDE THE BUILDING'S BASEMENT STAIRCASE PRIOR TO THE EXPLOSION.CON EDISON GDS PERSONNEL THEN GAINED ACCESS TO THE BUILDING AND DETECTED 0.2 PERCENT NATURAL GAS-IN-AIR AT THE FOUNDATION WALL IN THE BASEMENT IN THE VICINITY OF THE GAS METER, WHICH QUICKLY VENTED TO 0 PERCENT.THE GAS PIPING INSIDE THE BASEMENT AT THE GAS METER WAS FOUND INTACT. BY 22:45, THE FDNY TERMINATED ALL EVACUATIONS EXCEPT FOR THE AFFECTED BUILDING AT 2465 BROADWAY. THE AREA IS SUPPLIED BY AN 8-INCH AND 6-INCH LOW-PRESSURE POLYETHYLENE (LPPE) GAS MAIN, WITH A 4-INCH LPPE GAS SERVICE SUPPLYING THE BUILDING AT 2465 BROADWAY.CON EDISON CHECKED ODORANT LEVELS AND DISTRIBUTION SYSTEM PRESSURE SUPPLYING THE AREA AFTER THE INCIDENT AND FOUND BOTH TO BE WITHIN ACCEPTABLE RANGES. ON NOVEMBER 26, 2018, AT 10:56, A BASEBALL-SIZED HOLE WAS FOUND IN THE 6-INCH LPPE GAS MAIN IN FRONT OF 2465 BROADWAY. THE HOLE APPEARED TO HAVE BEEN CREATED BY THE ELECTRIC CABLE BURNOUT THAT HAD OCCURRED IN THAT AREA. THE AFFECTED SECTION OF 6-INCH LPPE GAS MAIN WAS CUT OUT AND CAPPED, AND THE THREE CLOSED MAIN VALVES WERE RE-OPENED, RESTORING GAS SUPPLY IN THE AFFECTED AREA.SUBSEQUENT LEAK SURVEYS CONDUCTED IN THE AREA IDENTIFIED TWO GAS LEAK (A TYPE 1 LEAK IN FRONT OF 256 WEST 92ND STREET AND A TYPE 3 LEAK IN FRONT OF 251 WEST 92ND STREET).CON EDISON PINPOINTED AND REPAIRED BOTH LEAKS. AS A RESULT OF THE EXPLOSION, ONE CON EDISON EMPLOYEE WAS TAKEN TO MT. SINAI MEDICAL CENTER, WHERE HE WAS EVALUATED AND RELEASED. NO OTHER INJURIES WERE REPORTED.MULTIPLE MEDIA OUTLETS AND AGENCIES WERE ON LOCATION.NYSPSC, NYCDEP,AND USDOT WERE NOTIFIED.
2025-03-31 10:13 | NO | YES | NO | 20180125 | 32892 | 2018-12-28 15:37 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2018-11-29 17:55 |  |  | 2018 | BELLE ISLE DOUGLAS MACARTHUR BRIDGE | DETROIT | WAYNE | MI | 48207 | 42.3422 | -82.9988 | [9 empty] | 2018-11-29 18:48 | 1231653 |  | NATURAL GAS |  | 1735 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-11-29 17:55 |  |  |  | 2018-11-29 17:55 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 300 |  | YES | [6 empty] | YES | BORED/DRILLED | DETROIT RIVER | 20 |  | INVESTOR OWNED |  | MAIN |  | 1995 | [5 empty] | 4 | API 5L | LTV | STEEL |  | OTHER | ELECTRICAL RESISTANCE WELDING | 0.237 | [6 empty] | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 529 | 610.129965536005647 | 141785 | 163529.824505713725255 | 131 | 151.090785416288733 | SUPPORTING COSTS |  | 4964 | 5010.940898345153664302600472813238770686 |  | 0 | 147409 | 72679.8373466284186098817966903073286052 | 169301.9861550111732993026004728132387707 | 19 | 0 | 0 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | OTHER | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | ELECTRIC | YES | 8225137802 |  |  | UTILITY OWNER | YES | YES | 40 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | CORRIE TOWNS | SUPERVISOR OF CODES AND STANDARDS | corrie.towns@dteenergy.com | 313-346-2896 |  |  |  |  | CORRIE TOWNS | SUPERVISOR OF CODES AND STANDARDS | 313-346-2896 | corrie.towns@dteenergy.com | DTE GAS' DISPATCH WAS INFORMED OF DTE ELECTRIC CONTRACTOR BORED THRU 4 INCH - 50LB STEEL MAIN (1WAY FEED) HIT IN THE MIDDLE OF THE MAIN ON BELLE ISLE KNOCKING OUT THE GAS FOR THE ENTIRE ISLAND.
2025-03-31 10:13 | NO | YES | NO | 20180127 | 31415 | 2018-12-31 15:07 | ORIGINAL FINAL | 11032 | SPIRE MISSOURI INC. EAST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2018-12-02 21:45 |  |  | 2018 | 39TH STREET AND MAGNOLIA AVENUE | SAINT LOUIS | SAINT LOUIS | MO | 63110 | 38.6078 | -90.2465 | [9 empty] | 2018-12-03 15:05 | 1231941 |  | NATURAL GAS |  | 20657 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-12-02 21:45 |  |  |  | 2018-12-02 22:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 30 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1957 | [5 empty] | 12 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | OTHER | GRAPHITIZATION | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 129246 | 149067.783602394302178 | 500 | 576.6823870850715 | 0 | 0 |  |  | 96166 | 97075.3711583924349881796690307328605201 |  | 0 | 225912 | 151778.6516645162002107423167848699763593 | 246719.8371478718086661796690307328605201 | 0 | 0 | 0 |  |  |  |  | 12 | 12 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT RESULT IN ANY ABNORMAL PIPELINE OPERATION OR PRESSURES THAT CAUSED OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | NO | NONE | [21 empty] | 2018-04-13 | NO | [227 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  |  |  |  | CRAIG HOEFERLIN | VP OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | WHILE PREPARING TO INSTALL A CLAMP TO REPAIR A LEAKING 12-INCH CAST IRON MAIN, A 22-INCH (AXIAL) BY 3-INCH (CIRCUMFERENTIAL) SECTION OF PIPE BROKE OUT FROM THE MAIN. THE SECTION OF FAILED PIPE WAS ISOLATED BY A VALVE AND A CONTROL FITTING TO MAKE THE AREA GAS SAFE. A TEMPORARY GAS FEED WAS INSTALLED TO SUPPLY THE EFFECTED GAS DISTRIBUTION MAIN BEFORE THE PERMANENT REPAIR COULD BE MADE. A 60-FOOT SECTION OF CAST IRON MAIN WAS REPLACED WITH 8-INCH PLASTIC PIPE TO COMPLETE THE REPAIR. THE GAS DISTRIBUTION MAIN WAS RETURNED TO NORMAL SERVICE. AN UPDATE TO THE NRC WAS MADE ON DECEMBER 5, 2018 AT 13:43. REPORT NUMBER 1232102.
2025-03-31 10:13 | NO | NO | NO | 20190001 | 31425 | 2019-01-03 15:19 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-12-04 21:35 |  |  | 2018 | I-20 AND LUMLEY RD. | MESQUITE | DALLAS | TX | 75181 | 32.7022 | -96.5551 | [9 empty] | 2018-12-06 11:01 | 1232169 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-12-04 21:43 |  |  |  | 2018-12-04 22:14 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1998 | [8 empty] | STEEL |  |  |  | 0.218 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 0.2 | 0.2 |  | CLASS 2 LOCATION | 0 | 0 | 50000 | 57668.23870850715 | 40000 | 46134.59096680572 | 0 | 0 |  |  | 40 | 40.37825059101654846335697399527186761229 |  | 0 | 90040 | 43029.3711103650041607565011820330969267 | 103843.2079259038865484633569739952718676 | 1 | 0 | 14 |  |  |  |  | 110 | 110 | 250 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ELIZABETH DELGADO | OPERATIONS MANAGER | elizabeth.delgado@atmosenergy.com | 972-485-6256 | 972-485-6267 |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC NO. 1232365 ON DECEMBER 4, 2018, AT 21:43, EMERGENCY RESPONDERS NOTIFIED ATMOS ENERGY THAT A THIRD PARTY VEHICLE FAILED TO STOP AND DROVE INTO THE ATMOS REGULATOR STATION AT I-20 AND LUMLEY ROAD IN MESQUITE, TX. AT 22:14, ATMOS ENERGY PERSONNEL ARRIVED ONSITE AND FOUND THAT THE VEHICLE HAD DAMAGED THE TEST T FITTING CAUSING A RELEASE OF GAS. IN ADDITION, EXTENSIVE DAMAGE WAS DONE TO THE REGULATOR STATION AND FENCING SURROUNDING THE STATION. THE LEAK WAS ELIMINATED BY TURNING THE REGULATOR STATION OFF. CNG WAS SET UP TO RESTORE SERVICE TO AFFECTED CUSTOMERS, WHICH WAS COMPLETED BY 17:00 ON DECEMBER 5, 2018. REPAIRS WERE COMPLETED AND THE NEW STATION WAS PUT IN SERVICE AT APPROXIMATELY 22:00 ON DECEMBER 12, 2018.
2025-03-31 10:13 | NO | YES | YES | 20190002 | 32825 | 2019-01-03 19:05 | SUPPLEMENTAL FINAL | 18104 | CPS ENERGY | 500 MCCULLOUGH | SAN ANTONIO | TX | 78215 | 2018-12-05 17:45 |  |  | 2018 | 9646 SOUTH BEND | SAN ANTONIO | BEXAR | TX | 78250 | 29.5163 | -98.6869 | [9 empty] | 2018-12-05 20:27 | 1232135 |  | NATURAL GAS |  | 120 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 7 | 2018-12-05 18:02 |  |  |  | 2018-12-05 18:51 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1980 | [5 empty] | 1.315 | ASTM D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3350 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 67500 | 77852.1222564846525 | 0 | 0 | 2000 | 2306.729548340286 | 0 | 0 |  |  | 534 | 539.049645390070921985815602836879432624 |  | 0 | 70034 | 33698.0448276350295460992907801418439716 | 80697.9014502150094219858156028368794326 | 0 | 0 | 1 |  |  |  |  | 9 | 9 | 33 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT |  |  | PIPE | [15 empty] | BUTT, HEAT FUSION |  | 1980 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [6 empty] | YES | [8 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | MICHAEL FUENTES | DIRECTOR GAS OPERATIONS AND CONSTRUCTION | mrfuentes@cpsenergy.com | 2102191309 |  |  |  |  | MICHAEL FUENTES | DIRECTOR OF GAS OPERATIONS AND CONSTRUCTION | 2102191309 | mrfuentes@cpsenergy.com | THE SAN ANTONIO POLICE DEPARTMENT REPORT STATED THAT THERE WERE THREE RESIDENTS AT HOME WHEN AN EXPLOSION OCCURRED IN BETWEEN TWO BATHROOMS NEAR THE MASTER BEDROOM. THE RESIDENTS WERE TRANSPORTED TO THE HOSPITAL FOR OBSERVATION AND ONE RESIDENT WAS ADMITTED FOR FURTHER EVALUATION. CPS ENERGY GAS TROUBLEMAN CONDUCTED AN OUTSIDE LEAK INVESTIGATION AND FOUND GAS READS UNDER THE SLAB, IN THE YARD, INSIDE TWO OTHER HOMES, AND IN THE YARDS OF TWO ADDITIONAL PROPERTIES. CPS ENERGY CREWS FOUND THE PRIMARY CAUSE OF THE GAS MIGRATION TO BE A GAS LEAK ON A CRACKED POLYETHYLENE BUTT FUSE NEAR THE SERVICE TAP ON THE 1" GAS SERVICE SERVING 9646 SOUTH BEND (ADDRESS OF INCIDENT). A SECONDARY GAS LEAK WAS ALSO FOUND AT THE RISER OF A 1" GAS SERVICE SERVING THE HOME NEXT DOOR TO THE INCIDENT (9642 SOUTH BEND). CPS ENERGY LEAK SURVEYED THE SURROUNDING AREA INCLUDING THE 2K GRID MAP THAT IS ON THE LEAK SURVEY CYCLE. CPS ENERGY HAD EXTERNAL TESTING CONDUCTED AND THE CONCLUSION WAS THAT THE PIPE MATERIAL WAS FIT FOR SERVICE SUPPORTING THE PRIMARY CAUSE AS A FUSION CONNECTION FAILURE.
2025-03-31 10:13 | NO | YES | NO | 20190003 | 31515 | 2019-01-04 12:03 | SUPPLEMENTAL FINAL | 31632 | NORTHWESTERN CORPORATION | 3010 W. 69TH ST. | SIOUX FALLS | SD | 57108 | 2018-12-07 16:26 |  |  | 2018 | INTERSECTION OF FARRELL AND TEXAS AVE. | BUTTE | SILVER BOW | MT | 59701 | 46.0052 | -112.5157 | [9 empty] | 2018-12-11 10:32 | 1232639 |  | NATURAL GAS |  | 5853 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-12-07 16:26 |  |  |  | 2018-12-07 16:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 63 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 12 | SCHEDULE 40 | UNKNOWN | STEEL |  | SEAMLESS | SEAMLESS | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 3 | 2 | [7 empty] | CLASS 3 LOCATION | 2400 | 2768.0754580083432 | 45585 | 52576.133230545968655 | 0 | 0 | 0 | 0 | N/A |  | 38796 | 39162.8652482269503546099290780141843972 |  | 0 | 86781 | 59149.8546536683944977304964539007092199 | 94507.0739367812622096099290780141843972 | 0 | 0 | 0 |  |  |  |  | 23 | 50 | 52 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS KNOWN THAT THE CONTROLLER WAS NOT INVOLVED IN THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | [7 empty] | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SITE DEVELOPMENT | NO | [5 empty] | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | DEVIN MCCARTHY | DOT COORDINATOR | devin.mccarthy@northwestern.com | 406-497-3218 |  |  |  |  | DEVIN MCCARTHY | DOT COORDINATOR | 406-497-3218 | devin.mccarthy@northwestern.com | *UPDATE: AFTER FURTHER INSPECTION OF THE AREA WHERE THIS INCIDENT OCCURRED, IT WOULD BE APPROPRIATE TO CORRECT THE CLASS LOCATION FROM 1 TO A CLASS 3. ALSO, WITH FURTHER REVIEW OF THE ROOT CAUSE - NWE HAS CHANGED THE SELECTION TO "ONE CALL NOTIFICATION PRACTICES NOT SUFFICIENT". THE REASON THAT "EXCAVATION PRACTICES NOT SUFFICIENT" WAS ORIGINALLY SELECTED WAS DUE TO, IN ADDITION TO THE ONE CALL CENTER NOT BEING CONTACTED, THE CONTRACTOR WAS NOT TO BE DOING ANY WORK IN ANY CONTEXT AT THE LOCATION WHERE THE INCIDENT OCCURRED. THE WORK BEING DONE WAS COMPLETELY OUT OF THE SCOPE OF THE PROJECT AND NO WORK SHOULD HAVE BEEN BEING DONE WHEN THE LINE WAS HIT. THIS IS A RECLAMATION PROJECTED THAT IS BEING LED BY THE STATE OF MONTANA. ___________________________________________________________________________________________________ *NO CHANGE IN REPORT - SHOULD HAVE BEEN MARKED AS "FINAL" REPORT IN ORIGINAL REPORT - EVENT OCCURRED ON DECEMBER 7, 2018 NORTHWESTERN ENERGY ORIGINAL REPORT WAS MADE TO THE NRC ON DECEMBER 11, 2018. THIS IS THE DATE WHEN CONFIRMED DISCOVERY WAS MADE THAT THE LOSS OF NATURAL GAS EXCEEDED 3 MILLION CUBIC FEET. THE 48 HOUR UPDATE WAS MADE ON DECEMBER 13, 2018. TWO ADDITIONS WERE GIVEN IN THE 48 HOUR UPDATE: THE AMOUNT OF GAS LOST WAS INCORRECTLY REPORTED - CORRECT AMOUNT WAS 5,853 MCF (5,853,000 CUBIC FEET). THE OTHER UPDATE WAS TO INCLUDE THE CONTRACTOR INVOLVED IN THE INCIDENT - M.K. WEEDEN. THE NRC REPORT NUMBER FOR THIS UPDATE IS INCIDENT REPORT # 1232850. NO INJURIES, DEATHS, OR EVACUATIONS OCCURRED WITH THIS INCIDENT. NO LOCATE TICKET WAS SUBMITTED BY THE EXCAVATING PARTY WHEN THIS WORK WAS BEING DONE. 16:26 MST M.K. WEEDEN HIT A 12-INCH STEEL GAS MAIN LOCATED NEAR THE INTERSECTION OF FARRELL AND TEXAS AVE. WITH AN EXCAVATOR. THE LINE WAS AN INTERMEDIATE PRESSURE LINE OPERATING AT 50 PSIG. 16:45 MST NORTHWESTERN WAS NOTIFIED BY THE CONTRACTOR THAT A NWE GAS LINE WAS HIT NEAR THE INTERSECTION OF FARRELL AND TEXAS AVE. EMERGENCY RESPONSE WAS NOTIFIED AND NORTHWESTERN ENERGY PERSONNEL WAS DISPATCH TO EVALUATE THE HIT LINE FROM A SAFE DISTANCE. ADDITIONAL RESOURCES WERE CONTACTED TO ASSIST WITH THE ASSESSMENT OF DAMAGES AND TRAFFIC CONTROL. EMERGENCY RESPONSE PERSONNEL WAS ALSO ONSITE TO ASSIST. 17:00 MST NORTHWESTERN ENERGY WITH OTHER PERSONNEL CREATED A 360 DEGREE ZONE AROUND THE LOCATION OF THE HIT LINE AND WAS MONITORING THE GAS LEVELS TO CREATE A SAFE ZONE. CONTINUOUS AIR MONITORING WAS DONE UNTIL THE FLOW OF GAS WAS SHUT DOWN. 17:10 MST DUE TO THE SIZE OF THE LINE, NORTHWESTERN ENERGY NEEDED FURTHER ASSISTANCE BY OUR GAS TRANSMISSION DEPARTMENT WITH EQUIPMENT AND MATERIALS TO MAKE THE REPAIR. 17:30 MST MORE NWE PERSONNEL ARRIVED ON SITE AND FURTHER EVALUATION WAS CONDUCTED TO FINALIZE THE SAFEST AND BEST WAY TO CORRECT THE SITUATION. 03:45 MST THE FLOW OF GAS WAS SHUT DOWN BY INSERTING STOPPER. WITH FURTHER INVESTIGATION OF THE PIPE ONCE SAFE, IT WAS FOUND THAT THE DAMAGE BY THE EXCAVATOR BUCKET CREATED TWO PUNCTURES HOLES IN THE PIPE. ONE OF THE PUNCTURES WAS MEASURED AT 3 INCHES BY 2 INCHES. THE SECOND MEASURED AT 4 INCHES BY 3 INCHES. 8:15 MST REPAIRS WERE COMPLETED ON DECEMBER 8TH AND PIPE LINE WAS PLACED BACK IN SERVICE.
2025-03-31 10:13 | NO | YES | NO | 20190004 | 31441 | 2019-01-07 15:41 | ORIGINAL FINAL | 11032 | SPIRE MISSOURI INC. EAST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2018-12-08 20:20 |  |  | 2018 | 4978 FYLER AVENUE | SAINT LOUIS | SAINT LOUIS | MO | 63139 | 38.6001 | -90.2739 | [9 empty] | 2018-12-10 16:41 | 1232577 |  | NATURAL GAS |  | 4654 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 8 | 2018-12-08 20:20 |  |  |  | 2018-12-08 20:20 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1949 | [5 empty] | 12 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | OTHER | GRAPHIZIATION | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 500 | 576.6823870850715 | 79889 | 92141.158443678554127 | 0 |  | 21666 | 21870.8794326241134751773049645390070922 |  | 0 | 102055 | 58632.7929105029937257588652482269503546 | 114588.7202633877391021773049645390070922 | 0 | 0 | 18 |  |  |  |  | 12 | 12 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ACTIONS OF THE CONTROLLER DID NOT CAUSE OR CONTRIBUTE TO THE INCIDENT. THE CONTROLLER(S) WERE NOT REQUIRED TO TAKE ANY ACTION TO ASSIST. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | NO | NONE | [21 empty] | 2018-04-19 | NO | [227 empty] | NICOLE CHRISTIANER | MANAGER OF PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  |  |  |  | CRAIG HOEFERLIN | VP OF OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | IN THE PROCESS OF REPAIRING A LEAKING 12-INCH CAST IRON MAIN, A 12-INCH (AXIAL) BY 2-INCH (CIRCUMFERENTIAL) SECTION OF PIPE BROKE OUT FROM THE MAIN. THE SECTION OF FAILED PIPE WAS ISOLATED BY A VALVE AND A CONTROL FITTING TO MAKE THE AREA GAS SAFE. RESIDENTS WHO WERE EVACUATED WERE ALLOWED TO RETURN AND GAS SERVICE WAS RESTORED TO THE CUSTOMERS WHO LOST GAS SERVICE. A 10-FOOT SECTION OF CAST IRON MAIN WAS LATER REPLACED WITH 12-INCH STEEL PIPE TO MAKE THE PERMANENT REPAIR. THE GAS DISTRIBUTION MAIN WAS RETURNED TO NORMAL SERVICE. AN UPDATE TO THE NRC WAS MADE ON DECEMBER 13, 2018 AT 13:13. REPORT NUMBER 1232893.
2025-03-31 10:13 | NO | YES | NO | 20190005 | 32625 | 2019-01-10 14:07 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2018-12-13 13:57 |  |  | 2018 | 100 GENERAL MCINTOSH BLVD. | SAVANNAH | CHATHAM | GA | 31401 | 32.0775 | -81.0802 | [9 empty] | 2018-12-13 15:15 | 1232909 |  | NATURAL GAS |  | 175.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-12-13 14:20 |  |  |  | 2018-12-13 14:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 840 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2007 | [5 empty] | 8 | API 5L | MAVERICK STEEL | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 0.1 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1667000 | 1922659.078541628381 | 5000 | 5766.823870850715 | 376500 | 434241.8374750588395 | CNG COSTS RELATED TO KEEPING CUSTOMERS IN SERVICE. |  | 724 | 730.846335697399527186761229314420803783 |  | 0 | 2049224 | 979222.1939160359013096926713947990543735 | 2363398.5862232353350271867612293144208 | 2 | 0 | 15 |  |  |  |  | 110 | 125 | 125 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | DRILLING | SITE DEVELOPMENT | NO |  |  |  | CONTRACT LOCATOR | NO | YES | 9 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | RICK SLAGLE | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | rslagle@southernco.com | 404-584-4910 |  |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | 404-584-4910 | rslagle@southernco.com | AT APPROXIMATELY 13:57 ON DECEMBER 13, 2018 ATLANTA GAS LIGHT COMPANY (AGLC) RECEIVED TELEPHONIC NOTICE FROM THE SAVANNAH FIRE DEPARTMENT INDICATING THAT DAMAGE HAD OCCURRED TO AGLC NATURAL GAS FACILITIES IN THE AREA OF 100 GENERAL MCINTOSH BLVD IN SAVANNAH, GA. SHORTLY AFTER ARRIVAL TO THE SITE, AGLC CREWS DETERMINED DAMAGE HAD OCCURRED TO A 125 PSIG 8-INCH STEEL MAIN THAT CROSSES THE SAVANNAH RIVER SUPPLYING CUSTOMERS TO HUTCHISON ISLAND. THE DAMAGED WAS FOUND TO OCCUR ON THE WEST LAND SIDE OF THE RIVER. TO STOP THE FLOW OF GAS AT THE DAMAGE, A NEARBY VALVE WAS TURNED OFF WHICH CAUSED A TOTAL OF SEVENTEEN CUSTOMERS TO LOSE NATURAL GAS SERVICE FOR APPROXIMATELY 9 HOURS. THE EXCAVATOR RESPONSIBLE FOR THE DAMAGE WAS DRILLING FOR PILINGS AS PART OF A SITE DEVELOPMENT PROJECT IN THE AREA. THERE WAS NO VALID LOCATE REQUEST AT THE TIME OF EXCAVATION. THE MOST RECENT LOCATE REQUEST FOR THE AREA OF THE DAMAGE BY THE EXCAVATOR WAS RECEIVED BY AGLC ON AUGUST 23, 2018. AS A NORMAL LOCATE REQUEST IN GEORGIA IS VALID FOR THIRTY (30) DAYS, THIS REQUEST WAS VALID UNTIL SEPTEMBER 22, 2018. AS THE PIPELINE IS STILL SHUT DOWN PENDING REPAIR OR REPLACEMENT, CUSTOMERS WHO LOST NATURAL GAS SERVICE DUE TO THE DAMAGE, ARE BEING PROVIDED SERVICE BY A COMPRESSED NATURAL GAS TANKER THAT HAS BEEN PLACED ON THE ISLAND. PIPELINE THAT WAS DAMAGED WAS REPLACED WITH A NEW 8-INCH STEEL PIPELINE. NATURAL GAS WAS RESTORED TO CUSTOMERS ON THE ISLAND ON MAY 15, 2019. DURING THE PIPELINE SHUTDOWN, CUSTOMERS WERE PROVIDED SERVICE BY COMPRESSED NATURAL GAS FACILITIES THAT WERE PLACED ON THE ISLAND. ADDITIONAL NRC REPORT NUMBER 1232992 WAS CREATED FOR THE SAME EVENT AFTER A 48-HOUR SUPPLEMENTAL CALL WAS PLACED WITH THE NRC.
2025-03-31 10:13 | NO | YES | NO | 20190006 | 31470 | 2019-01-10 18:00 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2018-12-10 08:59 |  |  | 2018 | 31010 N FISH LAKE RD | WAUCONDA | LAKE | IL | 60030 | 42.3107 | -88.1451 | [9 empty] | 2018-12-11 13:21 | 1232655 |  | NATURAL GAS |  | 2518 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-12-10 10:07 |  |  |  | 2018-12-10 09:38 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1971 | [5 empty] | 8.625 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.203 | [6 empty] | MECHANICAL PUNCTURE | 1 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 113165 | 130520.524668964232595 | 9828 | 11335.269000544165404 | 0 | 0 |  |  | 9065 | 9150.721040189125295508274231678486997636 |  | 0 | 132058 | 67217.3680098062256554420803782505910165 | 151006.5147096975232945082742316784869976 | 0 | 0 | 0 |  |  |  |  | 148 | 150 | 155 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 2701913 | ILLINOIS ONE CALL - JULIE |  | CONTRACT LOCATOR | NO |  |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | lquezad@southernco.com | 6303882316 |  |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | 6303882316 | lquezad@southernco.com | THIS IS A RURAL LOCATION. UNMARKED 3/4" SERVICE STUB WAS HIT, PULLING THE TEE FROM A MARKED 8" STEEL MAIN. A BYPASS WAS WELDED ON EITHER SIDE OF THE DAMAGED 8" MAIN TO KEEP GAS FLOWING AND NOT INTERRUPT DOWNSTREAM CUSTOMERS. THE DAMAGED SECTION WAS ISOLATED AND REPAIRED AND THE BYPASS WAS THEN REMOVED. NOTE: THE DAMAGED SECTION OF PIPE IS ACTUALLY IN THE CITY OF ROUND LAKE BUT THE CLOSEST METER TO THIS LOCATION IS THE ADDRESS INDICATED IN PART A. THE DAMAGED SECTION IS JUST SOUTH OF THE ADDRESS IN SECTION A.
2025-03-31 10:13 | NO | YES | YES | 20190007 | 32169 | 2019-01-15 14:48 | SUPPLEMENTAL FINAL | 4473 | ATMOS ENERGY CORPORATION - WEST TEXAS | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2018-12-15 16:08 |  |  | 2018 | 3700 PROGRESSIVE ROAD | HEREFORD | DEAF SMITH | TX | 79045 | 34.8286 | -102.3708 | [9 empty] | 2018-12-15 18:17 | 1233114 |  | NATURAL GAS |  | 3708 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO |  |  |  |  | NO | 0 | 2018-12-15 16:10 |  |  |  | 2018-12-15 16:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | BLOWING RELIEF VALVE. | CLASS 3 LOCATION | 3500 | 4036.7767095955005 | 340907 | 393190.125068020939701 | 2000 | 2306.729548340286 | 0 | 0 |  |  | 5600 | 5652.955082742316784869976359338061465721 |  | 0 | 352007 | 170704.16196297695898191016548463356974 | 405186.5864086990429858699763593380614657 | 0 | 0 | 0 |  |  |  |  | 200 | 200 | 240 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | YES | [7 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MIKE CULP | COMPLIANCE MANAGER | mike.culp@atmosenergy.com | 806-798-4440 | 806-798-4495 |  |  |  | MIKE CULP | COMPLIANCE MANAGER | 806-798-4440 | mike.culp@atmosenergy.com | ON DECEMBER 15, 2018 AT APPROXIMATELY 16:10, ATMOS RECEIVED A CALL FROM FIRE OFFICIALS STATING THAT A TRUCK HAD HIT A METER STATION AND THAT GAS WAS BLOWING. THE TRUCK HAD BEEN TRAVELING AT A HIGH RATE OF SPEED IN REVERSE AND WENT THROUGH A FENCE AND BUILDING BEFORE BECOMING LODGED ON TOP THE HEREFORD CITY GATE STATION. AN ATMOS EMPLOYEE ARRIVED ON THE SCENE AT 16:25. VALVES WERE OPERATED TO ISOLATE AND STOP FLOW OF GAS AT THE CITY GATE STATION. EMERGENCY OFFICIALS WERE THEN ABLE TO REMOVE AND TRANSPORT THE DRIVER TO THE HOSPITAL. DAMAGE ESTIMATES AND GAS LOSS CALCULATIONS ARE PENDING. FINAL REPAIRS TO THE AFFECTED GAS FACILITY ARE NOT COMPLETE. UPDATES TO THIS REPORT WILL BE COMPLETED ONCE REPAIRS ARE FINAL. 1ST NRC CALL ON 12-15-2018, #1233114. 2ND NRC CALL ON 12-17-2018, #1233290. INJURED INDIVIDUAL WAS HOSPITALIZED OVERNIGHT. NO FURTHER UPDATES HAVE BEEN PROVIDED. AS OF 3-7-2019 NO INFORMATION ON INDIVIDUAL INVOLVED IN THIS INCIDENT DRIVING THE TRUCK THAT HIT THE ATMOS ENERGY TOWN BORDER STATION HAS BEEN RECEIVED BY ATMOS. UPDATES WERE MADE TO PART - A REGARDING TOTAL MCF'S LOST, PART D REGARDING SUBPART #2 DAMAGES/REPAIR COSTS BOTH PRIVATE AND ATMOS ENERGY PROPERTIES AND YEAR/DATE CORRECTION TO PART -H. THE HEREFORD CITY GATE INVOLVED WITH THIS INCIDENT HAS BE COMPLETELY REBUILT AND WAS PUT BACK INTO FULL FLOW PRODUCTION ON 5-17-2019. PLEASE BE ADVISED THAT THIS IS THE FINAL SUPPLEMENTAL REPORT, PER MIKE CULP UPDATED ON 5-22-2019 INTO PHMSHA WEBSITE.
2025-03-31 10:13 | NO | NO | NO | 20190008 | 34900 | 2019-01-18 11:36 | SUPPLEMENTAL FINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2018-12-21 05:30 | EASTERN | NO | 2018 | 3377 CRUMPTON S | LAUREL | ANNE ARUNDEL | MD | 20724 | 39.0972 | -76.8183 |  |  |  | YES | [5 empty] | 2018-12-21 08:01 | 1233636 |  | NATURAL GAS |  | 2.36 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2018-12-21 05:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 2.36 | YES | 12 | 2018-12-21 07:20 |  |  |  | 2018-12-21 06:59 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1978 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.375 | D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 9.33 |  |  | 3406 | OTHER | [8 empty] | UNDETERMINED SOURCE | CLASS 3 LOCATION | 0 | 0 | 9024 | 10407.963722111370432 | 7023 | 8100.080808996914289 | 0 | 0 |  | 4.22 | 10 | 10.09456264775413711583924349881796690307 | 0 | 0 | 16057 | 7674.815025006449036189125295508274231678 | 18518.1390937560388581158392434988179669 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 90 | 90 | 99 | 192.619(A)(2) | 1978-05-11 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ABSENCE OF ANY EFFECT ( INDICATIONS OF ) ON SYSTEM PRESSURES /OPERATIONS. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | INVESTIGATORS WERE UNABLE TO DETERMINE THE SOURCE OF THE GAS LEAK OR THE SOURCE OF IGNITION DUE TO THE EXTENSIVE DAMAGE IN THE HOME FROM THE FIRE AND THE RESULTANT WATER DAMAGE FROM FIREFIGHTING ACTIVITIES. | [45 empty] | ROBERT REX | MANAGER - GAS ENGINEERING AND STANDARDS | robert.rex@delmarva.com | 410-470-6933 | 410-470-9549 |  |  |  | DANIEL A. NORDEN | MANAGER - GAS ENGINEERING AND ASSET PERFORMANCE | 410-470-6435 | daniel.a.norden@bge.com | ON DECEMBER 21, 2018, THE FIRE DEPARTMENT CONTACTED BGE AT 06:28 TO REQUEST ASSISTANCE DUE TO A FIRE AT THE DWELLING OF 3377 CRUMPTON S IN LAUREL, MD. A BGE GAS MECHANIC WAS IMMEDIATELY DISPATCHED TO THE PREMISE. HE ARRIVED AT 6:59AM, 31 MINUTES AFTER THE INITIAL CALL. THE DWELLING WAS ON FIRE, ENGULFED IN FLAMES, AND THE MECHANIC WAS UNABLE TO GET INTO THE PREMISE. HE BEGAN CANVASSING THE AREA FOR GAS LEAKS AND NEIGHBORING OCCUPANTS. THE GAS MECHANIC FOUND AN ODOR AT 3379 CRUMPTON S. THE PREMISES WAS EVACUATED WITH NO KNOWN INJURIES AT THE TIME. A GAS CONSTRUCTION MAINTENANCE AND REPAIR CREW WAS DISPATCHED TO THE SCENE AND TURNED OFF THE GAS AT THE RISER FOR BOTH DWELLINGS. THE FIRE DEPARTMENT WAS ON SITE WITH THE INCIDENT COMMAND EN ROUTE AT THE TIME. INVESTIGATORS WERE UNABLE TO DETERMINE THE SOURCE OF THE GAS LEAK OR THE SOURCE OF IGNITION DUE TO THE EXTENSIVE DAMAGE IN THE HOME FROM THE FIRE AND THE RESULTANT WATER DAMAGE FROM FIREFIGHTING ACTIVITIES.
2025-03-31 10:13 | NO | NO | NO | 20190009 | 31519 | 2019-01-21 11:54 | ORIGINAL FINAL | 32013 | AMERIGAS PROPANE LP | 500 N. GULPH RD. | KING OF PRUSSIA | PA | 19406 | 2018-12-20 09:13 |  |  | 2018 | 9412 WHEELER CT. | PLYMOUTH | AMADOR | CA | 95669 | 38.4813 | -120.8497 | [9 empty] | 2018-12-20 10:43 | 1233682 |  | PROPANE GAS |  | 387 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2018-12-20 09:44 |  |  |  | 2018-12-20 10:20 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 0.75 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2513 | MECHANICAL PUNCTURE | 4 | 0.5 | [7 empty] | CLASS 1 LOCATION | 2500 | 2883.4119354253575 | 150 | 173.00471612552145 | 325 | 374.843551605296475 | 0 | 0 |  |  | 13 | 13.122931442080378250591016548463356974 |  | 0 | 2988 | 1433.264547926479652245862884160756501182 | 3444.383134598255803250591016548463356974 | 0 | 0 | 80 |  |  |  |  | 10 | 10 | 10 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | TRENCHER | TELECOMMUNICATIONS | YES | 834600452 | USA NORTH |  | UTILITY OWNER | NO | YES | 4 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | DAVID HEDRICK | PIPELINE MANAGER | david.hedrick@amerigas.com | 2159704159 | 8663845120 |  |  |  | DAVID HEDRICK | PIPELINE MANAGER | 2159704159 | david.hedrick@amerigas.com | EXCAVATION CONTRACTOR REPORTED THE INTENT TO EXCAVATE THROUGH THE STATE ONE CALL REPORTING SYSTEM. AMERIGAS MANAGER INFORMED THE EXCAVATION CONTRACTOR THAT AMERIGAS UTILITIES WERE IN THE AREA OF THE PROPOSED EXCAVATION BUT EXACT MARKING OF THE UTILITY WAS NOT POSSIBLE DUE TO LACK OF TRACER WIRE. AMERIGAS MANAGER ALSO STATED AN UNDERSTANDING, BASED ON PRIOR EXPERIENCE THAT CONTRACTOR'S EXCAVATORS DID NOT GO VERY DEEP AND ALERTED CONTRACTOR THAT LINES SHOULD BE BURIED APPROXIMATELY 12". NO FURTHER COMMUNICATION WAS RECEIVED FROM EXCAVATION CONTRACTOR FOLLOWING REPORT OF UTILITY PRESENCE. EXCAVATING CONTRACTOR APPEARS TO HAVE BEEN OPERATING A TRENCHER AT A DEPTH OF APPROXIMATELY 12+ " IN THE AREA AND WITHIN INCHES OF MARKED UTILITIES. TRENCHER CHAIN APPEARS TO HAVE STRUCK THE FAR SIDE OF THE AMERIGAS PLASTIC PIPELINE AND PULLED IT UPWARD TEARING THE PIPE. EXCAVATING CONTRACTOR WAS BURNED AND GROUND TRANSPORTED TO LOCAL HOSPITAL WHERE HE WAS TREATED AND RELEASED. NOTIFICATION TO THE NATIONAL RESPONSE CENTER WAS NOT REQUIRED SINCE THERE WAS NO IN-PATIENT HOSPITALIZATION.
2025-03-31 10:13 | NO | YES | NO | 20190010 | 31966 | 2019-01-30 13:03 | SUPPLEMENTAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2019-01-07 18:00 |  |  | 2019 | SWANNANOA RIVER RD & FAIRVIEW RD. | ASHEVILLE | BUNCOMBE | NC | 28806 | 35.5748 | -82.5025 | [9 empty] | 2019-01-07 20:28 | 1234779 |  | NATURAL GAS |  | 504 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-01-07 18:00 |  |  |  | 2019-01-07 18:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | YES |  |  |  |  | YES | CASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1959 | [5 empty] | 4 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 0.4 | 0.4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 132444 | 149834.565252201737232 | 7200 | 8145.3963170536416 | 0 | 0 |  |  | 2175 | 2437.598425196850393700787401574803149606 |  | 0 | 141819 | 67685.4833094822706730393700787401574803 | 160417.5599944522292257007874015748031496 | 0 | 0 | 0 |  |  |  |  | 350 | 350 | 375 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK AMOUNT WAS TOO SMALL TO SHOW UP AND OR TRIGGER ANY ALARMS. | [12 empty] | YES | 1 | 0 | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | MARK HANNAH | OPERATIONS MANAGER | rhannah@scana.com | 828-670-3567 |  |  |  |  | SCOTT SWINDLER | GENERAL MANAGER-OPERATIONS | 704-810-3230 | mswindler@scana.com | UPDATE TO FINAL REPORT: REVISED PART A, 5.5F LAT. AND LONG. VALUES TO REFLECT A MORE ACCURATE LOCATION OF INCIDENT. REVISED PART C, 5 TO REFLECT OF HOLE SIZE OF 0.4 INCH INSTEAD OF 375.00 INCHES. THE ACTUAL SIZE WAS 0.375 INCH BUT SYSTEM ONLY ALLOWS ONE DECIMAL PLACE. UPDATED COST INFORMATION IN PART D. REPLACED SYMBOLS IN NARRATIVE THAT CAUSE PRINT ERRORS. ADDITIONAL ACTIONS: PROVIDED HUMAN FACTORS INVESTIGATION REPORT TO NCUC ON 2/22/2019 VIA EMAIL. PROVIDED FOLLOW-UP TRAINING DOCUMENTATION TO NCUC ON 2/22/2019 VIA EMAIL. PROVIDED OPERATOR QUALIFICATION AND PROCEDURE INFORMATION TO NCUC ON 2/22/2019 VIA EMAIL. ORIGINAL PROJECT PLAN ON 1/7/19, A PSNC ENERGY CONTRACTOR WAS RETIRING A 350 PSIG 4 IN. LATERAL (M-320) OFF ON OUR 8 IN. TRANSMISSION LINE (T-04) IN ASHEVILLE. THE SPECIFIC LOCATION OF THE WORK WAS NEAR THE INTERSECTION OF SWANNANOA RIVER AND FAIRVIEW ROADS. THIS WORK WAS THE FINAL STEP TO RETIRING A BRIDGE ATTACHMENT ON FAIRVIEW ROAD. THIS PROJECT INCLUDED REROUTING SOME SECTIONS AND DE-RATING PART OF THE 350 PSIG SYSTEM TO A STANDARD DISTRIBUTION SYSTEM PRESSURE OF 60 PSIG. THIS SECTION OF M-320 USED TO FEED SOME REGULATOR STATIONS THAT ARE NOW RETIRED. THE ORIGINAL PROJECT PLAN WAS TO EXCAVATE AND RETIRE THE 4 IN. LATERAL SECTION USING A 4 IN. TD WILLIAMSON (TDW) STOP-OFF FITTING AND REPAVE THIS AREA BY 11 PM THAT NIGHT. SUMMARY OF WHAT HAPPENED WHEN THE PIPE WAS EXPOSED AT ABOUT 11:00 AM IT WAS DISCOVERED THE PIPE WAS 6 IN. SO 6 IN. FITTINGS OF IDENTICAL PRESSURE SPECIFICATIONS WERE ROUNDED UP. A TDW THREAD-O-RING (TOR WHICH IS BASICALLY A 2IN. FITTING USED IN THE TAPPING OPERATION) AND THE 6 IN. STOP-OFF FITTING WERE WELDED ON THE PIPE. THE TOR WAS TAPPED AT ABOUT 6 PM BY OUR TAPPING CONTRACTOR, WHEN IT WAS DISCOVERED THAT THE 6 IN. PIPE WAS ACTUALLY CASING PIPE OVER THE 4 IN. PIPE. THE PILOT BIT PENETRATED THE 4 IN. LINE CREATING A 3/8 IN. HOLE THAT SENT GAS IN BOTH DIRECTIONS DOWN THE CASING. THE TAPPING CONTRACTOR TECHNICIAN AND THE PIPELINE CONTRACTOR SUPPORT PERSONNEL EVACUATED THE HOLE. PSNC ENERGY HAD AN INSPECTOR ON SITE AND ADDITIONAL PSNC ENERGY PERSONNEL WERE BROUGHT IN TO MONITOR BOTH ENDS OF THE CASINGS FOR GAS MIGRATION. GASEOUS ATMOSPHERE WAS ABOUT 25-30 FT. RADIUS FROM THE BELL HOLE CONTAINING THE TOR. THE PROJECT DESIGN SPECIFIED THE REMAINING LATERAL STUB TO BE AS SHORT AS POSSIBLE SO THERE WAS NO ROOM TO INSTALL ANOTHER STOP-OFF FITTING. THIS MADE THE REPAIR/SHUT-OFF PLAN MORE COMPLEX. THE SECTION OF TRANSMISSION LINE CONTAINING THE LATERAL CONNECTION WAS GOING TO HAVE TO BE ISOLATED TO STOP THE LEAK. THIS IS A SINGLE FEED SYSTEM SO A BYPASS WAS REQUIRED. PSNC ENERGY WAS ABLE TO ROUND UP TWO TDW 3-WAY TEES (WHICH ARE DESIGNED TO FACILITATE BOTH STOP-OFF AND BYPASS) FROM ANOTHER JOB. TRANSMISSION CONTRACT CREWS WERE BROUGHT IN TO WELD ON THE FITTINGS AND TO WELD UP AND INSTALL A 120 FT. 8 IN. BYPASS. TWO REMOTE BELL HOLES WERE DUG TO INSTALL THE FITTINGS ON T-04. THE SHUTDOWN PROCESS OF INSTALLING FITTINGS AND BYPASS, TESTING AND PURGING THE BYPASS, STOPPING OFF THE DAMAGED SECTION, AND TRANSFERRING THE FLOW TO THE BYPASS LASTED FROM APPROXIMATELY 8:00 PM ON 1/7/19 UNTIL 11:10 AM ON 1/8/19. REPLACING THE DAMAGED LATERAL CONTAINING THE SECTION OF T-04 WITH PRE-TESTED PIPE AND PLACING THE PIPELINE BACK IN SERVICE TOOK UNTIL 11:10 AM ON 1/8/19. BACKFILLING AND ROAD REPAIR LASTED THROUGH THE EVENING. OTHER INFORMATION OF NOTE THE EMERGENCY RESPONSE AND REPAIR PROCESSES REQUIRED THE SHUT-DOWN OF SWANNANOA RIVER ROADS. THE ENTIRE STOPPAGE OF THE LEAK AND REPAIR WERE WORKED OUTSIDE OF THE HAZARDOUS GASEOUS ENVIRONMENT. PSNC WORKED WITH LOCAL NEWS TO PUT OUT TRAFFIC ADVISORIES. PSNC ENERGY'S IN HOUSE INSPECTOR WAS DRUG TESTED SINCE HIS ACTIONS CONTRIBUTED TO THE INCIDENT. THE NCUC HAD PIPELINE SAFETY OFFICERS ON THE SCENE. SCANA GAS SERVICES FACILITATED A HUMAN FACTOR INVESTIGATION OF THE INCIDENT. THE HFI REPORT IS INCOMPLETE AS OF 1/29/19.
2025-03-31 10:13 | NO | NO | NO | 20190011 | 32322 | 2019-01-31 17:21 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2019-01-06 10:55 |  |  | 2019 | 25807 SE 157ND ST | ISSAQUAH | KING | WA | 98027 | 47.4656 | -121.9962 | [9 empty] | 2019-01-22 16:21 | 1235803 |  | NATURAL GAS |  | 461.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-01-06 09:38 |  |  |  | 2019-01-06 10:55 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1990 | [5 empty] | 2 | MPE | PLEXCO YELLOW STRIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | PINHOLE | [6 empty] | CLASS 4 LOCATION | 0 | 0 | 58000 | 65615.692554043224 | 4000 | 4525.220176140912 | 0 | 0 |  |  | 4079 | 4571.477690288713910761154855643044619423 |  | 0 | 66079 | 33279.1469466036695380577427821522309711 | 74712.3904204728499107611548556430446194 | 0 | 0 | 3 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | LEE MAXWELL | SR REGULATORY ANALYST | lee.maxwell@pse.com | 4254623575 |  |  |  |  | CHERYL MCGRATH | MANAGER COMPLIANCE PROGRAMS | 425-462-3207 | cheryl.mcgrath@pse.com | ON JANUARY 6, 2019 AT 9:38 PUGET SOUND ENERGY RESPONDED TO A GAS ODOR CALL AT 25807 SE 152ND ST IN ISSAQUAH. UPON ARRIVAL, THE PSE GAS FIRST RESPONDER IDENTIFIED AN UNDERGROUND LEAK ON A 2" PE DISTRIBUTION MAIN THAT WAS CAUSED BY AN ELECTRICAL GROUND FAULT FROM A DOWNED POWER LINE ARCING ON THE PE MAIN TRACER WIRE.. THE DOWNED POWER LINE WAS CAUSED BY A HEAVY WINDSTORM. PSE ORGANIZED A SPECIAL LEAK SURVEY OF THE SURROUNDING AREA AND FOUND A SECOND LEAK 150' EAST OF THE FIRST LEAK. PSE CONTROLLED THE SITUATION BY THE USE OF SQUEEZERS AT 19:44 ON JANUARY 6, 2019 RESULTING IN THE LOSS OF 3 CUSTOMERS. A FINAL REPAIR WAS MADE ON JANUARY 7, 2019 AT 18:00 BY REPLACING 290' OF THE 2" PE MAIN. THE MAIN REPLACEMENT COST AND RESPONSE WAS ESTIMATED AT $62,000 EXCEEDING THE FEDERAL $50,000 REPORTING THRESHOLD.
2025-03-31 10:13 | NO | YES | NO | 20190012 | 31600 | 2019-02-01 18:29 | ORIGINAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2019-01-04 14:25 |  |  | 2019 | NORTHERN BOULEVARD BET 112 PLACE AND 114 STREET | NEW YORK | QUEENS | NY | 11368 | 40.7584 | -73.8568 | [9 empty] | 2019-01-07 11:42 | 1234875 |  | NATURAL GAS |  | 10765 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-01-04 14:15 |  |  |  | 2019-01-04 14:22 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1936 | [5 empty] | 24 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | 24" HIGH PRESSURE STEEL MAIN DAMAGED BY A STREET COLLAPSE CAUSING A BLOWING GAS CONDITION. | CLASS 4 LOCATION | 0 | 0 | 900000 | 1018174.5396317052 | 12800 | 14480.7045636509184 | 0 | 0 |  |  | 44352 | 49706.8346456692913385826771653543307087 |  | 0 | 957152 | 473676.5637041569325291338582677165354331 | 1082362.07884102540973858267716535433071 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 80 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 24" HIGH PRESSURE STEEL MAIN DAMAGED BY A STREET COLLAPSE CAUSING A BLOWING GAS CONDITION. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | 24" HIGH PRESSURE STEEL MAIN DAMAGED BY A STREET COLLAPSE CAUSING A BLOWING GAS CONDITION. | [154 empty] | OSCAR LEON | OPERATIONS MANAGER - GAS EMERGENCY RESPOSNE CENTER | leono@coned.com | 718-319-2310 | 718-824-2219 |  |  |  | NICKOLAS HELLEN | DEPARTMENT MANAGER - GAS EMERGENCY RESPOSNE CENTER | 718-319-2351 | hellenn@coned.com | ON JANUARY 4, 2019, AT 14:15, THE FIRE DEPARTMENT OF THE CITY OF NEW YORK (FDNY) CALLED CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) AND REPORTED THAT THEY WERE RESPONDING TO A POSSIBLE GAS EXPLOSION IN THE STREET IN THE AREA OF NORTHERN BOULEVARD BETWEEN 112TH PLACE AND 114TH STREET IN QUEENS. CON EDISON'S GERC IMMEDIATELY DISPATCHED MULTIPLE PERSONNEL INCLUDING SUPERVISORS FROM ITS GAS DISTRIBUTION SERVICES (GDS) AND GAS EMERGENCY RESPONSE FORCE (ERF)/CONSTRUCTION DEPARTMENTS TO THE LOCATION. AT 14:16, CON EDISON'S GAS CONTROL GROUP REPORTED RECEIVING A LOW-PRESSURE ALARM AT GAS REGULATOR STATION GR-254, WHICH SUPPLIES THE SAME AREA. CON EDISON GDS PERSONNEL ARRIVED ON LOCATION AT 14:22 AND BEGAN INVESTIGATING. FDNY WAS ALREADY ON LOCATION AT THAT TIME. AT 14:25, ON-SITE GDS PERSONNEL REPORTED A STREET COLLAPSE IMMEDIATELY ADJACENT TO AN ACTIVE CONSTRUCTION SITE, AND THAT THE COLLAPSE HAD COMPROMISED A 24-INCH HIGH-PRESSURE STEEL GAS SUPPLY MAIN (INSTALLED IN 1936), CREATING A BLOWING GAS CONDITION WITH NO IGNITION. CON EDISON'S GERC THEN INITIATED A MULTIPLE RESOURCE RESPONSE EVENT (CODE MURRE) AND DISPATCHED ADDITIONAL PERSONNEL TO THE LOCATION FROM SEVERAL DEPARTMENTS, INCLUDING GDS, LEAK SURVEY, AND ITS GAS EMERGENCY RESPONSE GROUP (ERG). AT 14:26, CON EDISON'S GERC IDENTIFIED TWO HIGH-PRESSURE MAIN VALVES (46441 & 15123) FOR ISOLATING THE COMPROMISED 24-INCH STEEL SUPPLY MAIN. AT 14:50, GDS CLOSED MAIN VALVE 46441 BUT WAS UNABLE TO CLOSE MAIN VALVE 15123, WHICH WAS REPORTEDLY INOPERABLE. CON EDISON'S GERC THEN IDENTIFIED A BACK-UP HIGH-PRESSURE MAIN VALVE (21738), WHICH WAS CLOSED BY ON-SITE GDS PERSONNEL AT 15:42, THEREBY ISOLATING THE AFFECTED SUPPLY MAIN AND ELIMINATING THE BLOWING GAS CONDITION. THE INCIDENT RESULTED IN NO SYSTEM IMPACT OR GAS SERVICE INTERRUPTIONS. CON EDISON RECEIVED A TOTAL OF ONE-HUNDRED FIFTY-SIX (156) RELATED GAS ODOR COMPLAINTS. CON EDISON INVESTIGATED EACH COMPLAINT AND DETERMINED THEM ALL TO BE ASSOCIATED WITH THE INCIDENT. AT THE TIME OF THE INCIDENT, CON EDISON'S INITIAL CALCULATION DETERMINED THAT THE RUPTURED GAS MAIN HAD RELEASED LESS THAN THREE MILLION CUBIC FEET OF NATURAL GAS. SUBSEQUENTLY, ON JANUARY 7, 2019, BASED ON ADDITIONAL ANALYSIS, CON EDISON'S GAS ENGINEERING SYSTEM PLANNING GROUP DETERMINED THAT GREATER THAN TEN MILLION CUBIC FEET OF NATURAL GAS WAS LOST DURING THE INCIDENT (CON EDISON'S GAS ENGINEERING SYSTEM PLANNING GROUP CALCULATED THE TOTAL ESTIMATED VOLUME OF GAS RELEASED WAS 10,765 MSCF). CON EDISON NOTIFIED THE DEPARTMENT OF PUBLIC SERVICE STAFF (DPS STAFF), NEW YORK CITY DEPARTMENT OF ENVIRONMENTAL PROTECTION (NYCDEP), AND THE U.S. DEPARTMENT OF TRANSPORTATION (USDOT). MULTIPLE MEDIA OUTLETS WERE ON LOCATION DURING THE INCIDENT. MULTIPLE AGENCIES WERE ALSO ON LOCATION, INCLUDING FDNY, NEW YORK POLICE DEPARTMENT (NYPD), NEW YORK CITY DEPARTMENT OF TRANSPORTATION (NYCDOT), NEW YORK CITY EMERGENCY MANAGEMENT (NYCEM), AND DPS STAFF. THE AFFECTED SUPPLY MAIN WAS REPLACED AND RETURNED TO SERVICE BY CON EDISON ON JANUARY 19, 2019.
2025-03-31 10:13 | NO | NO | NO | 20190013 | 32786 | 2019-02-04 18:08 | SUPPLEMENTAL FINAL | 31636 | NORTHERN STATES POWER CO OF MINNESOTA | 414 NICOLLET MALL | MINNEAPOLIS | MN | 55402 | 2019-01-04 18:42 |  |  | 2019 | 5220 12TH ST S | FARGO | CASS | ND | 58104 | 46.8018 | -96.8014 | [9 empty] | 2019-01-08 14:25 | 1234842 |  | NATURAL GAS |  | 7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 40 | 2019-01-04 19:04 |  |  |  | 2019-01-04 19:04 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2001 | [8 empty] | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 50000 | 56565.2522017614 | 0 | 0 | 4152 | 4697.178542834266656 | 0 | 0 |  |  | 39 | 43.70866141732283464566929133858267716535 |  | 0 | 54191 | 25413.4945422654986362834645669291338583 | 61306.1394060129894906456692913385826772 | 1 | 0 | 0 |  |  |  |  | 51 | 51 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELEASE OCCURRED ON A METER SET AND AFTER REVIEWING DATA, THE RELEASE WAS NOT SIGNIFICANT ENOUGH TO CAUSE AN ALARM IN SCADA. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | LAB INSPECTION OF THE BROKEN REGULATOR WAS PERFORMED AND REVEALED NO EVIDENCE THAT THE BREAK WAS CAUSED BY CORROSION OVER TIME OR FROM A MATERIAL DEFECT. WE BELIEVE THE BREAK WAS CAUSED BY AN EXTERNAL FORCE, BUT CANNOT DETERMINE WHAT THE FORCE WAS OR WHAT OCCURRED. MEASUREMENTS SHOW THAT THE ROOF OVERHANG EXTENDED OUT BEYOND THE METER SET AND THEREFORE IT APPEARS THE METER SET WAS COVERED. | [154 empty] | ELISABETH KALLBERG | PRINCIPAL CONSULTANT GAS STANDARDS | elisabeth.m.kallberg@xcelenergy.com | 651-229-2282 |  |  |  |  | CHRISTOPHER AKINS | MANAGER GAS STANDARDS | 303-571-3298 | christopher.a.akins@xcelenergy.com | ON JANUARY 4, 2019, AT 18:43 XCEL ENERGY WAS NOTIFIED BY THE FARGO FIRE DEPARTMENT OF A FIRE AT 5220 12TH ST. S IN FARGO, ND, AT THE CHI COMMUNITY LIVING CENTER. VISUAL OBSERVATION AFTER THE FIRE SHOWED THAT THE REGULATOR BODY HAD BEEN CRACKED AND WAS BROKEN THROUGH COMPLETELY, RESULTING IN ESCAPING GAS. THE ESCAPING GAS APPEARS TO HAVE MIGRATED INTO AN INTERIOR UTILITY ROOM THROUGH A VENT; THE UTILITY ROOM WAS LOCATED DIRECTLY BEHIND THE METER. WE BELIEVE THE GAS IGNITED INSIDE THE UTILITY ROOM BASED ON EVIDENCE AT THE SCENE AND VIDEO FOOTAGE PRESERVED BY THE CHI COMMUNITY LIVING CENTER. WE ARE UNABLE TO DETERMINE WHAT CAUSED THE REGULATOR TO BREAK. POST-INCIDENT INSPECTION OF THE REGULATOR SUGGESTS THAT THE REGULATOR DID NOT BREAK DUE TO CORROSION OR MATERIAL DEFECT, WE BELIEVE IT WAS AN EXTERNAL FORCE BUT CANNOT DETERMINE WHAT THE FORCE WAS OR WHAT OCCURRED. ESTIMATED COSTS OF THE FIRE DAMAGE APPEAR TO EXCEED $50,000, BUT ARE NOT KNOWN AT THIS TIME.
2025-03-31 10:13 | NO | YES | NO | 20190014 | 31917 | 2019-02-07 15:47 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2018-10-30 09:57 |  |  | 2018 | 19366 WALTZ | NEW BOSTON | WAYNE | MI | 48164 | 42.1617 | -83.4031 | [9 empty] | 2019-01-04 14:19 | 1234563 |  | NATURAL GAS |  | 2431 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-10-30 09:57 |  |  |  | 2018-10-30 10:05 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | YES | [6 empty] | YES | BORED/DRILLED | HURON RIVER | UNKNOWN |  | PRIVATELY OWNED |  | MAIN |  | 1996 | [5 empty] | 6 | ASTM D2523 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 4.5 | 5.4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 150000 | 173004.71612552145 | 15000 | 17300.471612552145 | 0 | 0 |  |  | 6954 | 7019.758865248226950354609929078014184397 |  | 0 | 171954 | 85312.3891948496313475177304964539007092 | 197324.9466033218219503546099290780141844 | 0 | 0 | 0 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | OTHER | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | WATERWAY IMPROVEMENTS | YES | 82150258 |  |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | FRENAE SMITH | MANAGER CODES AND STANDARDS | frenae.smith@dteenergy.com | 313-389-7762 |  |  |  |  | FRENAE SMITH | MANAGER CODES AND STANDARDS | 313-389-7762 | frenae.smith@dteenergy.com | DTE GAS WAS NOTIFIED AT 9:57AM ON 10/30/18 OF A 3RD PARTY DAMAGE AT 19366 WALTZ IN NEW BOSTON, MICHIGAN. DTE GAS CREW ARRIVED ON-SITE AT 10:05AM. THE 3RD PARTY DAMAGE WAS TO A 6-INCH PLASTIC MAIN OPERATING AT 45 PSIG IN THE HURON RIVER. THE MPSC WAS NOTIFIED ON 10/30/18 OF THE INCIDENT.THE MAIN WAS TEMPORARILY REPAIRED ON 10/30/18 UNTIL THE PERMANENT REPAIR CAN BE MADE. IT WAS LATER DETERMINED THAT THE INCIDENT WAS GOING TO BE REPORTABLE TO THE NRC AND NOTIFICATIONS WAS MADE ON 1/4/19.
2025-03-31 10:13 | NO | NO | NO | 20190016 | 31690 | 2019-02-22 15:26 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2019-01-23 18:00 |  |  | 2019 | CR 4235 & CR 4270 | RHINELAND | KNOX | TX | 76371 | 33.4983 | -99.6875 | [9 empty] | 2019-01-24 10:37 | 1235920 |  | NATURAL GAS |  | 5160 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-01-23 18:00 |  |  |  | 2019-01-23 19:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1930 | [5 empty] | 8 | API 5L | UNKNOWN | STEEL |  | LAP WELDED | LAP WELD | 0.216 | [6 empty] | MECHANICAL PUNCTURE | 4 | 2 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 11740 | 13281.52121697357672 | 2000 | 2262.610088070456 | 0 | 0 |  |  | 24268 | 27197.9947506561679790026246719160104987 |  | 0 | 38008 | 31597.6505298727209301312335958005249344 | 42742.1260557002006990026246719160104987 | 0 | 0 | 0 |  |  |  |  | 235 | 235 | 260 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  |  |  | YES | [9 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [7 empty] | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | LARRY MORENO | OPERATIONS SUPERVISOR | larry.moreno@atmosenergy.com | 325-773-3058 | 325-773-5710 |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC REPORT NUMBER 1236052 AT 18:00 ON 1/23/2019, ATMOS ENERGY WAS NOTIFIED BY GAS CONTROL THAT PRESSURE HAD DROPPED ON LINE U NEAR RHINELAND, TEXAS. ATMOS ENERGY CREWS ARRIVED AT APPROXIMATELY 19:00 AND FOUND THAT A FARMER PLOWING HIS FIELD HAD HIT LINE U WITH HIS FARM EQUIPMENT. SINCE THIS LINE FEEDS 5 NEARBY TOWNS, CNG WAS CALLED IN TO HOLD UP PRESSURE. CNG WAS IN PLACE BY 12:30 ON 1/24/2019, AND BLOWDOWN OF THE LINE COMMENCED. A SPLIT SLEEVE WAS WELDED ONTO THE DAMAGE, THE LINE WAS PURGED AND THE SYSTEM WAS BACK UP BY 17:30 ON 1/24/2019.
2025-03-31 10:13 | NO | YES | NO | 20190017 | 32280 | 2019-02-28 11:44 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2019-02-03 08:50 |  |  | 2019 | 13921 INDUSTRIAL PARKWAY | CLEVELAND | CUYAHOGA | OH | 44135 | 41.4303 | -81.7903 | [9 empty] | 2019-02-03 10:10 | 1236659 |  | NATURAL GAS |  | 82 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2019-02-03 05:50 |  |  |  | 2019-02-03 05:00 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 18 |  | NO | [11 empty] | OTHER | CUSTOMER OWNED SERVICE | SERVICE |  | 1998 | [5 empty] | 1.375 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 2300000 | 2602001.6012810244 | 0 | 0 | 5000 | 5656.52522017614 | 0 | 0 |  |  | 246 | 275.700787401574803149606299212598425197 |  | 0 | 2305246 | 1080268.82817890422515748031496062992126 | 2607933.82728860211480314960629921259843 | 3 | 0 | 0 |  |  |  |  | 85 | 85 | 95 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | BOLTED |  | SERVICE OR MAIN TEE |  | UNKNOWN |  | OTHER | MATERIALS JOINED: 1ST PLASTIC, 2ND PLASTIC | [22 empty] | YES | FAILURE OF MECHANICAL JOINT ATTACHMENT | YES |  |  |  | POOR CONSTRUCTION/INSTALLATION PROCEDURES |  |  | NO | [86 empty] | JEFFERY BURDETTE | TECHNICAL CONSULTANT | jeffery.l.burdette@dominionenergy.com | 3307545524 |  |  |  |  | TERRY GLIDDEN | OPERATIONS MANAGER | 3303514326 | terry.l.glidden@dominionenergy.com | NATURAL GAS LEAKING FROM AN UNDERGROUND MECHANICAL SERVICE TEE IGNITED CAUSING FIRE DAMAGE TO A WAREHOUSE EXCEEDING $50,000. CONTRACTOR PIPELINE INSTALLATION RECORDS RELATING TO THE CUSTOMER-OWNED SERVICE PIPELINES IMPACTED BY THE INDUSTRIAL PARKWAY INCIDENT ARE ATTACHED TO THIS REPORT. THESE RECORDS WERE PROVIDED TO DEO FROM THE ATTORNEY FOR THE PROPERTY OWNER'S INSURER. THE MATERIAL TESTING PROTOCOLS AND ASSOCIATED LETTER REGARDING AN EVIDENCE EXAMINATION SCHEDULED FOR FRIDAY, APRIL 26, 2019 AT 10:00 A.M. IN CONNECTION WITH THE INCIDENT ARE ATTACHED TO THIS REPORT. ON APRIL 25TH, 2019 DEO HELD A MEETING TO CORRECT ORIGINALLY REPORTED TIMELINE DISCREPANCIES UTILIZING FLEET GPS REPORTS AND PHONE RECORDS. ON APRIL 29TH, 2019 DEO MET WITH THE INVESTIGATING PUCO INSPECTOR TO PRESENT THE AMENDED TIMELINE REPORT AND DISCUSSED MEETING RESULTS FOR CORRECTIVE ACTIONS. THE AMENDED TIMELINE REPORT AND MEETING NOTES ARE ATTACHED TO THIS REPORT. ON APRIL 26TH, 2019 MATERIAL TESTING WAS COMPLETED IN ACCORDANCE WITH THE PROVIDED TESTING PROTOCOLS. REPRESENTATIVES FROM THE PUCO AND DEO WERE IN ATTENDANCE. THE MATERIAL TESTING REPORT WAS COMPLETED ON MAY 17TH, 2019 AND IS ATTACHED TO THIS REPORT. IN ACCORDANCE WITH 192.617, DOMINION ENERGY OHIO WILL UTILIZE EXISTING DIMP PROCESSES TO ANALYZE THE RESULTS OF THE INDEPENDENT 3RD PARTY MATERIAL TESTING REPORT ALONG WITH PAST MECHANICAL FITTING FAILURE REPORTING DATA TO MAKE DETERMINATIONS ON ANY NECESSARY ADDITIONAL MEASURES NEEDED TO MINIMIZE THE POSSIBILITY OF A RECURRENCE.
2025-03-31 10:13 | NO | YES | NO | 20190018 | 32809 | 2019-02-28 17:50 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2019-01-29 16:00 |  |  | 2019 | INWOOD RD. AND HARRY HINES BLVD. | DALLAS | DALLAS | TX | 75235 | 32.8139 | -96.8464 | [9 empty] | 2019-01-30 17:50 | 1236391 |  | NATURAL GAS |  | 1651 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-01-29 16:13 |  |  |  | 2019-01-29 17:48 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 156 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2005 | [5 empty] | 8 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3406 | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 23414 | 26488.376301040828392 | 79700 | 90165.0120096076716 | 0 | 0 |  |  | 7765 | 8702.50656167979002624671916010498687664 |  | 0 | 110879 | 56364.662929643831490335958005249343832 | 125355.8948723282900182467191601049868766 | 0 | 0 | 0 |  |  |  |  | 26 | 26 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 1952271822 | TEXAS811 |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | MONICA DAVIDSON | OPERATIONS MANAGER | monica.davidson@atmosenergy.com | 214-426-7082 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | 48 HOUR NRC # 1236551 AT APPROX. 16:13 ON 1/29/2019, ATMOS ENERGY WAS NOTIFIED BY OUR CONTRACT LOCATOR OF AN EVENT IN THE AREA OF INWOOD RD AND HARRY HINES BLVD IN DALLAS. A THIRD PARTY CONTRACTOR BORING IN TELECOMMUNICATION DAMAGED AN 8-INCH DISTRIBUTION MAIN OWNED BY ATMOS ENERGY. ATMOS CREWS WERE ONSITE BY 17:48 ON 1/29/2019. ATMOS ENERGY PERFORMED EMERGENCY ACTIONS NEEDED TO ELIMINATE GAS FLOW BY ISOLATING THE DAMAGED SECTION OF PIPE. BY UTILIZING ENGINEERING CONTROLS, THE FLOW OF GAS WAS ELIMINATED AT 03:29 ON 1/31/2019. THE DAMAGED SECTION OF 8-INCH MAIN WAS REPLACED AND GAS FLOW REINSTATED ON 2/4/2019 AT APPROXIMATELY 13:15. THE DAMAGE DID NOT CAUSE AN INTERRUPTION IN SERVICE AS THE LINE IS A DUAL FEED; NO CUSTOMERS WERE AFFECTED. THE ONE-CALL TICKET NUMBER IS 1952271822. THE INVESTIGATION INDICATES THAT THE CONTRACTOR FAILED TO VERIFY LOCATION BY POT HOLING.
2025-03-31 10:13 | NO | YES | NO | 20190019 | 32649 | 2019-03-01 15:06 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2019-01-31 03:39 |  |  | 2019 | 15319 DARROW RD. | VERMILION | ERIE | OH | 44089 | 41.3893 | -82.3594 | [9 empty] | 2019-01-31 04:50 | 1236403 |  | NATURAL GAS |  | 21 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 2 | 2019-01-31 03:42 |  |  |  | 2019-01-31 04:05 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1972 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | DUE TO VEHICULAR DAMAGE | [5 empty] | CLASS 3 LOCATION | 212700 | 240628.5828662929956 | 1200 | 1357.5660528422736 | 4327 | 4895.156925540431556 | 0 | 0 |  |  | 69 | 77.33070866141732283464566929133858267717 |  | 0 | 218296 | 102322.3680102437768207322834645669291339 | 246958.6365533371180788346456692913385827 | 0 | 0 | 1 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ROB R. SMITH | MANAGER OF COMPLIANCE | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB R. SMITH | MANAGER OF COMPLIANCE | 614-818-2110 | rrsmith@nisource.com | AT APPROXIMATELY 03:39 ON 01-31-2019, A DRIVER OF A MOTOR VEHICLE FAILED TO CONTROL THE VEHICLE AND TRAVELED APPROXIMATELY 100 FEET OFF THE ROADWAY STRIKING THE METER SETTING AT 15319 DARROW RD., VERMILION. THE DRIVER OF THE VEHICLE FLED THE SCENE. THE DAMAGE TO THE METER SETTING RESULTED IN A RELEASE OF NATURAL GAS AND A SUBSEQUENT EXPLOSION AND FIRE. THE VERMILION TOWNSHIP FIRE DEPARTMENT EVACUATED THE OCCUPANTS OF THE HOME AND BATTLED THE FIRE UNTIL COLUMBIA GAS OF OHIO REPRESENTATIVES ARRIVED AT THE SCENE AND TURNED THE SERVICE LINE VALVE OFF TO STOP THE FLOW OF GAS. ONCE THE FIRE WAS CONTAINED, A SURFACE LEAK SURVEY WAS COMPLETED WITH NO LEAKAGE FOUND. THE RISER WAS DISASSEMBLED AND THE SERVICE LINE PASSED A PRESSURE TEST. THE SERVICE LINE WAS CUT AND PLUGGED AT THE MAIN AND NOT PLACED BACK IN SERVICE. THE NRC NUMBER WAS CORRECTED IN PART A. *******PER PHMSAS DIRECTION I UPDATED A-13B TO REFLECT THAT THE DISTRIBUTION SERVICE LINE WAS RESTARTED DESPITE BEING PHYSICALLY DISCONNECTED AND PLUGGED ON 1-31-19 AT 10:00AM.*******
2025-03-31 10:13 | NO | YES | NO | 20190020 | 32148 | 2019-03-01 15:21 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2019-01-31 13:37 |  |  | 2019 | 1245 COLES BLVD. | PORTSMOUTH | SCIOTO | OH | 45662-2653 | 38.7591 | -82.9847 | [9 empty] | 2019-01-31 15:55 | 1236454 |  | NATURAL GAS |  | 760 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 25 | 2019-01-31 13:37 |  |  |  | 2019-01-31 12:46 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 16 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | LEAK |  |  | OTHER | LOCALIZED CORROSION | [5 empty] | CLASS 3 LOCATION | 200000 | 226261.0088070456 | 20000 | 22626.10088070456 | 20000 | 22626.10088070456 | 0 | 0 |  |  | 2600 | 2913.91076115485564304461942257217847769 |  | 0 | 242600 | 115148.1668274252621522309711286089238845 | 274427.1213296095756430446194225721784777 | 0 | 0 | 3 |  |  |  |  | 38 | 38 | 56 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ALARM WAS TRIGGERED. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | NO | NONE | [21 empty] | 2017-09-22 | NO | [227 empty] | ROB R. SMITH | MANAGER OF COMPLIANCE | rrsmith@nisource.com | 614-818-2110 | 614-818-2151 |  |  |  | ROB R. SMITH | MANAGER OF COMPLIANCE | 614-818-2110 | rrsmith@nisource.com | ON JANUARY 31, 2019 COLUMBIA WAS CALLED TO 1209 COLES BLVD FOR AN ODOR IN THE ATMOSPHERE. COLUMBIA PERSONNEL WERE ON-SITE INVESTIGATING THE ODOR REPORT WHEN AN EXPLOSION OCCURRED AT 1245 COLES BLVD. UNIT 29. PRIOR TO THE EXPLOSION COLUMBIA EMPLOYEES CONDUCTED A LEAK INVESTIGATION, ESTABLISHED A LEAKAGE PERIMETER, REMOVED MANHOLE COVERS TO FACILITATE VENTING, SET UP TRAFFIC CONTROL, CALLED FOR ADDITIONAL SUPPORT, EVACUATED THE EIGHT UNIT APARTMENT BUILDING AND TURNED THE SERVICE OFF TO ALL UNITS. A LEAK WAS DISCOVERED ON A 6" BARE STEEL MAIN APPROXIMATELY 85' FROM THE FOUNDATION OF 1245 COLES BLVD UNIT 32. THE 6" BARE STEEL MAIN WAS OPERATING AT 38 POUNDS AT THE TIME OF THE INCIDENT. A NON-CAUSAL LEAK WAS DETECTED NEARBY ON THE 4" BARE STEEL MAIN OPERATING AT 3.9 POUNDS. THE LEAKS WERE REPAIRED AND SERVICE RESTORED TO FIVE OF THE EIGHT UNITS. COLUMBIA WORKED WITH THE PUCO, STATE FIRE MARSHALL AND THE PORTSMOUTH FIRE DEPARTMENT TO COMPLETE THE INVESTIGATION. IT'S COLUMBIA'S OPINION THAT THE LEAK FROM THE 6" BARE STEEL MAIN LIKELY MIGRATED THROUGH THE COMBINATION STORM AND SANITARY SEWER INTO THE FLOOR DRAIN OF 1245 COLES BLVD, UNIT 29. COLUMBIA VERIFIED THAT THE FLOOR DRAIN OF UNIT 29 DIRECTLY COMMUNICATED WITH THE COMBINATION STORM DRAIN AND SANITARY SEWER VIA USE OF A VIDEO CAMERA. COLUMBIA IS REPLACING BOTH THE 6" BARE STEEL AND 4" BARE STEEL MAINS WITHIN THE AREA OF 1245 COLES BLVD IN 2019. COLUMBIA CONSIDERS THIS ITS FINAL REPORT AND NO OTHER REPORTS ARE FORTHCOMING.
2025-03-31 10:13 | NO | YES | YES | 20190021 | 32949 | 2019-03-04 18:12 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-02-02 22:54 |  |  | 2019 | 406 IRWIN AVENUE | PONTIAC | OAKLAND | MI | 48341 | 42.6204 | -83.2723 | [9 empty] | 2019-02-03 02:18 | 1236645 |  | NATURAL GAS |  | 95.7 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 3 | 2019-02-02 21:45 |  |  |  | 2019-02-02 22:18 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | BURIED REGULATOR | UNKNOWN | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 59405 | 67205.17614091271934 | 48804 | 55212.211369095267312 | 2124 | 2402.891913530824272 | 0 | 0 |  |  | 307 | 344.065616797900262467191601049868766404 |  | 0 | 110640 | 52015.0970484174175643595800524934383202 | 125164.3450403367111864671916010498687664 | 0 | 0 | 2 |  |  |  |  | 259 | 259 | 274 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FACILITY IS NOT MONITORED BY SCADA | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | OTHER | THE SOURCE OF THE BLOWING GAS WAS DETERMINED TO BE A LEAK ON THE 3/4 INCH PIPE THREAD THAT TIED INTO THE HIGH PRESSURE REGULATOR. | [36 empty] | YES | THE SOURCE OF THE BLOWING GAS WAS DETERMINED TO BE A LEAK ON THE 3/4 INCH PIPE THREAD THAT TIED INTO THE HIGH PRESSURE REGULATOR. |  | YES |  |  |  | OTHER | CIRCUMFERENTIAL CRACK AT THE THREAD | NO | [86 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON FEBRUARY 2, 2019 AT APPROXIMATELY 22:54 HOURS A HOME EXPLOSION AND SUBSEQUENT FIRE OCCURRED AT 406 IRWIN AVENUE, PONTIAC, MICHIGAN (OAKLAND COUNTY). A MALE OCCUPANT WAS INJURED IN THE EXPLOSION AND TRANSPORTED TO THE LOCAL HOSPITAL. THE HOME WAS A COMPLETE LOSS WITH AN ESTIMATED VALUE OF APPROXIMATELY $59,400. PRIOR TO THE EXPLOSION, AT APPROXIMATELY 21:45 HOURS CONSUMERS ENERGY RECEIVED AND RESPONDED TO AN OUTSIDE LEAK INVESTIGATION AT 443 SOUTH BOULEVARD, PONTIAC, MI. THE GAS SERVICE WORKER (GSW) ARRIVED ONSITE AT APPROXIMATELY 22:18, HEARD BLOWING GAS AT/NEAR THE SERVICE TEE AND REQUESTED A DISTRIBUTION CREW. THE GSW ALSO OBTAINED 6% FREE AIR READS AT THE PROPERTY ENTRANCE AND ADVISED THE OCCUPANTS NOT TO RE-ENTER THE HOME. WHILE CONTINUING TO INVESTIGATE THE AREA, THE GSW HEARD WHAT HE BELIEVED MAY HAVE BEEN AN EXPLOSION NEARBY (APPROXIMATELY 500 FEET FROM THE SOUTH BLVD. LOCATION) AND NOTIFIED HIS FIELD LEADER. FURTHER INVESTIGATION OF THE AREA DETERMINED GAS READS (APPROXIMATELY 55% GAS) IN THE SANITARY SEWER SYSTEM LOCATED APPROXIMATELY 73 FEET WEST OF THE SEWER LEAD SERVING 406 IRWIN AVE. GAS READS WERE ALSO OBTAINED AT 398 IRWIN AVE. RESULTING IN AN EVACUATION OF THE OCCUPANT AT THIS PROPERTY. (FOLLOWING ADDITIONAL INVESTIGATION, THE SEWER LEAD FOR 406 IRWIN AVENUE WAS LATER DETERMINED TO BE SOUTH OF THE SANITARY SEWER LOCATED AT THE INTERSECTION OF GOING STREET AND IRWIN AVENUE) THE DISTRIBUTION CREW ARRIVED ON FEBRUARY 3, 2019 AT APPROXIMATELY 00:35 HOURS. THE SOURCE OF THE BLOWING GAS WAS DETERMINED TO BE A LEAK ON THE 3/4 INCH PIPE THREAD THAT TIED INTO THE HIGH PRESSURE REGULATOR. THE SERVICE LINE, REGULATOR AND SECURITY WERE REPLACED AND GAS READS BEGAN TO DISSIPATE FROM THE SANITARY SEWER. ON FEBRUARY 20, 2019 THE INTERESTED PARTIES MET ON-SCENE TO CONDUCT A JOINT SCENE INVESTIGATION. THE PARTIES AGREED THE CURRENT WEATHER CONDITIONS AND THE STRUCTURAL INTEGRITY OF THE PROPERTY MADE IT UNSAFE TO PROCEED FORWARD WITH THE INVESTIGATION. THE JOINT SCENE INVESTIGATION WAS POSTPONED FOR APPROXIMATELY 30 DAYS. UNTIL A FULL ON-SCENE INVESTIGATION CAN BE COMPLETED THE CAUSE AND ORIGIN REMAINS CLASSIFIED AS UNDETERMINED. ON MARCH 25, 2019 A JOINT SCENE INVESTIGATION WAS PERFORMED, THE LOCATION WAS CAREFULLY EXCAVATED AND ALL GAS APPLIANCES WERE REMOVED AND TRANSPORTED TO THE SAFETY ENGINEERING LABORATORIES, INC. (SEL) FOR FUTURE INVESTIGATION AND TESTING. THE FOLLOWING DAY, MARCH 26, 2019 DESTRUCTIVE TESTING FOR THE FAILURE THAT OCCURRED ON THE BURIED REGULATOR LOCATED AT 443 SOUTH BOULEVARD WAS PERFORMED AT THE CONSUMERS ENERGY TRAIL STREET LABORATORY. ON APRIL 10, 2019 A JOINT SCENE EXAM WAS HELD WITH CONSUMERS ENERGY, SEL AND THE MPSC. THE BASEMENT OF THE RESIDENCE WAS EXCAVATED AND WATER DRAINED IN THE ATTEMPT TO LOCATE, TRACE AND VIDEO (PHOTOGRAPH) THE SEWER LINE FROM THE INSIDE OF THE HOME TO THE SANITARY SEWER UNDER THE ROADWAY. DURING THE INVESTIGATION, A HOLE (APPROXIMATELY 4X4) CUT INTO THE TOP OF THE METAL SEWER LINE IN THE BASEMENT BEFORE THE SEWER TRAP WAS DISCOVERED. THE SEWER LINE ALSO RAN INTO A REPAIRED SINKHOLE AREA ON GOINGS INSTEAD OF IRWIN AS PREVIOUSLY DESCRIBED BY THE CITY OF PONTIAC WATER DEPARTMENT EMPLOYEE FROM AN EARLIER INVESTIGATION. FOLLOWING A SERIES ON INVESTIGATIVE ACTIVITIES, IT HAS BEEN DETERMINED THE PROBABLE CAUSE OF THE EXPLOSION WAS THE IGNITION OF NATURAL GAS. THE IGNITION SOURCE REMAINS UNDETERMINED. ADDITIONALLY, THE CAUSE OF THE EXPLOSION REMAINS UNCONFIRMED DUE TO THE LACK OF COOPERATION BY THE LEGAL REPRESENTATIVE FOR THE PROPERTY'S RESIDENT.
2025-03-31 10:13 | NO | NO | NO | 20190022 | 31738 | 2019-03-05 10:25 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2019-02-08 13:15 |  |  | 2019 | PRUDENCE AND CALLE MADERO | TUCSON | PIMA | AZ | 85710 | 32.2178 | -110.8323 | [9 empty] | 2019-02-08 15:20 | 1237225 |  | NATURAL GAS |  | 249 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 35 | 2019-02-08 13:15 |  |  |  | 2019-02-08 13:28 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 84 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1986 | [5 empty] | 4.5 | API 5LX | UNKNOWN | STEEL |  | OTHER | ERW | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1680 | 1900.59247397918304 | 1000 | 1131.305044035228 | 47320 | 53533.35468374698896 | RELIGHTS |  | 1494 | 1674.377952755905511811023622047244094488 |  | 0 | 51494 | 24976.5286314791255905511811023622047244 | 58239.6301545173055118110236220472440945 | 63 | 0 | 893 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 1 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | [7 empty] | YES | [6 empty] | UTILITY | AUGER | POLE | YES | 2019012801165 |  |  | CONTRACT LOCATOR | YES | YES | 8 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | MARK HINGSTRUM | ADMINISTRATOR-DIVISION COMPLIANCE | mark.hingstrum@swgas.com | 520-794-6108 | 520-794-6166 |  |  |  | TODD DIDIER | DIRECTOR-GAS OPERATIONS | 520-794-6066 | todd.didier@swgas.com | ON FEBRUARY 8, 2019, A FOUR INCH STEEL DISTRIBUTION MAIN LOCATED AT PRUDENCE ROAD AND CALLE MADERO WAS HIT AND DAMAGED BY A THIRD PARTY EXCAVATOR. THIRTY FIVE INDIVIDUALS WERE EVACUATED FROM MULTIPLE BUILDINGS DUE TO THE PROXIMITY OF ESCAPING GAS. A VALVE ISOLATION PLAN WAS UTILIZED TO SAFELY CONTROL THE FLOW OF GAS AND RESULTED IN AN OUTAGE OF 956 ACCOUNTS. REPAIRS TO THE DAMAGED FACILITY WERE COMPLETED 7.5 HOURS AFTER INITIAL SHUTDOWN AND THE ISOLATED SECTIONS WERE PLACED BACK INTO SERVICE. ON FEBRUARY 9, 2019, AT 1830 HOURS, CUSTOMER RELIGHTS WERE COMPLETED AND DOOR TAGS WERE HUNG FOR THE REMAINING CGI'S. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20190023 | 31826 | 2019-03-05 10:27 | SUPPLEMENTAL FINAL | 11320 | LAWRENCEVILLE, CITY OF | P.O. BOX 2200 435 WEST PIKE STREET | LAWRENCEVILLE | GA | 30046 | 2019-02-08 03:20 |  |  | 2019 | 300 SIMONTON ROAD | LAWRENCEVILLE | GWINNETT | GA | 30046 | 33.9354 | -83.9788 | [9 empty] | 2019-02-08 07:45 | 1237153 |  | NATURAL GAS |  | 353.32 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2019-02-08 03:20 |  |  |  | 2019-02-08 04:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2003 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 2 | 2 |  | CLASS 3 LOCATION | 900 | 1018.1745396317052 | 6500 | 7353.482786228982 | 13330 | 15080.29623698958924 | 0 | 0 |  |  | 3485 | 3905.761154855643044619422572178477690289 |  | 0 | 24215 | 13326.1535527634764409711286089238845144 | 27357.7147177059194846194225721784776903 | 1 | 0 | 1 |  |  |  |  | 150 | 150 | 150 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | KYLE HAMBY | REGULATORY COMPLIANCE SUPERVISOR | kyle.hamby@lawrencevillega.org | 7702777455 | 7709955383 |  |  |  | KYLE HAMBY | REGULATORY COMPLIANCE SUPERVISOR | 7702777455 | kyle.hamby@lawrencevillega.org | AT APPROXIMATELY 03:05 AM, A DRIVER OF A VEHICLE WAS BEING PURSUED BY LAW ENFORCEMENT AT A HIGH RATE OF SPEED WHEN IT LOST CONTROL AND EXITED THE ROADWAY AND STRUCK AN ABOVE GROUND, TWO INCH MONITORING STATION. THE STATION WAS BROKEN AT GROUND LEVEL AND ALMOST INSTANTLY IGNITED. THE STATION WAS A TWO WAY FEED. 150 PSIG ON THE INLET SIDE AND 60 PSIG ON THE OUTLET SIDE. THE INLET VALVE TO THE 150 PSIG SIDE WAS CUT OFF AT 4:23 AM AND CREWS HAD TO DIG TWO BELL HOLES TO STOP THE 60 PSIG DOWNSTREAM SIDE TO SQUEEZE OFF THE PE MAINS THAT WERE BACK FEEDING THE STATION. TOTAL SHUT OFF AND ISOLATION OF THE STATION OCCURRED AT 08:30 AM. THE DRIVER WAS APPREHENDED AND SUSTAINED MINOR INJURIES CONSISTENT WITH AN AIRBAG DEPLOYING AND WAS TREATED AND RELEASED FROM THE EMERGENCY ROOM.
2025-03-31 10:13 | NO | YES | NO | 20190024 | 39078 | 2019-03-05 22:01 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2019-02-06 13:14 | PACIFIC | NO | 2019 | 3300 GEARY BLVD. | SAN FRANCISCO | SAN FRANCISCO | CA | 94118 | 37.7819 | -122.4544 |  | YES |  |  |  | YES |  |  |  | 2019-02-06 14:58 | 1237005 |  | NATURAL GAS |  | 1924 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2019-02-06 13:22 | OPERATOR/CONTRACTOR |  | 1924 | YES | 100 | 2019-02-06 13:14 |  |  |  | 2019-02-06 13:29 | 2019-02-06 13:50 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 42 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1997 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 8 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 122275 | 138330.3242594075037 | 280708 | 317566.376301040781424 | 0 | 0 |  | 3 | 5772 | 6468.881889763779527559055118110236220472 | 0 | 0 | 408755 | 194802.8349027429548689527559055118110236 | 462365.5824502120646515590551181102362205 | 34 | 0 | 294 | 0 | 0 | 12 | 6 | 47.5 | 50 | 60 | 192.619(A)(2) | 2000-03-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE EVENT WAS CAUSED BY A 3RD PARTY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [8 empty] | YES | NO | MEASURED DEPTH FROM GRADE | 42 | CONTRACTOR | BACKHOE/TRACKHOE | TELECOMMUNICATIONS | YES | 902101666 | SINGLE ON-CALL CENTER STATE- 811 | Unknown | FACILITY OWNER | YES | YES | 31 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ENZA BARBATO | REGULATORY COMPLIANCE | e1bo@pge.com | [5 empty] | SUSIE RICHMOND | REGULATORY COMPLIANCE MANAGER | 925-786-0267 | gsr8@pge.com | ON FEBRUARY 06, 2019 AT APPROXIMATELY 13:14 HOURS, PG&E WAS NOTIFIED OF A THIRD-PARTY DIG-IN WITH SUBSEQUENT IGNITION NEAR 3300 GEARY BLVD. IN SAN FRANCISCO. THIRD PARTY CONTRACTOR, KILFORD ENGINEERING, DAMAGED A 2' GAS MAIN AT THE CONNECTION TO A 4-INCH MAIN. THE EXCAVATOR HAD A VALID USA TICKET (X902101666) AND PG&E FACILITIES WERE PROPERLY LOCATED & MARKED. THE CONTRACTOR FAILED TO EXPOSE THE FACILITIES WITH HAND TOOLS PRIOR TO USE OF POWER-DRIVEN EXCAVATION EQUIPMENT. POLICE AND FIRE PERSONNEL EVACUATED MULTIPLE BUILDINGS SURROUNDING THE AREA (APPROXIMATELY 1 BLOCK IN EACH DIRECTION OF THE INCIDENT- APPROXIMATELY 100 PEOPLE) AND CONTROLLED THE SPREAD OF FIRE. NO INJURIES OR FATALITIES WERE REPORTED. PG&E'S M&C CREW ARRIVED ON-SITE AT 13:29 HOURS, AND THE AREA WAS ISOLATED BY 15:36 HOURS. REPAIRS WERE COMPLETED, AND SERVICE RESTORATION BEGAN ON 2/7/19. BY 2/7/19 AT 2200 HOURS, ALL AFFECTED CUSTOMERS HAD BEEN RESTORED OR BEEN LEFT A NOTE TO CALL FOR RELIGHT. THIS INCIDENT WAS REPORTED TO THE CPUC ON 2/6/19 AT 14:28 HOURS DUE TO THE SIGNIFICANT NEWS MEDIA COVERAGE OBSERVED ON SITE AT APPROXIMATELY 13:50 HOURS. THE INCIDENT WAS REPORTED TO DOT (#1237005) ON 2/6/19 AT 14:58 HOURS, ONCE ESTIMATED COSTS WERE DETERMINED TO BE GREATER THAN $50,000 (AT THE TIME OF THIS REPORT, TOTAL DAMAGES AND COSTS ARE STILL BEING ESTIMATED).
2025-03-31 10:13 | NO | YES | NO | 20190025 | 32045 | 2019-03-12 17:30 | SUPPLEMENTAL FINAL | 32198 | MINNESOTA ENERGY RESOURCES CORPORATION | 2685 145TH STREET WEST | ROSEMOUNT | MN | 55068 | 2019-02-16 01:10 |  |  | 2019 | 3918 18TH AVE NW | ROCHESTER | OLMSTED | MN | 55901 | 44.0641 | -92.4886 | [9 empty] | 2019-02-16 15:42 | 1237865 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2019-02-16 01:25 |  |  |  | 2019-02-16 01:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 200000 | 226261.0088070456 | 1038 | 1174.294635708566664 | 325 | 367.6741393114491 | 0 | 0 | LOCAL PAPER ESTIMATED DAMAGE TO BUILDING AT OVER $200K. |  | 100 | 112.073490813648293963254593175853018373 |  | 0 | 201463 | 94452.8357363056364491627296587926509186 | 227915.0510728792640579632545931758530184 | 1 | 0 | 0 |  |  |  |  | 50 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LINDSAY K LYLE | ENGINEERING MANAGER | lindsay.lyle@minnesotaenergyresources.com | 651-322-8909 | 920-272-4000 |  |  |  | LINDSAY K LYLE | ENGINEERING MANAGER | 651-322-8909 | lindsay.lyle@minnesotaenergyresources.com | VEHICLE LOST CONTROL AND STRUCK BARRICADED COMMERCIAL METER SET. VEHICLE PUSHED BARRICADE OVER CRACKING FITTING ON METER CAUSING IGNITION. FIRE ON THE VEHICLE, BUILDING, AND METER SET. FIRE DEPARTMENT TURNED OFF GAS AND EXTINGUISHED FLAMES/BURNING BUILDING. CALL CENTER RECEIVED 911 CALL @ 01:25, ORDER WAS DISPATCHED TO MERC EMPLOYEE @ 01:29 TECHNICIAN ARRIVED @ 01:39, FIRE DEPARTMENT SHUT OFF GAS AT METER SET @ 01:45 THE FIRE WAS EXTINGUISHED IN BACK OF BUILDING, POLICE REPORT @ 01:50 RISER SHUT OFF VALVE WAS PLUGGED BY MERC TECH. SERVICE LINE TO BE ABANDONED UNTIL TENANT REQUESTS GAS TO BE TURNED ON.
2025-03-31 10:13 | NO | NO | NO | 20190026 | 32199 | 2019-03-14 19:52 | SUPPLEMENTAL | 180 | SPIRE ALABAMA INC. | 605 RICHARD ARRINGTON JR BLVD N | BIRMINGHAM | AL | 35203 | 2019-02-12 11:00 |  |  | 2019 | ABRAHAM WOODS JR DR & 15TH ST N | BIRMINGHAM | ALABAMA | AL | 35203-2749 | 33.5182 | -86.8196 | [9 empty] | 2019-02-13 11:13 | 1237545 |  | NATURAL GAS |  | 128.22 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-02-12 11:00 |  |  |  | 2019-02-12 11:43 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 65 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2010 | [5 empty] | 10 | X52 | CONSOLIDATED | STEEL |  | OTHER | UNKNOWN | 0.365 | [6 empty] | MECHANICAL PUNCTURE | 0.2 | 0.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 55012 | 62235.353082465962736 | 1500 | 1696.957566052842 | 0 | 0 |  |  | 1519 | 1702.396325459317585301837270341207349081 |  | 0 | 58031 | 28053.6619272671138890918635170603674541 | 65634.7069739781223213018372703412073491 | 0 | 0 | 0 |  |  |  |  | 200 | 200 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS CAUSED BY EXCAVATION DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | NO |  |  |  | CONTRACT LOCATOR | NO |  |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | SHAUN SLADE | MANAGER - PIPELINE SAFETY | shaun.slade@spireenergy.com | 205-326-8410 |  |  |  |  | CRAIG HOEFERLIN | VICE PRESIDENT - OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | ON FEBRUARY 12, 2019 AT APPROXIMATELY 11:00 AM, A THIRD PARTY CONTRACTOR WAS EXCAVATING NEAR THE INTERSECTION OF ABRAHAM WOODS JR DR & 15 ST N IN BIRMINGHAM, AL. THE CONTRACTOR'S ONE CALL LOCATE REQUEST FOR THE EXCAVATION WORK HAD BEEN EXPIRED FOR APPROXIMATELY 5 WEEKS, AND A NEW LOCATE TICKET HAD NOT BEEN REQUESTED. A TRACKHOE STRUCK THE 10" STEEL MAIN AND CAUSED A PINHOLE LEAK. THE LEAK WAS TEMPORARILY REPAIRED WITH A CLAMP AND A NEW SECTION OF MAIN WAS INSTALLED ON FEBRUARY 14TH TO REPLACE THE DAMAGED SECTION. SPIRE DETERMINED THAT REPAIR COSTS WOULD EXCEED $50,000 AT AROUND NOON ON FEBRUARY 13TH AND MADE THE INCIDENT REPORT TO THE NRC.
2025-03-31 10:13 | NO | YES | NO | 20190027 | 32336 | 2019-03-16 15:24 | SUPPLEMENTAL FINAL | 31636 | NORTHERN STATES POWER CO OF MINNESOTA | 414 NICOLLET MALL | MINNEAPOLIS | MN | 55402 | 2019-02-14 23:21 |  |  | 2019 | 8 ST S AND 16 AVE S | MOORHEAD | CLAY | MN | 56560 | 46.8586 | -96.7681 | [9 empty] | 2019-02-15 10:18 | 1237757 |  | NATURAL GAS |  | 3852 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-02-14 23:12 |  |  |  | 2019-02-14 23:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 25000 | 28282.6261008807 | 321158 | 363327.665332265754024 | 0 | 0 |  |  | 16615 | 18621.0104986876640419947506561679790026 |  | 0 | 362773 | 179418.7627246154850657375328083989501312 | 410231.3019318341180659947506561679790026 | 0 | 0 | 950 |  |  |  |  | 30.5 | 25 | 25 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LISA KALLBERG | PIPELINE COMPLIANCE CONSULTANT | elisabeth.m.kallberg@xcelenergy.com | 651-229-2282 |  |  |  |  | LAUREN GILLILAND | DIRECTOR GAS GOVERNANCE | 303-571-3255 | lauren.gilliland@xcelenergy.com | ON FEBRUARY 14, 2019, A SNOW PLOW HIT ABOVEGROUND PIPING FOR A PRESSURE RECORDING CHART AT A REGULATOR STATION THAT WAS INSTALLED IN A VAULT. THE IMPACT DAMAGED PIPING IN THE VAULT CAUSING THE REGULATOR TO FAIL WHICH RESULTED IN THE ACTIVATION OF THE RELIEF VALVE. THE MAOP OF THE SYSTEM IS 25 PSIG AND THE HIGHEST PRESSURE OBSERVED WAS 30.5 PSIG. AT APPROXIMATELY 12:00 ON FEBRUARY 15, 2019 THE SYSTEM WAS SHUT-IN BY CLOSING AN EMERGENCY VALVE, CAUSING AN OUTAGE TO 950 CUSTOMERS. REPAIRS WERE INITIALED AT APPROXIMATELY 16:00 ON FEBRUARY 15, 2019. REPAIRS WERE COMPLETED BY 19:30, THE SYSTEM WAS STARTED UP AND LEAK SURVEYED. CUSTOMER RELIGHTS STARTED AT APPROXIMATELY 23:00 AND CONTINUED UNTIL FEBRUARY 16, 2019 AT 16:00. ADDITIONAL LEAK SURVEYS WERE CONDUCTED FEBRUARY 16 STARTING AT 19:00. AFTER THE SECOND SURVEY NO FURTHER LEAKS WERE DISCOVERED. ON FEBRUARY 17, STARTING AT 11:00, ONE MORE SURVEY WAS CONDUCTED WITH NO FURTHER LEAKS DISCOVERED.
2025-03-31 10:13 | NO | YES | NO | 20190028 | 32427 | 2019-03-18 09:20 | SUPPLEMENTAL FINAL | 12876 | DOMINION ENERGY UTAH/WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2019-02-16 16:00 |  |  | 2019 | 9740 BYPASS ROAD | ALTA | SALT LAKE COUNTY | UT | 84092 | 40.5864 | -111.649 | [9 empty] | 2019-02-16 20:24 | 1237885 |  | NATURAL GAS |  | 11.32 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 3 | 2019-02-16 19:58 |  |  |  | 2019-02-16 16:21 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2016 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 650000 | 735348.2786228982 | 300 | 339.3915132105684 | 9400 | 10634.2674139311432 | 0 | 0 |  |  | 50 | 56.03674540682414698162729658792650918635 |  | 0 | 659750 | 309156.0006010059242490813648293963254593 | 746377.9742954467357469816272965879265092 | 0 | 0 | 3 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | ACCUMULATED SNOW AND SNOW SLIDE ONTO THE NATURAL GAS METER. | [154 empty] | LAUREN SKUFCA | ENGINEER-PIPELINE COMPLIANCE | lauren.l.skufca@dominionenergy.com | 8013243746 |  |  |  |  | REID HESS | MANAGER- GAS OPERATIONS | 8013243374 | reid.hess@dominionenergy.com | ON FEBRUARY 16, 2019 DOMINION ENERGY UTAH (DEU) WAS NOTIFIED OF A HOUSE FIRE AT 9740 BYPASS ROAD, ALTA, UTAH. DEU SENT A TECHNICIAN TO THE SITE. UPON ARRIVAL THE TECHNICIAN WAS UNABLE TO ACCESS THE GAS METER DUE TO EXCESSIVE AMOUNTS OF SNOW (ABOUT 12' OF SNOW FROM GROUND LEVEL). LATER, DEU DISPATCH RECEIVED AN UPDATED CALL FROM THE FIRE DEPARTMENT STATING THAT A NATURAL GAS EXPLOSION MAY HAVE OCCURRED. ADDITIONAL RESOURCES WERE SENT TO ASSIST WITH SECURING THE SERVICE LINE TO THE PROPERTY. COMPANY REPORTED THE INCIDENT UPON DISCOVERY AND SUSPECTED NATURAL GAS INVOLVEMENT. AFTER THE FIRE WAS CONTAINED, DEU CREWS EXCAVATED THE NATURAL GAS METER AND FOUND IT WAS DAMAGED. THE GAS SERVICE LINE TO THE UNIT WAS SECURED AT 02:30 ON FEBRUARY 17, 2019. A VIEWING OF THE METER AND RISER EVIDENCE WAS CONDUCTED WITH THE INVOLVED PARTIES AND THE STATE OF UTAH PIPELINE SAFETY ON APRIL 23, 2019. BASED ON INFORMATION FROM THE EVENT INVESTIGATION, DEU BELIEVES THAT SNOW LOAD, ALONG WITH A SNOW SLIDE FROM THE ROOF OF THE BUILDING DAMAGED THE NATURAL GAS METER CAUSING A LEAK. LEAKING GAS ACCUMULATED AND IGNITED FROM AN UNDETERMINED IGNITION SOURCE. THIS IS SUBSTANTIATED THROUGH INVESTIGATION AND DOCUMENTED IN THE UNIFIED FIRE INVESTIGATION REPORT.
2025-03-31 10:13 | NO | NO | NO | 20190029 | 31803 | 2019-03-18 12:05 | ORIGINAL | 3600 | DUMAS, CITY OF | 124 W. 6TH BOX 438 | DUMAS | TX | 79029 | 2018-12-21 16:25 |  |  | 2018 | 404 PINE | DUMAS | MOORE | TX | 79029 | 35.8636 | -101.9651 | [9 empty] | 2018-12-26 13:05 | DO NOT KNOW NRC REPORT NUMBER |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-12-21 16:30 |  |  |  | 2018-12-21 16:30 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | OTHER | SEWER VENT PIPE |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OTHER | SEWER | UNKNOWN | [8 empty] | OTHER | SEWER | [9 empty] | OTHER | [8 empty] | SEWER GAS | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WE DO NOT HAVE AN ESTIMATE ON COST |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 20 | 20 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | PATTY STAHL | GAS CLERK | pstahl@dumastx.gov | 806-935-4707 | 806-935-5477 |  |  |  | JACK BRASWELL | GAS SUPERINTENDENT | 806-935-4707 | jbraswell@dumastx.gov | ON DECEMBER 21,2018 CITY UTILITIES WERE CALL OUT TO A HOUSE EXPLOSION AT 404 PINE IN DUMAS, TEXAS UTILITIES WERE TURNED OFF AFTER FURTHER INVESTIGATION. IT WAS DETERMINED THAT SEWER GAS WAS THE FAULT OF THE EXPLOSION
2025-03-31 10:13 | NO | NO | NO | 20190031 | 32804 | 2019-03-22 16:54 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2019-02-27 17:25 |  |  | 2019 | RIVER BEND & OAK LANE | GEORGETOWN | WILLIAMSON | TX | 78628 | 30.6604 | -97.6912 | [9 empty] | 2019-02-27 17:25 | 1238800 |  | NATURAL GAS |  | 106.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 86 | 2019-02-27 17:25 |  |  |  | 2019-02-20 18:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1973 | [5 empty] | 3 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 78 | 88.241793434747784 | 4236 | 4792.208166533225808 | 0 | 0 |  |  | 507 | 568.21259842519685039370078740157480315 |  | 0 | 4821 | 2546.96592339488509768503937007874015748 | 5448.66255839317044239370078740157480315 | 24 | 0 | 49 |  |  |  |  | 31 | 30 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | LEAK SURVEY INDICATING PRESENCE OF RESIDUAL GAS |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT COULD NOT BE SEEN BY CONTROLLERS | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 1973 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [6 empty] | YES | YES | [7 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | MICHAEL LABAY | DIRECTOR OF OPERATIONS | michael.labay@atmosenergy.com | 512-310-3820 | 512-310-3880 |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC# 1239009 ON FEBRUARY 27, 2019, OUT OF AN ABUNDANCE OF CAUTION BASED ON CIRCUMSTANCES THAT AROSE IN GEORGETOWN, TEXAS, ATMOS ENERGY DETERMINED THAT IN THE JUDGMENT OF THE OPERATOR CONDITIONS BECAME SIGNIFICANT AND WARRANTED A TELEPHONIC INCIDENT REPORT TO ITS SAFETY REGULATORS DUE TO AN ABNORMAL, CONTINUED PRESENCE OF RESIDUAL GAS FOLLOWING A ROUTINE RESPONSE TO A LEAK INVESTIGATION. SPECIFICALLY, ATMOS ENERGY HAD PREVIOUSLY RESPONDED TO A REPORT OF PRESENCE OF A NATURAL GAS ODOR AND DISCOVERED A LEAK AT THE INTERSECTION OF RIVER BEND DR. AND OAK LN. PER APPLICABLE RULES AND ATMOS ENERGY'S ROUTINE OPERATING PROCEDURES APPROVED BY THE RAILROAD COMMISSION, CREWS TOOK IMMEDIATE ACTION TO REPAIR DISCOVERED LEAKS, AND BEGAN CONTINUOUS MONITORING. DURING THE PROCESS OF CONTINUOUS MONITORING, ATMOS ENERGY CONDUCTED PRECAUTIONARY EVACUATIONS OF THE IMMEDIATE AREA BEGINNING FEBRUARY 21, 2019. THE MAIN SERVING THE AFFECTED AREA WAS SHUT DOWN AT APPROXIMATELY 10:00 PM ON FEBRUARY 21, 2019. HOWEVER, THE SOIL OR OTHER CONDITIONS WITHIN THE AREA APPEARED TO BE CAUSING NATURAL GAS TO VENTILATE SLOWLY. THUS, AS THE LEAK MONITORING AND SURVEY ACTIVITY WAS EXPANDED, UNSAFE LEVELS OF RESIDUAL GAS WERE DETECTED TO STILL BE PRESENT IN A LARGER AREA WHICH LED TO ADDITIONAL EVACUATIONS. AT THIS POINT, ATMOS ENERGY ELECTED TO MAKE A REPORT. THE CONDITIONS IN GEORGETOWN RESULTED IN DISCONNECTION OF SERVICE TO 73 METERS AND THE EVACUATION OF 86 STRUCTURES. EVACUATIONS WERE LIFTED ACCORDING TO OUR PROCEDURES AND IN COORDINATION WITH THE CITY OF GEORGETOWN, AND SERVICE HAS BEEN RESTORED TO ALL CUSTOMERS. ATMOS ENERGY'S ROOT CAUSE ANALYSIS OF THE LEAK IN QUESTION DETERMINED THE CAUSE OF THE LEAK TO BE IMPROPER BUTT FUSION ON THE 3-INCH MAIN.
2025-03-31 10:13 | NO | YES | NO | 20190032 | 33364 | 2019-03-28 17:35 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2019-02-26 13:56 |  |  | 2019 | 801 CAPITAL CENTRE BLVD | LARGO | PRINCE GEORGE'S COUNTY | MD | 20774 | 38.9023 | -76.8456 | [9 empty] | 2019-02-26 19:00 | 1238694 |  | NATURAL GAS |  | 4832 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-02-26 13:56 |  |  |  | 2019-02-26 13:59 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2018 | [5 empty] | 12 | ASTM D2513 | DURA-LINE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 4710 | MECHANICAL PUNCTURE | 3.5 | 5 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 440 | 497.77421937550032 | 109270 | 123617.70216172936356 | 383 | 433.289831865492324 | ADMINISTRATIVE |  | 14036 | 15730.6351706036745406824146981627296588 |  | 0 | 124129 | 66136.1221099364489951207349081364829396 | 140279.4013835740307446824146981627296588 | 44 | 0 | 767 |  |  |  |  | 49 | 49 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE EASEMENT | [10 empty] | DEVELOPER | BACKHOE/TRACKHOE | UNKNOWN/OTHER | YES | 19088162 | N/A |  | CONTRACT LOCATOR | NO | YES | 17 | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | ARTHUR GROFF | SUPERVISOR - PIPELINE SAFETY AND COMPLIANCE | agroff@washgas.com | 7037507792 |  |  |  |  | STEPHEN PRICE | AVP SAFETY QUALITY SYSTEM PROTECTION | 7037504586 | sprice@washgas.com | WASHINGTON GAS RECEIVED A CALL FROM A THIRD-PARTY EXCAVATOR AT 1:56PM ON TUESDAY, FEBRUARY 26, 2019. UPON ARRIVAL, WASHINGTON GAS FOUND A 12-INCH PLASTIC MAIN PIPE HAD BEEN DAMAGED DURING EXCAVATION AND GAS WAS BLOWING. WASHINGTON GAS CREWS REDUCED NATURAL GAS PRESSURE IN THE AREA TO MINIMIZE GAS LOST. WASHINGTON GAS SHUT THE MAIN DOWN BY SQUEEZE-OFF AT 9:07PM ON FEBRUARY 26, 2019, WHICH RESULTED IN AN OUTAGE OF 767 RESIDENTIAL CUSTOMERS AND 44 COMMERCIAL CUSTOMERS. THE DAMAGED SECTION WAS CUT OUT AND REPLACED AND THE MAIN WAS RE-ENERGIZED ON FEBRUARY 27, 2019. ON WEDNESDAY, FEBRUARY 27, WASHINGTON GAS FOUND THAT MISS UTILITY MARKS HAD NOT BEEN PRESERVED ON THE SITE.
2025-03-31 10:13 | NO | YES | NO | 20190033 | 33153 | 2019-03-29 20:56 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2019-02-28 15:40 |  |  | 2019 | 3281 SOUTH UPPER TRUCKEE | SOUTH LAKE TAHOE | EL DORADO | CA | 96150 | 38.8182 | -120.0203 | [9 empty] | 2019-02-28 18:24 | 1238918 |  | NATURAL GAS |  | 4 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2019-02-28 15:09 |  |  |  | 2019-02-28 15:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.14 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 138000 | 156120.096076861464 | 274 | 309.977582065652472 | 0 | 0 |  |  | 24 | 26.89763779527559055118110236220472440945 |  | 0 | 138298 | 64813.5268501765930255590551181102362205 | 156456.9712967223920625511811023622047244 | 0 | 0 | 1 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | SEE PART H, NARRATIVE | [154 empty] | MINDI DAGERMAN | ENGINEERING SUPERVISOR COMPLIANCE | mindi.dagerman@swgas.com | 775-887-2837 |  |  |  |  | MATTHEW HELMERS | DIRECTOR OF DISTRICT OPERATIONS NNV | 775-887-2744 | matthew.helmers@swgas.com | SOUTHWEST GAS WAS NOTIFIED OF A STRUCTURE FIRE AT 3281 SOUTH UPPER TRUCKEE ROAD IN SOUTH LAKE TAHOE, CA. ONCE CREWS WERE ON SCENE, IT WAS DETERMINED THAT NATURAL GAS WAS BLOWING FROM THE METER SET ASSEMBLY. THE LAKE VALLEY FIRE DEPARTMENT WAS ALREADY ON SCENE AND FIRE DEPARTMENT PERSONNEL WERE ABLE TO SECURE THE FLOW OF GAS UTILIZING THE VALVE ON THE RISER (STOPCOCK). SOUTHWEST GAS PERSONNEL ON SCENE CONDUCTED A LEAK SURVEY AND FOUND NO INDICATION OF BELOW GROUND NATURAL GAS READS. ONCE THE FIRE WAS EXTINGUISHED, A FAILURE WAS DISCOVERED ON A 3/4" STEEL NIPPLE JUST ABOVE THE STOPCOCK. THE APPARENT CAUSE OF THE DAMAGE TO THE METER SET ASSEMBLY WAS SNOW LOAD, BUT THE CAUSE OF THAT LOADING IS UNDER INVESTIGATION. A SUPPLEMENTAL REPORT WILL BE PROVIDED WHEN THAT INVESTIGATION IS COMPLETE. SUPPLEMENT: THE INCIDENT OCCURRED DURING AN EXTREME WEATHER EVENT WITH EXCESSIVE SNOW. THE CAUSE OF THE FAILURE OF THE PIPE NIPPLE WAS THE APPLICATION OF UP TO FOUR SUCCESSIVE DYNAMIC LOADINGS OF SNOW AND/OR ICE FALLING ONTO THE PIPE NIPPLE FROM THE ROOF OF THE RESIDENCE. THE SNOW AND/OR ICE WAS EITHER "NATURAL FORCE DAMAGE," "OTHER OUTSIDE FORCE DAMAGE," OR A COMBINATION OF BOTH. THE PRECISE CAUSE OR CAUSES CANNOT BE DETERMINED DUE TO THE LOSS OF EVIDENCE CAUSED BY THE FIRE AND THE FIRE-FIGHTING EFFORTS.
2025-03-31 10:13 | NO | NO | NO | 20190034 | 32205 | 2019-04-01 14:06 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2019-03-05 11:00 |  |  | 2019 | INTERSECTION OF KENT AVENUE AND BROADWAY | BROOKLYN | KINGS | NY | 11249 | 40.712 | -73.9681 | [9 empty] | 2019-03-05 14:42 | 1239301 |  | NATURAL GAS |  | 1158 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2019-03-05 11:24 |  |  |  | 2019-03-05 11:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 12 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | MECHANICAL PUNCTURE | 6 | 6 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 11800 | 13349.3995196156904 | 36240 | 40998.49479583666272 | 0 | 0 |  |  | 5155 | 5777.388451443569553805774278215223097113 |  | 0 | 53195 | 27853.6904309099207702887139107611548556 | 60125.2827668959226738057742782152230971 | 1 | 0 | 0 |  |  |  |  | 0.3 | 0.33 | 0.43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER'S ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY. THIS INCIDENT WAS DUE TO A REPORT OF CONTRACTOR DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY | 2019-02-19 | NO |  |  | YES | YES |  | YES | [6 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 190590316 | NEW YORK 811 |  | CONTRACT LOCATOR | YES | YES | 7 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER GAS WORK METHODS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER GAS WORK METHODS | 6317703549 | corinne.byrnes@nationalgrid.com | **SUPPLEMENT CREATED 5/28/2019. REVISED NUMBER OF INDIVIDUALS INJURED TO 0 BASED ON INFORMATION AT SITE. WE DO NOT KNOW THE EXTENT OF THE INJURIES, BUT 4 PEOPLE WERE TREATED FOR MINOR INJURIES (MINOR BURNS, SPRAIN). NO FURTHER DETAIL HAS BEEN PROVIDED AND NO UPDATE HAS BEEN PROVIDED TO THE COMPANY REGARDING MORE SERIOUS INJURY TO ANY INDIVIDUAL(S).** AT 11:38, NATIONAL GRID DISPATCH AND SCHEDULE WAS NOTIFIED BY THE FDNY OF A FIRE IN A TRENCH AT THE INTERSECTION OF KENT AVE AND BROADWAY. CUSTOMER METER SERVICES (CMS) WAS DISPATCHED TO THE LOCATION.AND DISCOVERED 12 INCH CAST IRON MAIN LEAKING AND IGNITED INSIDE THE TRENCH. THE ROOT CAUSE OF THE INCIDENT WAS THIRD PARTY DAMAGE AS A RESULT OF CITY/STATE CONSTRUCTION ACTIVITY. THE GAS MAIN WAS MARKED OUT BUT MARK-OUT FAILED TO MARK THE LOCATION OF A TEE CONNECTION AND STUB. THERE WAS A 1 FOOT GAP BETWEEN GAS MAIN AND NEW WATER MAIN. ADDITIONALLY, IT WAS FOUND THAT THE NATIONAL GRID INSPECTOR ON-SITE FAILED TO IDENTIFY THE TEE THAT WAS ON THE PRINT IDS BUT NOT ON THE MARKOUT. THE CONTRACTOR HIT THE STUB PIECE WHILE EXCAVATING WITH THE BACKHOE AND THE GAS MAIN IGNITED. FIELD OPERATIONS LOCATED THE DAMAGE AND SECURED THE MAIN ON EITHER SIDE OF THE FIRE ON 3/5/2019 AT 20:00. THERE WERE 4 INJURIES ON THE LOCATION (3 MALES WERE TAKEN TO CORNELL MEDICAL CENTER FOR FIRE RELATED INJURIES AND 1 MALE WAS TAKEN TO WYCKOFF HOSPITAL FOR A NON-FIRE RELATED INJURY). FIELD OPERATIONS SECURED THE MAIN ON EITHER SIDE OF THE FIRE AT (3/5/2019 AT APPROX. 20:00) USING STOPPER AND CREATING A FIREWALL, CAUSING THE TEMPORARY INTERRUPTION OF SERVICE TO (1) CUSTOMER. FIELD OPERATIONS REPLACED A 7 FOOT SECTION OF THE AFFECTED MAIN TO MAKE THE REPAIR. AS A RESULT OF THIS INCIDENT, AN INCIDENT ANALYSIS WAS PERFORMED. AS RECOMMENDED BY PRINCIPLES OF PIPELINE SAFETY MANAGEMENT, ALL FUTURE CITY/STATE CONSTRUCTION DAILY REPORTS WILL NOW INCLUDE DOCUMENTATION FOR THE INSPECTOR TO VERIFY THE GAS MARKOUTS AND PERFORM THE JOB WALK-THROUGH.
2025-03-31 10:13 | NO | NO | NO | 20190035 | 33613 | 2019-04-02 13:53 | SUPPLEMENTAL FINAL | 8170 | ALLIANT ENERGY - INTERSTATE POWER AND LIGHT COMPANY | 200 1ST STREET SE | CEDAR RAPIDS | IA | 52401 | 2019-03-09 13:05 |  |  | 2019 | 401 W. VAN WEISS BOULEVARD | WEST BURLINGTON | DES MOINES | IA | 52655-1535 | 40.8175 | -91.1608 | [9 empty] | 2019-03-11 11:26 | 1239797 |  | NATURAL GAS |  | 37 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2019-03-09 13:10 |  |  |  | 2019-03-09 13:26 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 88000 | 99554.843875100064 | 1100 | 1244.4355484387508 | 2193 | 2480.951961569255004 | 0 | 0 |  |  | 100 | 112.073490813648293963254593175853018373 |  | 0 | 91393 | 42879.2488668100090591627296587926509186 | 103392.3048759217180979632545931758530184 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 190460180 |  |  | CONTRACT LOCATOR | NO | YES | 3238 | EXCAVATION ISSUE | EXCAVATOR FAILED TO PROTECT/SHORE/SUPPORT FACILITIES | [170 empty] | RICHARD A. SUBLETT | SR. MANAGER COMPLIANCE AND OPERATIONAL PERFORMANCE | richardsublett@alliantenergy.com | 319-786-4008 | 319-786-7633 |  |  |  | RICHARD A. SUBLETT | SR. MANAGER COMPLIANCE AND OPERATIONAL PERFORMANCE | 319-786-4008 | richardsublett@alliantenergy.com | ON MARCH 9, 2019 AT 13:10, ALLIANT ENERGY - INTERSTATE POWER & LIGHT (IPL) RECEIVED A CALL FROM A CUSTOMER AT 401 W. VAN WEISS BLVD IN WEST BURLINGTON, IOWA STATING SHE HAD SOME WORK DONE AROUND HER HOUSE AND A CLUMP OF DIRT FELL ON HER GAS METER AND SHE COULD SMELL AND HEAR NATURAL GAS LEAKING. THE CUSTOMER WAS INSTRUCTED TO EVACUATE THE HOUSE. IPL DISPATCHED A SERVICE MECHANIC, WHO ARRIVED ONSITE AT 13:26 TO FIND THE GAS HAD IGNITED. HE IMMEDIATELY REQUESTED ADDITIONAL GAS PERSONNEL FOR ASSISTANCE. POLICE WERE ALREADY ONSITE AND THE FIRE DEPARTMENT ARRIVED SHORTLY AFTER AND SPRAYED WATER ON THE SIDE OF THE HOUSE TO MINIMIZE DAMAGE UNTIL THE GAS COULD BE SHUT OFF. DUE TO THE FROZEN GROUND, HAND DIGGING TO EXPOSE THE SERVICE LINE WAS DIFFICULT. AFTER TWO ADDITIONAL IPL EMPLOYEES ARRIVED WITH A MINI-EXCAVATOR, THE 3/4 INCH STEEL SERVICE LINE WAS EXPOSED AND SQUEEZED OFF AT APPROXIMATELY 14:50, ALLOWING FIREFIGHTERS TO EXTINGUISH THE FIRE. SHORTLY AFTER, THE SERVICE LINE WAS EXPOSED AT THE SERVICE TEE AND WAS CUT OFF AND CAPPED. A BASEMENT CONTRACTOR HAD BEEN PERFORMING EXTERIOR BASEMENT WALL REPAIR WORK AROUND THE PERIMETER OF THE HOUSE AND HAD EXPOSED THE STEEL SERVICE LINE ALONG THE EAST SIDE OF THE HOUSE. IPL IS UNAWARE WHETHER THE CONTRACTOR PROVIDED ANY SUPPORT TO THE EXPOSED SERVICE LINE IN THE EXCAVATION. THERE WAS NO ACTIVE WORK BEING PERFORMED BY THE CONTRACTOR AT THE TIME OF THE INCIDENT. THE TRENCH WALL COLLAPSED ONTO THE SERVICE LINE AND RISER, CAUSING THE THREADS ON THE 3/4 INCH NIPPLE AT THE INLET TO THE SERVICE REGULATOR TO BREAK OFF COMPLETELY. THIS ALLOWED GAS OPERATING AT 55 PSIG TO ESCAPE ALONG THE OUTER BASEMENT WALL. THE GAS WAS IGNITED BY AN UNKNOWN SOURCE, POSSIBLY STATIC OR BY ROCKS BEING BLOWN AROUND BY THE FORCE OF THE GAS. THE INCIDENT WAS NOT IMMEDIATELY REPORTED ON MARCH 9, 2019, AS INITIAL DAMAGE ESTIMATES INDICATED THE DAMAGES WOULD BE LESS THAN $50,000. UPON SEEING REVISED DAMAGE ESTIMATES, THE INCIDENT WAS CALLED INTO THE NATIONAL RESPONSE CENTER ON MARCH 11, 2019. ORIGINAL NRC REPORT NUMBER: 1239797 REVISED NRC REPORT NUMBER: 1239801 (TO MAKE CORRECTION TO AN INCORRECT DATE) 48 HOUR NRC UPDATE NUMBER: 1239986 UPDATE (04/17/2020): -NEW SERVICE LINE TO HOUSE INSTALLED ON 07/22/2019 -REPORT CHANGED TO FINAL.
2025-03-31 10:13 | NO | YES | NO | 20190036 | 32159 | 2019-04-04 16:03 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2019-03-06 13:45 |  |  | 2019 | 2920 VANCE STREET EXTENSION | REIDSVILLE | ROCKINGHAM | NC | 27320 | 36.3528 | -79.6972 | [9 empty] | 2019-03-07 10:47 | 1239453 |  | NATURAL GAS |  | 3.16 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-03-06 13:45 |  |  |  | 2019-03-06 14:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | OTHER | PNG SERVICE | SERVICE |  | 2009 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 181652 | 205503.823859087236656 | 0 | 0 | 0 | 0 |  |  | 3 | 3.36220472440944881889763779527559055118 |  | 0 | 181655 | 85116.6307415136468449448818897637795276 | 205507.1860638116461048188976377952755906 | 0 | 1 | 0 |  |  |  |  | 460 | 460 | 500 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | UTILITY | DIRECTIONAL DRILLING | NATURAL GAS | YES | 190570435 | 811 |  | CONTRACT LOCATOR | YES | YES | 9 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | CHRISTOPHER RANSOME | PIPELINE SAFETY AND COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | CONTRACTOR WAS PERFORMING AN HDD TO INSTALL DISTRIBUTION PIPELINE IN DOT ROW. DRILL HEAD STRUCK CAP THAT WAS INSTALLED AS PART OF A BOX SECTION ON AN INDUSTRIAL SERVICE LINE. TWO PINHOLES WERE MADE IN THE CAP, WHICH CAUSED THE RELEASE OF GAS. THE INDUSTRIAL CUSTOMER WAS PUT ON AN ALTERNATIVE FUEL WHILE GAS MAIN AND SERVICE IN AREA WAS REPAIRED.
2025-03-31 10:13 | NO | NO | NO | 20190037 | 32431 | 2019-04-08 21:24 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-03-09 11:58 |  |  | 2019 | PARKDALE AVENUE AND MILLER AVENUE | ROCHESTER | OAKLAND | MI | 48307 | 42.6865 | -83.1241 | [9 empty] | 2019-04-01 12:03 | 1241570 |  | NATURAL GAS |  | 598 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 2 | 2019-03-09 11:58 |  |  |  | 2019-03-09 12:33 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1962 | [5 empty] | 6 | API 5L | UNKNOWN | STEEL |  |  |  | 0.219 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 56532 | 63954.936749399509296 | 2861 | 3236.663730984787308 | 0 | 0 |  |  | 1662 | 1862.661417322834645669291338582677165354 |  | 0 | 61055 | 29551.8166182990303444645669291338582677 | 69054.2618977071312496692913385826771654 | 0 | 0 | 2 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  |  |  | YES | [8 empty] | YES | INTERFERENCE TESTING | YES | NO |  | YES | NO | [8 empty] | YES | COAL TAR | [21 empty] | 2015-06-19 | NO | [227 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON MARCH 9, 2019 AT APPROXIMATELY 11:58 HOURS CONSUMERS ENERGY WAS NOTIFIED OF AN ODOR OF GAS BY THE PROPERTY OWNER AT 712 PARKDALE AVENUE, ROCHESTER (OAKLAND COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) ARRIVED AT THE PROPERTY AT APPROXIMATELY 12:33 HOURS AND BEGAN PERFORMING A LEAK INVESTIGATION. READINGS WERE DISCOVERED (1.5% LEL) INSIDE THE HOME AT OR NEAR THE FLOOR DRAIN. THE GSW EXPANDED THE LEAK INVESTIGATION AND DISCOVERED 30% GAS READS AT THE SEWER. THE GSW REQUESTED ADDITIONAL ASSISTANCE AND CONTINUED THE INVESTIGATION TO IDENTIFY THE SOURCE OF GAS. ADDITIONAL RESOURCES ARRIVED TO ASSIST WITH INVESTIGATING NEARBY HOMES AND SEWERS. INITIAL READS DISCOVERED DURING THE LEAK INVESTIGATION WERE AS FOLLOWS: 712 PARKDALE, 615 PARKDALE AND 815 MILLER HAD LOW READS RANGING FROM 0.5% TO 1.5% LEL. 702 PARKDALE HAD 30% LEL AND 703 PARKDALE HAD 9% LEL IN THE HOME. PER PROCEDURES, BOTH 702 AND 703 WERE EVACUATED AND DISPATCH NOTIFIED LOCAL UTILITY TO DE-ENERGIZE 702 AND 703 PARKDALE. OUTSIDE GAS READS WERE ALSO DISCOVERED AT THE WALL OF BOTH 702 PARKDALE AVE. (90%) AND 703 PARKDALE AVE. (100%). CONSUMERS ENERGY EMPLOYEES CONTINUED TO PERFORM LEAK PINPOINTING AND CONTINUOUS MONITORING OF THE LOCATION UNTIL THE SOURCE OF GAS WAS IDENTIFIED. THE SOURCE OF GAS WAS DISCOVERED ON MARCH 10, 2019 AT APPROXIMATELY 21:45 HOURS AND WAS DETERMINED TO BE A CORROSION LEAK ON A 6" STEEL END CAP AT THE INTERSECTION OF PARKDALE AVENUE AND MILLER AVENUE. THE LEAK WAS CONTAINED BY INSTALLING A TEMPORARY PLUG AND CE EMPLOYEES REMAINED ON SITE TO MONITOR UNTIL A PERMANENT REPAIR WAS COMPLETED THE END CAP WAS REPLACED ON MARCH 11, 2019 AT APPROXIMATELY 12:00 HOURS AND SERVICE WAS RESTORED TO 702 AND 703 PARKDALE AVENUE AT APPROXIMATELY 16:00 HOURS. GAS SERVICE CONTINUED TO MONITOR THE AREA UNTIL GAS READS IN THE HOUSES, OUTSIDE AERATION SPOTS AND SEWER MAINTAINED ZERO ON MARCH 14, 2019 AT APPROXIMATELY 15:07 HOURS.
2025-03-31 10:13 | NO | YES | YES | 20190038 | 32189 | 2019-04-19 08:51 | SUPPLEMENTAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2019-03-20 16:45 |  |  | 2019 | 718 RIVER RD | GLENDIVE | DAWSON | MT | 59330 | 47.0936 | -104.7589 | [9 empty] | 2019-03-20 17:46 | 1240601 |  | NATURAL GAS |  | 0.01 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 1 | 2019-03-20 17:27 |  |  |  | 2019-03-20 17:00 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 210000 | 237574.05924739788 | 11000 | 12444.355484387508 | 18000 | 20363.490792634104 | 0 | 0 |  |  | 1 | 1.12073490813648293963254593175853018373 |  | 0 | 239001 | 111985.1128952156271469816272965879265092 | 270383.0262593276284829396325459317585302 | 0 | 0 | 2 |  |  |  |  | 42 | 42 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | NUT FOLLOWER |  | COUPLING |  | UNKNOWN |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | FITTING FAILURE |  | YES |  |  |  | OTHER | MECHANICAL NUT FOLLOWER FITTING | NO | [86 empty] | JOSH SANDERS | DIRECTOR OF OPS POLICY AND PROCEDURE | josh.sanders@mdu.com | 701-222-7773 |  |  |  |  | JOSH SANDERS | DIRECTOR OF OPS POLICY AND PROCEDURE | 701-222-7773 | josh.sanders@mdu.com | AT 16:45 ON 3/20/2019 LOCAL MANAGEMENT WAS INFORMED BY EMERGENCY RESPONDERS THAT A POSSIBLE EXPLOSION HAD OCCURRED AT 718 RIVER RD, GLENDIVE, MT. TECHNICIANS WERE DISPATCHED IMMEDIATELY AFTER NOTIFICATION AND UPON ARRIVAL TECHNICIANS BEGAN TO MAKE THE SCENE SAFE. THE TECHNICIANS CONFIRMED THAT AN EXPLOSION HAD OCCURRED AT A PRIVATE RESIDENCE RESULTING IN BURN INJURIES TO A RESIDENT. GAS METER TO THE HOME WAS SHUT OFF. A COMBUSTIBLE GAS INDICATOR WAS USED INSIDE THE HOME, DETECTING A PRESENCE OF NATURAL GAS. THE INVESTIGATION CONTINUED OUTSIDE WITH THE PRESENCE OF GAS BEING FOUND IN SOIL. DURING THIS INVESTIGATION A LEAK WAS DETECTED ON A MECHANICAL NUT FOLLOWER COUPLING ON THE 2IN STEEL MAIN WHICH WAS SECURED AT 04:48 3/21/2019. FOLLOW UP INVESTIGATION PROVED NO INDICATION OF LEAKS ON THE JURISDICTIONAL SERVICE LINE. ADDITIONALLY, TESTING OF CUSTOMER OWNED FACILITIES PROVIDED NO INDICATION OF MATERIAL LEAKS. THE MAIN HAD BEEN INSTALLED IN 1962. NO INDICATIONS OF A LEAK WERE FOUND IN THE PRIOR TWO LEAK SURVEYS, CONDUCTED IN 2014 AND 2018, RESPECTIVELY. IN THE ABSENCE OF ANOTHER IDENTIFIABLE SOURCE, THE LEAKING MECHANICAL FITTING ON THE MAIN MAY HAVE BEEN A SOURCE OF FUEL FOR THE EXPLOSION THAT OCCURRED. HOWEVER, AN IDENTIFIED PATH OF MIGRATION HAS NOT BEEN DETERMINED FOR THE SOURCE OF FUEL TO ENTER THE HOME. EXTREME WINTER TEMPERATURE AND FROST CONDITIONS AT THE MECHANICAL FITTING MAY HAVE AFFECTED SOIL CONDITIONS SURROUNDING THE FITTING ALONG WITH POTENTIAL FOR ABNORMAL CONTRACTION/EXPANSION OF THE FITTING AND PIPE COMPONENTS. A REQUIRED FOLLOW UP REPORT #1240787 WAS SUBMITTED AS THE 48 HOUR FOLLOW UP REPORT.
2025-03-31 10:13 | YES | NO | NO | 20190039 | 33044 | 2019-04-26 12:47 | SUPPLEMENTAL FINAL | 13299 | NEW JERSEY NATURAL GAS CO | 1415 WYCKOFF ROAD | WALL | NJ | 07719 | 2019-03-29 13:37 |  |  | 2019 | 44 BONAIRE DRIVE | BERKELEY TOWNSHIP | OCEAN | NJ | 08721 | 39.9777 | -74.2618 | [9 empty] | 2019-04-01 09:04 | 1241551 |  |  |  | 10.64 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2019-03-29 13:37 |  |  |  | 2019-03-29 13:51 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 11 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1988 | [5 empty] | 0.5 | ASTM D2513 | PHILLIPS DRISCOPIPE, INC. | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 3408 | OTHER | [8 empty] | FIRE DAMAGED THE GAS SERVICE LINE. | CLASS 3 LOCATION | 100000 | 113130.5044035228 | 10 | 11.31305044035228 | 1338 | 1513.686148919135064 | 0 | 0 | NON-OPERATOR PRIVATE PROPERTY DAMAGE COST ESTIMATED TO BE MORE THAN $100,000. |  | 102 | 114.31496062992125984251968503937007874 |  | 0 | 101450 | 47592.618950453479588125984251968503937 | 114769.8185635122086038425196850393700787 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | MOBEEN KHAN | DIRECTOR - SYSTEM ENHANCEMENT | mukhan@njng.com | 732-919-8035 | 732-919-0936 |  |  |  | MOBEEN KHAN | DIRECTOR - SYSTEM ENHANCEMENT | 732-919-8035 | mukhan@njng.com | ON MARCH 29, 2019, NJNG RESPONDED TO A HOUSE FIRE AT 44 BONAIRE DRIVE, BERKELEY TOWNSHIP CALLED INTO DISPATCH BY THE FIRE DEPARTMENT. FIRE DEPARTMENT OFFICIALS EVACUATED 2 PEOPLE FROM NEARBY HOMES WITHIN THE VICINITY OF THE AFFECTED HOME. THE RESIDENCE AT 44 BONAIRE DRIVE WAS VACANT. THE FIRE CHIEF AND INVESTIGATOR PROVIDED NJNG THE FOLLOWING PRELIMINARY FINDINGS: HEAVY HYDROCARBONS OR ACCELERANT IN THE AREA. AT THE TIME THE INITIAL INCIDENT REPORT WAS PREPARED, THE CAUSE OF FIRE WAS STILL UNDER INVESTIGATION. THE NATURAL GAS SERVICE FEEDING THIS RESIDENCE WAS A 1/2" HDPE LINE OPERATING AT 55 PSI. THE METER LOCATION WAS OUTSIDE LEFT, APPROXIMATELY 15 FEET FROM CORNER OF HOUSE. NEITHER THE METER OR ABOVEGROUND PIPING WERE COMPROMISED; HOWEVER, A HOLE WAS NOTED AT THE 6 O'CLOCK POSITION ON THE SERVICE LINE. IN OR ABOUT JULY 2019, THE BERKELEY TOWNSHIP POLICE CHARGED THE NEIGHBORING PROPERTY OWNER WITH CRIMINAL MISCHIEF FOR RECKLESSLY OR NEGLIGENTLY DAMAGING PROPERTY WHILE EMPLOYING OR HANDLING FIRE, "BY POURING GASOLINE INTO A GROUNDHOG HOLE AND CAUSING A STRUCTURE FIRE AT 44 BONAIRE DRIVE IN BERKELEY TOWNSHIP." THE NEIGHBOR IS APPROXIMATELY 80 YEARS OLD. DURING OUR DISCUSSIONS WITH THE PROSECUTOR, SHE ADVISED THAT THEIR EXPERT HAS OPINED THAT THE GAS LINE WAS ATTACKED BY FIRE, WHICH IS JUST WHAT OUR EXPERTS SAY. A REVIEW OF NJNG RECORDS REVEAL THERE IS NO HISTORY OF A GAS LEAK OR LEAKS AT THE PROPERTY OR IN THE NEIGHBORHOOD IN THE SEVERAL YEARS BEFORE THE INCIDENT. BASED ON THE FOREGOING, WE CONCLUDE THAT THE GAS PIPE WAS COMPROMISED AS A RESULT OF THE NEIGHBOR POURING GASOLINE INTO THE GROUNDHOG HOLE CAUSING A FIRE.
2025-03-31 10:13 | NO | YES | NO | 20190040 | 32523 | 2019-04-26 12:48 | SUPPLEMENTAL FINAL | 13299 | NEW JERSEY NATURAL GAS CO | 1415 WYCKOFF ROAD | WALL | NJ | 07719 | 2019-04-02 11:32 |  |  | 2019 | 2313 ROUTE 547 | MANCHESTER | OCEAN | NJ | 08759 | 40.0162 | -74.3102 | [9 empty] | 2019-04-03 13:52 | 1241762 |  | NATURAL GAS |  | 12.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 4 | 2019-04-02 11:32 |  |  |  | 2019-04-02 11:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 61 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1988 | [5 empty] | 12 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 0.1 | 0.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 91658 | 103693.157726180928024 | 38452 | 43500.941553242587056 | 0 | 0 |  |  | 123 | 137.850393700787401574803149606299212598 |  | 0 | 130233 | 61090.9010568034845487401574803149606299 | 147331.9496731243024815748031496062992126 | 2 | 0 | 0 |  |  |  |  | 52 | 52 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | NATURAL GAS | YES | 190601126 |  |  | CONTRACT LOCATOR | YES | YES | 9 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | MOBEEN KHAN | DIRECTOR - SYSTEM ENHANCEMENT | mukhan@njng.com | 732-919-8035 | 732-919-0936 |  |  |  | MOBEEN KHAN | DIRECTOR - SYSTEM ENHANCEMENT | 732-919-8035 | mukhan@njng.com | ON APRIL 2, 2019, NJNG RESPONDED TO AN ODOR CALLED IN BY OCEAN COUNTY SHERRIFF'S OFFICE AT 11:32 A.M. UPON ARRIVAL AT 2313 ROUTE 547, MANCHESTER AT 11:40 A.M., GAS-IN-AIR PERCENTAGES WERE CONFIRMED WITHIN THE VICINITY OF AN EXCAVATOR INSTALLING A NEW GAS MAIN. FURTHER INVESTIGATION CONFIRMED THE EXCAVATOR DAMAGED A GAS FACILITY WHILE HORIZONTAL DIRECTIONALLY DRILLING THE NEW GAS MAIN. NJNG CONFIRMED THE EXCAVATOR DAMAGED THE 12-INCH STEEL MAIN LOCATED UNDER THE ROADWAY WHILE REAMING WHICH CREATED A DENT AND SMALL MECHANICAL PUNCTURE IN THE PIPELINE. THE EXCAVATOR HAD A VALID ONE CALL TICKET AND THE 12-INCH STEEL MAIN WAS PROPERLY LOCATED. NJNG CLOSED VALVES TO SHUT DOWN GAS FLOW TO THE DAMAGED FACILITY. THE DAMAGED SECTION WAS BLOWN DOWN AND REPLACED ON APRIL 3, 2019. THERE WERE NO INJURIES OR FATALITIES AND THE ESCAPING NATURAL GAS DID NOT IGNITE OR EXPLODE AS A RESULT OF THIS DAMAGE. THIS WAS A REPORTABLE INCIDENT AS THE OPERATOR EMERGENCY RESPONSE AND REPAIR COSTS EXCEEDED $50,000.
2025-03-31 10:13 | NO | YES | YES | 20190041 | 32715 | 2019-04-26 16:02 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2019-03-27 07:21 |  |  | 2019 | 2805 HOMESTEAD NORTH | PONCA CITY | KAY | OK | 74604 | 36.7331 | -97.0442 | [9 empty] | 2019-03-27 18:14 | 1241237 |  | NATURAL GAS |  | 0 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 0 | 2019-03-27 07:21 |  |  |  | 2019-03-27 07:46 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 40 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1976 | [5 empty] | 2 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | 10000 | 11313.05044035228 | 500 | 565.652522017614 | 15572 | 17616.682145716570416 | 0 | 0 |  |  | 0 | 0 |  | 0 | 26072 | 12216.103905346506744 | 29495.385108086464416 | 0 | 0 | 4 |  |  |  |  | 47 | 47 | 52 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | STRESS-INDUCED CRACK NEAR PIPE JOINT. |  |  |  |  | YES | [9 empty] | YES |  |  |  | OTHER | STRESS-INDUCED CRACK NEAR PIPE JOINT. | NO | [86 empty] | SETH SLIFER | SR. COMPLIANCE SPECIALIST | seth.slifer@oengas.com | 405-248-7018 |  |  |  |  | MEGHAN BOOKER | DIRECTOR ENGINEERING | 405-530-2501 | meghan.booker@onegas.com | THE CAUSE OF THE INCIDENT WAS NOT A CONSTRUCTION DEFECT AS ORIGINALLY THEORIZED. THE POST-INCIDENT LABORATORY EXAMINATION OF THE PIPE AND WELD TOOK PLACE MAY 14-15, 2019. THE PRELIMINARY REPORT FROM THE EXPERT INDICATED THAT THE BOND AT THE PIPE JOINT DID NOT HAVE ANY EVIDENCE OF DE-BONDING AND HAD COMPARABLE TENSILE STRENGTH TO EXEMPLAR FUSION BOND JOINTS. THE LEAK THAT OCCURRED AT THE PIPE JOINT APPEARS TO BE FROM A STRESS-INDUCED CRACK NEAR THE PIPE JOINT.
2025-03-31 10:13 | NO | NO | NO | 20190043 | 32213 | 2019-04-29 08:14 | SUPPLEMENTAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY | CANONSBURG | PA | 15317 | 2019-03-28 20:53 |  |  | 2019 | OLD TRAIL AND PLANK RD | SHREWSBURY | YORK | PA | 17361 | 39.7848 | -76.6724 | [9 empty] | 2019-03-29 00:13 | 1241336 |  | NATURAL GAS |  | 4200 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-03-28 20:53 |  |  |  | 2019-03-28 21:27 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 3 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1963 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | PIPELINE WAS SEVERED BY A FARMERS PLOW | CLASS 2 LOCATION | 0 | 0 | 9950 | 11256.4851881505186 | 11000 | 12444.355484387508 | 0 | 0 |  |  | 13986 | 15674.5984251968503937007874015748031496 |  | 0 | 34936 | 24316.0986461960528350393700787401574803 | 39375.4390977348769937007874015748031496 | 0 | 0 | 1 |  |  |  |  | 52 | 52 | 57 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | FARMER | FARM EQUIPMENT | AGRICULTURE | NO | [5 empty] | YES | 13 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | AGRICULTURAL ACTIVITY EXCLUDED IN PA ONE CALL ACT | [169 empty] | RICHARD BURKE | OPERATIONS COMPLIANCE MANAGER | rburke@nisource.com | 7244166332 |  |  |  |  | MICHAEL DAVIDSON | VICE PRESIDENT AND GENERAL MANAGER | 724-416-6308 | mdavids@nisource.com | AT APPROXIMATELY 7:12 PM ON THURSDAY, MARCH 28TH, A FARMER USING A CULTIVATOR ON THE PROPERTY IN THE VICINITY OF PLANK AND OLD TRAIL RD HIT AND TORE IN HALF A 6" BARE STEEL MAIN LINE. BEFORE REPAIRS COULD BE MADE, 4,200 MCF OF NATURAL GAS WAS LOST. THE FACILITY WAS SHUT DOWN AT 6:05 AM. THE FACILITY WAS THEN ABANDONED.
2025-03-31 10:13 | NO | YES | YES | 20190044 | 33568 | 2019-04-30 17:03 | SUPPLEMENTAL FINAL | 18104 | CPS ENERGY | 500 MCCULLOUGH | SAN ANTONIO | TX | 78215 | 2019-04-01 11:43 |  |  | 2019 | 625 GILLETTE | SAN ANTONIO | BEXAR | TX | 78214 | 29.33 | -98.5169 | [9 empty] | 2019-04-01 15:06 | 1241611 |  | NATURAL GAS |  | 100 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2019-04-01 13:18 |  |  |  | 2019-04-01 13:34 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE |  | 1966 | [5 empty] | 1 | API 5L | UNKNOWN | STEEL |  |  |  | 0.179 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 7800 | 8824.1793434747784 | 6700 | 7579.7437950360276 | 0 | 0 |  |  | 520 | 582.782152230971128608923884514435695538 |  | 0 | 15020 | 7333.120599716872930446194225721784776903 | 16986.7052907417771286089238845144356955 | 0 | 0 | 1 |  |  |  |  | 9 | 9 | 33 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | NUT FOLLOWER |  |  |  | UNKNOWN |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | GROUND MOVEMENT |  |  |  | YES |  |  |  | NO | [86 empty] | MICHAEL FUENTES | DIRECTOR GAS CONSTRUCTION | mrfuentes@cpsenergy.com | 2102191309 |  |  |  |  | MICHAEL FUENTES | DIRECTOR GAS CONSTRUCTION | 2102191309 | mrfuentes@cpsenergy.com | SAN ANTONIO FIRE DEPARTMENT REPORTED THAT A FLASH FIRE OCCURRED AT A TELEPHONE MANHOLE AT 625 GILLETTE ST. IN SAN ANTONIO. CONTRACTOR M&M STRIPING WAS WORKING ON PAINTING A CROSSWALK AND ONE OF THEIR EMPLOYEES WAS USING A PEAR BURNER TO HEAT THE AREA NEAR THE TELEPHONE MANHOLE. A FLASH FIRE OCCURRED AND THE EMPLOYEE SUSTAINED BURNS ON HIS LEGS AND CHEST AREA. CPS ENERGY GAS OPERATIONS PERSONNEL RESPONDED AND CONDUCTED A LEAK INVESTIGATION. A GAS LEAK WAS FOUND APPROXIMATELY 375 FEET AWAY FROM THE TELEPHONE MANHOLE AT A 1" STEEL SERVICE LINE TO A HOME ADDRESS. THE CAUSE OF THE GAS LEAK WAS FOUND TO BE A 1" STEEL COUPLING. CPS ENERGY LEAK CREWS RERAN THE SERVICE LINE AND CONDUCTED AN ADDITIONAL LEAK SURVEY OF THE SURROUNDING AREA. CPS ENERGY HAD EXTERNAL TESTING CONDUCTED AND THE CONCLUSION WAS THAT THE MOST PROBABLE CAUSE OF THE COUPLING LEAK WAS AXIAL MOVEMENT BETWEEN THE PIPE AND THE GASKET CAUSED BY EXTERNAL PIPE FORCES.
2025-03-31 10:13 | NO | YES | YES | 20190045 | 33396 | 2019-05-02 10:47 | SUPPLEMENTAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2019-04-03 01:41 |  |  | 2019 | 214 ROYAL TIGER RD #B | BRECKENRIDGE | SUMMIT | CO | 80424 | 39.4878 | -106.0412 | [9 empty] | 2019-04-03 04:10 | 1241717 |  | NATURAL GAS |  | 30 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 0 | 2019-04-03 01:41 |  |  |  | 2019-04-03 03:21 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1963 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.109 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 0.8 | 0.8 |  | CLASS 3 LOCATION | 63228 | 71530.155324259395984 | 2500 | 2828.26261008807 | 6240 | 7059.34347477982272 | 0 | 0 |  |  | 94 | 105.34908136482939632545931758530183727 |  | 0 | 72062 | 33818.2490153102561522729658792650918635 | 81523.1104904921181003254593175853018373 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT DID NOT AFFECT SYSTEM PARAMETERS MONITORED BY SCADA | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | SNOW/ICE FELL FROM ROOF DAMAGING METER SET. | [154 empty] | DARREN GREEN | GAS DISTRIBUTION ENGINEER | darren.v.green@xcelenergy.com | 303-571-3893 |  |  |  |  | MARK NOLAN | PRINCIPAL ENGINEER | 303-571-3931 | mark.nolan@xcelenergy.com | ON APRIL 3, 2019, AN EXPLOSION OCCURRED AT A RESIDENCE IN BRECKENRIDGE, CO. THE GAS METER SET SUSTAINED SIGNIFICANT DAMAGE, AND IT IS NOT KNOWN IF THE DAMAGE AND GAS RELEASE OCCURRED BEFORE OR AFTER THE EXPLOSION. THE FAILURE ANALYSIS CONCLUDES THAT THE RISER FAILURE WAS DUE TO A SINGLE, DYNAMIC EXTERNAL FORCE. THE MOST LIKELY CAUSE IS ICE FALLING ONTO METER SET. NOTE: RESPONSE A13(B) INDICATES PIPELINE WAS RESTARTED, BUT THE SERVICE IS PERMANENTLY CUT-OFF. IF A NEW GAS SERVICE IS REQUIRED, THE OLD SERVICE WILL NOT BE USED. UPDATED 03-02-2020 TO CHANGE PART G CAUSE TO OTHER OUTSIDE FORCE DAMAGE. THE 48-HR CONFIRMATION NOTICE TO NRC WAS GIVEN #1242183.
2025-03-31 10:13 | NO | NO | NO | 20190046 | 32074 | 2019-05-03 14:52 | ORIGINAL FINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2019-04-04 10:29 |  |  | 2019 | 201 W CHOCOLATE AVENUE | DERRY | DAUPHIN | PA | 17033 | 40.2841 | -76.6544 | [9 empty] | 2019-04-04 22:03 | 1241904 |  | NATURAL GAS |  | 225 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 75 | 2019-04-04 10:29 |  |  |  | 2019-04-04 10:39 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2003 | [5 empty] | 4 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 4 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1000 | 1131.305044035228 | 59000 | 66746.997598078452 | 0 | 0 |  |  | 1000 | 1120.734908136482939632545931758530183727 |  | 0 | 61000 | 29149.9025992447669816272965879265091864 | 68999.0375502501629396325459317585301837 | 223 | 2 | 24 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS INCIDENT OCCURRED AS A RESULT OF A 3RD PARTY EXCAVATION DAMAGE ON A MEDIUM PRESSURE DISTRIBUTION LINE. ACTIONS BY THE CONTROLLER WERE NOT NEEDED TO DETECT OR RESPOND TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | ELECTRIC | YES | 20190864239 |  |  | UTILITY OWNER | YES | YES | 22 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JOHN TOUMEH | SENIOR ENGINEER | jtoumeh@ugi.com | 717 675 4606 |  |  |  |  | KELLY ANN BEAVER | VP ENGINEERING AND OPERATIONS SUPPORT | 6107963601 | kbeaver@ugi.com | ON APRIL 4, 2019 3RD PARTY CONTRACTOR WAS PERFORMING EXCAVATION USING HORIZONTAL DIRECTIONAL DRILLING (HDD) METHODS ALONG THE 200 BLOCK OF WEST CHOCOLATE AVENUE. IN THE PROCESS OF HDD WORK, THE 3RD PARTY CONTRACTOR FAILED TO EXPOSE A PROPERLY MARKED UGI FACILITY IN THE PUBLIC RIGHT OF WAY, THAT HAPPENED TO BE IN THE BORE PATH. THE DRILL SUBSEQUENTLY PIERCED OUR MAIN WHICH WAS PART OF A DISTRIBUTION NETWORK IN A COMMERCIAL AREA. THIS EVENT IS BEING REPORTED AS AN INCIDENT DUE TO THE COST OF THIS REPAIR EXCEEDING THE $50,000 REPORTING THRESHOLD. PLEASE NOTE UGI UPDATED THE NRC ON APRIL 5, 2019 AT APPROXIMATELY 16:16 WITH GAS LOST CALCULATIONS AND THE AMOUNT OF INDIVIDUALS EVACUATED. THE UPDATED NRC NUMBER IS 1241967.
2025-03-31 10:13 | NO | YES | YES | 20190049 | 35879 | 2019-05-10 11:21 | SUPPLEMENTAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2019-04-10 10:06 | EASTERN | YES | 2019 | 115 N DUKE STREET | DURHAM | DURHAM | NC | 27701 | 35.596 | -78.5429 | YES | [8 empty] | 2019-04-10 11:17 | 1242352 |  | NATURAL GAS |  | 36 | 0 | YES | 1 | 0 | 0 | 0 | 1 | 2 | YES | 0 | 0 | 1 | 2 | 2 | 5 | YES | 2019-04-10 10:06 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 36 | YES | 10 | 2019-04-10 09:35 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2019-04-10 09:48 | 2019-04-10 10:03 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 18 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2008 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO | 0.75 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 0.3 | 1.2 | [7 empty] | CLASS 3 LOCATION | 35000000 | 39595676.54123298 | 24381 | 27582.348278622893868 | 15542 | 17582.742994395513576 | 0 | 0 | UNKNOWN. INVESTIGATION IS ONGOING. | 4.3056 | 155 | 173.713910761154855643044619422572178478 | 0 | 0 | 35040078 | 16418208.41735996954965315223097112860892 | 39641015.34641675956229964304461942257218 | 20 | 0 | 0 | 18 | 2 | 6 | 20 | 58 | 58 | 60 | 192.619(A)(2) | 2008-01-29 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 2.4 |  | YES | YES | YES | NO | NO | OTHER | NOTIFICATION FROM EXCAVATOR VIA THEIR NC-811 NOTIFICATION |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | WHILE THERE ARE TWO SCADA MONITORING POINTS ON THE DISTRIBUTION SYSTEM, BOTH ARE LOCATED ON LARGER DIAMETER FEEDER MAINS APPROXIMATELY 2 MILES UPSTREAM; THE VOLUME OF GAS LOST WAS INCONSEQUENTIAL VS. THE LINE-PACK AND DELIVERY CAPACITIES IN THESE FEEDER MAINS SUCH THAT THERE WAS NOT A SIGNIFICANT OR CORRELATING RESULTANT PRESSURE DROP AT THESE POINTS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 190931483 |  |  | CONTRACT LOCATOR | YES | UNKNOWN/OTHER |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JERAMY FREE | ENGINEER III - PIPELINE COMPLIANCE | jeramy.free@dominionenergy.com | 803-260-3602 |  | MARTIN WOLFE | martin.wolfe@dominionenergy.com | 919-598-7406 | SCOTT SWINDLER | DIRECTOR - GAS OPERATIONS CONSTRUCTION AND MAINT | 704-810-3230 | scott.swindler@dominionenergy.com | REVISION TO ORIGINAL REPORT: FINAL REPORT, D2A UPDATED TO $35,000,000, D2E UPDATED TO $35,039,922.69. DUE TO FORM TEMPLATE UPDATES, INJURED PERSONS NOT IN A10 WERE ADDED TO D4 AND D5, ADDED INFORMATION TO A8, A21A, A21B, B3B, C3C, C3D, C3F, E3A, E3B, E3C, E5, AND E6. PUBLIC SERVICE COMPANY OF NORTH CAROLINA, INCORPORATED D/B/A NAME IS DOMINION ENERGY NORTH CAROLINA. PSNC IS USED IN THIS SUPPLEMENTAL REPORT TO BE CONSISTENT WITH THE ORIGINAL REPORT. ON THE MORNING OF APRIL 10, 2019, A THIRD-PARTY TELECOMMUNICATIONS CONTRACTOR (OPTIC CABLE TECHNOLOGY LLC), WHILE IN THE PROCESS OF BORING NEW FACILITIES VIA HORIZONTAL DIRECTIONAL DRILLING ALONG NORTH DUKE STREET IN DURHAM, NC, DAMAGED BELOW-GROUND SERVICE LINE PIPING IN PSNCS NATURAL GAS SYSTEM. OPTIC CABLE TECHNOLOGY'S THREE-PERSON CREW STRUCK AND DAMAGED THE SERVICE LINE FEEDING THE STRUCTURE AT 115 NORTH DUKE STREET AT APPROXIMATELY 9:06AM. OPTIC CABLE TECHNOLOGY'S CREW DID NOT CALL 911 BUT NOTIFIED NC-811, THE STATE'S ONE-CALL OFFICE, OF THE DAMAGE AT APPROXIMATELY 9:31AM. NC-811 AUTOMATICALLY GENERATED A DAMAGE TICKET, WHICH WAS DELIVERED TO PSNC AT APPROXIMATELY 9:35AM. AN ORDER WAS AUTOMATICALLY DISPATCHED TO PSNC'S FIRST RESPONDER AT APPROXIMATELY 9:36AM. THE FIRST RESPONDER REVIEWED THE TICKET AT APPROXIMATELY 9:43AM AND BEGAN HEADING TO THE SITE. PSNC RECEIVED A CALL FROM 911 AT APPROXIMATELY 9:48AM, NOTING THAT THE FIRE DEPARTMENT WAS ALREADY ON THE SCENE. PSNC'S DISPATCH CONTACTED THE FIRST RESPONDER EN ROUTE TO ADVISE HIM OF A GAS ODOR AND A DAMAGED LINE AT 115 NORTH DUKE STREET. THE FIRE DEPARTMENT ISSUED A COMBINATION OF EVACUATION AND SHELTER IN PLACE ORDERS AT APPROXIMATELY 9:58AM. PSNC'S FIRST RESPONDER ARRIVED AT APPROXIMATELY 10:03AM. BETWEEN HIS ARRIVAL AND APPROXIMATELY 10:06AM, PSNC'S FIRST RESPONDER AS WELL AS PSNC'S DISPATCH CONTACTED ADDITIONAL PSNC RESOURCES TO ASSIST WITH SECURING AND MAKING THE GAS LEAK SAFE. AT APPROXIMATELY 10:06AM, THE STRUCTURE AT 115 NORTH DUKE STREET EXPLODED. BETWEEN 10:26AM AND 10:50AM, ADDITIONAL PSNC EMPLOYEES, INCLUDING A CONSTRUCTION CREW, ARRIVED AT THE SITE. CREWS CONVENED AT THE INCIDENT COMMAND CENTER TO EVALUATE OPTIONS TO SHUT OFF THE GAS FLOW. BY 11:05AM, THE CREWS IDENTIFIED THE PROPER VALVE, SECURED THE NECESSARY TOOLS, AND, AT APPROXIMATELY 11:10AM, SHUT OFF GAS FLOW TO THE IMPACTED AREA BY CLOSING A VALVE LOCATED APPROXIMATELY THREE BLOCKS FROM THE SCENE. THE EXPLOSION ALSO SEVERELY INJURED A MEMBER OF OPTIC CABLE TECHNOLOGY'S CREW, THE OWNER/OPERATOR OF PS SPLICING LLC (WHICH HIRED OPTIC CABLE TECHNOLOGY TO PERFORM THE HORIZONTAL DIRECTIONAL DRILLING WORK), PSNC'S FIRST RESPONDER, AND A FIREFIGHTER. AN ESTIMATED 25 PEOPLE WERE INJURED IN THE EXPLOSION AND TAKEN TO LOCAL AREA HOSPITALS, AND 5 INDIVIDUALS WERE REPORTEDLY ADMITTED. PSNC'S FIRST RESPONDER DIED IN THE HOSPITAL ON APRIL 25, 2019 AS A RESULT OF INJURIES THAT HE SUSTAINED IN THE EXPLOSION. THE EXPLOSION KILLED THE OCCUPANT OF THE STRUCTURE AT 115 NORTH DUKE STREET. THE EXPLOSION RESULTED IN THE STRUCTURES AT 115 NORTH DUKE STREET AND 111 NORTH DUKE STREET BEING CONDEMNED BY THE DURHAM FIRE DEPARTMENT. BOTH STRUCTURES HAVE SINCE BEEN DEMOLISHED. APPROXIMATELY 21 BUILDINGS IN TOTAL WERE REPORTEDLY DAMAGED BY THE EXPLOSION. PSNC'S INVESTIGATION HAS REVEALED THAT THE SERVICE LINE TO THE STRUCTURE AT 115 NORTH DUKE STREET WAS STRUCK AND DAMAGED DURING OPTIC CABLE TECHNOLOGY'S HORIZONTAL DIRECTIONAL DRILLING WORK. APPROXIMATELY 1 HOUR LATER, AND ONLY 3 MINUTES AFTER THE ARRIVAL OF PSNC'S FIRST RESPONDER TO THE SCENE, THE ESCAPING GAS FROM THE DAMAGED SERVICE LINE IGNITED AND RESULTED IN THE EXPLOSION. PSNC'S UNDERGROUND FACILITIES, INCLUDING THE SERVICE LINE, WERE ACCURATELY LOCATED AND MARKED BY PSNC'S CONTRACTOR (SOUTHERN CROSS INC.) PRIOR TO THE DATE OF THE EXPLOSION, BUT OPTIC CABLE TECHNOLOGY'S CREW FAILED TO POT-HOLE AND VERIFY THE LOCATION OF THE SERVICE LINE UNDER THE SIDEWALK AS PART OF THEIR HORIZONTAL DIRECTIONAL DRILLING WORK.
2025-03-31 10:13 | NO | NO | NO | 20190050 | 32594 | 2019-05-10 13:02 | SUPPLEMENTAL FINAL | 30967 | GREATER MINNESOTA GAS INC. | 1900 CARDINAL LANE PO BOX 798 | FARIBAULT | MN | 55021 | 2019-04-17 13:17 |  |  | 2019 | 22705 BALSA CIR | PRIOR LAKE | SCOTT | MN | 55372 | 44.6204 | -93.4522 | [9 empty] | 2019-04-17 14:55 | 1243024 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2019-04-17 13:17 |  |  |  | 2019-04-17 13:45 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | METER SET RISER AND SERVICE LINE | 1999 | [8 empty] | OTHER | MULTIPLE | [9 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 1 LOCATION | 50000 | 56565.2522017614 | 7000 | 7919.135308246596 | 3413 | 3861.144115292233164 | 0 | 0 | N/A |  | 4 | 4.48293963254593175853018372703412073491 |  | 0 | 60417 | 28310.8164060557451889265091863517060367 | 68350.0145649327750957585301837270341207 | 0 | 0 | 1 |  |  |  |  | 70 | 70 | 76 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  | ,,, | NO | [218 empty] | TAYLOR LARSON | ENGINEER | tlarson@greatermngas.com | 507-327-8211 |  |  |  |  | TAYLOR LARSON | ENGINEER | 507-327-8211 | tlarson@greatermngas.com | LIGHTNING STRUCK THE GROUND AND/OR THE HOME ADJACENT TO THE NATURAL GAS SERVICE LINE. CURRENT FROM THE LIGHTNING STRIKE TRAVELED THROUGH THE ENTIRE TRACER WIRE ALONG THE SERVICE LINE RESULTING IN A BELOW GROUND LEAK NEAR THE METER SET AND DISINTEGRATION OF THE TRACER WIRE. THE GAS IGNITED RESULTING IN A HOUSE FIRE NEAR THE METER SET. COMPANY RESPONDERS EXCAVATED THE SERVICE LINE NEAR THE MAIN AND SQUEEZED THE PLASTIC LINE TO ELIMINATE THE SOURCE OF GAS. THE NEW PRAGUE FIRE DEPARTMENT PUT OUT THE FIRE. THE SERVICE WAS THEN CUT AND CAPPED. THE LIGHTNING STRIKE MAY HAVE ALSO CAUSED A LEAK IN THE ABOVE GROUND METER SET. IT WAS NOT CLEAR IF A POTENTIAL LIGHTNING STRIKE NEAR THE HOME AND METER SET WAS THE PRIMARY CAUSE OR IF IT WAS DUE TO A POTENTIAL LIGHTNING STRIKE TO THE GROUND AND TRAVELING TO THE METER SET ALONG THE TRACER WIRE.
2025-03-31 10:13 | NO | NO | NO | 20190051 | 32129 | 2019-05-14 16:40 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2019-04-17 00:35 |  |  | 2019 | 1175 E. FLAMINGO ROAD | LAS VEGAS | CLARK COUNTY | NV | 89119 | 36.1141 | -115.138 | [9 empty] | 2019-04-18 08:51 | 1243087 |  | NATURAL GAS |  | 235 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-04-17 01:10 |  |  |  | 2019-04-17 01:10 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 34 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2015 | [5 empty] | 2 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | MECHANICAL PUNCTURE | 4 | 2.4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 79778 | 90253.253803042419384 | 1843 | 2084.995196156925204 | 0 | 0 |  |  | 554 | 620.887139107611548556430446194225721785 |  | 0 | 82175 | 38818.0903420899678448215223097112860892 | 92959.1361383069561365564304461942257218 | 211 | 0 | 453 |  |  |  |  | 28 | 33 | 33 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS LINE WAS DAMAGED BY A THIRD PARTY CONTRACTOR. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | TRENCHER | ELECTRIC | YES | 909100557 |  |  | CONTRACT LOCATOR | YES | YES | 19 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | YVONNE BRODEUR | COMPLIANCE SPECIALIST | yvonne.brodeur@swgas.com | 702-365-2149 | 702-365-2205 |  |  |  | ANTHONY HILLS | DIRECTOR OF GAS OPERATIONS | 702-365-2049 | anthony.hills@swgas.com | SOUTHWEST GAS WAS NOTIFIED ON APRIL 17, 2019 AT 00:35 PST BY LAS VEGAS ELECTRIC OF A DAMAGE THAT OCCURRED ON A 2-INCH PE SERVICE LINE TO 1175 E. FLAMINGO ROAD LOCATED ON MARYLAND PKWY SOUTH OF FLAMINGO RD IN LAS VEGAS, NV. THE FLOW OF GAS TO THE SECTION OF PIPE WAS TAKEN OUT OF SERVICE BY UTILIZING THE VALVE ISOLATION PLAN WHILE REPAIRS WERE COMPLETED, WHICH RESULTED IN AN OUTAGE OF 664 ACTIVE CUSTOMERS. BASED ON COMMUNICATIONS THAT THE PUBLIC UTILITIES COMMISSION OF NEVADA'S REGULATORY OPERATIONS STAFF HAD WITH THE PIPELINE AND HAZARDOUS MATERIALS SAFETY ADMINISTRATION'S ACCIDENT INVESTIGATION DIVISION, PART A, 4 "LOCAL TIME AND DATE OF THE INCIDENT" REFLECTS THE TIME SOUTHWEST GAS WAS NOTIFIED OF A DAMAGE ON THE PIPELINE. AT THE TIME, NO INCIDENT REPORTING CRITERIA WAS MET. PART A, 6: SOUTHWEST GAS NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) TELEPHONICALLY OF THE INCIDENT ON APRIL 18, 2019 AT 08:51 PST, DUE TO INCREASING COSTS ASSOCIATED WITH THE REPAIR AND RELIGHT ACTIVITIES, THAT WOULD POSSIBLY MEET THE $50,000 REPORTING CRITERIA. THE NRC ISSUED REPORT NUMBER 1243087 FOR THE INCIDENT. SOUTHWEST GAS PROVIDED A 48-HOUR UPDATE TELEPHONICALLY TO THE NRC ON APRIL 19, 2019 AT 14:14 PST. THE NRC ISSUED REPORT NUMBER 1243222 FOR THE UPDATED REPORT.
2025-03-31 10:13 | NO | NO | NO | 20190052 | 32187 | 2019-05-23 14:44 | ORIGINAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2019-04-29 14:53 |  |  | 2019 | 270 GEORGE WASHINGTON BLVD. | OSWEGO CITY | OSWEGO | NY | 13126 | 43.4536 | -76.5331 | [9 empty] | 2019-04-30 17:14 | 1244229 |  | NATURAL GAS |  | 3650 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-04-29 15:14 |  |  |  | 2019-04-29 15:45 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | FOLLOWING ANNUAL PERFORMANCE TESTING ON RELIEF, RELIEF VALVE LOADING PRESSURE WAS NOT RETURNED TO CORRECT POSITION AND ALLOWED LOADING PRESSURE TO GRADUALLY DECREASE UNTIL MAIN VALVE OPENED AND ALLOW GAS TO VENT. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 8957 | 10038.4225721784776902887139107611548556 |  | 0 | 8957 | 9286.128608923884514435695538057742782152 | 10038.4225721784776902887139107611548556 | 0 | 0 | 0 |  |  |  |  | 85.78 | 85 | 90 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM OPERATORS CORRECTLY AND PROMPTLY IDENTIFIED PROBLEM AND COMMUNICATED IT TO FIELD PERSONNEL. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | INCORRECT OPERATION | INCORRECT VALVE POSITION | [222 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER GAS WORK METHODS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER GAS WORK METHODS | 6317703549 | corinne.byrnes@nationalgrid.com | ON 4/29/2019 A ROUTINE ANNUAL PERFORMANCE TEST WAS CONDUCTED ON A 90 PSIG REGULATOR STATION, GRS-824-228) IN OSWEGO, NY. UPON COMPLETION OF THE RELIEF VALVE TEST, THE CREW LEFT THE STATION. APPROX. 2 HOURS LATER THE RELIEF VALVE BEGAN VENTING GAS. THE RELIEF VALVE ASSOCIATED WITH THAT REGULATOR STATION VENTED GAS FROM APPROX. 2:53 PM (14:53) UNTIL 3:47 PM (15:47). THE ABNORMAL OPERATING CONDITION (AOC) WAS DETECTED BY SCADA AND COMMUNICATED FROM THE CONTROL CENTER TO FIELD PERSONNEL. . FIELD PERSONNEL RETURNED TO THE STATION AND DETERMINED THAT THE RELIEF VALVE PILOT HAD NOT BEEN RETURNED TO THE CORRECT OPERATING POSITION AND THEN CORRECTED THE CONDITION. VOLUME OF VENTED GAS WAS APPROX. 3,650,000 CFH BASED ON CAPACITY OF THE VALVE. OUTLET MAOP OF THE STATION IS 90 PSIG. RELIEF VALVE SETTING WAS 94 PSIG (WITH MAXIMUM OF 99 PSIG). NO CUSTOMERS WERE IMPACTED BY THIS RELEASE OF GAS. (NO OUTAGES NOR OVERPRESSURIZATION OCCURRED.)
2025-03-31 10:13 | NO | YES | NO | 20190053 | 32200 | 2019-05-28 11:09 | ORIGINAL FINAL | 15931 | PUBLIC SERVICE CO OF COLORADO | 1800 LARIMER STREET | DENVER | CO | 80202 | 2019-04-30 12:25 |  |  | 2019 | 22555 TREETOP LANE | GOLDEN | JEFFERSON | CO | 80401 | 39.6974 | -105.2547 | [9 empty] | 2019-04-30 13:56 | 1244219 |  | NATURAL GAS |  | 47 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 6 | 2019-04-30 11:37 |  |  |  | 2019-04-30 12:24 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 32 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1994 | [5 empty] | 0.75 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 3 LOCATION | 151010 | 170838.37469975978028 | 6206 | 7020.879103282624968 | 2944 | 3330.562049639711232 | 0 | 0 |  |  | 105 | 117.677165354330708661417322834645669291 |  | 0 | 160265 | 75152.2458666846437530708661417322834646 | 181307.4930180364471886614173228346456693 | 0 | 0 | 5 |  |  |  |  | 56 | 56 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT DID NOT RESULT IN PRESSURES OUT SIDE NORMAL RANGES OR ANY ALARMS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | HAND TOOLS | ELECTRIC | NO | [5 empty] | YES | 4 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | KATHERINE FUHR | GAS DISTRIBUTION ENGINEER | katherine.fuhr@xcelenergy.com | 303-571-3365 |  |  |  |  | MARK NOLAN | PRINCIPAL ENGINEER | 303-571-3931 | mark.nolan@xcelenergy.com | THE LOCAL FIRE DEPARTMENT NOTIFIED OUR DISPATCH OF A GAS LEAK. THE COMPANY RESPONDER HAD JUST ARRIVED WHEN THE EXPLOSION OCCURRED. THE FIRE DEPARTMENT HAD ALREADY EVACUATED OCCUPANTS AND NO INJURIES WERE SUFFERED. THE GAS LEAK WAS CAUSED BY A THIRD PARTY EXCAVATOR INSTALLING AN ELECTRIC GROUND ROD. PLEASE NOTE RESPONSE TO A13B INDICATES THAT SERVICE TO STRUCTURE WAS INITIALLY SQUEEZED OFF AND THEN PERMANENTLY CUT-OFF. IF AND WHEN SERVICE IS RESUMED TO THIS ADDRESS, A NEW SERVICE WILL BE INSTALLED. PLEASE NOTE ORIGINAL NRC REPORT NUMBER IS 1244219. REPORT WAS CORRECTED TO A PIPELINE INCIDENT AND ISSUED NRC NUMBER 1244222.
2025-03-31 10:13 | NO | YES | NO | 20190054 | 32226 | 2019-05-31 15:34 | ORIGINAL FINAL | 11032 | SPIRE MISSOURI INC. EAST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2019-05-01 00:08 |  |  | 2019 | 3000 REGIS DR | FRONTENAC | ST. LOUIS COUNTY | MO | 63131-2528 | 38.6351 | -90.4328 | [9 empty] | 2019-05-01 08:49 | 1244264 |  | NATURAL GAS |  | 4.93 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2019-05-01 00:08 |  |  |  | 2019-05-01 00:31 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | LIGHTNING STRIKE CREATED HOLE | [5 empty] | CLASS 3 LOCATION | 150000 | 169695.7566052842 | 642 | 726.297838270616376 | 500 | 565.652522017614 | 0 | 0 |  |  | 23 | 25.77690288713910761154855643044619422572 |  | 0 | 151165 | 70841.8252173042445145774278215223097113 | 171013.4838684595694836115485564304461942 | 0 | 0 | 1 |  |  |  |  | 21 | 21 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROLLER(S) ACTIONS DID NOT RESULT IN ANY ABNORMAL PIPELINE OPERATION OR PRESSURES THAT CAUSED OR CONTRIBUTED TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  |  |  |  | CRAIG HOEFERLIN | VP OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | ON MAY 1, 2019, LIGHTING STRUCK THE NATURAL GAS REGULATOR AT 3000 REGIS DRIVE RESULTING IN A SMALL LEAK AND FIRE AT THE METER SET. THE STRUCTURE WAS ON FIRE WHEN THE FIRE DEPARTMENT ARRIVED. THE FIRE DEPARTMENT EXTINGUISHED THE FIRE, AND THE GAS SERVICE LINE WAS ABANDONED. NRC INCIDENT REPORT WAS UPDATED ON MAY 3, 2019 AT 12:05, REPORT NUMBER 1244537.
2025-03-31 10:13 | NO | YES | NO | 20190056 | 32507 | 2019-06-05 17:53 | SUPPLEMENTAL FINAL | 12876 | DOMINION ENERGY UTAH/WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2019-05-06 12:18 |  |  | 2019 | 16840 N 3000 E | MORONI | SAN PETE | UT | 84646 | 39.5178 | -111.5822 | [9 empty] | 2019-05-06 15:57 | 1244845 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2019-05-06 13:04 |  |  |  | 2019-05-06 13:04 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | UNKNOWN | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | UNDETERMINED THROUGH INVESTIGATION. | CLASS 3 LOCATION | 200000 | 226261.0088070456 | 300 | 339.3915132105684 | 1000 | 1131.305044035228 | 0 | 0 |  |  | 0 | 0 |  | 0 | 201300 | 94319.6423805711801 | 227731.7053642913964 | 0 | 0 | 1 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | LAUREN SKUFCA | ENGINEER-PIPELINE COMPLIANCE | lauren.l.skufca@dominionenergy.com | 8013243746 |  |  |  |  | REID HESS | MANAGER-GAS OPERATIONS | 8013243374 | reid.hess@dominionenergy.com | ON MAY 6, 2019 DOMINION ENERGY UTAH (DEU) WAS NOTIFIED OF A HOUSE FIRE AT 16840 N 3000 E, MORONI, UTAH. DEU SENT A TECHNICIAN TO THE SITE. UPON ARRIVAL THE TECHNICIAN NOTED THAT THERE WAS AN EXPLOSION FROM THE INSIDE OF THE HOME. THE METER WAS NOT ACCESSIBLE SO OUR TECHNICIAN TOOK MEASURES TO CUT AND CAP THE SERVICE LINE TO SECURE THE GAS SERVICE. THE MAIN AND SERVICE LINE WERE LEAK DETECTED AND NO GAS WAS DETECTED. DUE TO THE NATURE OF THE HOME'S LOCATION AND THE LOCAL FIRE DEPARTMENT'S RESOURCES, THE STATE FIRE INVESTIGATOR CHOSE TO LET THE FIRE BURN. THE HOME WAS A TOTAL LOSS (ESTIMATED $200K). AN EYE WITNESS STATED TO DEU EMPLOYEES THAT WHEN HE ARRIVED THE FIRE APPEARED TO BE ON THE WEST SIDE OF THE HOME. WITNESS WENT TO THE NORTH SIDE WITH THE INTENTION OF SHUTTING OFF THE GAS METER AS A PRECAUTION. WITNESS STATED FLAMES WERE ROLLING OUT OF THE NORTH SIDE OF THE HOME AT THAT TIME AND IT WAS TOO HOT TO GET TO THE METER. WITNESS WAS UNABLE TO SHUT THE VALVE OFF. DEU EMPLOYEE ASKED IF AT THE TIME THE WITNESS WAS TRYING TO SHUT OF THE GAS, WHETHER OR NOT THE METER WAS INVOLVED IN THE FIRE. WITNESS STATED THERE WAS NO FIRE AT THE METER. WITNESS STATED THERE WAS NO FIRE NEAR THE METER UNTIL AFTER THE NORTH WALL OF THE HOME FELL ON THE METER. DEU PRESSURE TESTED THE BURIED SERVICE LINE AFTER THE FIRE WAS OUT. THE TEST PASSED. DEU AND UTAH PIPELINE SAFETY REVIEWED THE METER EVIDENCE ON JUNE 17, 2019. DEU CONDUCTED AN ADDITIONAL PRESSURE TEST OF THE REMAINING SECTION OF SERVICE LINE/RISER DURING THE EVIDENCE REVIEW AND IT PASSED. THE INVESTIGATIVE REPORT FROM THE UTAH STATE FIRE MARSHAL STATES "IT IS THE OPINION OF THIS INVESTIGATOR THAT THIS WAS A NATURAL GAS EXPLOSION. IT WAS NOT POSSIBLE TO DETERMINE THE CAUSE OR LOCATION OF THE GAS LEAK OR THE IGNITION SOURCE THAT IGNITED THE GAS."
2025-03-31 10:13 | NO | YES | YES | 20190057 | 32555 | 2019-06-08 16:41 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2019-05-10 11:45 |  |  | 2019 | 490 CRAMERTOWN LOOP | MARTINSVILLE | MORGAN | IN | 46151 | 39.422 | -86.4001 | [9 empty] | 2019-05-10 13:48 | 1245246 |  | NATURAL GAS |  | 77 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 3 | 2019-05-10 11:45 |  |  |  | 2019-05-10 12:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2019 | [5 empty] | 6 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | OTHER | [8 empty] | ADJACENT HDPE PIPE MELTED IN FIRE AND RELEASED GAS | CLASS 2 LOCATION | 0 | 0 | 15000 | 16969.57566052842 | 17000 | 19232.185748598876 | 60000 | 67878.30264211368 | TRUCK, AIR COMPRESSOR, AND FIBER LINE REPAIR |  | 260 | 291.391076115485564304461942257217847769 |  | 0 | 92260 | 43376.3948341525622152230971128608923885 | 104371.4551273564615643044619422572178478 | 0 | 0 | 171 |  |  |  |  | 52 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | FAILURE TO FOLLOW PROCEDURES REMOVING TOOL HANDLE AND NOT REPLACING CUPS AFTER EACH STOP ATTEMPT |  |  | YES |  |  | DECOMMISSIONING | YES | NO, BUT THEY WERE PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | ADAM GILLES | REGIONAL OPERATIONS DIRECTOR | adam.gilles@centerpointenergy.com | 8125688554 |  |  |  |  | ADAM GILLES | REGIONAL OPERATIONS DIRECTOR | 8125688554 | adam.gilles@centerpointenergy.com | ON 5/10/19, MILLER PIPELINE (MPL), THE CONTRACTOR PERFORMING WORK FOR VECTREN, A CENTERPOINT ENERGY COMPANY, WAS ATTEMPTING TO TAP AND STOP A 4" STEEL MAIN ON CRAMERTOWN LOOP IN MARTINSVILLE, INDIANA WHEN THE PIPELINE IGNITED AT APPROXIMATELY 11:45 AM. A VECTREN EMPLOYEE WHO WAS INSPECTING RECEIVED SECOND AND THIRD-DEGREE BURNS ON BOTH ARMS FROM THE INITIAL FLASH FIRE. THE WORK BEING PERFORMED AT THE TIME OF THE INCIDENT WAS THE REPLACEMENT OF 4" STEEL PIPELINE WITH 6" HD PLASTIC PIPELINE. THE 6" HD PLASTIC HAD BEEN GASSED UP AND CONNECTED INTO THE 4" STEEL PIPELINE. WHILE THE CREW WAS ABANDONING THE SECTION OF THE 4" STEEL REPLACED BY THE 6" HD PLASTIC, THE RUBBER STOPPER (SEALING ELEMENT) FAILED AND GAS WAS RELEASED AND IGNITED.
2025-03-31 10:13 | NO | YES | NO | 20190058 | 32536 | 2019-06-12 12:34 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2019-05-13 22:32 |  |  | 2019 | 15563 FELDSPAR DR. | CHINO HILLS | SAN BERNARDINO | CA | 91709-2125 | 33.9708 | -117.7502 | [9 empty] | 2019-05-14 05:55 | 1245573 |  | NATURAL GAS |  | 2270 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-05-13 22:32 |  |  |  | 2019-05-13 23:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1978 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 1.3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 95090 | 107575.79663730983052 | 200 | 226.2610088070456 | 0 | 0 |  |  | 13620 | 15264.4094488188976377952755905511811024 |  | 0 | 108910 | 58768.8515887075632197637795275590551181 | 123066.4670949357737577952755905511811024 | 0 | 0 | 0 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | AUGER | FENCING | YES | 191190876 | USA NORTH |  | UTILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | AUSTIN WALKER | PIPELINE SAFETY COMPLIANCE ADVISOR | awalker4@semprautilities.com | 818-632-8407 |  |  |  |  | AUSTIN WALKER | PIPELINE SAFETY COMPLIANCE ADVISOR | 818-632-8407 | awalker4@semprautilities.com | ON MAY 14, 2019, A THIRD PARTY CONTRACTOR WHILE AUGURING TO INSTALL GUARD RAIL POSTS DAMAGED AN 8-INCH STEEL MAIN CAUSING A GAS LEAK. SOCALGAS COMPANY CREW RESPONDED AND CONTROLLED THE GAS. NO INJURIES OR FURTHER DAMAGE RESULTED FROM THIS INCIDENT. THE 8-INCH STEEL MAIN WAS REPAIRED BY REPLACING A SECTION OF THE PIPE. INVESTIGATION OF THE INCIDENT SHOWED THAT THERE WAS A VALID USA TICKET FOR THE CONTRACTOR AND THE 8-INCH MAIN WAS PROPERLY MARKED. THE CONTRACTOR FAILED TO USE HAND TOOLS WHERE REQUIRED. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE AND ESTIMATED PROPERTY DAMAGE OF $50,000 OR MORE. 8/9/2019 UPDATE: UPDATED PART D (2B.) ESTIMATED COST OF OPERATOR'S PROPERTY DAMAGE & REPAIRS FROM $200,000 TO $95,090. SUBMITTED FINAL REPORT.
2025-03-31 10:13 | NO | NO | NO | 20190059 | 32466 | 2019-06-14 08:38 | SUPPLEMENTAL FINAL | 12420 | MICHIGAN GAS UTILITIES CO | 899 S TELEGRAPH ROAD | MONROE | MI | 48161 | 2019-05-15 13:40 |  |  | 2019 | 408 W. EXCHANGE ST | SPRING LAKE | OTTAWA | MI | 49456 | 43.0756 | -86.2024 | [9 empty] | 2019-05-16 11:09 | 1245847 |  | NATURAL GAS |  | 1773 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 4 | 2019-05-15 13:55 |  |  |  | 2019-05-15 13:58 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 28 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1959 | [5 empty] | 4.5 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.237 | [6 empty] | OTHER | [8 empty] | BULLDOZER KNOCKED A TEE OFF THE MAIN. THE HOLE WAS 3/8" DIAMETER | CLASS 3 LOCATION | 0 | 0 | 71002 | 80324.920736589258456 | 8178 | 9251.812650120094584 | 0 | 0 |  |  | 6102 | 6838.724409448818897637795275590551181102 |  | 0 | 85282 | 43426.2169140386897418897637795275590551 | 96415.4577961581719376377952755905511811 | 1 | 0 | 9 |  |  |  |  | 352 | 350 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | GRADER/SCRAPER | SEWER (SANITARY/STORM) | YES | 90160331 |  |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | NATHAN LEE | COMPLIANCE SUPERVISOR | nathan.lee@michigangasutilities.com | 517-278-3524 | 517-278-3528 |  |  |  | NATHAN LEE | COMPLIANCE SUPERVISOR | 517-278-3524 | nathan.lee@michigangasutilities.com | 3/4' STEEL SERVICE TEE ATTACHED OUR 4' HIGH PRESSURE STEEL GAS MAIN AT 408 W EXCHANGE WAS BROKE OFF OF THE GAS MAIN BY THE BLADE OF A BULLDOZER WHILE THE AREA WAS BEING BACKFILLED BY THE WEST MICHIGAN DIRTWORKS ROAD CONSTRUCTION CREW AT APPROX. 1:45PM ON 5/15/19. DAMAGING PARTY CALLED AN MGU EMPLOYEE DIRECTLY AT 1:43PM TO NOTIFY OF DAMAGE. DAMAGING PARTY THEN CALLED THE MGU GAS EMERGENCY # AT 1:55PM. TEN NEARBY HOUSES DOWNWIND OF THE DAMAGE WERE EVACUATED BY EMERGENCY RESPONDERS AND MGU EMPLOYEES AS A SAFETY PRECAUTION. IT WAS DECIDED THE BLOWING GAS WAS ESCAPING INTO THE ATMOSPHERE WAS NOT PRESENTING AN IMMEDIATE DANGER AND MGU AND KPI WOULD PROCEED WITH INSTALLING A PERMANENT BYPASS AROUND THE DAMAGE LOCATION. DURING THE COURSE OF THIS REPAIR, MGU EMPLOYEES WERE ROUTINELY CHECKING GAS CONCENTRATION LEVELS IN THE AIR AND BUILDINGS DOWNWIND OF THE BLOWING GAS. AT APPROX. 9:15AM ON FRIDAY 5/17/19, THE STOPPERS WERE SET AND THE BLOWING GAS WAS STOPPED. A SERVICE TECH ARRIVED ON SITE AT APPROX. 1PM AND BEGAN TURNING ON GAS TO THE CUSTOMERS THAT WERE TURNED OFF AS A SAFETY PRECAUTION. THE ENTIRE PROJECT WAS COMPLETED AT APPROX. 6PM ON FRIDAY 5/17/19. ORIGINAL NRC REPORT NUMBER IS 1245847, REVISED NRC REPORT NUMBER IS 1246181.
2025-03-31 10:13 | NO | YES | NO | 20190060 | 33124 | 2019-06-18 17:59 | SUPPLEMENTAL FINAL | 32513 | AMEREN ILLINOIS COMPANY | 10 EXECUTIVE DR. | COLLINSVILLE | IL | 62234 | 2019-05-16 11:25 |  |  | 2019 | 20275 N OLD CENTRALIA LN | DIX | JEFFERSON | IL | 62830 | 38.4192 | -88.9917 | [9 empty] | 2019-05-18 15:33 | 1246077 |  | NATURAL GAS |  | 7040 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 1 | 2019-05-16 11:25 |  |  |  | 2019-05-16 11:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 41 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2018 | [5 empty] | 0.75 | ASTM A106 | MICHIGAN SEAMLESS TUBE | STEEL |  | SEAMLESS | SEAMLESS | 0.113 | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 1 | 0.7 |  | CLASS 1 LOCATION | 0 | 0 | 37522 | 42448.827862289825016 | 155412 | 175818.379503602853936 | 0 | 0 |  |  | 25013 | 28032.9422572178477690288713910761154856 |  | 0 | 217947 | 116331.8440236003867694435695538057742782 | 246300.1496231105267210288713910761154856 | 0 | 0 | 1 |  |  |  |  | 700 | 704 | 720 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | WHILE GAS CONTROL DOES MONITOR THE ADJACENT PRESSURE SYSTEM, IT WOULD NOT DETECT THE RATE OF GAS RELEASE FROM THIS 3/4" SERVICE WHICH WAS PULLED APART DURING THE DAMAGE. | [12 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO |  |  |  |  | YES | [9 empty] | CONTRACTOR | BACKHOE/TRACKHOE | NATURAL GAS | YES | 1283576 | ILLINOIS - JULIE |  | CONTRACT LOCATOR | NO | YES | 23 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | JOHN BOZARTH | DIRECTOR PIPELINE SAFETY AND QUALITY MGMT | jbozarth@ameren.com | 217-625-6854 |  |  |  |  | JOHN BOZARTH | DIRECTOR PIPELINE SAFETY AND QUALITY MGMT | 217-625-6854 | jbozarth@ameren.com | REPORT UPDATED AND MARKED FINAL WITH FINAL COST ON 12/20/2019. SECOND PARTY CONTRACTOR FOR AMEREN ILLINOIS WAS EXCAVATING TO EXPOSE A 10" GAS MAIN FOR MAINTENANCE. CONTRACTOR HAD CALLED JULIE (ILLINOIS ONE-CALL) FOR A LOCATE REQUEST. AMEREN ILLINOIS GAS DID NOT APPEAR ON THE LOCATE REQUEST, REPORTEDLY DUE TO A TICKET ENTRY ERROR BY THE ONE-CALL CENTER. THE CONTRACT LOCATOR WAS NOTIFIED TO LOCATE THE VICINITY FOR A DIFFERENT UTILITY, AND ATTEMPTED TO LOCATE THE GAS LINE SINCE THE CONTRACTOR ALSO LOCATES FOR AMEREN ILLINOIS. THE LOCATOR COULD NOT COMPLETELY MARK THE GAS FACILITIES DUE TO STANDING WATER ON THE GROUND, HE WAS ABLE TO MARK ONLY A PORTION OF THE MAIN AND NOT THE 3/4" SERVICE THAT WAS ULTIMATELY DAMAGED. THE LOCATOR REPORTEDLY CONTACTED THE EXCAVATOR TO NOTIFY THAT HE COULD NOT COMPLETE THE LOCATE DUE TO WATER. THE EXCAVATOR PROCEEDED TO DIG TO EXCAVATE THE MAIN AND DAMAGED THE BURIED, UNMARKED 3/4" STEEL HIGH PRESSURE GAS SERVICE, TEARING THE SERVICE IN TWO DOWNSTREAM OF THE SERVICE TEE OFF THE MAIN. AMEREN ILLINOIS ISOLATED THE DAMAGE BY INSTALLING TWO 10" LINE STOPPERS AND RUNNING A BYPASS TO KEEP GAS SERVICE TO DOWNSTREAM COMMUNITIES. DUE TO VERY WET GROUND CONDITIONS AND DEPTH OF PIPE, THE EMERGENCY RESPONSE TOOK A LITTLE OVER TWO DAYS TO GET THE LINE SAFELY SHUT DOWN TO MAKE THE SERVICE REPAIRS. INITIAL ESTIMATES DURING THE RESPONSE INDICATED THAT THE GAS LOSS WOULD NOT EXCEED THE INCIDENT REPORTING THRESHOLD OF 3000 MCF. ONCE THE LINE WAS SHUT DOWN AND THE DAMAGE WAS ANALYZED, IT WAS DETERMINED THAT THE SIZE OF PUNCH (ORIFICE) IN THE SERVICE TEE WAS LARGER THAN ESTIMATED RESULTING IN A TOTAL LOSS OF 7040 MCF. IT WAS AT THIS TIME ON 5/18/2019 THAT IT WAS DETERMINED THE THRESHOLD FOR AN INCIDENT HAD BEEN MET AND THE NRC WAS NOTIFIED. THE LINE WAS SUBSEQUENTLY PLACED BACK INTO NORMAL SERVICE ON 5/18/2019 WITH ONE SERVICE INTERRUPTION TO THE EFFECTED CUSTOMER.
2025-03-31 10:13 | NO | YES | YES | 20190061 | 32521 | 2019-06-20 15:32 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-05-21 16:00 |  |  | 2019 | 3369 ANTIGUA | AUBURN HILLS | OAKLAND | MI | 48236 | 42.6907 | -83.3042 | [9 empty] | 2019-05-21 17:00 | 1246382 |  | NATURAL GAS |  | 154.47 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2019-05-21 16:00 |  |  |  | 2019-05-21 16:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 12 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2016 | [5 empty] | 2 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 20 |  |  | 2708 | MECHANICAL PUNCTURE | 0.5 | 2 | [7 empty] | CLASS 3 LOCATION | 55000 | 62221.77742193754 | 63846 | 72229.301841473166888 | 1357 | 1535.180944755804396 | 0 | 0 |  |  | 394 | 441.569553805774278215223097112860892388 |  | 0 | 120597 | 56729.9082569643103417611548556430446194 | 136427.8297619722855622152230971128608924 | 0 | 0 | 0 |  |  |  |  | 54 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | YES |  |  |  |  | YES | [9 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 91360018 |  |  | UTILITY OWNER | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | CARMELLA KING |  | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON MAY 21, 2019 AT APPROXIMATELY 16:00 HOURS A CONSUMERS ENERGY DISTRIBUTION CREW DAMAGED A 2" PLASTIC MEDIUM PRESSURE NATURAL GAS PIPELINE DURING A PIPELINE LOWERING PROJECT. THE PIPELINE IS LOCATED NEAR 3369 ANTIGUA DRIVE, AUBURN HILLS, MICHIGAN (OAKLAND COUNTY). THE INCIDENT WAS REPORTED TO THE NRC AND MPSC AS 3355 KASSANDRA WAY, AUBURN HILLS, MICHIGAN PER CONSUMERS ENERGY'S SIMS RECORD(SERVICE CARD RECORD). WHILE ATTEMPTING TO EXPOSE THE PIPELINE DAMAGE, THE OPERATOR MADE CONTACT WITH THE ELECTRIC SERVICE LINE (LOCATED IN A JOINT TRENCH WITH APPROXIMATELY 19.5" SEPARATION) CAUSING THE BLOWING GAS TO IGNITE. THE EMPLOYEE OPERATING THE EXCAVATION EQUIPMENT WAS INJURED AND THE EQUIPMENT AND BUILDING UNDER CONSTRUCTION WERE SIGNIFICANTLY DAMAGED BY FIRE. A GAS SERVICE WORKER (GSW) ARRIVED AT APPROXIMATELY 16:19 HOURS AND BEGAN MONITORING THE SURROUNDING BUILDING FOR GAS MIGRATION. THE GSW'S CONTINUOUSLY MONITORED THE SITE UNTIL THE FIRE WAS EXTINGUISHED AND THE PIPELINE WAS CAPPED. THE DISTRIBUTION CREW ARRIVED AT APPROXIMATELY 17:18 HOURS, THE PIPELINE WAS SQUEEZED AT TWO REMOTE LOCATIONS STOPPING GAS FROM BLOWING. ONCE THE FIRE WAS EXTINGUISHED, THE PIPELINE WAS CUT AND CAPPED AND THE AREA WAS SECURED FOR FURTHER INVESTIGATION. ON MAY 22, 2019 A CREW RETURNED TO THE ANTIGUA LOCATION TO REMOVE THE DAMAGED PORTION OF THE PIPELINE AND THE EXCAVATING EQUIPMENT. THE DAMAGED PORTION OF THE PIPE WAS TRANSPORTED TO THE CONSUMERS ENERGY ROYAL OAK SERVICE CENTER AND STORED IN A SECURE LOCATION FOR FUTURE INVESTIGATION. THE DAMAGED SECTION OF PIPELINE WAS REPLACED BY INSTALLING (OPEN TRENCHING) 208' OF 2" PLASTIC PIPELINE AT THE APPROPRIATE DEPTH. NORMAL OPERATIONS RESUMED ON MAY 24, 2019 AT APPROXIMATELY 16:00 HOURS. AN RCA TEAM WAS ASSEMBLED TO INVESTIGATE THE DETAILS OF THE INCIDENT, DETERMINE THE ROOT CAUSE AND/OR CONTRIBUTING FACTORS AND IMPLEMENT MEASURES TO PREVENT FUTURE OCCURRENCES. THE RESULTS OF THE INVESTIGATION WILL BE PROVIDED TO THE MICHIGAN PUBLIC SERVICE COMMISSION (MPSC) UPON COMPLETION.
2025-03-31 10:13 | NO | YES | NO | 20190062 | 34752 | 2019-06-24 13:43 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2019-05-24 14:50 | MOUNTAIN | NO | 2019 | 4306 COUNTY ROAD 22 | FREDERICK | WELD | CO | 80516 | 40.146 | -104.9749 | [6 empty] | YES |  |  | 2019-06-04 14:55 | 1247821 |  | NATURAL GAS |  | 9762 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2019-05-24 14:50 | YES | OPERATOR | 2019-05-24 14:50 | 2019-05-24 15:09 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6 | API 5L | UNKNOWN | STEEL |  | SEAMLESS |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 33718 | 38145.343474779817704 | 2000 | 2262.610088070456 | 0 | 0 |  | 4.5475 | 44393 | 49752.7847769028871391076115485564304462 | 0 | 0 | 80111 | 62760.0013217923520413805774278215223097 | 90160.7383397531608431076115485564304462 | 4 | 1 | 0 | 0 | 0 | 0 | 5 | 250 | 250 | 250 | 192.619(A)(1) | 2019-05-24 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SYSTEM IS NOT MONITORED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 914101991 |  |  | CONTRACT LOCATOR | YES | YES | 3 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | STONEY DAVIDSON | PIPELINE SAFETY AND COMPLIANCE COORDINATOR | stoney.davdison@blackhillscorp.com | 719 359-0586 |  |  |  |  | STONEY DAVIDSON | PIPELINE SAFETY AND COMPLIANCE COORDINATOR | 719 359-0586 | stoney.davdison@blackhillscorp.com | 14:50 FIELD RESOURCE CENTER (FRC) RECEIVED CALL FROM DAMAGING PARTY. -14:53 FRC DISPATCHED OPERATIONS TECH #1 -15:09 OPERATIONS TECH #1 ARRIVED ON SCENE AND COMMUNICATED WITH FD/PD AND ASSESSED THE SITUATION. -15:14 OPERATIONS TECH #1 CALLED IN CODE 2, REQUESTING BHE PERSONNEL TO ASSIST. -BHE OPERATIONS TECHS #2&#3 ARRIVE TO ASSIST. -OPERATIONS USED MAPPING AND LOCATING EQUIPMENT TO DETERMINE THE 6' HIGH PRESSURE WAS THE MAIN DAMAGED, NOT THE 2' PE. -OPERATIONS SUPERVISOR CONTACTED CONTRACT WELDER TO MOBILIZE FOR SHUT DOWN AND REPAIR. -OPERATIONS SUPERVISOR/MANAGER DETERMINED THAT THE VENTING GAS COULD SAFELY CONTINUE TO VENT TO ATMOSPHERE AND DID NOT PRESENT A HAZARD TO THE PUBLIC OR PROPERTY. -APPROXIMATELY TWO MILES OF LINE PACK BEGAN TO BE REDUCED DOWN TO 100 PSI TO SAFELY PERFORM STOPPLING PROCEDURE. -2:30 LEAK WAS STOPPED AND REPAIRS BEGAN. -5:30 PRESSURE WAS RESTORED. -COMMERCIAL CUSTOMER'S SERVICE WAS RESTORED ON THE MORNING OF MAY 28, 2019.
2025-03-31 10:13 | NO | YES | NO | 20190063 | 32666 | 2019-06-27 10:41 | SUPPLEMENTAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2019-06-02 07:00 |  |  | 2019 | 831 ARBOR STREET | CONCORD | CABARRUS | NC | 28025 | 35.4333 | -80.6012 | [9 empty] | 2019-06-02 09:12 | 1247562 |  | NATURAL GAS |  | 3596 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 74 | 2019-06-02 07:00 |  |  |  | 2019-06-02 07:22 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1978 | [5 empty] | 2 | API 5L | UNKNOWN | STEEL |  | OTHER | ERW | 0.154 | [6 empty] | OTHER | [8 empty] | ELECTRICAL ARC INTO THE SIDE OF 2" STEEL PIPE 1/2" DIAMETER HOLE | CLASS 3 LOCATION | 100000 | 113130.5044035228 | 260 | 294.13931144915928 | 13542 | 15320.132906325057576 | 0 | 0 | NONE |  | 155 | 173.713910761154855643044619422572178478 |  | 0 | 113957 | 53482.9207849219327361522309711286089239 | 128918.4905320581717116430446194225721785 | 0 | 0 | 6 |  |  |  |  | 20 | 20 | 66 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | MARK HANNAH | OPERATIONS MANAGER | rhannah@scana.com | 828-670-3513 |  |  |  |  | SCOTT SWINDLER | GENERAL MANAGER-OPERATIONS AND MAINTENANCE | 704-810-3230 | mswindler@scana.com | UPON ARRIVAL A NATURAL GAS FIRE WAS FOUND BURNING AT THE BASE OF A MUNICIPAL OWNED POWER POLE ON THE RIGHT FRONT CORNER OF 831 ARBOR ST NE AND A NATURAL GAS FIRE APPROX. 2 BLOCKS AWAY ON THE RIGHT SIDE OF HOME AT 776 ARBOR ST NE. AT THE HOUSE, GAS HAD IGNITED ON THE UNION FOR THE FILTER RIGHT ABOVE THE LOCK-WING SERVICE VALVE AND SET THE HOME ON FIRE. THE FIRE DEPARTMENT WAS ABLE TO TURN THE GAS OFF AT THE LOCK-WING SERVICE VALVE, ON THE METER SET, AND EXTINGUISH THE FLAMES. AT THE POWER POLE, AFTER DETERMINING THAT THERE WAS NO GAS MIGRATING UNDERGROUND, THE DECISION WAS MADE TO DIG UP THE 2" STEEL MAIN IN REMOTE HOLES ON EITHER SIDE OF THE FIRE AND SQUEEZE THE LINE OFF. IT WAS DETERMINED THAT A SQUIRREL SHORTED THE OVERHEAD POWER FACILITY TO THE GROUND ON THE POWER POLE. THE GROUND ROD FOR THE POLE WAS WITHIN 6" OF THE 2" COATED AND WRAPPED STEEL GAS MAIN. THE GROUNDED CURRENT CAUSED AN ARC BURN HOLE IN THE PIPE AT THE GROUND ROD AND AT THE HOUSE RISER CAUSING FIRES AT BOTH LOCATIONS. REPAIRS TO THE MAIN WERE MADE AND SERVICE WAS RESTORED TO THE CUSTOMERS IMPACTED.
2025-03-31 10:13 | NO | NO | NO | 20190064 | 32352 | 2019-06-28 10:42 | ORIGINAL FINAL | 12582 | ATMOS ENERGY CORPORATION - MISSISSIPPI | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2019-06-04 20:49 |  |  | 2019 | CLINTON BLVD. AND FLAG CHAPEL RD. | JACKSON | HINDS | MS | 39209 | 32.3321 | -90.2657 | [9 empty] | 2019-06-04 22:28 | 1247854 |  | NATURAL GAS |  | 1479 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2019-06-04 21:32 |  |  |  | 2019-06-04 21:26 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2002 | [8 empty] | STEEL |  | OTHER | ERW | 0.154 | [6 empty] | OTHER | [8 empty] | OTHER OUTSIDE FORCE - VEHICLE | CLASS 3 LOCATION | 3000 | 3393.915132105684 | 42300 | 47854.2033626901444 | 27200 | 30771.4971977582016 | 2250 | 2545.436349079263 | MEALS AND LODGING |  | 3676 | 4119.821522309711286089238845144356955381 |  | 0 | 78426 | 38835.384451042920054461942257217847769 | 88684.8735639430042860892388451443569554 | 26 | 0 | 785 |  |  |  |  | 135 | 135 | 160 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | MICHAEL L. JEUKENS | COMPLIANCE ENGINEER | michael.jeukens@atmosenergy.com | (601)592-5362 | (601)360-1489 |  |  |  | JAMES E. MCKENZIE | VICE PRESIDENT - TECHNICAL SERVICES | (601)420-5013 | james.mckenzie@atmosenergy.com | ATMOS ENERGY RECEIVED AN EMERGENCY LEAK CALL AT 20:49 ON JUNE 4, 2019, AT 5249 CLINTON BLVD., JACKSON, MS. ATMOS ENERGY ARRIVED ONSITE AT 21:26 AND DETERMINED THAT THE EVENT MET THE DEFINITION OF A REPORTABLE INCIDENT AT 21:32. THE TELEPHONIC REPORT WAS MADE AT 22:28, WITHIN ONE HOUR OF DISCOVERY. WHEN ATMOS ENERGY ARRIVED ONSITE, EMERGENCY RESPONDERS WERE PRESENT AT THE SCENE, AND REPORTED THAT A 2005 NISSAN ALTIMA WAS TRAVELING SOUTH ON FLAG CHAPEL ROAD. AT THE INTERSECTION OF FLAG CHAPEL ROAD AND CLINTON BOULEVARD, THE VEHICLE LEFT THE ROADWAY AND COLLIDED WITH ATMOS ENERGY'S PROTECTIVE BARRIER AND ULTIMATELY ITS GAS REGULATION DISTRIBUTION STATION, LOCATED IN THE SOUTHWEST CORNER OF CLINTON BOULEVARD AND FLAG CHAPEL RD. THE IMPACT CAUSED THE DISTRIBUTION STATION TO SEPARATE FROM ITS CONNECTING PIPING. THE RESULTING ESCAPING GAS IGNITED, CAUSING A FIRE AND LOSS OF GAS SERVICE TO CONNECTED CUSTOMERS. ATMOS ENERGY COMPLETED A SHUTDOWN OF THE FACILITIES AT 03:25 ON JUNE 5, 2019, AND THEN COMPLETED THE NECESSARY REPAIRS . SERVICE WAS RESTORED AT 07:50 ON JUNE 5, 2019.
2025-03-31 10:13 | NO | YES | NO | 20190065 | 32358 | 2019-06-28 15:29 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2019-05-31 07:54 |  |  | 2019 | INTERSECTION OF BAIN STREET AND UNION STREET | JURUPA VALLEY | RIVERSIDE | CA | 91752 | 34.0126 | -117.5071 | [9 empty] | 2019-05-31 20:41 | 1247471 |  | NATURAL GAS |  | 3250 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-05-31 07:54 |  |  |  | 2019-05-31 09:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 32 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1950 | [5 empty] | 10 | X42 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 9 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 120000 | 135756.60528422736 | 200 | 226.2610088070456 | 0 | 0 |  |  | 19500 | 21854.3307086614173228346456692913385827 |  | 0 | 139700 | 76536.5603418868415417322834645669291339 | 157837.1970016958229228346456692913385827 | 0 | 1 | 9 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | YES | 183390070 | DIGALERT |  | UTILITY OWNER | UNKNOWN/OTHER | YES | 11 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ALI MATIN | PIPELINE SAFETY COMPLIANCE ADVISOR | amatin@semprautilities.com | 909-919-0463 |  |  |  |  | ALI MATIN | PIPELINE SAFETY COMPLIANCE ADVISOR | 909-919-0463 | amatin@semprautilities.com | ON MAY 31, 2019, A THIRD-PARTY CONTRACTOR DAMAGED A 10-INCH STEEL MAIN ON BAIN STREET IN JURUPA VALLEY, WHILE GRADING THE ROAD FOR A CONSTRUCTION PROJECT. SOCALGAS COMPANY CREW RESPONDED AND CONTROLLED THE GAS. NO INJURIES OR FURTHER DAMAGE RESULTED FROM THIS INCIDENT. THE 10-INCH STEEL MAIN WAS REPAIRED BY REPLACING A SECTION OF THE PIPE. INVESTIGATION OF THE INCIDENT SHOWED THAT THERE WAS A VALID USA TICKET FOR THE CONTRACTOR AND THE 10-INCH MAIN WAS PROPERLY MARKED. THE CONTRACTOR FAILED TO MAINTAIN MARKINGS AND POT-HOLE WHICH RESULTED IN THE DAMAGE. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE EXCEEDING 3,000,000 CUBIC FEET AND ESTIMATED PROPERTY DAMAGE OF $50,000 OR MORE.
2025-03-31 10:13 | NO | NO | NO | 20190066 | 33259 | 2019-06-28 16:41 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2019-05-30 07:30 |  |  | 2019 | 2122 S. 49TH W. AVE. | TULSA | TULSA | OK | 74132-3470 | 36.1329 | -96.0474 | [9 empty] | 2019-06-18 10:23 | 1249263 |  | NATURAL GAS |  | 33 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-05-30 07:30 |  |  |  | 2019-05-30 07:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6 | 6 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.28 | [6 empty] | OTHER | [8 empty] | TORE OFF SERVICE TEE. | CLASS 3 LOCATION | 9943 | 11248.566052842272004 | 37978 | 42964.702962369888984 | 11946 | 13514.570056044833688 | 0 | 0 |  |  | 172 | 192.766404199475065616797900262467191601 |  | 0 | 60039 | 28229.1599039511742398398950131233595801 | 67920.6054754564697416167979002624671916 | 4 | 0 | 108 |  |  |  |  | 40 | 40 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS RESULT FROM THIRD PARTY CONTRACTOR. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | SETH SLIFER | SR. COMPLIANCE SPECIALIST | seth.slifer@onegas.com | 405-248-7018 |  |  |  |  | MEGHAN BOOKER | DIRECTOR OF ENGINEERING | 405-530-2501 | meghan.booker@onegas.com | ARK WRECKING DROVE A SKYJACK FORKLIFT OFF THE ROAD AVOIDING ONCOMING TRAFFIC INTO ONG'S 6" CS MAIN SERVICE TEE. REPAIRS WERE COMPLETED AND SERVICE RESTORED FIVE DAYS LATER.
2025-03-31 10:13 | NO | YES | YES | 20190067 | 32376 | 2019-07-03 09:28 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2019-06-06 18:42 |  |  | 2019 | 5415 AVENUE M | SANTA FE | GALVESTON | TX | 77510 | 29.3655 | -95.0894 | [9 empty] | 2019-06-06 19:40 | 1248095 |  | NATURAL GAS |  | 165 |  | NO | [5 empty] | 0 | YES | 0 | 2 | 0 | 0 | 0 | 2 | YES |  |  |  |  | NO | 0 | 2019-06-06 18:42 |  |  |  | 2019-06-06 18:42 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1947 | [5 empty] | 2.75 | API 5L A-25 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.21 | [6 empty] | OTHER | [8 empty] | TAPPING VALVE INADVERTENTLY BUMPED IN THE OPEN POSITION. | CLASS 3 LOCATION | 8200 | 9276.7013610888696 | 28000 | 31676.541232986384 | 5090 | 5758.34267413931052 | 0 | 0 |  |  | 976 | 1093.837270341207349081364829396325459318 |  | 0 | 42266 | 20358.4011916444907840682414698162729659 | 47805.4225385557714690813648293963254593 | 0 | 0 | 6 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | INCORRECT OPERATION | INCORRECT VALVE POSITION | [222 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | LESLIE DAVENPORT | COMPLIANCE COORDINATOR LL | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-923-7307 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steven.yarborough@centerpointenergy.com | WHILE A CONTRACTOR'S CREW WAS PERFORMING TAPPING OPERATIONS, A CREW MEMBER INADVERTENTLY BUMPED THE SLIDE VALVE OPEN AND NATURAL GAS WAS RELEASED. THE CONTRACTOR HAS IDENTIFIED A GRINDER AT THE JOB SITE AS A PROBABLE SOURCE OF IGNITION."
2025-03-31 10:13 | NO | NO | NO | 20190068 | 32384 | 2019-07-05 10:27 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2019-02-04 17:00 |  |  | 2019 | 5101 E ROSEDALE STREET | FORT WORTH | TARRANT | TX | 76105 | 32.7319 | -97.2451 | [9 empty] | 2019-06-06 15:35 | 1248069 |  | NATURAL GAS |  | 467 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-02-04 18:00 |  |  |  | 2019-02-04 18:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 60 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 2016 | [5 empty] | 16 | API 5L X52 | AMERICAN STEEL PIPE CO | STEEL |  |  |  | 0.375 | [6 empty] | OTHER | [8 empty] | THIRD PARTY HIT TAP | CLASS 2 LOCATION | 0 | 0 | 4303 | 4868.005604483586084 | 65905 | 74558.65892714170134 | 0 | 0 |  |  | 2221 | 2489.152230971128608923884514435695538058 |  | 0 | 72429 | 35198.7538846475452621942257217847769029 | 81915.8167625964160329238845144356955381 | 0 | 0 | 0 |  |  |  |  | 24 | 24 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | NO | [5 empty] | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JEFF JORDAN | OPERATION SUPERVISOR | jeffrey.jordan@atmosenergy.com | 817-207-2872 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT - TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ADDITIONAL NRC NUMBER: 1248291 IT WAS DISCOVERED ON 2/4/19 THAT NORTH TEXAS CONSTRUCTION, INC. STRUCK A 1" SERVICE TAPPING TEE AND PULLED IT FROM A 16-INCH COATED STEEL MAIN. THE EXCAVATOR DID NOT HAVE A VALID LOCATE TICKET FOR THE DAMAGE AREA. DAMAGE OCCURRED APPROXIMATELY 68 FEET BEYOND THE SCOPE OF LOCATE REQUEST 1951847238. REPAIRS WERE MADE BY RETIRING THE SERVICE TAP AT THE MAIN, AND THE LINE WAS BACK IN SERVICE AT 00:30 ON 2/6/19. ON 6/6/19, IT WAS DETERMINED THAT THE DOLLAR AMOUNT EXCEEDED $50,000 AND THE INCIDENT WAS REPORTED TELEPHONICALLY TO NRC AND RRC ON 6/6/19.
2025-03-31 10:13 | NO | YES | NO | 20190069 | 32385 | 2019-07-05 12:14 | ORIGINAL FINAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2019-06-06 13:45 |  |  | 2019 | 1716 GUINOTTE AVE | KANSAS CITY | JACKSON COUNTY | MO | 64120 | 39.1166 | -94.5614 | [9 empty] | 2019-06-06 20:27 | 1248099 |  | NATURAL GAS |  | 11780.48 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-06-06 13:30 |  |  |  | 2019-06-06 13:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 84 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1937 | [5 empty] | 24 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | STRAIGHT SEAM WELDED PIPE | 0.288 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 487309 | 551295.129703762921452 | 500 | 565.652522017614 | 0 | 0 |  |  | 58163 | 65185.3044619422572178477690288713910761 |  | 0 | 545972 | 288864.4080450713645853884514435695538058 | 617046.0866877227926698477690288713910761 | 1 | 0 | 0 |  |  |  |  | 58 | 58 | 58 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER(S) ACTIONS DID NOT CAUSE OR CONTRIBUTE TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | A SINKHOLE REMOVED THE SUPPORT UNDER THE 24" MAIN. | [154 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY | nicole.christianer@spireenergy.com | 314-349-2929 |  |  |  |  | CRAIG HOEFERLIN | VP OPERATION SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | A WATER MAIN BREAK CAUSED A LARGE SINKHOLE BELOW THE GAS DISTRIBUTION MAIN, RESULTING IN A LEAK ON A 24" DRESSER COUPLING. ONE COMMERCIAL SERVICE WAS AFFECTED AND HAS BEEN PLACED BACK INTO SERVICE. GAS WAS MADE SAFE ON JUNE 10, 2019 BY ABANDONING THE AFFECTED SECTION OF MAIN. A 48 HOUR UPDATE TO THE NRC WAS MADE ON JUNE 8, 2019 AT 13:09. REPORT NUMBER 1248257.
2025-03-31 10:13 | NO | YES | NO | 20190071 | 33146 | 2019-07-09 11:14 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2019-05-18 10:20 |  |  | 2019 | 16641 S TAMIAMI TRL | FT MYERS | LEE | FL | 33908 | 26.5002 | -81.8542 | [9 empty] | 2019-05-29 21:15 | 1247206 |  | NATURAL GAS |  | 5226 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 25 | 2019-05-18 10:31 |  |  |  | 2019-05-18 11:17 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2000 | [5 empty] | 8.187 | API 5L | UNKNOWN | STEEL |  |  |  | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 2 | 8 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 64828 | 73340.243394715760784 | 37133 | 42008.750200160121324 | 0 | 0 |  |  | 53658 | 60136.3937007874015748031496062992125984 |  | 0 | 155619 | 103403.7787143100593371574803149606299213 | 175485.3872956632836828031496062992125984 | 19 | 0 | 0 |  |  |  |  | 350 | 350 | 476 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EVENT WAS CAUSED BY 3RD PARTY EXCAVATION. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | INTERSTATE HIGHWAY | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | STORM DRAIN/CULVERT | NO | [5 empty] | YES | 36 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | SANDRA PANOS | SUPERVISOR OF QUALITY ASSURANCE | sjpanos@tecoenergy.com | 813-205-3699 |  |  |  |  | SANDRA PANOS | SUPERVISOR OF QUALITY ASSURANCE | 813-205-3699 | sjpanos@tecoenergy.com | CONTRACTOR, COUGAR CONTRACTING LLC, DAMAGED PEOPLES GAS' (PGS') 8" STEEL HIGH PRESSURE MAIN DURING EXCAVATION. CONTRACTOR FAILED TO OBTAIN A LOCATE REQUEST FOR THE EXCAVATION TIME FRAME. LAST LOCATE REQUEST HAD BEEN OBTAINED 60 DAYS PRIOR AND WAS EXPIRED. TO MAKE THE REPAIR, A STYLE 220 REINFORCING SLEEVE WAS WELDED OVER THE DAMAGE LOCATION TO STOP THE FLOW OF GAS. PGS THEN APPLIED AN F1 COATING TO THE AREA THEN THE SLEEVE WAS X-RAYED. PGS THEN CONDUCTED A MAG-PARTICLE FILLET WELD TEST AND AN ULTRASONIC TEST.
2025-03-31 10:13 | NO | YES | NO | 20190072 | 32399 | 2019-07-09 13:07 | ORIGINAL FINAL | 603 | CENTERPOINT ENERGY RESOURCES CORP. | 10825 E GEDDES AVE SUITE 410 | CENTENNIAL | CO | 80112 | 2019-06-20 10:25 |  |  | 2019 | BYERS ST & 24TH ST | BATESVILLE | INDEPENDENCE | AR | 72501 | 35.7702 | -91.6253 | [9 empty] | 2019-06-20 13:30 | 1249533 |  | NATURAL GAS |  | 95 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2019-06-20 10:43 |  |  |  | 2019-06-20 11:08 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 18 |  | NO | [11 empty] | OTHER | PUBLICLY TRADED LDC | SERVICE |  | 2015 | [5 empty] | 1 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | UNKNOWN | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 0 | 0 | 2651 | 2999.089671737389428 | 450000 | 509087.2698158526 | TRENCHER DAMAGE |  | 480 | 537.952755905511811023622047244094488189 |  | 0 | 453131 | 212588.4497337153582781811023622047244094 | 512624.3122434955012390236220472440944882 | 10 | 0 | 4 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | MUNICIPALITY | TRENCHER | WATER | YES | 1906051211 |  |  | CONTRACT LOCATOR | NO | YES | 3 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | STEVEN LEWIS | AREA MANAGER | steven.lewis@centerpointenergy.com | 870-569-4032 | 870-569-4098 |  |  |  | KEITH KITTINGER | REGIONAL OPERATIONS DIRECTOR | 501-377-4669 | keith.kittinger@centerpointenergy.com | THE CITY OF BATESVILLE WAS INSTALLING A NEW WATER MAIN IN THE MIDDLE OF BYERS STREET WHEN THEY STRUCK A 1" CTS PLASTIC GAS SERVICE TO 2485 HARRISON ST. THE CITY WAS USING A T655 VERMEER TRENCHER TO TRENCH THROUGH THE ASPHALT. AFTER STRIKING THE 1" PLASTIC GAS SERVICE LINE, THE ESCAPING NATURAL GAS IGNITED. THE T655 TRENCHER WAS TOTALED (COMPLETE LOSS) AS A RESULT OF THE FIRE. THE CNP FIRST RESPONDERS SECURED THE AREA ALONG WITH THE BATESVILLE FIRE DEPARTMENT. THE CNP LOCAL CREW WAS CALLED AND SQUEEZED THE 2" PLASTIC MAIN TO STOP THE FLOW OF GAS. THE 1" SERVICE WAS THEN CAPPED OFF FOR PERMANENT REPAIR. 10 COMMERCIAL CUSTOMERS AND 4 RESIDENTIAL CUSTOMERS WERE TEMPORARILY TURNED OFF DUE TO THESE REPAIRS. THERE WERE MARKINGS ON THE GROUND INDICATING LOCATION OF THE MAIN, HOWEVER THE SERVICE LINE ITSELF WAS NOT LOCATED OR MARKED.
2025-03-31 10:13 | YES | NO | NO | 20190074 | 33780 | 2019-07-12 08:50 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2019-05-06 20:45 |  |  | 2019 | 14218 PARK AVE | BURNSVILLE | DAKOTA | MN | 55337 | 44.7454 | -93.2632 | [9 empty] | 2019-05-06 20:38 | 1244866 |  | NATURAL GAS |  | 18.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2019-05-06 20:46 |  |  |  | 2019-05-06 21:30 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1979 | [5 empty] | 0.5 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.9 |  | 2306 | OTHER | [8 empty] | AN ELECTRIC COMPANY TECHNICIAN BURNED THROUGH THE SERVICE LINE WITH A TORCH WHILE MAKING A REPAIR ON A ELECTRIC SERVICE. | CLASS 3 LOCATION | 200000 | 226261.0088070456 | 4243 | 4800.127301841472404 | 304 | 343.916733386709312 | 0 | 0 |  |  | 150 | 168.110236220472440944881889763779527559 |  | 0 | 204697 | 95996.544548324631366244094488188976378 | 231573.1630784942541569448818897637795276 | 0 | 0 | 6 |  |  |  |  | 50 | 50 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | AARON ABRAHAMSON | OPERATIONS SPECIALIST II | aaron.abrahamson@centerpointenergy.com | 612-321-5514 |  |  |  |  | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 612-321-5316 | dean.headlee@centerpointenergy.com | AS OF MAY 19, 2020 CENTERPOINT ENERGY HAS COMPLETED ITS INVESTIGATION OF THE INCIDENT AT 14218 PARK AVE IN BURNSVILLE. FURTHER INVESTIGATION REVEALED CENTERPOINT ENERGY'S FACILITIES WERE NOT AT FAULT, THE NATURAL GAS SERVICE LINE WAS DAMAGED BY A TORCH USED BY THE ELECTRIC COMPANY REPAIRING THE ELECTRIC SERVICE TO 14218 PARK AVE RESULTING IN THE RELEASE AND IGNITION OF NATURAL GAS. ON MAY 6, 2019, A CONTRACTOR DAMAGED THE ELECTRIC SERVICE WHILE INSTALLING A COMMUNICATIONS LINE TO 14218 PARK AVE IN BURNSVILLE. DAKOTA ELECTRIC ASSOCIATION WAS NOTIFIED AND SENT A CREW TO REPAIR THE DAMAGED ELECTRIC SERVICE AND THE INCIDENT HAPPENED WHILE THE ELECTRIC SERVICE WAS BEING REPAIRED. CENTERPOINT'S FIRST RESPONDER AND REPAIR CREW WERE NOTIFIED AT 20:42 AND THE REPAIR CREW WAS ONSITE AT 21:30. CENTERPOINT'S REPAIR CREW SHUT THE MAIN DOWN LOSING 6 CUSTOMERS AT 22:16. A LEAK INVESTIGATION WAS PERFORMED AND DID NOT FIND ANY GAS READINGS NEAR THE EXCAVATION, NEAR THE FOUNDATIONS OF ADJACENT BUILDINGS OR SEWER STRUCTURES. THE SERVICE LINE WAS CAPPED A FEW FEET FROM THE EXCAVATION WHERE THE INCIDENT OCCURRED AND PRESSURED TESTED TO COMPANY STANDARDS. THE PRESSURE TEST VERIFIED THE SERVICE LINE WAS NOT COMPROMISED AND WAS WITNESSED BY VICA LIVSHUTZ OF MNOPS. ON MAY 29TH, 2019 WITH ALL PARTIES IN ATTENDANCE THE REMAINING SERVICE WAS TESTED. THE FIRST AIR TEST CONFIRMED THE INTEGRITY OF THE SERVICE LINE UP TO THE DAMAGED AREA WAS NOT COMPROMISED. A SECOND PRESSURE TEST FROM THE DAMAGED AREA TO THE SERVICE RISER DID NOT HOLD AIR, DUE TO A HOLE IN THE SERVICE LINE NEAR THE HEAT SHIELD DAKOTA ELECTRIC ASSOCIATION INSTALLED DURING THE ELECTRIC SERVICE REPAIR. ALL AIR TESTS WERE PERFORMED TO COMPANY STANDARDS. AS OF JULY 11, 2019, THE FIRE INVESTIGATION AT 14218 PARK AVE IS STILL IN PROGRESS AND CAUSE OF THE INCIDENT HAS NOT YET BEEN DETERMINED, BUT CENTERPOINT ENERGY BELIEVES ITS FACILITIES WERE NOT AT FAULT FOR THE INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20190075 | 32418 | 2019-07-12 10:30 | ORIGINAL FINAL | 11320 | LAWRENCEVILLE, CITY OF | P.O. BOX 2200 435 WEST PIKE STREET | LAWRENCEVILLE | GA | 30046 | 2019-07-12 02:32 |  |  | 2019 | 2385 MITCHELL RD. | LAWRENCEVILLE | GWINNETT | GA | 30046 | 34.0432 | -83.9734 | [9 empty] | 2019-07-12 05:08 | 1251679 |  | NATURAL GAS |  | 116 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2019-07-12 02:32 |  |  |  | 2019-07-12 03:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | 0 | 0 | 200 | 226.2610088070456 | 2643 | 2990.039231385107604 | 0 | 0 |  |  | 100 | 112.073490813648293963254593175853018373 |  | 0 | 2943 | 1435.769638983278409162729658792650918635 | 3328.373731005801497963254593175853018373 | 0 | 0 | 1 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  | ,,, | NO | [218 empty] | KYLE HAMBY | REGULATORY COMPLIANCE SUPERVISOR | kyle.hamby@lawrencevillega.org | 7702777455 |  |  |  |  | KYLE HAMBY | REGULATORY COMPLIANCE SUPERVISOR | 7702777455 | kyle.hamby@lawrencevillega.org | AT 02:32 AM, BRIAN COOPER RECEIVED A CALL FROM THE CALL CENTER STATING THAT LIGHTNING HAD HIT A TREE AND RAN TO THE GAS MAIN CAUSING A GROUND FIRE. FIRE DEPARTMENT WAS ON SCENE WETTING DOWN THE JOINING AREA TO KEEP THE FIRE FROM SPREADING. BRIAN ARRIVED ON SCENE AT 03:35 AM. CALLED THE ON-CALL CREW AT 03:53 AM AS WELL AS THE ON CALL SUPERVISOR, KYLE HAMBY. THE CREW, AS WELL AS KYLE HAMBY, ARRIVED ON SCENE AT 05:00 AM AND BEGIN ASSESSING THE SITUATION. BEGAN DIGGING BELL HOLES ON EITHER SIDE OF THE FIRE TO SQUEEZE OFF PLASTIC MAIN AT 05:15 AM. KYLE HAMBY CALLED NRC AT 05:08 AM AS WELL AS JEFF BAGGETT WITH THE GEORGIA PSC. MAIN WAS SQUEEZED OFF AT 05:55 AM PUTTING OUT THE FIRE AND STOPPING THE ESCAPE OF NATURAL GAS. SCENE WAS DECLARED SAFE, AND FIRE DEPARTMENT LEFT JUST AFTER 06:00 AM. ONE CUSTOMER WAS AFFECTED.
2025-03-31 10:13 | NO | NO | NO | 20190076 | 32736 | 2019-07-18 13:24 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2019-06-18 16:00 |  |  | 2019 | SEIDEL RD | WINTER GARDEN | ORANGE | FL | 34787 | 28.4249 | -81.6198 | [9 empty] | 2019-06-19 14:40 | 1249427 |  | NATURAL GAS |  | 112 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-06-18 16:09 |  |  |  | 2019-06-18 16:25 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 180 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2017 | [5 empty] | 4 | ASTM D2513 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 39265 | 44420.69255404322742 | 17643 | 19959.614891913527604 | 0 | 0 |  |  | 1114 | 1248.498687664041994750656167979002624672 |  | 0 | 58022 | 27819.3268749733104535328083989501312336 | 65628.8061336207970187506561679790026247 | 0 | 0 | 194 |  |  |  |  | 43 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EVENT WAS CAUSED BY 3RD PARTY EXCAVATOR | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 160900759 |  |  | UTILITY OWNER | YES | YES | 20 | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | AMBER STONE | COORDINATOR SMS DOCUMENTATION | alstone@tecoenergy.com | 813-275-3723 |  |  |  |  | RUSSELL HARRIS | MANAGER PIPELINE SAFETY COMPLIANCE | 407-420-6667 | rharris@tecoenergy.com | CONTRACTOR, GAMEZ PROFESSIONAL DRILLING, INC., DAMAGED PEOPLES GAS' (PGS') 4' PLASTIC GAS MAIN DURING INSTALLATION OF A COMMUNICATIONS CABLE. THE CONTRACTOR REQUESTED AND OBTAINED A LOCATE FOR THE EXCAVATION, THE GAS PIPELINE WAS CORRECTLY MARKED, AND THE LOCATE MARKS WERE VISIBLE IN THE AREA. THE GAS MAIN WAS DAMAGED DURING THE 3RD PARTY'S DIRECTIONAL DRILLING PROCESS. THE RESULTING GAS LEAK WAS MADE SAFE BY SQUEEZING THE 4' PLASTIC GAS MAIN AND WAS REPAIRED BY INSTALLING A NEW 4' PLASTIC PIPE. THE PIPE HAD A LEAKAGE RESURVEY PERFORMED AFTER THE REPAIR ON 06/19/19.
2025-03-31 10:13 | NO | YES | NO | 20190077 | 33141 | 2019-07-19 16:47 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2019-04-17 12:47 |  |  | 2019 | 6015 WHITE DRIVE | PRIOR LAKE | SCOTT | MN | 55372 | 44.7159 | -93.3986 | [9 empty] | 2019-04-17 14:31 | 1243017 |  | NATURAL GAS |  | 16 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2019-04-17 12:47 |  |  |  | 2019-04-17 13:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | COPPER | [10 empty] | LEAK |  |  | OTHER | LIGHTNING STRIKE | [5 empty] | CLASS 3 LOCATION | 130000 | 147069.65572457964 | 2877 | 3254.764611689350956 | 2490 | 2816.94955964771772 | 0 | 0 |  |  | 141 | 158.023622047244094488188976377952755906 |  | 0 | 135508 | 63572.7435968022391834094488188976377953 | 153299.3935179639527704881889763779527559 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | NO | [218 empty] | AARON ABRAHAMSON | OPERATION SPECIALIST II | aaron.abrahamson@centerpointenergy.com | 612-321-5514 |  |  |  |  | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 612-321-5366 | dean.headlee@centerpointenergy.com | LIGHTNING STRUCK THE METER AT 6015 WHITE DR AND STARTED A FIRE. THE FIRE DEPARTMENT WORKED TO SUPPRESS THE FIRE UNTIL THE GAS COULD BE SHUT OFF, GAS WAS OFF AT 14:30 ON APRIL 17TH.THE SERVICE LINE WAS TEMPORARILY CAPPED IN THE BLVD UNTIL IT CAN BE ABANDONED AT THE MAIN. CENTERPOINT ENERGY HAS NOT RECEIVED AN ESTIMATE ON THE DAMAGE. THE SERVICE LINE HAS BEEN ABANDONED AT THE MAIN. NO OTHER DETAILS HAVE CHANGED. THE NATIONAL RESPONSE CENTER REPORT NUMBER AND NUMBER OF PEOPLE THAT WERE EVACUATED HAS BEEN CORRECTED. UPDATE 1/2/2020: COSTS REGARDING THE DAMAGE TO THE OPERATOR AND PUBLIC PROPERTY HAVE BEEN UPDATED. THE COSTS ASSOCIATED WITH PRIVATE PROPERTY WERE FROM A NFIRS-1 BASIC REPORT PREPARED BY THE PRIOR LAKE FIRE DEPARTMENT. THE SERVICE LINE WAS ABANDONED AT THE MAIN ON MAY 1, 2018 AND A NEW SERVICE HAS NOT BEEN INSTALLED.
2025-03-31 10:13 | NO | NO | NO | 20190078 | 32449 | 2019-07-19 17:51 | ORIGINAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2018-09-14 08:30 |  |  | 2018 | OYKEY TRAIL & LAKESHORE DR | HUDSON OAKS | PARKER | TX | 76087 | 32.7588 | -97.6983 | [9 empty] | 2019-06-27 11:20 | 1250283 |  | NATURAL GAS |  | 1024 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2018-09-14 08:30 |  |  |  | 2018-09-14 09:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 54 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2018 | [5 empty] | 4 | ASTM D2513 PE2406 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.395 |  | 2406 | OTHER | [8 empty] | 4" DRISCOPIPE PLASTIC MAIN WAS CUT IN HALF BY TRACKHOE | CLASS 3 LOCATION | 0 | 0 | 5485 | 6326.205786323234355 | 0 | 0 | 65400 | 75430.0562307273522 | SERVICE RESTORATION LABOR TO COMPLETE 1673 CUSTOMER OUTAGE |  | 3440 | 3472.529550827423167848699763593380614657 |  | 0 | 74325 | 37073.2848909884020050591016548463356974 | 85228.7915678780097228486997635933806147 | 73 | 0 | 1600 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | LINE WAS CUT IN HALF IN CLOSE PROXIMITY TO THE REGULATOR STATION FEEDING THE SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SITE DEVELOPMENT | YES | 1875060829 | TX-811 |  | CONTRACT LOCATOR | NO | YES | 72 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | DEAN LAFLAMME | DIRECTOR ENGINEERING | dean.laflamme@onegas.com | 512-370-8213 |  |  |  |  | DEAN LAFLAMME | DIRECTOR ENGINEERING | 512-370-8213 | dean.laflamme@onegas.com | ON 9/14/18 A CONTRACTOR DOING SITE DEVELOPMENT WORK TO CONSTRUCT A NEW HEB (GROCERY STORE) DAMAGED OUR 4" DRISCOPIPE (PE) FACILITIES WITH A TRACKHOE AND RESULTED IN OUR FACILITIES BEING CUT IN HALF. THIS DAMAGE CAUSED A LOSS OF SERVICE TO 1673 CUSTOMERS DUE TO THE FACT THIS WAS A ONE WAY FEED. THE PROPERTY DAMAGE TOTAL WAS $5,484.65 WHICH INCLUDED A REPLACEMENT OF 3' OF 4" PE. THE SERVICE RESTORATION LABOR COST WAS THE MOST SIGNIFICANT CONTRIBUTOR TO THE COST AND EXCEEDED THE $50,000 REPORTABLE THRESHOLD. LABOR COSTS WERE HIGH DUE TO THE FACT THAT THE INCIDENT OCCURRED ON FRIDAY AND THE SERVICE RESTORATION CONTINUED THROUGHOUT THE WEEKEND. IN ADDITION, PERSONNEL FROM OTHER OPERATING AREAS ASSISTED WITH THE SERVICE RESTORATION. DURING AN INTERNAL AUDIT OF TEXAS GAS SERVICE RECORDS IT WAS DETERMINED THAT THIS EVENT WAS OVER $50,000 WHICH IS THE REPORTABLE THRESHOLD. AFTER CONFIRMATION THAT THE EXPENDITURES WERE APPLICABLE TOWARDS THE REPORTING REQUIREMENTS ON 6/27/19 THE INCIDENT WAS REPORTED TIMELY TO PHMSA AND THE RAILROAD COMMISSION OF TEXAS.
2025-03-31 10:13 | NO | YES | NO | 20190079 | 32458 | 2019-07-22 18:03 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2019-07-02 10:03 |  |  | 2019 | SCOTTSDALE RD & SKY SONG BLVD | SCOTTSDALE | MARICOPA | AZ | 85257 | 33.4645 | -111.926 | [9 empty] | 2019-07-02 12:37 | 1250776 |  | NATURAL GAS |  | 219 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 15 | 2019-07-02 10:03 |  |  |  | 2019-07-02 10:20 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | UNDER CONCRETE | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2016 | [5 empty] | 2 | ASTM D2513 | CHEVRON PHILLIPS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 8100 | MECHANICAL PUNCTURE | 2.5 | 0.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 136417 | 154329.240192153698076 | 2000 | 2262.610088070456 | 0 | 0 |  |  | 247 | 276.821522309711286089238845144356955381 |  | 0 | 138664 | 65111.724100540313613461942257217847769 | 156868.6718025338653620892388451443569554 | 100 | 0 | 1573 |  |  |  |  | 26 | 26 | 30 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | [7 empty] | YES | [6 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | YES | 201905001569 |  |  | CONTRACT LOCATOR | YES | YES | 23 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | SHAWN BRINK | ADMINISTRATOR DIVISION COMPLIANCE | shawn.brink@swgas.com | 6024845489 | 6024845322 |  |  |  | HENGAMEH NAJAFI | DIRECTOR CENTRAL SUPPORT | 6024845355 | hengameh.najafi@swgas.com | ON JULY 2, 2019 AT 10:03 SOUTHWEST GAS CORPORATION (SWG) WAS NOTIFIED BY SCOTTSDALE FIRE DEPARTMENT OF A POSSIBLE BORE HIT AT SCOTTSDALE ROAD, NORTH OF SKY SONG BOULEVARD. SWG CREWS RESPONDED AND FOUND THAT A 2" SERVICE LINE HAD BEEN HIT BY THE HORIZONTAL DRILLING BIT BEING OPERATED BY A 3RD PARTY CONTRACTOR WORKING FOR A COMMUNICATIONS UTILITY COMPANY. SWG CONTROLLED THE FLOW OF GAS BY UTILIZING VALVES WHICH RESULTED IN AN OUTAGE OF 1,673 ACCOUNTS. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THE INCIDENT. SWG NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) ON JULY 2, 2019 AT 12:37 AND WAS GIVEN THE NRC REPORT #1250776. SWG PROVIDED AN UPDATE TO THE NRC ON JULY 3, 2019 AT 15:00 AND WAS GIVEN NRC REPORT #1250908.
2025-03-31 10:13 | NO | YES | NO | 20190080 | 32910 | 2019-07-23 19:16 | SUPPLEMENTAL FINAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2019-06-23 23:08 |  |  | 2019 | INDIAN CREEK DRIVE AT ROUTE EE | LANAGAN | MCDONALD COUNTY | MO | 64847-8888 | 36.5996 | -94.45 | [9 empty] | 2019-06-24 10:36 | 1249893 |  | NATURAL GAS |  | 74.49 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-06-23 23:15 |  |  |  | 2019-06-24 23:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 6.5 | 2.1 |  | CLASS 2 LOCATION | 0 | 0 | 140077 | 158469.816653322632556 | 500 | 565.652522017614 | 0 | 0 |  |  | 368 | 412.430446194225721784776902887139107612 |  | 0 | 140945 | 66249.2439536931777182388451443569553806 | 159447.8996215344722777847769028871391076 | 10 | 0 | 75 |  |  |  |  | 50 | 50 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ACTIONS OF THE CONTROLLER DID NOT CAUSE OR CONTRIBUTE TO THE EVENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | FLOODING CAUSED TREE TO OVERTURN, THE TREE'S ROOT SYSTEM THEN FRACTURED 2 INCH DISTRIBUTION MAIN. | NO | [218 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY | nicole.christianer@spireenergy.com | 314-349-2929 |  |  |  |  | CRAIG HOEFERLIN | VP OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | FLOODING CAUSED TREE TO OVERTURN, TREES ROOT SYSTEM THEN FRACTURED 2 INCH COATED STEEL MAIN NEAR INTERSECTION OF STATE HIGHWAY EE AND INDIAN CREEK LANAGAN, MISSOURI. GAS WAS MADE SAFE AT APPROXIMATELY 02:07 JUNE 24TH. A TEMPORARY BYPASS WAS INSTALLED UNTIL A PERMANENT REPAIR WAS COMPLETED. A 48 HOUR UPDATE TO THE NRC WAS MADE ON JUNE 26, 2019 AT 11:06AM. REPORT NUMBER 1250151.
2025-03-31 10:13 | NO | YES | NO | 20190081 | 33727 | 2019-07-24 15:34 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2019-06-21 07:00 |  |  | 2019 | 479 BROADWAY | LAWRENCE | ESSEX | MA | 01841 | 42.6839 | -71.1553 | [9 empty] | 2019-06-25 13:45 | 1250043 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2019-06-21 03:30 |  |  |  | 2019-06-21 03:35 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | 2009 | [8 empty] | OTHER | METER | [9 empty] | OTHER | [8 empty] | THE FIRE DEPARTMENT IDENTIFIED SEVERAL POSSIBLE IGNITION SOURCES, BUT WAS UNABLE TO DETERMINE THE CAUSE OF THE FIRE. METER HAD BEEN SHUT OFF SINCE 2016. EXAMINATION CONFIRMED THE GAS METER HAD BEEN TAMPERED WITH. | CLASS 3 LOCATION | 273600 | 309525.0600480383808 | 100 | 113.1305044035228 | 100 | 113.1305044035228 | 0 | 0 | 2A-LAWRENCE ASSESSORS INFORMATION |  | 0 | 0 |  | 0 | 273800 | 128289.7073214127626 | 309751.3210568454264 | 1 | 0 | 0 |  |  |  |  | 0.2 | 0.2 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | THEFT OF TRANSPORTED COMMODITY | [156 empty] | KATHERINE SILVER | COMPLIANCE MANAGER | ksilver@nisource.com | 508-864-1836 |  |  |  |  | KATHERINE SILVER | COMPLIANCE MANAGER | 508-864-1836 | ksilver@nisource.com | METER AT THIS LOCATION HAD BEEN SHUT OFF SINCE 2016. COLUMBIA GAS WAS CALLED TO SCENE TO SHUT OFF GAS TO THE BUILDING AROUND 0330 A.M. ON JUNE 21, 2019. GAS WAS SHUT OFF AT THE CURB VALVE. AT APPROXIMATELY 7:00 A.M. ON 6/21/19 THE FIRE CHIEF CALLED THE OPERATING CENTER MANAGER TO INFORM THE COMPANY THEY WOULD BE INVESTIGATING THE CAUSE OF THE FIRE. ON 6/25/2019 THE FIRE MARSHALL GAINED ACCESS TO PROPERTY TO INVESTIGATE. THEY FOUND THE METER LOCK REMOVED AND METER VALVE IN THE ON POSITION. THE INDEX TO THE METER HAD BEEN REMOVED AS WELL. A SECOND INVESTIGATION TOOK PLACE 8/6/2019 WHEN THE PROPERTY WAS SAFE TO RE-ENTER. THIS TEAM CONFIRMED THE GAS METER HAD BEEN TAMPERED WITH. UNABLE TO ELIMINATE MULTIPLE SOURCES OF IGNITION, THE CAUSE OF THE FIRE REMAINS UNDETERMINED AND THE INVESTIGATION HAS BEEN CLOSED.
2025-03-31 10:13 | NO | YES | NO | 20190082 | 32479 | 2019-07-29 16:18 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2019-07-01 14:27 |  |  | 2019 | TELL ROAD SW AT PINELLA DRIVE SW | ATLANTA | FULTON | GA | 30331 | 33.6805 | -84.5307 | [9 empty] | 2019-07-02 14:48 | 1250772 |  | NATURAL GAS |  | 7463 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-07-01 14:30 |  |  |  | 2019-07-01 14:47 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 96 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2004 | [5 empty] | 4 | ASTM D2513 | PHILLIPS-DRISCO PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 114380 | 129398.67093674937864 | 10000 | 11313.05044035228 | 0 | 0 |  |  | 20222 | 22663.5013123359580052493438320209973753 |  | 0 | 144602 | 79243.6404766858455224671916010498687664 | 163375.2226894376166452493438320209973753 | 0 | 0 | 84 |  |  |  |  | 45 | 45 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | ELECTRIC | YES | 4189400028 |  |  | CONTRACT LOCATOR | YES | YES | 26 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | 404-584-4910 | rslagle@southernco.com | A 4-INCH PLASTIC NATURAL GAS MAIN WAS RUPTURED BY A CONTRACT CREW WHILE INSTALLING ELECTRIC CABLE BY DIRECTIONAL DRILLING. ONCE THE INCIDENT WAS MADE SAFE IT WAS IDENTIFIED THAT REPAIRS TO THE AFFECTED PIPELINE WOULD EXCEED THE $50,000 THRESHOLD FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. NOTIFICATION TO THE ONE-CALL CENTER WAS MADE WHERE THE MAIN WAS CORRECTLY LOCATED, HOWEVER, THE EXCAVATOR FAILED TO POTHOLE WHERE THE FACILITY WAS DAMAGED. ADDITIONAL NRC REPORT NUMBER 1251281 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2025-03-31 10:13 | NO | YES | YES | 20190083 | 33391 | 2019-08-01 11:34 | SUPPLEMENTAL FINAL | 20211 | ATMOS ENERGY CORPORATION - KY/MID-STATES (MID-STATES) | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2019-07-03 09:35 |  |  | 2019 | INTERSECTION OF VOLUNTEER PARKWAY AND BROAD STREET | BRISTOL | SULLIVAN | TN | 37620 | 36.5928 | -82.189 | [9 empty] | 2019-07-03 10:42 | 1250847 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | YES | 3 | 0 | 0 | 0 | 0 | 3 | YES |  |  |  |  | NO | 0 | 2019-07-03 09:35 |  |  |  | 2019-07-03 08:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 42 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1954 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 5000 | 5656.52522017614 | 0 | 0 |  |  | 0 | 0 |  | 0 | 5000 | 2342.763099368385 | 5656.52522017614 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FAILURE OCCURRED DURING SCHEDULED OPERATIONS AND NOT VISIBLY MONITORED THRU SCADA | [12 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | ALTHOUGH NO DIRECT SOURCE OF IGNITION HAS BEEN DETERMINED, SEVERAL STEPS WERE CONDUCTED TO CONSTRUCTION PRACTICES AS A RESULT: 1. IMMEDIATE REVIEW OF HAZARDOUS ENVIRONMENT AWARENESS, ENGINEERING CONTROLS, AND MONITORING OF HAZARDOUS ENVIRONMENTS WAS CONDUCTED WITH FIELD EMPLOYEES (MEMO DATED 9/3/19). 2. REVIEW OF COMPANY PROCEDURES REGARDING PPE LEVELS AND WORK TASKS BEING PERFORMED. 3. REVIEW OF PRACTICES REGARDING EXISTING REPAIR CLAMPS DURING REPAIRS. |  | YES |  |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | JACK M. SANDERS | MANAGER OF COMPLIANCE | jack.sanders@atmosenergy.com | 615-771-8387 |  |  |  |  | GREG W. SMITH | DIRECTOR SYSTEM INTEGRITY AND COMPLIANCE | 615 771-8356 | greg.smith@atmosenergy.com | ORIGINAL DOT INCIDENT REPORT #1250847 48 HR. NRC FOLLOW UP REPORT #1250999 ON 7/3/19 AT APPROX. 0830 ATMOS ENERGY CONSTRUCTION CREW ARRIVED FOR A SCHEDULED GRADE 2 LEAK REPAIR ON A 6' STEEL MAIN WITHIN THE INTERSECTION OF VOLUNTEER PARKWAY AND BROAD ST. UPON EXPOSURE, LEAK APPEARED TO BE BETWEEN (2) EXISTING CLAMPS INSTALLED DURING A PRIOR REPAIR. THE CREW ENTERED THE EXCAVATION WITH INTENT TO TIGHTEN THE EXISTING CLAMPS TO REMEDY THE LEAK. SAFETY PRECAUTIONS WERE IN PLACE INCLUDING ACTIVE MONITORING OF % GAS WITHIN THE BELL HOLE AND MANNED FIRE EXTINGUISHER. AT NO TIME WAS A SIGNIFICANT RELEASE OF GAS HEARD OR RECORDED BY INSTRUMENT WHICH WOULD INDICATE A FLAMMABLE ENVIRONMENT. HOWEVER, DURING THE REPAIR AT APPROX. 0935, NATURAL GAS IGNITED/FLASHED AND INJURED THREE CONSTRUCTION EMPLOYEES. NO SUSTAINED FLAME EXISTED WHICH REQUIRED SHUTDOWN OF THE GAS PIPING SYSTEM AND PUBLIC RISK WAS ASSESSED AND CONFIRMED AS NON-HAZARDOUS WITH LOCAL EMERGENCY RESPONSE PERSONNEL ON THE SCENE. REPORTING TO TPUC, PHMSA, AND OSHA WAS COMPLETED WHEN THE OPERATOR CONFIRMED THAT THERE WAS PERSONAL INJURY NECESSITATING IN-PATIENT HOSPITALIZATION. THE DECISION WAS MADE TO INITIATE A REPLACEMENT PROJECT RATHER THAN A TEMPORARY REPAIR. REPLACEMENT OF THE PIPELINE WAS COMPLETED ON 9/25/19 AS DESCRIBED PER THE PROJECT SCOPE IN THE ORIGINAL REPORT NARRATIVE (#1250999).
2025-03-31 10:13 | NO | NO | NO | 20190084 | 32782 | 2019-08-01 16:17 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2019-07-01 01:09 |  |  | 2019 | 17555 HEIDELBERG WAY | LAKEVILLE | DAKOTA | MN | 55044 | 44.6952 | -93.2369 | [9 empty] | 2019-07-01 04:18 | 1250731 |  | NATURAL GAS |  | 0.01 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-07-01 01:09 |  |  |  | 2019-07-01 01:52 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2006 | [8 empty] | OTHER | DIE-CAST ALUMINIUM | [9 empty] | OTHER | [8 empty] | HEAT FROM A FIRE CAUSED BY A LIGHTNING STRIKE WEAKENED THE BACK OF THE METER CAUSING IT TO BURST AND RELEASE A SMALL AMOUNT OF GAS. | CLASS 3 LOCATION | 50000 | 56565.2522017614 | 400 | 452.5220176140912 | 1500 | 1696.957566052842 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 51900 | 24317.8809714438363 | 58714.7317854283332 | 0 | 0 | 1 |  |  |  |  | 2 | 2 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  | ,,, | NO | [218 empty] | AARON ABRAHAMSON | OPERATION SPECIALIST II | aaron.abrahamson@centerpointenergy.com | 612-321-5514 |  |  |  |  | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 612-321-5366 | dean.headlee@centerpointenergy.com | THE LAKEVILLE FIRE DEPARTMENT ARRIVED ON SCENE AND FOUND THE CORNER OF THE HOUSE NEAR THE METER SET ON FIRE.THE FIRE DEPARTMENT EXTINGUISHED THE FLAMES AND TURNED THE SERVICE VALVE ON THE RISER OFF. WHILE THE FIRE DEPARTMENT WAS INSIDE A LOUD "POP" WAS HEARD OUTSIDE. UPON FURTHER INVESTIGATION THE FIRE ON THE CORNER OF THE HOUSE NEAR THE METER SET HAD WEAKENED THE BACK OF THE METER AND CAUSED IT TO BURST WHICH RELEASED A SMALL AMOUNT OF GAS, THERE WAS NO FIRE OR DAMAGE CAUSED BY THE RELEASE OF GAS. CENTERPOINT ENERGY'S FIRE INVESTIGATOR FOUND LIGHTNING HAD STRUCK THE HOUSE OPPOSITE OF WHERE THE METER IS LOCATED. THE LIGHTNING THEN TRAVELED THROUGH THE HOUSE AND CAUSED A FIRE ON THE CORNER OF THE HOUSE NEAR THE GAS METER. THE METER SET WAS NEVER ON FIRE AND THE FIRE WAS NOT GAS FED. CENTERPOINT BELIEVES ITS FACILITIES DID NOT CONTRIBUTE TO THE DAMAGE CAUSED BY THE LIGHTNING STRIKE. UPDATE 10/04/2019 THE METER AND SET WAS REPLACED AND GAS SERVICE WAS REINSTATED SEPTEMBER 17 2019. NO OTHER DETAILS HAVE CHANGED.
2025-03-31 10:13 | NO | YES | NO | 20190086 | 32579 | 2019-08-01 21:11 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2019-07-05 20:30 |  |  | 2019 | 1661 N BROWN RD | INYOKERN | KERN | CA | 93555 | 35.6202 | -117.8117 | [9 empty] | 2019-07-07 21:57 | 1251255 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-07-05 20:22 |  |  |  | 2019-07-04 10:33 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1987 | [5 empty] | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | UNKNOWN |  |  |  | UNKNOWN |  | OTHER | [8 empty] | MULTIPLE LEAKS ACROSS VARYING AREAS | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 2670000 | 3020584.46757405876 | 0 | 0 |  |  | 9 | 10.08661417322834645669291338582677165354 |  | 0 | 2670009 | 1251044.82577137900732283464566929133858 | 3020594.55418823198834645669291338582677 | 0 | 0 | 157 |  |  |  |  | 51 | 51 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | NOTIFIED VIA DISPATCH |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO ALARMS COMING INTO GAS CONTROL | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [56 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | EARTHQUAKE |  |  |  |  | NO | [218 empty] | ALBERTA EKUKINAM | REGULATORY COMPLIANCE | u.alberta.ekukinam@pge.com | 9252443262 |  |  |  |  | SUSIE RICHMOND | MANAGER - REGULATORY COMPLIANCE | 9253285776 | susie.richmond@pge.com | ON JULY 4, 2019 AT APPROXIMATELY 1033 HOURS, PG&E WAS NOTIFIED OF A MAGNITUDE 6.3 EARTHQUAKE NEAR THE TOWN OF RIDGECREST WITH NO KNOWN DAMAGE. ON JULY 5, 2019 AT APPROXIMATELY 2022 HOURS, PG&E WAS NOTIFIED OF ANOTHER MAGNITUDE 7.1 EARTHQUAKE NEAR THE TOWN OF RIDGECREST. THE OEC AND GEC WERE ACTIVATED TO SUPPORT THIS EVENT. AS OF 7/5/19 AT APPROXIMATELY 2220 HOURS, PG&E RECEIVED MORE THAN 10 GAS ODOR CALLS AND PG&E PERSONNEL WERE ALREADY ON-SCENE DUE TO THE INITIAL EARTHQUAKE ON 7/4/19. INSPECTIONS, LEAK SURVEYS, AND PATROLS WERE CONDUCTED AT THE IMPACTED AREAS THROUGHOUT THE WEEKEND. AS OF 7/7/19 AT 2000 HOURS, THE REPAIR CREWS HAVE COMPLETED 19 DISTRIBUTION GRADE 1 LEAK REPAIRS AND FIELD SERVICES HAVE RESTORED SERVICE TO APPROXIMATELY 157 CUSTOMERS. ON 7/11/19 AT 0900 HOURS, PG&E CONDUCTED CLEARANCES FOR L-372 MP 2.84 AND L-311 MP 34.75 SHUTDOWNS NEAR THE FAULT CROSSING LOCATIONS TO REPLACE THE DAMAGED SECTIONS OF BOTH TRANSMISSION PIPELINES. THERE WERE NO CONFIRMED RELEASES FROM PG&E TRANSMISSION FACILITIES AND THE TRANSMISSION PIPELINES AT THE FAULT CROSSINGS ARE IN A CLASS 1, NON-HCA LOCATION. LNG TO SUPPLY RIDGECREST WAS SCHEDULED FOR 7/10/19 AND AS OF 7/24/19, PG&E HAS COMPLETED THE FOLLOWING REPAIR ACTIVITIES IN THE RIDGECREST AND TRONAS AREAS: - GRADE 1 LEAKS - COMPLETED 53, OPEN 0, CANCELLED 5 - GRADE 2 LEAKS - COMPLETED 74, OPEN 0, CANCELLED 3 - GRADE 3 LEAKS - COMPLETED 58, OPEN 162, CANCELLED 0 THERE ARE NO REPORTS OF INJURIES OR FATALITIES AND POLICE, FIRE, AND MEDIA WERE REPORTED ON-SITE. THIS INCIDENT WAS REPORTED ON 7/5/19 TO THE CPUC DUE TO PUBLIC ATTENTION AND SUSPICION OF NATURAL GAS INVOLVEMENT AND TO THE DOT (NRC#1251255) ON 7/7/19 AT 1857 HOURS ONCE IT WAS DETERMINED THAT REPAIR COSTS WOULD EXCEED $50K. THE COST CRITERIA WAS DETERMINED ON 7/7/19 AT APPROXIMATELY 1830 HOURS. AN UPDATE TO THE DOT(#NRC1251313) WAS PROVIDED ON 7/8/19.
2025-03-31 10:13 | NO | YES | YES | 20190087 | 35282 | 2019-08-02 14:10 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD N.E. SUITE 20 | ALBUQUERQUE | NM | 87109 | 2019-07-03 08:34 | MOUNTAIN | NO | 2019 | 5204 N. ATKINSON | ROSWELL | CHAVEZ | NM | 88201 | 33.4595 | -104.5062 | [5 empty] | YES |  |  |  | 2019-07-03 15:52 | 1250910 |  | NATURAL GAS |  | 1 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2019-07-03 08:34 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 10 | 2019-07-03 15:40 |  |  |  | 2019-07-03 15:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER A BUILDING |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1990 | [5 empty] | 2 | ASTM D2513 | DRISCO PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.216 |  | 3408 | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | 250000 | 282826.261008807 | 182 | 205.897518014411496 | 12505 | 14146.96957566052614 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 262687 | 123082.682056756590099 | 297179.128102481937636 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 45 | 45 | 51 | 192.619(A)(1) | 2013-05-07 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, ELECTROFUSION |  | 1990 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) |  |  |  |  | YES |  | YES | [8 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | YES | 1990 | 112 | [84 empty] | ANDREA MARTINEZ | PIPELINE SAFETY MANAGEMENT SYSTEMS MANAGER | andrea.martinez@nmgco.com | 505-697-3518 |  |  |  |  | TOM BULLARD | VP ENG-GAS MGMT-TECH SERVICES | 5056973599 | tom.bullard@nmgco.com | ON JULY 3, 2019, AN EXPLOSION OCCURRED AT 08:18 AT 5204 N. ATKINSON IN ROSWELL, NM 88201. AT 8:34, NM GAS WAS NOTIFIED BY DISPATCH THAT THERE WAS A HOUSE FIRE AT THE ADDRESS. NM GAS ARRIVED AT THE PROPERTY AT 08:53. THE GAS METER FOR THE PROPERTY HAD ALREADY BEEN TURNED OFF AT THE SERVICE VALVE BY THE ROSWELL FIRE DEPARTMENT. NM GAS REMOVED, CAPPED OFF, AND PLUGGED THE METER AND CUSTOMER SERVICE LINE. THE SERVICE RISER WAS SOAPED AND NO LEAKS WERE OBSERVED. NM GAS REMOVED THE METER AND THEN PROBED THAT AREA WHERE THE METER WAS LOCATED FOR THE PRESENCE OF GAS. NO GAS WAS DETECTED. NM GAS LEFT BECAUSE THE STRUCTURE WAS STILL BURNING, PREVENTING ANY FURTHER INVESTIGATION. NM GAS RETURNED TO THE SCENE AT 12:15 AFTER LOCAL AUTHORITIES SUPPRESSED THE STRUCTURE FIRE. NM GAS BEGAN PROBING FOR GAS AT 12:45. AT 13:10, GAS ODORANT TESTING WITH A HEATH ODOROMETER WAS CONDUCTED REVEALING SUFFICIENT ODORANT AT 0.38% GAS-IN-AIR. AT 13:20, THE LEAK WAS PINPOINTED NEAR THE MAIN AND SERVICE AT THE SW CORNER OF THE INTERSECTION OF ISLER AND ATKINSON. SUBSURFACE IN GROUND GAS CONCENTRATION READINGS OF 96% WERE REGISTERED AT THE SW CORNER OF THE INTERSECTION OF ISLER AND ATKINSON. AT 15:15 EXCAVATION BEGAN AT THE SW CORNER OF THE INTERSECTION OF ISLER AND ATKINSON. AT 15:40 NM GAS UNCOVERED THE LEAK AT THE SW CORNER OF THE INTERSECTION OF ISLER AND ATKINSON. AT 16:00 AND 16:05, ADDITIONAL GAS ODORANT TESTING WITH A HEATH ODOROMETER WAS PERFORMED SHOWING APPROPRIATE ODORANT LEVELS AT 0.32% GAS-IN-AIR. AT 16:14, THE LEAK WAS SEALED OFF BY SQUEEZING OFF FLOW 54 FEET UPSTREAM OF THE LEAK LOCATION. THE LEAK WAS REPAIRED AT 18:40 BY REPLACEMENT OF A 2" TEE FITTING. RE-LIGHTING OF THE SURROUNDING HOMES BEGAN AT 19:00 FOR THE 13 CUSTOMERS AFFECTED BY THE OUTAGE FOR REPAIRS AND WAS COMPLETED BY 21:00. FIVE NO ACCESS TAGS WERE LEFT ON CUSTOMERS' DOORS. GAS ODORANT TESTING WAS PERFORMED BY NM GAS ONE LAST TIME AT 21:30. READINGS CONFIRMED PROPER ODORANT AT 0.24% GAS-IN-AIR. ADDITIONAL NRC REPORT #1250929. ESTIMATED DAMAGES WERE $262,687. REGARDING QUESTIONS PART A #7 AND PART A #21C THE FORM DOES NOT ALLOW AN ENTRY OF "UNKNOWN" BECAUSE A CALCULATION CANNOT BE PERFORMED DUE TO LIMITED OR UNKNOWN INFORMATION NEEDED TO PERFORM THE CALCULATION, PHMSA APPROVED THE AMOUNT ENTERED IN RESPONSE TO EACH OF THESE QUESTIONS.
2025-03-31 10:13 | NO | NO | NO | 20190088 | 32945 | 2019-08-12 09:18 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2019-07-20 11:54 |  |  | 2019 | 14151 GREEN VIEW CT | EDEN PRAIRIE | HENNEPIN | MN | 55346 | 44.873 | -93.4569 | [9 empty] | 2019-07-20 14:07 | 1252640 |  | NATURAL GAS |  | 8.09 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2019-07-20 11:35 |  |  |  | 2019-07-20 11:54 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1974 | [8 empty] | COPPER | [10 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 50000 | 56565.2522017614 | 200 | 226.2610088070456 | 1600 | 1810.0880704563648 | 0 | 0 |  |  | 50 | 56.03674540682414698162729658792650918635 |  | 0 | 51850 | 24322.8629797976759490813648293963254593 | 58657.6380264316345469816272965879265092 | 0 | 0 | 0 |  |  |  |  | 50 | 50 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  | ,,, | NO | [218 empty] | AARON ABRAHAMSON | OPERATION SPECIALIST II | aaron.abrahamson@centerpointenergy.com | 612-321-5514 |  |  |  |  | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 612-321-5366 | dean.headlee@centerpointenergy.com | LIGHTNING STRUCK A TREE NEAR 14151 GREEN VIEW CT, EDEN PRAIRIE, MN CAUSING A FIRE AND A GAS LEAK. THE ESTIMATED COST OF DAMAGE FROM THE INCIDENT EXCEEDS $50,000. ALL INVESTIGATIONS COMPLETE AND SERVICE RESTORED ON 10/28/2019.
2025-03-31 10:13 | NO | YES | YES | 20190089 | 32618 | 2019-08-12 21:24 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2019-07-15 10:58 |  |  | 2019 | 23562 WOODEN HORSE TRAIL | MURRIETA | RIVERSIDE | CA | 92562 | 33.5974 | -117.2115 | [9 empty] | 2019-07-15 16:46 | 1252045 |  | NATURAL GAS |  | 9.47 |  | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | YES | 25 | 2019-07-15 10:58 |  |  |  | 2019-07-15 11:23 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 25 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1996 | [5 empty] | 0.5 | D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 7 |  |  | 2406 | MECHANICAL PUNCTURE | 0.7 | 0.6 | [7 empty] | CLASS 3 LOCATION | 1200000 | 1357566.0528422736 | 3000 | 3393.915132105684 | 15207 | 17203.755804643712196 | 2000 | 2262.610088070456 | PORTA POTTIES AND FOOD |  | 57 | 63.88188976377952755905511811023622047244 |  | 0 | 1220264 | 571790.2811263887675169527559055118110236 | 1380490.21575685723172355905511811023622 | 0 | 0 | 7 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | DRILLING | ELECTRIC | NO | [5 empty] | YES |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | KHOA LE | SR PIPELINE SAFETY AND COMPLIANCE ADVISOR | kle2@semprautilities.com | 6268934536 |  |  |  |  | KHOA LE | SR PIPELINE SAFETY AND COMPLIANCE ADVISOR | 6268934536 | kle2@semprautilities.com | AT APPROXIMATELY 10:58 AM ON JULY 15TH, 2019, MURRIETA POLICE & FIRE NOTIFIED SOCALGAS OF A THIRD-PARTY DAMAGE AT 23562 WOODEN HORSE TRAIL, MURRIETA. SOCALGAS CREW RESPONDED AND WAS INFORMED BY FIRE DEPARTMENT PERSONNEL ON-SCENE THAT A THIRD-PARTY CONTRACTOR DAMAGED A GAS SERVICE LINE CAUSING A RELEASE OF GAS. CREW INITIATED WORK TO CONTROL THE GAS. DURING THE PROCESS OF GETTING THE GAS UNDER CONTROL, AN EXPLOSION OCCURRED RESULTING IN 1 COMPANY EMPLOYEE FATALITY AND MULTIPLE INJURIES. ONE OF THE INDIVIDUAL INJURED WAS ADMITTED TO THE HOSPITAL. INVESTIGATION SHOWED THAT THE CONTRACTOR DID NOT REQUEST A ONE CALL TICKET FOR THE WORK PERFORMED. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO A GAS RELEASE, FATALITY, AND DAMAGES EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, PLEASE CONTACT KHOA LE AT (626) 893 - 4536.
2025-03-31 10:13 | NO | YES | NO | 20190090 | 32569 | 2019-08-16 09:30 | ORIGINAL FINAL | 2432 | FLORIDA CITY GAS | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2019-07-24 17:26 |  |  | 2019 | 756 E PRIMA VISTA BLVD (NW CORNER OF E PRIMA VISTA BLVD & NE CAMINO ST) | PORT ST LUCIE | ST LUCIE | FL | 34952 | 27.3262 | -80.3242 | [9 empty] | 2019-07-25 12:10 | 1253132 |  | NATURAL GAS |  | 4050 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 4 | 2019-07-24 17:26 |  |  |  | 2019-07-24 18:09 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 108 |  | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2007 | [5 empty] | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2.5 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 3000 | 3393.915132105684 | 450000 | 509087.2698158526 | 0 | 0 |  |  | 50000 | 56036.7454068241469816272965879265091864 |  | 0 | 503000 | 264091.6071439830300813648293963254593176 | 568517.9303547824309816272965879265091864 | 3 | 0 | 24 |  |  |  |  | 40 | 45 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS A THIRD PARTY DAMAGE WHICH WAS REPORTED IMMEDIATELY TO THE CALL CENTER. IT WOULD NOT BE POSSIBLE TO IDENTIFY THE DAMAGE FROM INCREASE IN FLOW ON THE SCADA SYSTEM. THE CONTROLLER'S ACTION WERE DETERMINED TO HAVE NO ACTION ON THE CAUSE OF OR A CONTRIBUTING FACTOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | ELECTRIC | YES | 203908145 | SUNSHINE 811 |  | UTILITY OWNER | YES | YES | 40 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | SERGEY PESCHANYY | ENGINEERING LEADER REGULATORY COMPLIANCE QA | sergey.peschanyy@nexteraenergy.com | 7864132955 |  |  |  |  | SERGEY PESCHANYY | ENGINEERING LEADER REGULATORY COMPLIANCE QA | 7864132955 | sergey.peschanyy@nexteraenergy.com | ON 7/24/19 AT APPROXIMATELY 17:26 FLORIDA CITY GAS WAS NOTIFIED OF A RUPTURED GAS MAIN AT 756 E PRIMA VISTA BLVD, PORT ST LUCIE, FL. FLORIDA CITY GAS FIRST RESPONDER WAS DISPATCHED AT 17:29 AND ARRIVED ON SITE AT 18:09. UPON ARRIVAL REPORTED BLOWING GAS CONDITION DUE TO DIRECTIONAL BORE MACHINE. THERE WERE NO FATALITIES OR INJURIES AS A RESULT OF THIS INCIDENT OR DURING THE RESPONSE TO THIS INCIDENT. THE INCIDENT SITE WAS MADE SAFE AT APPROXIMATELY 23:30 ON JULY 25, 2019. THE PORT ST LUCIE FIRE DEPARTMENT, POLICE DEPARTMENT, PUBLIC WORKS AND MEDIA OUTLETS WERE ON LOCATION. A THIRD PARTY CONTRACTOR WAS EXCAVATING WITH DIRECTIONAL BORING MACHINE WHEN IT HIT THE 4-INCH GAS MAIN. EXCAVATOR STATED THAT THE 4-INCH GAS MAIN WAS SPOTTED PRIOR TO EXCAVATION BEGAN; HOWEVER, THE SOFT DIG TOOK PLACE APPROX. 10 FT NORTH OF THE CROSSING POINT. EXCAVATOR FURTHER STATED THE DEPTH OF GAS MAIN AT THE POINT OF CONFLICT WAS ASSUMED TO BE THE SAME DEPTH AS WHERE THE SPOT DIG TOOK PLACE. THE RUPTURE WAS ISOLATED BY SQUEEZING OFF THE 4-INCH GAS MAIN AT APPROXIMATELY 23:30, 7/25/19, AS A RESULT GAS SERVICE TO 27 ACTIVE CUSTOMERS WAS INTERRUPTED. THE DEPTH OF DAMAGED SECTION OF THE 4-INCH GAS MAIN WAS APPROXIMATELY 9FT, WHICH WAS DAMAGED BY A DIRECTIONAL DRILL DURING PULLBACK. THE DAMAGED SECTION WAS REPLACED WITH PRESSURE TESTED SECTION OF 4-INCH PE AND SERVICES WERE RELIT SUBSEQUENTLY. THE CAUSE OF THE INCIDENT WAS DETERMINED TO BE FAILURE OF THE EXCAVATOR TO COMPLY WITH F.S 556.105.5(C): EXCAVATOR DID NOT SPOT DIG THE UNDERGROUND UTILITY BEFORE USING MECHANIZED EQUIPMENT WITHIN THE TOLERANCE ZONE OF THE MARKED UTILITY AND AT THE POINT OF CROSSING.
2025-03-31 10:13 | NO | YES | NO | 20190091 | 32573 | 2019-08-16 14:56 | ORIGINAL FINAL | 12876 | DOMINION ENERGY UTAH/WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2019-07-17 11:38 |  |  | 2019 | 368 W 3000 N (W MILLCREEK CIRCLE) | PLEASANT GROVE | UTAH | UT | 84062 | 40.3962 | -111.7461 | [9 empty] | 2019-07-17 13:16 | 1252286 |  | NATURAL GAS |  | 13 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2019-07-17 12:31 |  |  |  | 2019-07-17 12:03 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2005 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | DAMAGE | [5 empty] | CLASS 3 LOCATION | 1000000 | 1131305.044035228 | 300 | 339.3915132105684 | 3400 | 3846.4371497197752 | 0 | 0 |  |  | 58 | 65.00262467191601049868766404199475065617 |  | 0 | 1003758 | 470346.3958008054054249343832020997375328 | 1135555.87532283025961049868766404199475 | 0 | 0 | 1 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LAUREN SKUFCA | ENGINEER-COMPLIANCE | lauren.l.skufca@dominionenergy.com | 8013243746 |  |  |  |  | REID HESS | MANAGER- GAS OPERATIONS | 8013243374 | reid.hess@dominionenergy.com | DOMINION ENERGY UTAH (DEU) WAS NOTIFIED ON JULY 17, 2019 AT 11:38 FROM A CUSTOMER (3RD PARTY) OF A DAMAGED AND LEAKING METER. DEU RESPONDED TO FIND THAT THE NATURAL GAS METER HAD BEEN PULLED OFF OF THE RISER AND FUEL LINE BY A VEHICLE. THE ESCAPING GAS FROM THE DAMAGED METER CAUGHT FIRE AND IGNITED CAUSING THE RESIDENCE TO CATCH ON FIRE. UPON DEU ARRIVAL, THE LOCAL FIRE DEPARTMENT HAD ALREADY ARRIVED AND WAS ABLE TO STOP THE FLOW OF GAS BY TURNING THE SERVICE VALVE AT APPROXIMATELY 11:58 AM. AFTER THE AREA WAS CLEARED BY THE FIRE DEPARTMENT, DEU CREWS LEAK SCREENED THE AREA AND PRESSURE TESTED THE SERVICE LINE WITH NO LEAKS FOUND. DEU THEN RETIRED THE SERVICE LINE TO THE RESIDENCE.
2025-03-31 10:13 | YES | NO | NO | 20190092 | 33562 | 2019-08-20 19:39 | SUPPLEMENTAL FINAL | 18112 | SAN DIEGO GAS & ELECTRIC CO | 8326 CENTURY PARK COURT | SAN DIEGO | CA | 92123 | 2019-07-21 13:45 |  |  | 2019 | 13115 SILVER SADDLE LANE | POWAY | SAN DIEGO | CA | 92064 | 33.008 | -117.047 | [9 empty] | 2019-07-21 16:03 | 1252731 |  | NATURAL GAS |  | 1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2019-07-21 13:28 |  |  |  | 2019-07-21 13:55 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | STRUCTURE FIRE MELTED REGULATOR AND METER | CLASS 3 LOCATION | 0 | 0 | 610 | 690.09607686148908 | 200 | 226.2610088070456 | 0 | 0 |  |  | 6 | 6.72440944881889763779527559055118110236 |  | 0 | 816 | 385.748094538623251889763779527559055118 | 923.081495117353577637795275590551181102 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | BRYON WALSH | PIPELINE SAFETY AND COMPLIANCE ADVISOR | bwalsh@sdge.com | 6199921473 |  |  |  |  | BRYON WALSH | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 6199921473 | bwalsh@sdge.com | ON JULY 21ST, 2019, SDG&E WAS NOTIFIED OF A STRUCTURE FIRE AT 13115 SILVER SADDLE LANE, POWAY. SDG&E PERSONNEL WERE SENT TO THE SCENE TO INVESTIGATE. WHEN THE CREW ARRIVED, THEY FOUND THE SERVICE VALVE HAD BEEN SHUT BY THE FIRE DEPT. THE SERVICE VALVE WAS FOUND TO BE LEAKING GAS LIKELY DUE TO THE HEAT OF THE FIRE OR THROUGH THE VALVE CLOSURE OPERATION PERFORMED BY THE FIRE DEPARTMENT. THE GAS REGULATOR AND METER WERE COMPLETELY MELTED. CREW DUG A REMOTE CONTROL HOLE TO CONTROL THE GAS AT 15:25. CREW REPLACED THE SERVICE VALVE AND CONDUCTED A PRESSURE TEST ON THE ABANDONED SECTION OF THE SERVICE. THE PRESSURE TEST HELD, CONFIRMING NO LEAKS ON THAT SECTION OF THE SERVICE. THE REMAINING SERVICE AND SERVICE TO MAIN CONNECTION WERE ALL CHECKED FOR UNDERGROUND LEAKAGE WITH NO UNDERGROUND INDICATIONS OF GAS LEAKAGE WERE FOUND. LAST LEAK SURVEY COMPLETED ON 09/06/2018 AND SHOWS NO LEAKAGE FOUND. THERE WERE NO INJURIES, NOR FATALITIES REPORTED DUE TO THE RELEASE OF GAS. THE FIRE DEPARTMENT DID NOT DO ANY TYPE OF INVESTIGATION ON THE CAUSE OF THE FIRE, AS THEY SUSPECTED NO FOUL PLAY. THIS WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE, MEDIA, AND DAMAGES EXCEEDING $50,000. 04/01/2020- SDG&E INVESTIGATION DETERMINED THE FIRE STARTED FROM ANOTHER SOURCE OTHER THAN SDG&E FACILITIES, AS A RESULT SDG&E FACILITIES WERE SECONDARY TO THE FIRE. AT THIS TIME, SDG&E WILL BE CLOSING OUT THE FILE ON THIS CASE.
2025-03-31 10:13 | NO | YES | NO | 20190093 | 32595 | 2019-08-22 12:54 | ORIGINAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2019-07-29 12:30 |  |  | 2019 | ENTIRE CITY | ALICE | JIM WELLS | TX | 78332 | 27.7598 | -98.0717 | [9 empty] | 2019-07-29 13:10 | 1253528 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-07-29 12:30 |  |  |  | 2019-07-29 12:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | OTHER | LOSS OF GAS SUPPLY FROM SUPPLIER |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | LOSS OF GAS SUPPLY FROM SUPPLIER | UNKNOWN | [8 empty] | OTHER | LOSS OF GAS SUPPLY FROM SUPPLIER | [9 empty] | OTHER | [8 empty] | LOSS OF GAS SUPPLY FROM SUPPLIER | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 565000 | 639187.34987990382 | 0 | 0 |  |  | 0 | 0 |  | 0 | 565000 | 264732.230228627505 | 639187.34987990382 | 0 | 0 | 4134 |  |  |  |  | 0 | 0 | 0 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | NOTIFICATION FROM SUPPLIER |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | ALL OTHER CAUSES | MISCELLANEOUS | [232 empty] | MISCELLANEOUS | LOSS OF GAS SUPPLY FROM SUPPLIER | [47 empty] | LESLIE DAVENPORT | COMPLIANCE COORDINATOR LL | leslie.davenport@centerpointenergy.com | 713-967-7325 | 713-967-7307 |  |  |  | STEVE YARBROUGH | REGIONAL OPERATIONS DIRECTOR | 713-207-5700 | steve.yarbrough@centerpointenergy.com | LOSS OF GAS SUPPLY FROM ENERGY TRANSFER PIPELINE TO CENTERPOINT ENERGY DISTRIBUTION SYSTEM IN ALICE, TEXAS, FORCED CENTERPOINT ENERGY TO PERFORM RE-LITE OF APPROXIMATELY 4100 CUSTOMERS.
2025-03-31 10:13 | NO | YES | YES | 20190095 | 36146 | 2019-08-30 15:40 | SUPPLEMENTAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY SUITE 100 | CANONSBURG | PA | 15317 | 2019-07-31 15:45 | EASTERN | YES | 2019 | 100 PARK LANE | WASHINGTON | WASHINGTON | PA | 15301 | 40.163 | -80.2525 | YES | [8 empty] | 2019-07-31 16:29 | 1253797 |  | NATURAL GAS |  | 3 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 1 | 0 | 0 | 1 | NO | [5 empty] | 0 | 2019-07-31 16:03 |  |  |  | 2019-07-31 16:03 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 | NO | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2013 |  | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | OTHER | NO REGULATOR FOR UPRATE | [5 empty] | CLASS 3 LOCATION | 272000 | 307714.971977582016 | 337 | 381.249799839871836 | 10000 | 11313.05044035228 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 282337 | 132289.741037274343149 | 319409.272217774167836 | 0 | 0 | 63 | 2 | 0 | 1 | 0 | 40 | 40 | 45 | 192.619(A)(2) | 1982-07-15 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 9 | 0 | YES | 8 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | SERVICE REGULATOR WAS NOT INSTALLED AT 100 PARK LANE, WASHINGTON, PA BEFORE INCREASING LINE PRESSURE AS PART OF AN UPRATE OPERATION. |  |  |  | YES | WHILE THE COMPANY HAS ESTABLISHED PROCEDURES AND PROCESSES TO BE TAKEN FOR UPRATES THAT INCLUDE REVIEW OF MATERIALS, MAPS, AND RECORDS, IN THIS INSTANCE THAT REVIEW DID NOT IDENTIFY 100 PARK LANE, WASHINGTON, PA AS BEING SERVED FROM THE SYSTEM THAT WAS INVOLVED IN THE UPRATE PROJECT. | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | RICHARD BURKE | OPERATIONS COMPLIANCE MANAGER | rburke@nisource.com | 17243217155 |  |  |  |  | CURTIS J. ANSTEAD |  | 4199576404 | cjanstead@nisource.com | ON JULY 31, 2019 A HOME AT 100 PARK LANE, WASHINGTON, PA EXPLODED. THREE EMERGENCY RESPONDERS AND THE CUSTOMER AT 100 PARK LANE WERE SENT TO THE HOSPITAL, ONE OF WHOM REQUIRED ADMITTANCE. THERE WERE NO LIFE THREATENING INJURIES. THE COMPANY WAS IN THE FINAL STAGES OF A PRESSURE UPRATE PROJECT. THE GAS SYSTEM PRESSURE WAS BEING INCREASED FROM LOW PRESSURE (INCHES OF WATER COLUMN) TO MEDIUM PRESSURE (40 PSIG). SERVICE AND MAINLINE RECORDS DID NOT INDICATE THAT 100 PARK LANE WAS SERVED FROM THE SYSTEM BEING UPRATED. THEREFORE A SERVICE REGULATOR WAS NOT INSTALLED AT THE METER ON THE PREMISES TO CONTROL ELEVATED PRESSURE. SINCE NO SERVICE REGULATOR WAS INSTALLED, GAS ENTERED THE HOUSE AND REACHED APPLIANCES AT A LINE PRESSURE OF 40 PSIG. THE FIRE MARSHAL'S REPORT INDICATES THAT THE FURNACE IN THE HOME WAS THE SOURCE OF IGNITION. AFTER THE INCIDENT, IT WAS DISCOVERED THE SERVICE LINE FOR 100 PARK LANE WAS TAPPED INTO A MAINLINE THAT WAS PART OF THE UPRATE PROJECT.
2025-03-31 10:13 | NO | YES | NO | 20190096 | 32643 | 2019-08-30 22:44 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2019-07-30 11:30 |  |  | 2019 | 1355 TERRELL MILL ROAD | MARIETTA | COBB | GA | 30067 | 33.9212 | -84.4643 | [9 empty] | 2019-08-02 12:48 | 1254010 |  | NATURAL GAS |  | 112 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-07-30 11:30 |  |  |  | 2019-07-30 11:49 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 72 |  | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2017 | [5 empty] | 2 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | LEAK |  |  | OTHER | PLASTIC PIPE MELTED | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 100000 | 113130.5044035228 | 200000 | 226261.0088070456 | 0 | 0 |  |  | 700 | 784.514435695538057742782152230971128609 |  | 0 | 300700 | 141291.5077468800028871391076115485564304 | 340176.0276462639380577427821522309711286 | 0 | 0 | 0 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | TELECOMMUNICATIONS FIELD PERSONNEL |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | 404-584-4910 | rslagle@southernco.com | A LEAK WAS REPORTED IN A TELECOMMUNICATIONS DUCT WHERE AFTER DAYS OF INVESTIGATING, VENTING, AND PINPOINTING, THE ESCAPING GAS WAS DISCOVERED TO BE COMING FROM A 2-INCH PLASTIC NATURAL GAS MAIN THAT HAD MELTED BY BEING IN CLOSE PROXIMITY TO A COMMUNICATIONS CABLE. DUE TO THE LENGTH OF TIME PERFORMING THE INVESTIGATION AND REPAIRING THE LEAK IT WAS DETERMINED THAT COSTS WOULD EXCEED THE $50,000 THRESHOLD FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. ADDITIONAL NRC REPORT NUMBER 1254106 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2025-03-31 10:13 | NO | NO | NO | 20190097 | 32702 | 2019-09-05 12:58 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2019-07-31 14:45 |  |  | 2019 | 1201 ST. CHARLES ST | ELGIN | KANE | IL | 60120 | 42.0103 | -88.2671 | [9 empty] | 2019-08-05 18:21 | 1254314 |  | NATURAL GAS |  | 5.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-07-31 14:45 |  |  |  | 2019-07-31 14:45 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 3.5 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.266 | [6 empty] | MECHANICAL PUNCTURE | 0.6 | 0.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 78000 | 88241.793434747784 | 0 | 0 |  |  | 20 | 22.41469816272965879265091863517060367454 |  | 0 | 78020 | 36567.8392582832889396325459317585301837 | 88264.2081329105136587926509186351706037 | 25 | 0 | 0 |  |  |  |  | 150 | 155 | 155 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | lquezad@southernco.com | 6303882316 |  |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | 6303882316 | lquezad@southernco.com | WHILE TAPPING A FITTING ON AN EXTRA THICK 3-INCH SERVICE LINE TO ABANDON THE SERVICE LINE, THE HOLE SAW CREATED A HAIRLINE CRACK ON THE SIDE OF THE PIPE, GENERATING A SMALL LEAK. IN ORDER TO STOP THE LEAK, THE 12-INCH HEADER HAD TO BE STOPPED. THERE ARE NO REPAIR COSTS ASSOCIATED WITH THIS INCIDENT SINCE THE REASON FOR THE WORK BEING PERFORMED WAS TO ABANDON THE 3" SERVICE LINE. THE HAIRLINE CRACK WIDTH HAD TO BE ROUNDED UP TO 0.1 SINCE THE DATABASE DOES NOT ACCEPT VALUES LESS THAN ONE DECIMAL POINT.
2025-03-31 10:13 | NO | NO | NO | 20190098 | 32743 | 2019-09-05 17:03 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2019-05-23 15:00 |  |  | 2019 | 1230 HUNTERS LAKE DRIVE | CUYAHOGA FALLS | SUMMIT | OH | 44221 | 41.119 | -81.457 | [10 empty] | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 1.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2019-05-29 15:11 |  |  |  | 2019-05-29 15:11 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2002 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 100000 | 113130.5044035228 | 1000 | 1131.305044035228 | 0 | 0 | 0 | 0 |  |  | 31 | 34.74278215223097112860892388451443569554 |  | 0 | 101031 | 47355.9537148529255564304461942257217848 | 114296.5522297102589711286089238845144357 | 0 | 0 | 0 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | NOTIFICATION FROM PUCO GAS PIPELINE SAFETY INSPECTOR |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JEFFERY BURDETTE | TECHNICAL CONSULTANT | jeffery.l.burdette@dominionenergy.com | 3307545524 |  |  |  |  | TERRY GLIDDEN | PIPELINE SAFETY MANAGER | 3303514326 | terry.l.glidden@dominionenergy.com | ON MAY 23, 2019, AT APPROXIMATELY 3PM A FIRE OCCURRED AT 1230 HUNTERS LAKE DRIVE, CUYAHOGA FALLS, OH 44221. THIS FIRE RESULTED IN DAMAGE TO SEVERAL APARTMENTS AT THE PROPERTY AND AN ESTIMATED $100,000 IN PROPERTY DAMAGE. THE FIRE WAS CAUSED BY A RELEASE OF NATURAL GAS ON HOUSELINE PIPING DOWNSTREAM OF THE OUTSIDE METER SETTING. THE RELEASE OF GAS RESULTED FROM A DOMINION ENERGY OHIO GAS METER BEING STRUCK BY A RIDING MOWER. FORCE FROM THIS IMPACT RESULTED IN DAMAGE TO THE HOUSELINE PIPING LOCATED WITHIN THE BUILDING AND THE RESULTING GAS LEAK CAUSED THE FIRE. DOMINION ENERGY OHIO WOULD NOTE THAT THIS WAS AN UNUSUAL SITUATION IN THAT THE COMPANY WAS NOT CALLED INTO THE ORIGINAL SITUATION BY THE FIRE DEPARTMENT, AND THUS DID NOT GAIN FIRSTHAND AWARENESS OF EITHER THE UPSTREAM DAMAGE OR THE CAUSE OF THE DOWNSTREAM RELEASE, BUT WAS ONLY APPRISED OF THE SITUATION AND CONCLUSIONS SECONDHAND AND AFTER THE FACT BY THE PUCO ON MAY 29, 2019. DOMINION ENERGY OHIO DID NOT INITIALLY AGREE THAT THIS EVENT MET THE DEFINITION OF A REPORTABLE INCIDENT. ON AUGUST 6, 2019, THE PUCO ISSUED A LETTER OF NON-COMPLIANCE STATING THIS EVENT IS A REPORTABLE INCIDENT BY DEFINITION AND PHMSA INTERPRETATION. AS PART OF CORRECTING THIS REPORTING ISSUE IDENTIFIED BY THE PUCO, AND IN RESPONSE TO THE NON-COMPLIANCE LETTER, THIS INCIDENT REPORT IS BEING FILED.
2025-03-31 10:13 | NO | NO | NO | 20190099 | 32933 | 2019-09-06 15:11 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-08-09 14:28 |  |  | 2019 | 3340 W. TIENKEN | ROCHESTER HILLS | OAKLAND | MI | 48309 | 42.6941 | -83.2006 | [9 empty] | 2019-08-09 20:28 | 1254737 |  | NATURAL GAS |  | 4046 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-08-09 14:28 |  |  |  | 2019-08-09 14:50 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1968 | [5 empty] | 6 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 3 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 48066 | 54377.308246597269048 | 1093 | 1236.516413130504204 | 0 | 0 |  |  | 9265 | 10383.6089238845144356955380577427821522 |  | 0 | 58424 | 32639.0244345958094277769028871391076115 | 65997.4335836122876876955380577427821522 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | ELECTRIC | YES | 92182061 |  |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON AUGUST 9, 2019 AT APPROXIMATELY 14:28 HOURS CONSUMERS ENERGY WAS NOTIFIED OF DAMAGE TO A 6" STEEL MEDIUM PRESSURE NATURAL GAS PIPELINE LOCATED NEAR 3340 W. TIENKEN, ROCHESTER HILLS, MICHIGAN (OAKLAND COUNTY). A CONSUMERS ENERGY GAS SERVICE WORKER (GSW) ARRIVED AT APPROXIMATELY 14:50 HOURS CONFIRMING DAMAGE TO THE PIPELINE AND REQUESTED A DISTRIBUTION CREW. THE DAMAGE LOCATION AND SURROUNDING AREAS WERE CONTINUOUSLY MONITORED UNTIL REPAIRS WERE COMPLETED. FURTHER INVESTIGATION DETERMINED A CONTRACTOR BORING CONDUIT FOR ELECTRIC HAD PREVIOUSLY EXPOSED AND SUCCESSFULLY CROSSED THE PIPELINE. HOWEVER DURING THE PULL BACK THEIR BORE SHOT APPEARED TO FLEX UPWARD RESULTING IN LOSS OF CLEARANCE AND SUBSEQUENT DAMAGE TO THE NATURAL GAS PIPELINE. THE DISTRIBUTION CREW ARRIVED ONSITE AT APPROXIMATELY 16:57 HOURS. MUELLER CONTROL FITTINGS WERE INSTALLED TO ISOLATE THE DAMAGE SEGMENT AND A PLIDCO BOLTED SPLIT SLEEVE FITTING USED AS A TEMPORARY REPAIR. A PUMPKIN WAS INSTALLED ON AUGUST 22, 2019 TO PERMANENTLY REPAIR THE DAMAGED SEGMENT.
2025-03-31 10:13 | NO | YES | NO | 20190101 | 34389 | 2019-09-13 09:44 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-08-14 15:56 |  |  | 2019 | 4675 HACKETT ROAD | SAGINAW | SAGINAW | MI | 48603 | 43.4767 | -84.0699 | [9 empty] | 2019-08-16 12:10 | 1255353 |  | NATURAL GAS |  | 2511 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-08-14 15:56 |  |  |  | 2019-08-14 16:35 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 55 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1942 | [5 empty] | 12 | API 5L | NATIONAL TUBE | STEEL |  | OTHER | UNKNOWN | 0.203 | [6 empty] | MECHANICAL PUNCTURE | 12 | 6 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 294600 | 333282.4659727781688 | 167 | 188.927942353883076 | 0 | 0 |  |  | 5750 | 6444.22572178477690288713910761154855643 |  | 0 | 300517 | 144075.1361915429934033569553805774278215 | 339915.6196369168287788871391076115485564 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | TRENCHER | DRAINAGE | YES | 91981987 |  |  | CONTRACT LOCATOR | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON AUGUST 14, 2019 AT APPROXIMATELY 15:56 HOURS CONSUMERS ENERGY (CE) WAS NOTIFIED OF DAMAGE TO A 12" STEEL MEDIUM PRESSURE NATURAL GAS PIPELINE. THE PIPELINE WAS STRUCK BY A TRENCHING MACHINE BEING USED TO INSTALL DRAIN TILE IN A FARM FIELD. THE DAMAGE OCCURRED NEAR 4675 HACKETT ROAD, SAGINAW (SAGINAW COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) AND DISTRIBUTION CREW ARRIVED AT APPROXIMATELY 16:35 AND 16:41 HOURS RESPECTIVELY. THE GSW MONITORED THE SITE CONTINUOUSLY UNTIL THE DAMAGED PIPELINE SEGMENT WAS ISOLATED AND THE BLOWING GAS CONTAINED. POLICE AND FIRE PERSONNEL WERE ONSITE AND PORTIONS OF THE ROAD WERE CLOSED AS A SAFETY PRECAUTION. THERE WERE NO FATALITIES OR INJURIES AS A RESULT OF THE DAMAGE. THE PIPELINE WAS ISOLATED AT APPROXIMATELY 19:17 HOURS BY SQUEEZING AN 8" PLASTIC PIPELINE AT THE CONSUMERS ENERGY'S ZILWAUKEE CITY GATE (CUT AND CAP NORTH OF THE DAMAGE) AND CLOSING VALVE M1312 TO THE SOUTH OF THE DAMAGE LOCATION. ONCE THE PIPELINE WAS ISOLATED AND BLOWING GAS CONTAINED, A LOCATION UPSTREAM OF VALVE M1312 WAS CUT AND CAPPED. AN INCIDENT INVESTIGATION DETERMINED THE ROOT CAUSE AS A THIRD PARTY DAMAGE. SEVERAL FACTORS THAT MAY HAVE CONTRIBUTED TO THE DAMAGE WERE ALSO IDENTIFIED AS FOLLOWS (1) FACILITY NOT LOCATED OR MARKED - THE ONE CALL TICKET POSITIVE RESPONSE 001(NO CONFLICT) WAS PROVIDED BY THE STAKING CONTRACTOR FOLLOWING A CONVERSATION WITH A REPRESENTATIVE OF THE COMPANY INSTALLING DRAIN TILES. (2) UNCLEAR COMMUNICATION BETWEEN THE CE STAKING CONTRACTOR AND THE CONTRACTOR INSTALLING THE DRAINAGE TILE. THE STAKING TECHNICIAN SPOKE WITH CONTRACTOR AND WAS ADVISED (PER DOCUMENTED NOTES) THE ENTIRE SQUARE DOESN'T NEED TO BE MARKED HE NEEDS THE FIELD EAST OF HACKETT THAT ISN'T PLANTED MARKED. APPROXIMATELY 40' OF 12" STEEL MEDIUM PRESSURE PIPELINE WAS REPLACED BETWEEN THE ZILWAUKEE CITY GATE (NORTH ISOLATION POINT) AND THE SOUTHERLY ISOLATION POINT NEAR VALVE M1312. FOLLOWING THE PIPELINE INSTALLATION, TEMPORARY ODORIZATION EQUIPMENT WAS INSTALLED TO ENSURE ADEQUATE ODOR INTENSITY AS A RESULT OF DERATING FROM TRANSMISSION PIPELINE. ON JULY 20TH AT APPROXIMATELY 15:00 HOURS, CREWS TURNED THE ODORIZATION EQUIPMENT ON AND OPENED VALVES TO INTRODUCE GAS FLOW ON THE PIPELINE, RETURNING THE PIPELINE TO NORMAL OPERATIONS.
2025-03-31 10:13 | NO | YES | NO | 20190102 | 34424 | 2019-09-17 14:54 | SUPPLEMENTAL FINAL | 32198 | MINNESOTA ENERGY RESOURCES CORPORATION | 2685 145TH STREET WEST | ROSEMOUNT | MN | 55068 | 2019-08-18 01:41 |  |  | 2019 | 60 HUBBARD AVE | BUTTERFIELD | WATONWAN | MN | 56120 | 43.958 | -94.7973 | [9 empty] | 2019-08-20 10:20 | 1255527 |  | NATURAL GAS |  | 108 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 200 | 2019-08-18 01:41 |  |  |  | 2019-08-18 02:46 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1991 | [8 empty] | STEEL |  | SEAMLESS | SEAMLESS | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 98016 | 110885.995196156907648 | 25960 | 29368.67894315451888 | 0 | 0 | NEW REGULATOR STATION, FINAL RESTORATION COMPLETED IN LATE SUMMER 2020 |  | 450 | 504.330708661417322834645669291338582677 |  | 0 | 124426 | 58555.8150345298458937322834645669291339 | 140759.0048479728438508346456692913385827 | 21 | 8 | 217 |  |  |  |  | 33 | 33 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [56 empty] | HIGH WINDS | [5 empty] | YES |  |  |  | YES | THUNDERSTORMS | [213 empty] | LINDSAY K LYLE | ENGINEERING MANAGER | lindsay.lyle@minnesotaenergyresources.com | 6513228909 | 9202724000 |  |  |  | LINDSAY K LYLE | ENGINEERING MANAGER | 6513227909 | lindsay.lyle@minnesotaenergyresources.com | DURING LOCAL THUNDERSTORMS WITH EXTREMELY HIGH WINDS, A TREE TOPPLED AND LANDED ON A DISTRICT REGULATOR STATION. CURRENT DISTRICT REGULATOR STATION IS THE ONLY FEED FOR THE SMALL TOWN (<250 CUSTOMERS). THE FORCE OF THE TREE CAUSED A FLANGE ON THE INLET SIDE TO CRACK, RESULTING IN A GAS LEAK. THE OUTLET PIPING ALSO BROKE CAUSING THE DOWNSTREAM PRESSURE SIDE TO RELEASE INTO ATMOSPHERE. THE EMERGENCY VALVE FOR THE STATION WAS TURNED OFF, RESULTING IN ALL CUSTOMERS WITHOUT GAS UNTIL THE REPAIRS WERE MADE.
2025-03-31 10:13 | NO | NO | NO | 20190103 | 32953 | 2019-09-18 13:08 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-08-22 14:07 |  |  | 2019 | 3700 DEERFIELD ROAD APT. V12/13 | MOUNT PLEASANT | ISABELLA | MI | 48858 | 43.3355 | -84.4638 | [9 empty] | 2019-08-22 15:48 | 1256076 |  | NATURAL GAS |  | 12 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2019-08-22 14:07 |  |  |  | 2019-08-22 14:39 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | OTHER | CUSTOMER FUEL LINE | OUTSIDE METER/REGULATOR SET |  | 2007 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 50000 | 56565.2522017614 | 189 | 213.816653322658092 | 100 | 113.1305044035228 | 0 | 0 |  |  | 0 | 0 |  | 0 | 50289 | 23563.042700827342653 | 56892.199359487580892 | 0 | 0 | 12 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEA | 989-791-5749 | jason.pionk@cmsenergy.com | ON AUGUST 22, 2019 AT APPROXIMATELY 14:07 HOURS CONSUMERS ENERGY WAS NOTIFIED OF AN EXPLOSION THAT OCCURRED AT AN APARTMENT COMPLEX LOCATED AT 3700 DEERFIELD ROAD, APT. V12 MOUNT PLEASANT (ISABELLA COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED AT APPROXIMATELY 14:39 HOURS. FIRE AND POLICE WERE ONSITE AND THE METERS TO BUILDING V HAD BEEN SHUT-OFF AT THE LOCKWING BY FIRE PERSONNEL. THE GSW MONITORED THE AREA AND SURROUNDING BUILDINGS FOR GAS MIGRATION. NO ADDITIONAL NATURAL GAS READS WERE FOUND. AN INCIDENT INVESTIGATION DETERMINED THE NATURAL GAS METER SERVING UNIT V12 WAS HIT BY A THIRD PARTY PERFORMING MOWING SERVICES. THE IMPACT TO THE METER BROKE THE CUSTOMER FUEL LINE ALLOWING GAS TO ESCAPE AND ENTER INTO THE BUILDING. THE SUSPECTED IGNITION SOURCE WAS THE WATER HEATER. THE GAS METER WAS REMOVED FROM THE UNIT AND WILL BE REPLACED WHEN REPAIRS HAVE BEEN COMPLETED. ESTIMATED COST OF PUBLIC AND NON-OPERATOR PRIVATE PROPERTY DAMAGE IS ANTICIPATED TO EXCEED $50,000. HOWEVER AN EXACT AMOUNT HAS NOT BEEN PROVIDED TO CONSUMERS ENERGY. ON OCTOBER 17, 2019 AT APPROXIMATELY 11:08 HOURS THE GAS METER WAS INSTALLED AT THE REQUEST OF THE CUSTOMER.
2025-03-31 10:13 | YES | NO | NO | 20190104 | 32757 | 2019-09-19 18:37 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2019-08-24 07:52 |  |  | 2019 | 1007 HALF MOON BAY DRIVE | CROTON-ON-HUDSON | WESTCHESTER | NY | 10520 | 41.1917 | -73.8896 | [9 empty] | 2019-08-24 11:35 | 1256244 |  | NATURAL GAS |  | 10 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2019-08-24 07:52 |  |  |  | 2019-08-24 08:06 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | OUTSIDE METER/REGULATOR SET. | UNKNOWN | [8 empty] | OTHER | METER SET. | [9 empty] | LEAK |  |  | OTHER | METER MELTED. | [5 empty] | CLASS 4 LOCATION | 50000 | 56565.2522017614 | 200 | 226.2610088070456 | 800 | 905.0440352281824 | 500 | 565.652522017614 | 0 |  | 10 | 11.20734908136482939632545931758530183727 |  | 0 | 51510 | 24140.8273775626069698162729658792650919 | 58273.4171168956068293963254593175853018 | 0 | 0 | 1 |  |  |  |  | 60 | 60 | 90 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SECONDARY IGNITION AT GAS METER SET DURING ONGOING BUILDING FIRE. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | OSCAR LEON | GAS EMERGENCY RESPONSE CENTER-OPERATIONS MANAGER | leono@coned.com | 718-319-2310 | 718-824-2219 |  |  |  | NICKOLAS HELLEN | GAS EMERGENCY RESPONSE CENTER-DEPARTMENT MANAGER | 718-319-2350 | hellenn@coned.com | AT 07:52 ON AUGUST 24, 2019, THE CROTON-ON-HUDSON FIRE DEPARTMENT (CHFD) CONTACTED CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) AND REPORTED A BUILDING FIRE AT 1007 HALF BAY MOON DRIVE. THE GERC IMMEDIATELY DISPATCHED CON EDISON GAS DISTRIBUTION SERVICES (GDS) PERSONNEL AND SUPERVISORS TO THE LOCATION. THE BUILDING INVOLVED WAS SUPPLIED BY A 1-INCH HIGH-PRESSURE HIGH-DENSITY POLYETHYLENE (HDPE) GAS SERVICE (INSTALLED IN 2004). AT 07:58, THE CHFD REPORTED A SECONDARY GAS IGNITION AT THE METER SET UP LOCATED OUTSIDE THE BUILDING. ADDITIONAL CON EDISON PERSONNEL FROM GDS, GAS CONSTRUCTION, AND THE GAS EMERGENCY RESPONSE GROUP (ERG) WERE THEN DISPATCHED TO THE LOCATION BY THE GERC. GDS ARRIVED AT 08:06 AND CONFIRMED THE REPORTED SECONDARY GAS IGNITION. AT 08:35, GDS CLOSED THE CURB VALVE ON THE 1-INCH HDPE GAS SERVICE TO 1007 HALF BAY MOON DRIVE, THEREBY EXTINGUISHING THE SECONDARY FIRE AT THE OUTDOOR GAS METER SET UP; HOWEVER, THE STRUCTURAL FIRE REMAINED ONGOING AT THAT TIME. AS A PRECAUTION, GDS ALSO CLOSED THE HEAD-OF-SERVICE VALVES TO 1004, 1005, AND 1006 HALF MOON BAY DRIVE AT THEIR OUTDOOR METER SETS. IN ADDITION, NEARBY RADIAL HIGH-PRESSURE MAIN VALVE #39289 WAS LOCATED AND STAFFED FOR CONTINGENCY ISOLATION PURPOSES. AT 11:25, GDS REPORTED THAT THE CHFD HAD EXTINGUISHED THE STRUCTURAL FIRE. A SPECIAL LEAK SURVEY WAS PERFORMED BY CON EDISON AND NO GAS ODORS OR READINGS WERE DETECTED. GDS PERFORMED AN INTEGRITY TEST ON THE HOUSE PIPING INSIDE 1007 HALF MOON BAY DRIVE DOWNSTREAM OF THE GAS METER AND THE TEST PASSED. CON EDISON GAS CONSTRUCTION ALSO PERFORMED A PRESSURE TEST ON THE GAS SERVICE LINE, FROM THE CURB VALVE TO THE HEAD-OF SERVICE VALVE, UNDER LINE PRESSURE (60 PSI), AND THE TEST PASSED. PRESSURE AND ODORANT READINGS WERE WITHIN THE ACCEPTABLE RANGES. CON EDISON PERSONNEL CUT AND CAPPED THE GAS SERVICE LINE TO 1007 HALF MOON BAY DRIVE AT THE CURB VALVE AND ISSUED A WARNING TAG. BASED ON THEIR INVESTIGATION, THE CHFD REPORTED THE PRIMARY CAUSE OF THE FIRE IS UNDETERMINED. IT WAS NOTED, HOWEVER, THAT INTERIOR RENOVATIONS WERE ONGOING IN 1007 HALF MOON BAY DRIVE AT THE TIME OF THE FIRE. THERE WERE NO REPORTED INJURIES. MULTIPLE MEDIA OUTLETS WERE ON LOCATION. NYSPSC AND USDOT WERE NOTIFIED. NYSPSC RESPONDED TO THE LOCATION.
2025-03-31 10:13 | NO | YES | NO | 20190105 | 33939 | 2019-09-19 21:24 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2019-08-24 19:19 |  |  | 2019 | 30157 HWY 96 | KINDERHOOK | PIKE | IL | 62345 | 39.7008 | -91.1535 | [9 empty] | 2019-08-25 00:55 | 1256300 |  | NATURAL GAS |  | 244 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-08-24 19:19 |  |  |  | 2019-08-24 20:18 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1967 | [8 empty] | OTHER | STEEL FITTINGS OF REGULATING STATION | [9 empty] | OTHER | [8 empty] | REGULATORS AND RELIEF SHEARED OFF DUE TO VEHICLE STRIKING THEM AT HIGH RATE OF SPEED. | CLASS 3 LOCATION | 0 | 0 | 127200 | 143902.0016012810016 | 1000 | 1131.305044035228 | 9700 | 10973.6589271417116 | FOOD AND LODGING |  | 820 | 919.002624671916010498687664041994750656 |  | 0 | 138720 | 65463.5375141758588249343832020997375328 | 156925.9681971298572104986876640419947507 | 13 | 0 | 85 |  |  |  |  | 230 | 255 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | lquezad@southernco.com | 6303882316 |  |  |  |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | 6303882316 | lquezad@southernco.com | NOTE: THE BASIS FOR THIS REPORT IS THE COST OF EMERGENCY RESPONSE AND REPAIRS. THE DAMAGE TO THE REGULATING FACILITY LEAD TO THE INTERRUPTION OF GAS SERVICE TO 98 CUSTOMERS. A DRIVER FROM THE GENERAL PUBLIC EXPERIENCED A MEDICAL EMERGENCY AND LOST CONTROL OF HIS VEHICLE AND LEFT THE ROAD. THE VEHICLE STRUCK A SMALL ABOVE GROUND NATURAL GAS REGULATING FACILITY. THE COMPANY LATER LEARNED THE DRIVER HAD DIED. THE FATALITY IS NOT BELIEVED TO HAVE BEEN CAUSED BY THE RELEASE OF GAS. NOTE 2: SUBMITTING SUPPLEMENTAL REPORT TO REMOVE FATALITY SINCE IT WAS NOT CAUSED BY THE RELEASE OF GAS.
2025-03-31 10:13 | NO | YES | YES | 20190106 | 34668 | 2019-09-21 14:59 | SUPPLEMENTAL FINAL | 2288 | CHATTANOOGA GAS CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2019-08-23 07:05 | EASTERN | NO | 2019 | 411 HAWKWOOD CT | HIXSON | HAMILTON | TN | 37343 | 35.1817 | -85.2233 | [5 empty] | YES |  |  |  | 2019-08-23 09:24 | 1256131 |  | NATURAL GAS |  | 402.6 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2019-08-23 07:14 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 402.6 | YES | 2 | 2019-08-23 07:14 |  |  |  | 2019-08-23 07:33 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  | 15 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1978 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 0.5 | UNKNOWN | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 200000 | 226261.0088070456 | 300 | 339.3915132105684 | 6400 | 7240.3522818254592 | 0 | 0 |  | 0.473 | 190 | 212.939632545931758530183727034120734908 | 0 | 0 | 206890 | 97046.8081551856238265091863517060367454 | 234053.6922346275593585301837270341207349 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 56 | 58 | 60 | 192.619(A)(2) | 1978-06-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 13 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [9 empty] | YES |  |  |  | OTHER | DUCTILE CRACK | NO | [86 empty] | RICK SLAGLE | DIRECTOR COMPLIANCE QUALITY ASSURANCE | rslagle@southernco.com | [5 empty] | RICK SLAGLE | DIRECTOR COMPLIANCE QUALITY ASSURANCE | 404-673-1063 | rslagle@southernco.com | CHATTANOOGA GAS COMPANY RESPONDED TO A FIRE CALL AT 411 HAWKWOOD CT IN HIXSON, TN ON AUGUST 23, 2019 AT 7:30 AM. BAR HOLE TESTING OVER THE 1/2-INCH PE SERVICE THAT WAS CONDUCTED AS PART OF THE EMERGENCY RESPONSE INDICATED GAS READINGS AT THE BUILDING WALL NEAR THE SERVICE RISER. A SUBSEQUENT PRESSURE TEST OF THE SERVICE LINE DID NOT HOLD PRESSURE. INITIAL EXCAVATION OF THE FACILITIES DETERMINED CAUSE OF LEAKAGE TO BE A LEAKING SOCKET FUSION ON A TRANSITION FITTING THAT TRANSITIONED THE 1/2-INCH PE SERVICE PIPE TO THE 3/4-INCH STEEL SERVICE RISER. FURTHER INVESTIGATION REVEALED A CRACK IN THE BODY OF THE 1/2-INCH PE SERVICE PIPE TO BE THE CAUSE OF LEAKAGE. THE ORIGINAL REPORT FOR THIS INCIDENT DOCUMENTED THE APPARENT CAUSE IN PART G AS "G8 - OTHER INCIDENT CAUSE" AS THE CAUSE OF THE LEAKING SOCKET FUSION AT THE TIME WAS STILL UNDER INVESTIGATION. AS THE ABOVE NOTED CRACK WAS FOUND, THE APPARENT CAUSE IN PART G HAS BEEN CHANGED TO "G5 - PIPE, WELD, OR JOINT FAILURE" - BODY OF PIPE - CRACK. THE ESTIMATED VOLUME OF GAS THAT WAS RELEASED FROM THE TIME THE INCIDENT WAS REPORTED UNTIL THE FACILITIES WERE CUT AND CAPPED (5HOURS - 1 MINUTE) WAS 402.6 MCF. THE GAS WAS DISCHARGING THROUGH A BROKEN 3/4" PIPE AT THE METER SET FOR APPROXIMATELY THIS TIME PERIOD. TOTAL ESTIMATED VOLUME AND COST OF GAS RELEASED COULD NOT BE DETERMINED AS THE LENGTH OF TIME THAT FACILITIES HAD BEEN LEAKING COULD NOT BE DETERMINED. THE ORIGINAL TELEPHONIC REPORT TO THE NRC INDICATED INJURY REQUIRING INPATIENT HOSPITALIZATION. THIS HAS BEEN CHANGED TO FATALITY AS THE HOSPITALIZED PERSON SUCCUMBED TO THE INJURIES SUSTAINED FROM THE FIRE. ADDITIONAL NRC REPORT NUMBER 1256276 WAS CREATED FOR THE SAME EVENT AFTER A 48-HOUR SUPPLEMENTAL CALL WAS PLACED WITH THE NRC.
2025-03-31 10:13 | NO | NO | NO | 20190107 | 32740 | 2019-09-23 17:18 | ORIGINAL FINAL | 18308 | NV ENERGY | P. O. BOX 10100 | RENO | NV | 89520 | 2019-08-26 11:10 |  |  | 2019 | 2879 BARONG CT | RENO | WASHOE | NV | 89523 | 39.5438 | -119.8769 | [9 empty] | 2019-08-26 12:47 | 1256443 |  | NATURAL GAS |  | 5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2019-08-26 11:15 |  |  |  | 2019-08-26 11:35 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1994 | [8 empty] | STEEL |  | OTHER | ERW | 0.133 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 81000 | 91635.708566853468 | 150 | 169.6957566052842 | 5000 | 5656.52522017614 | 0 | 0 |  |  | 20 | 22.41469816272965879265091863517060367454 |  | 0 | 86170 | 40386.5431102537564896325459317585301837 | 97484.3442417976218587926509186351706037 | 0 | 0 | 11 |  |  |  |  | 86 | 86 | 90 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | SUSAN BURNETTE | SR GAS COMPLIANCE ANALYST | sburnette@nvenergy.com | (775)834-7278 | (775)834-7131 |  |  |  | JAY WIGGINS | GAS OPERATIONS AND COMPLIANCE MANAGER | (775)834-7850 | jwiggins@nvenergy.com | ON AUGUST 26, 2019 AT 11:15 AM NV ENERGY (NVE) GAS DISPATCH WAS NOTIFIED BY RENO FIRE DISPATCH THAT A RECREATIONAL VEHICLE HAD HIT A GAS METER SET AND IT WAS LEAKING GAS. NVE GAS DISPATCH CONTACTED A NVE GAS SERVICEMAN AND INSPECTOR TO RESPOND. NVE PERSONNEL ON SCENE WERE ATTEMPTING TO CONTROL THE FLOW OF GAS WHEN TWO RENO FIREFIGHTERS OPERATED THE MAIN CIRCUIT BREAKER ON THE ELECTRIC PANEL THAT WAS 36" FROM THE DAMAGED, LEAKING RISER AT THE GAS METER SET. THIS CAUSED A FLASH IGNITION OF NATURAL GAS THAT BURNED THE TWO RENO FIREFIGHTERS. THE TWO RENO FIREFIGHTERS WERE TRANSPORTED TO THE HOSPITAL WHERE THEY WERE TREATED AND RELEASED THAT SAME DAY. A SHORT TIME LATER, AFTER THE FIRST IGNITION, A SECOND IGNITION OCCURRED IN THE ATTIC OF THE HOME ABOVE THE GARAGE CAUSING A FIRE IN THE ATTIC SPACE. NVE PERSONNEL ISOLATED GAS AT A MAIN VALVE, RESULTING IN AN OUTAGE TO 11 CUSTOMERS AND STOPPING THE FLOW OF GAS TO THE DAMAGED RISER. THE SERVICE LINE TO THE DAMAGED RISER WAS RETIRED AT THE CURB AND SERVICE WAS RESTORED TO THE 10 OTHER AFFECTED CUSTOMERS. NVE PERSONNEL OBSERVATION, PHYSICAL EVIDENCE, AND TESTIMONY BY RENO FIRE PERSONNEL INDICATE THAT THE METER SET WAS DAMAGED BY THE HOMEOWNER WHEN HE ATTEMPTED TO MOVE HIS RECREATIONAL VEHICLE PAST THE METER SET. THE RECREATIONAL VEHICLE STEP WAS NOT RETRACTED AND IT CONTACTED THE METER SET AS HE WAS DRIVING FORWARD. THE THREADED JOINT BETWEEN THE GAS METER VALVE AND THE RISER WAS CRACKED DUE TO THIS IMPACT. NVE MANAGEMENT ON SCENE DETERMINED THAT THE PROPERTY DAMAGE TO THE HOME WOULD EXCEED $50,000 FOR THIS EVENT. NVE NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) ON AUGUST 26TH AT 12:47 AND WAS GIVEN NRC INCIDENT REPORT #1256443. NV ENERGY PROVIDED AN UPDATE TO THE NRC ON AUGUST 28TH AT 10:09 AND WAS GIVEN NRC INCIDENT REPORT #1256658.
2025-03-31 10:13 | NO | YES | NO | 20190108 | 34650 | 2019-09-24 14:58 | SUPPLEMENTAL FINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2019-08-25 08:00 | EASTERN | NO | 2019 | 8865 STANFORD BLVD | COLUMBIA | HOWARD | MD | 21045 | 39.191 | -76.8181 |  |  | YES | [6 empty] | 2019-08-25 10:00 | 1256316 |  | NATURAL GAS |  | 360 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2019-08-25 07:09 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 360 | YES | 0 | 2019-08-25 07:09 |  |  |  | 2019-08-25 07:36 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 34 | YES | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1997 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | YES | 2 | D2513 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | OTHER | [8 empty] | BURN THROUGH - AN APPARENT QUARTER SIZE HOLE WAS FOUND IN THE GAS PIPE DURING THE EXCAVATION AND PRESSURE TESTING. THE CAUSE OF THE HOLE IS FROM AN ELECTRICAL FAULT OF UNKNOWN ORIGIN. | CLASS 1 LOCATION | 7000000 | 7919135.308246596 | 15000 | 16969.57566052842 | 5000 | 5656.52522017614 | 0 | 0 |  | 1.53 | 551 | 617.524934383202099737532808398950131234 | 0 | 0 | 7020551 | 3289810.63823237264498687664041994750656 | 7942378.93406168376209973753280839895013 | 22 | 0 | 0 | 0 | 0 | 0 | 22 | 90 | 90 | 90 | 192.619(A)(4) | 1997-10-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | ROBERT REX | MANAGER - GAS ENGINEERING AND STANDARDS | robert.rex@delmarva.com | 410-470-6933 | 410-470-9549 |  |  |  | DANIEL A. NORDEN | MANAGER - GAS ENGINEERING AND PROGRAM MANAGEMENT | 410-470-6435 | daniel.a.norden@bge.com | ON AUGUST 25TH, 2019 AT 07:09 THE HOWARD COUNTY FIRE DEPARTMENT NOTIFIED BGE OF AN OUTSIDE GAS ODOR AT THE LOCATION OF 8865 STANFORD BLVD. BGE IMMEDIATELY DISPATCHED A GAS FITTER TO THE PREMISE FOR INVESTIGATION. A GAS MAINTENANCE AND REPAIR CREW WAS ALSO DISPATCHED THERE WAS AN EXPLOSION IN THE BUILDING AT 08:00. THE GAS EMERGENCY PLAN WAS PUT INTO AFFECT AND NOTIFICATIONS WERE IMPLEMENTED STARTING AT 08:02. THE MARYLAND PUBLIC SERVICE COMMISSION WAS NOTIFIED AND A REPORT TO THE NATIONAL RESPONSE CENTER WAS ISSUED. THE SERVICE WAS ABANDONED ON 8/26/2020 12:00PM. THERE ARE MULTIPLE FACILITIES NEAR AND/OR CROSSING BGE'S FACILITIES WHICH WERE EVALUATED ALONG WITH BGE'S FACILITIES. THE FACILITIES WHICH CROSS BGE'S FACILITIES ARE COMMUNICATIONS FACILITIES, PRIVATE AREA LIGHTING FACILITIES, AND THE BUILDING'S ELECTRICAL SERVICE. THE EXPLOSION WAS THE RESULT OF A DIFFUSE FUEL AND AIR MIXTURE. THE FUEL WAS NATURAL GAS. THE SOURCE OF THE FUGITIVE NATURAL GAS WAS A COMPROMISE IN THE INTEGRITY OF THE GAS SERVICE CAUSED BY THERMAL DEGRADATION OF ITS POLYETHYLENE TUBING FROM AN ELECTRICAL FAULT OF UNKNOWN ORIGIN. A COMPREHENSIVE ANALYSIS WAS CONDUCTED OF ALL THE FACILITIES IN THE AREA, INCLUDING THE COMMUNICATIONS FACILITIES AND THE PRIVATE AREA LIGHTING FACILITIES IN THE AREA, BUT DID NOT YIELD ADDITIONAL RELEVANT INFORMATION.
2025-03-31 10:13 | NO | NO | NO | 20190109 | 32752 | 2019-09-25 19:57 | ORIGINAL FINAL | 11032 | SPIRE MISSOURI INC. EAST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2019-08-26 19:42 |  |  | 2019 | 15933 CLAYTON ROAD | BALLWIN | SAINT LOUIS | MO | 63011 | 38.6071 | -90.5859 | [9 empty] | 2019-08-29 14:21 | 1256773 |  | NATURAL GAS |  | 118 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-08-26 19:42 |  |  |  | 2019-08-26 19:42 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 60 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1964 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 70536 | 79797.732586068842208 | 500 | 565.652522017614 | 0 | 0 |  |  | 550 | 616.40419947506561679790026246719160105 |  | 0 | 71586 | 33854.3138790998002118950131233595800525 | 80979.7893075615218247979002624671916011 | 0 | 0 | 0 |  |  |  |  | 18.95 | 19.02 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF GAS RELEASED WAS NOT DETECTABLE BY THE SCADA SYSTEM AND THE CONTROLLER(S) TOOK NO ACTIONS THAT WOULD HAVE CONTRIBUTED TO OR CAUSED THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1964 | YES | YES | YES |  |  | 2019 |  |  |  |  | YES | OTHER | MASTIC | [20 empty] | 2019-08-12 | NO | [227 empty] | NICOLE CHRISTIANER | MANAGER OF PPIELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  |  |  |  | CRAIG HOEFERLIN | VP OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | WHILE INVESTIGATING A NON-HAZARDOUS LEAK, AN 8-INCH STEEL MAIN WAS DISCOVERED TO BE LEAKING DUE TO CORROSION. THE COATING APPEARED TO HAVE BEEN PREVIOUSLY DAMAGED DURING A FIBER OPTIC CONDUIT INSTALLATION. GAS WAS MADE SAFE BY INSTALLING CONTROL FITTINGS ON BOTH ENDS OF STEEL MAIN. A 21-FOOT SECTION OF STEEL MAIN WAS REPLACED TO COMPLETE THE REPAIR AND RETURNED THE MAIN TO NORMAL SERVICE. A 48 HOUR UPDATE TO THE NRC WAS MADE ON AUGUST 31, 2019 AT 14:43. REPORT NUMBER 1256971.
2025-03-31 10:13 | NO | YES | YES | 20190110 | 32789 | 2019-09-26 09:22 | SUPPLEMENTAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2019-08-28 17:55 |  |  | 2019 | 10000 RESEARCH BLVD | AUSTIN | TRAVIS | TX | 78759 | 30.3896 | -97.7465 | [9 empty] | 2019-08-28 22:13 | 1256708 |  | NATURAL GAS |  | 1053 |  | NO | [5 empty] | 0 | YES | 0 | 1 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2019-08-28 17:55 |  |  |  | 2019-08-28 17:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2019 | [5 empty] | 12 | API 5L | TMK IPSCO (KY) | STEEL |  | OTHER | ERW | 0.375 | [6 empty] | OTHER | [8 empty] | 12" VALVE BLEED BY | CLASS 3 LOCATION | 0 | 0 | 15000 | 16969.57566052842 | 10000 | 11313.05044035228 | 0 | 0 |  |  | 3731 | 4181.461942257217847769028871391076115486 |  | 0 | 28731 | 15581.9126097028173884514435695538057743 | 32464.0880431379178477690288713910761155 | 0 | 0 | 0 |  |  |  |  | 243 | 245 | 265 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS AMOUNT WAS TOO SMALL TO DETECT VIA THE SCADA SYSTEM | [12 empty] | YES | 1 | 0 | YES | 9 | 0 | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | WELDER FLASHED EXCAVATION HOLE WITH WELDING TORCH. |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | DEAN LAFLAMME | DIRECTOR ENGINEERING TEXAS GAS SERVICE | dlaflamme@onegas.com | 512-370-8213 |  |  |  |  | DEAN LAFLAMME | DIRECTOR ENGINEERING TEXAS GAS SERVICE | 512-370-8213 | dlaflamme@onegas.com | A COMMERCIAL CUSTOMER REQUESTED THAT TGS RELOCATE A 125' SECTION OF A 12" COATED STEEL PIPELINE TO ACCOMMODATE THE CUSTOMER'S NEW BUILDING CONSTRUCTION. THE CUSTOMER'S NEW BUILDING PLAN REQUIRED A FOOTER IN CLOSE PROXIMITY TO THE EXISTING PIPELINE. ON 8-28-19, AFTER ISOLATION WAS COMPLETE, WORK BEGAN. THE ENTIRE 125' OF 12" COATED STEEL MAIN WAS LAID IN A NEW DITCH AND GETTING PREPARED FOR TWO 12" STEEL TIE-INS TO COMPLETE THE RELOCATION. LATER IN THE DAY, UPON DETECTING NATURAL GAS BLEEDING THROUGH A 12" ISOLATION VALVE INTO THE ISOLATED PIPELINE, THE TEXAS GAS SERVICE INSPECTOR ORDERED WORK TO STOP UNTIL A THREAD-O-RING (TOR) COULD BE INSTALLED TO PULL GAS FROM THE ISOLATED PIPING WHERE HOT WORK WAS GOING TO BE PERFORMED. WHILE THE TOR FITTING WAS BEING OBTAINED, THE CONTRACTOR'S FOREMAN DIRECTED HIS WELDER TO ATTEMPT TO IGNITE THE GAS IN THE NORTH TRENCH TO TEST FOR GAS. THE SPARK TRAVELED DOWN THE PIPE TO THE SOUTH TRENCH AND IGNITED THE GAS THERE CAUSING AN INJURY TO THE EMPLOYEE. THE INSPECTORS, FOREMAN AND WELDER WERE DISQUALIFIED AND REQUIRED TO RETRAIN AND BE RE-EVALUATED PRIOR TO ANY RETURN TO WORK. IN ADDITION TO THE RETRAIN AND RE-EVALUATION OF THE AFFECTED EMPLOYEES, TEXAS GAS SERVICE WILL BE PERFORMING A SAFETY TRAINING COVERING THE IMPORTANCE OF FOLLOWING CONSTRUCTION AND SAFETY PROTOCOLS WHEN PERFORMING ANY CONSTRUCTION WORK FOR TEXAS GAS SERVICE. TEXAS GAS SERVICE AT 21:45 (8/28/19) WAS NOTIFIED THAT THE INJURY (BURNS) TO THE EMPLOYEE WOULD CAUSE INPATIENT HOSPITALIZATION WHICH WAS THE CONFIRMED DISCOVERY TIME THIS IS A REPORTABLE INCIDENT. THE EMPLOYEE WAS RELEASED FROM THE HOSPITAL ON 8/29/19. THE 48 HRS. PHMSA NOTICE REQUIREMENT WAS CALLED IN ON 8/30/19 @ 11:01 AM (NRC#1256868). NOTE: RELOCATION WAS FOR A NEW COMMERCIAL CUSTOMER (CAR DEALERSHIP THAT DID NOT HAVE EXISTING ADDRESS). THE LAT / LONG COORDINATES USED FOR THE INCIDENT ON PART A (5F) IS AT THE SPECIFIC LOCATION OF THE INCIDENT SITE. (THE ACTUAL ADDRESS USED IN THE REPORT IS THE CLOSEST KNOWN ACTIVE ADDRESS WHICH IS 10000 RESEARCH BLVD). THE ACTUAL INCIDENT LOCATION IS ACROSS THE STREET FROM THE 10000 RESEARCH BLVD ADDRESS ON THE REPORT WHICH THE LAT / LONG COORDINATES POINT TO.
2025-03-31 10:13 | NO | YES | NO | 20190111 | 32755 | 2019-09-26 09:48 | ORIGINAL FINAL | 11713 | KEYSPAN ENERGY DELIVERY - LONG ISLAND | 175 EAST OLD COUNTRY ROAD | HICKSVILLE | NY | 11801 | 2019-08-29 11:30 |  |  | 2019 | MILL ROAD AND PENINSULA BLVD (INTERSECTION) | HEWLETT | NASSAU | NY | 11557 | 40.6435 | -73.704 | [9 empty] | 2019-09-04 14:00 | 1257226 |  | NATURAL GAS |  | 85 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 250 | 2019-08-29 11:34 |  |  |  | 2019-08-29 11:34 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | PURGE RISER ON SERVICE | 1959 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.113 | [6 empty] | MECHANICAL PUNCTURE | 1.4 | 1.4 | [7 empty] | CLASS 3 LOCATION | 125000 | 141413.1305044035 | 14168 | 16028.329863891110304 | 3193 | 3612.257005604483004 | 0 | 0 |  |  | 336 | 376.566929133858267716535433070866141732 |  | 0 | 142697 | 67051.9659745294447828267716535433070866 | 161430.2843030329515757165354330708661417 | 5 | 0 | 0 |  |  |  |  | 46.6 | 48 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS NOT CAUSED BY FACTORS WITHIN THE CONTROL ROOM'S CONTROL. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | MILLING EQUIPMENT | CURB/SIDEWALK | YES | 191610373 | NEW YORK 811 |  | CONTRACT LOCATOR | NO | YES | 8 | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER GAS WORK METHODS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER GAS WORK METHODS | 6317703549 | corinne.byrnes@nationalgrid.com | A THIRD-PARTY CONSTRUCTION COMPANY (OPAL CONSTRUCTION) DAMAGED AN 1 1/4" PURGE RISER ON A 2" STEEL MAIN AT MILL RD AND PENINSULA BLVD IN HEWLETT WHILE DOING RECONSTRUCTION TO A PARKING LOT DURING THE MILLING PHASE OF RECONSTRUCTION. A MARKOUT REQUEST WAS ISSUED SEVERAL MONTHS EARLIER BUT PAINT MARKS WERE NOT MAINTAINED OR VISIBLE. THE MAIN CAUGHT FIRE DUE TO THE DAMAGE. A PAVING MACHINE ALSO CAUGHT FIRE AND SUSTAINED SIGNIFICANT DAMAGE. ESTIMATED TIME OF INCIDENT IS APPROX. 11:30 AM. ESTIMATED VALUE (SALVAGE VALUE) OF PAVING TRUCK WAS $125,000. THERE WERE NO INJURIES. THE FIRE DEPARTMENT WAS ON LOCATION AND EVACUATED A NEARBY SHOPPING MALL AS A PRECAUTION. A FIELD OPERATIONS CREW RESPONDED IMMEDIATELY AT 11:34 AM AND AT 12:37 PM PERFORMED A SQUEEZE OFF ON THE MAIN TO MAKE SAFE. THIS RESULTED IN A SUPPLY INTERRUPTION OF FIVE SERVICES. THE MAIN WAS REPAIRED ON 08/29/2019 AT APP. 20:01, GASSED IN AT 8:15 PM. REPAIR WAS MADE BY THREADING AND CAPPING 1 1/4" DAMAGED RISER. SERVICES WERE RESTORED ON 8/30/2019 AT 11:00 AM.
2025-03-31 10:13 | NO | YES | NO | 20190112 | 32903 | 2019-09-27 11:53 | SUPPLEMENTAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2019-09-01 00:28 |  |  | 2019 | 911 HAMPTON RD. | LYNDEN | WHATCOM | WA | 98264 | 48.9429 | -122.4407 | [9 empty] | 2019-09-03 13:24 | 1257142 |  | NATURAL GAS |  | 12 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2019-09-01 00:28 |  |  |  | 2019-09-01 01:05 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2003 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | VEHICLE HIT METER SET ASSEMBLY BREAKING THE THREADED 3/4" PIPE NIPPLE BETWEEN THE SHUT OFF VALVE AND THE HOUSE REGULATOR. | CLASS 3 LOCATION | 400500 | 453087.670136108814 | 500 | 565.652522017614 | 700 | 791.9135308246596 | 0 | 0 |  |  | 53 | 59.39895013123359580052493438320209973753 |  | 0 | 401753 | 188272.5349098177306900262467191601049869 | 454504.6351390823211958005249343832020997 | 0 | 0 | 1 |  |  |  |  | 28 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.com | 208-377-6032 |  |  |  |  | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 208-377-6032 | greg.watkins@mdu.com | ON SUNDAY SEPTEMBER 1, AT APPROXIMATELY 12:04 A.M., A MOTOR VEHICLE ATTEMPTING TO EVADE THE POLICE, STRUCK AND DAMAGED THE METER SET ASSEMBLY AT 911 HAMPTON RD, LYNDEN, WA. GAS IGNITED AND BURNED BOTH THE HOME AND CAR. A COMPANY SERVICE MECHANIC RESPONDED ON SITE AT 1:05 A.M. AND SAW THE HOUSE FULL OF SMOKE AND THE VEHICLE BURNED. THE FIRE DEPARTMENT HAD TURNED OFF THE REMOTE HIGH PRESSURE SERVICE SET (HPSS)/FARM TAP FEEDING THE METER SET ASSEMBLY AT APPROXIMATELY 12:30 A.M. PRIOR TO THE SERVICE MECHANICS ARRIVAL. THE SERVICE MECHANIC INSTALLED A LOCKING DEVICE ON THE HPSS AND PERFORMED A LEAK INVESTIGATION. THE FIRE DEPARTMENT HAD NOT RULED THE CAUSE OF FIRE AT THAT TIME. THE FIRE DEPARTMENTS FINAL REPORT REGARDING THE FIRE THAT OCCURRED AT 911 HAMPTON RD., LYNDEN, WA STATED THE ITEM THAT FIRST IGNITED WAS "UNDETERMINED" AND THE CAUSE OF THE IGNITION WAS "UNINTENTIONAL". THE SERVICE MECHANIC RETURNED TO THE SITE AT 8:10 A.M. ON 9/2/2019 TO COMPLETE THE INVESTIGATION. PER POLICE REPORT, VEHICLE DRIVER WAS TAKEN INTO CUSTODY AND THERE WAS NO MENTION OF HOSPITALIZATION OR INJURY. THE SERVICE LINE WAS ABANDONED ON 10/31/2019. A NEW SERVICE LINE WILL BE INSTALLED WHEN THE HOME IS REPAIRED OR REBUILT. ORIGINAL NRC# 1257142 48-HR UPDATE NRC# 1257331
2025-03-31 10:13 | NO | NO | NO | 20190113 | 32787 | 2019-09-30 15:35 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2019-08-30 20:53 |  |  | 2019 | 13401 SR 4 | BELLEVUE | ERIE | OH | 44811 | 41.2905 | -82.7832 | [9 empty] | 2019-08-31 11:33 | 1256941 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-08-30 22:45 |  |  |  | 2019-08-30 22:45 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | FARM TAP METER/REGULATOR SET |  | 2016 | [8 empty] | OTHER | DUAL RUN MONITOR & CONTROL REGULATOR SET | [9 empty] | OTHER | [8 empty] | NON-JURISDICTIONAL REGULATORS RELIEVED | CLASS 3 LOCATION | 10119 | 11447.675740592472132 | 1500 | 1696.957566052842 | 3500 | 3959.567654123298 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 15119 | 7084.047059870122563 | 17104.200960768612132 | 1 | 0 | 0 |  |  |  |  | 294.2 | 294.2 | 345 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [73 empty] | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE | rrsmith@nisource.com | 614-460-5491 | 614-818-2151 |  |  |  | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE | 614-460-5491 | rrsmith@nisource.com | ON AUGUST 30, 2019 COLUMBIA RESPONDED TO A LARGE COMMERCIAL CUSTOMER TO INVESTIGATE A RELIEVING CUSTOMER-OWNED HOUSE LINE REGULATOR. COLUMBIA DISCOVERED THAT IT HAD EXCEEDED THE NORMAL HOUSELINE OPERATING PRESSURE OF 45 PSIG. COLUMBIA FIRST RESPONDERS INVESTIGATED AND DISCOVERED THE HOUSE LINE OPERATING PRESSURE HAD REACHED 177.9 PSIG. COLUMBIA THEN SHUT THE VALVES FEEDING THE STATION AND DEPRESSURIZED THE HOUSE LINES DOWN TO 0 PSIG. THE OVER PRESSURIZED HOUSE LINES RESULTED IN POTENTIAL DAMAGE TO 18 CUSTOMER-OWNED REGULATORS. COLUMBIA REBUILT THE JURISDICTIONAL REGULATOR STATION AND INSTALLED PARTIAL PRESSURE RELIEF VALVE. COLUMBIA HAS WORKED WITH THE CUSTOMER TO SAFELY REPLACE ALL POTENTIALLY DAMAGED CUSTOMER-OWNED HOUSE LINE REGULATORS. COLUMBIA CONDUCTED A FULL SCALE JURISDICTIONAL REGULATOR INSPECTION IN THE FIELD ON COLUMBIA-OWNED REGULATORS AS WELL AS CONDUCTED TESTING IN THE LAB TO TRY TO ASCERTAIN THE CAUSE OF THE FAILURE. COLUMBIA WAS UNABLE TO DUPLICATE THE FAILURE IN THE LABORATORY AND BELIEVES THE LIKELY CAUSE OF THE FAILURE WAS DEBRIS ON A SEALING SURFACE THAT ALLOWED AN INTERMITTENT BLEED THROUGH. PLEASE CONSIDER THIS A FINAL REPORT.
2025-03-31 10:13 | NO | YES | NO | 20190115 | 33317 | 2019-10-04 11:03 | SUPPLEMENTAL FINAL | 12606 | THE EMPIRE DISTRICT GAS COMPANY | 602 JOPLIN STREET | JOPLIN | MO | 64801 | 2019-09-07 15:00 |  |  | 2019 | HIGHLAND AVENUE | LEXINGTON | LAFAYETTE COUNTY | MO | 64067-1217 | 39.1798 | -93.8951 | [9 empty] | 2019-09-07 16:05 | 1257545 |  | NATURAL GAS |  | 750 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 130 | 2019-09-06 06:00 |  |  |  | 2019-09-06 06:35 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | OTHER | STAINLESS STEEL | [9 empty] | OTHER | [8 empty] | STAINLESS STEEL CONTROL LINES ON BOTH THE OPERATING REGULATOR AND MONITORING REGULATOR AT THIS REGULATOR STATION WERE SEVERED BY A VEHICLE THAT CRASHED IN TO THE BUILDING AT THIS LOCATION. | CLASS 2 LOCATION | 0 | 0 | 106700 | 120710.2481985588276 | 181300 | 205105.6044835868364 | 0 | 0 |  |  | 3000 | 3362.204724409448818897637795275590551181 |  | 0 | 291000 | 138053.3907440914169448818897637795275591 | 329178.0574065551128188976377952755905512 | 1 | 0 | 0 |  |  |  |  | 135 | 29 | 35 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | DAVID HINDS | MANAGER - COMPLIANCE | david.hinds@libertyutilities.com | 573-719-1175 | 573-248-1701 |  |  |  | DAVID HINDS | MANAGER - COMPLIANCE | 573-719-1175 | david.hinds@libertyutilities.com | AT APPROXIMATELY 5:50 A.M. ON SEPTEMBER 6TH, 2019, A TRUCK DRIVEN BY AN UNKNOWN INDIVIDUAL LEFT THE ROADWAY NEAR HIGHLAND AVENUE & 224 HIGHWAY IN LEXINGTON MISSOURI AND CRASHED IN TO A DISTRICT REGULATOR STATION OWNED BY THE EMPIRE DISTRICT GAS COMPANY. THE IMPACT OF THE CRASH SEVERED THE CONTROL LINES FOR BOTH THE OPERATING REGULATOR AND THE MONITORING REGULATOR AT THIS LOCATION AND CREATED AN OVERPRESSURE SITUATION THAT EXCEEDED THE MAOP ON THE SYSTEM SERVED BY THIS DISTRICT REGULATOR STATION. THE COST OF THE EMERGENCY RESPONSE TO THIS INCIDENT AND THE REPAIRS NEEDED TO REPLACE THE DISTRICT REGULATOR STATION DAMAGED BY THE CRASH IS ESTIMATED AT $288,000. 02/11/2020 - THE REPAIRS TO THE DAMAGED REGULATOR STATION HAVE BEEN COMPLETED AND A GUARDRAIL HAS BEEN INSTALLED AT THE LOCATION THE VEHICLE IN QUESTION LEFT THE ROADWAY. THE NRC REPORT NUMBER HAS BEEN CHANGED FROM #1257712 TO THE ORIGINAL NRC REPORT NUMBER OF #1257545. THE TIME AND DATE AN INCIDENT REPORTING CRITERIA WAS MET HAS BEEN CHANGED TO 09/07/2019 AT 15:00 AS THAT IS WHEN IT WAS DETERMINED THAT THIS INCIDENT WOULD RESULT IN COSTS EXCEEDING $50,000. THE LOCAL TIME THAT OPERATOR IDENTIFIED FAILURE HAS BEEN CHANGED TO 09/06/2019 AT 06:00 AS THAT IS WHEN THE LOCAL OPERATIONS MANAGER FOR THE LEXINGTON SERVICE AREA RECEIVED AN ALERT OF AN OVERPRESSURE SITUATION AT THIS REGULATOR STATION.
2025-03-31 10:13 | NO | NO | NO | 20190116 | 32797 | 2019-10-10 15:39 | ORIGINAL FINAL | 2196 | CENTRAL HUDSON GAS & ELECTRIC CORP | 284 SOUTH AVENUE | POUGHKEEPSIE | NY | 12601 | 2019-08-20 15:23 |  |  | 2019 | MYERS CORNER ROAD & BROTHERS RD | WAPPINGERS FALLS | DUTCHESS COUNTY | NY | 12590 | 41.6057 | -73.8649 | [10 empty] | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 100 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-08-20 15:23 |  |  |  | 2019-08-20 15:49 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2018 | [5 empty] | 6 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 9.33 |  |  | 3408 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 23020 | 26042.64211369094856 | 56386 | 63789.766212970366008 | 0 | 0 |  |  | 1700 | 1905.249343832020997375328083989501312336 |  | 0 | 81106 | 38968.3565252902457307664041994750656168 | 91737.6576704933355653753280839895013123 | 0 | 0 | 267 |  |  |  |  | 110 | 110 | 120 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | YES | [7 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | STORM DRAIN/CULVERT | YES | 7259149032 | NEW YORK |  | CONTRACT LOCATOR | YES | YES | 10 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | LENORE J CLARKE | SECTION ENGINEER-GAS SYSTEM SAFETY AND COMPLIANCE | lclarke@cenhud.com | 845 486 5521 |  |  |  |  | PAUL E. HAERING | SENIOR VICE PRESIDENT - ENGINEERING AND OPERATIONS | 845 486 5351 | phaering@cenhud.com | ON AUGUST 20, 2019, THE CONTRACTOR WAS BUILDING OUT THE WING WALLS FOR THE CREEK'S UNDERGROUND CULVERT THAT CROSSED UNDER MYERS CORNERS ROAD. THE CONTRACTOR WAS UTILIZING A HYDRAULIC HAMMER ON A LARGE EXCAVATOR WHEN THEY STRUCK THE 6' PLASTIC 120 PSIG GAS MAIN TWICE. THE FIRST DAMAGE CAUSED A SIGNIFICANT INDENT BUT NO LEAK. THE SECOND INDENT WAS LOCATED A FOOT AWAY AND CAUSED A PIPE WALL RUPTURE. THIS INCIDENT REQUIRED DAMAGE CLAIM TO BE COMPILED AND ESTIMATED COST WAS ONLY DETERMINED AT THIS TIME TO EXCEED $50,000.
2025-03-31 10:13 | NO | NO | NO | 20190117 | 32806 | 2019-10-11 15:18 | ORIGINAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2019-08-15 11:55 |  |  | 2019 | 47 INGALLS AVENUE | TROY | RENSSELEAR | NY | 12180 | 42.7471 | -73.6811 | [9 empty] | 2019-10-04 16:10 | 1260268 |  | NATURAL GAS |  | 800 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 6 | 2019-08-15 11:55 |  |  |  | 2019-08-15 11:55 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 40 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1953 | [5 empty] | 12 | API 5L GRADE B | UNKNOWN | STEEL |  | SEAMLESS | SEAMLESS | 0.33 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 1.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 61500 | 69575.260208166522 | 2500 | 2828.26261008807 | 0 | 0 |  |  | 3525 | 3950.590551181102362204724409448818897638 |  | 0 | 67525 | 33641.8952309704461102362204724409448819 | 76354.1133694356943622047244094488188976 | 0 | 0 | 0 |  |  |  |  | 210 | 210 | 225 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS NOT CAUSED BY CONTROLLER ACTIONS OR CONTROL ROOM ISSUES. | [12 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | 2019-04-20 | NO | [12 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | 521954900200 | DIG SAFELY NEW YORK |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER GAS WORK METHODS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER GAS WORK METHODS | 6317703549 | corinne.byrnes@nationalgrid.com | ON 8/15/2019, A NATIONAL GRID CREW WAS IMPACTING SHALE TO INSTALL A 4" DISTRIBUTION GAS MAIN FOR A MAIN REPLACEMENT JOB IN UPSTATE NY. THE IMPACTOR HEAD, INCORRECTLY SET TO "AUTOMATIC", MADE CONTACT WITH A NATIONAL GRID TRANSMISSION GAS MAIN, WHICH WAS PREVIOUSLY EXPOSED, AND RESULTED IN AN UNCONTROLLED RELEASE OF GAS TO THE ATMOSPHERE. APPROX. 4-6 HOMES WERE TEMPORARILY EVACUATED AND ALLOWED TO RETURN AT 15:20 THE SAME DAY. THE GAS TRANSMISSION PIPELINE WAS SHUT DOWN FOR REPAIRS. THE DAMAGED PIPELINE WAS REPLACED WITH A NEW CYLINDER SECTION. NO CUSTOMER SERVICES WERE IMPACTED.
2025-03-31 10:13 | NO | NO | NO | 20190118 | 32812 | 2019-10-14 11:32 | ORIGINAL FINAL | 8160 | INTERMOUNTAIN GAS CO | 555 SOUTH COLE ROAD | BOISE | ID | 83709 | 2019-10-03 12:30 |  |  | 2019 | INTERSECTION OF HWY 39 AND W 1900 S | ABERDEEN | BINGHAM | ID | 83210 | 42.9221 | -112.8495 | [9 empty] | 2019-10-03 14:22 | 1260164 |  | NATURAL GAS |  | 0.42 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-10-03 12:30 |  |  |  | 2019-10-03 13:17 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2012 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | VEHICLE IMPACT BROKE A 1/4" X 3/4" THREADED FITTING. | CLASS 1 LOCATION | 26200 | 29640.1921537229736 | 300 | 339.3915132105684 | 306 | 346.179343474779768 | 0 | 0 |  |  | 166 | 186.041994750656167979002624671916010499 |  | 0 | 26972 | 12732.1212658665940609501312335958005249 | 30511.8050051589779359790026246719160105 | 0 | 0 | 0 |  |  |  |  | 170 | 170 | 175 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.com | 208-377-6032 |  |  |  |  | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 208-377-6032 | greg.watkins@mdu.com | A 10 WHEELER FARM TRUCK HAULING POTATOES FLIPPED OVER WHILE MAKING A TURN NEAR AN INTERMOUNTAIN GAS COMPANY DISTRICT REGULATOR STATION. THE TRUCK STRUCK A POWER POLE AND THE CHAIN LINK FENCE ENCLOSURE OF THE DISTRICT REGULATOR STATION. THE IMPACT PUSHED A FENCE POST INTO A 1/4" X 3/4" THREADED FITTING WHICH SUBSEQUENTLY BROKE CAUSING AN UNCONTROLLED RELEASE OF GAS. AN INTERMOUNTAIN GAS FIRST RESPONDER SHUT OFF THE INLET AND OUTLET VALVES OF THE REGULATOR STATION. BECAUSE THE REPAIRS WERE MINOR AND THEREFORE MADE QUICKLY, DOWNSTREAM CUSTOMERS WERE NOT INTERRUPTED. WHEN THE INITIAL REPORT WAS MADE TO THE NRC, INTERMOUNTAIN GAS ESTIMATED THE COST OF THE VEHICLE TO BE OVER $50,000. ACTUAL COSTS WERE $26,200.
2025-03-31 10:13 | NO | YES | NO | 20190119 | 32850 | 2019-10-18 15:34 | ORIGINAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2019-06-06 09:50 |  |  | 2019 | STELTON RD. & JESSE WAY | PISCATAWAY | MIDDLESEX | NJ | 08854 | 40.5307 | -74.4173 | [9 empty] | 2019-06-07 09:49 | 1248121 |  |  |  | 532.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-06-06 09:55 |  |  |  | 2019-06-06 10:15 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | OTHER | DRIP RISER | 1949 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | DRIP RISER WAS CONTACTED | [5 empty] | CLASS 4 LOCATION | 111219 | 125822.615692554022932 | 0 | 0 | 7302 | 8260.789431545234856 | 0 | 0 |  |  | 2051 | 2298.627296587926509186351706036745406824 |  | 0 | 120572 | 57659.6898894443971763175853018372703412 | 136382.0324206871842971863517060367454068 | 0 | 0 | 0 |  |  |  |  | 28 | 28 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | MILLING EQUIPMENT | ROAD WORK | NO | [5 empty] | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | ROGER GUNNELS | PRINCIPAL REGULATORY SPECIALIST | roger.gunnels@pseg.com | 973-513-2474 |  |  |  |  | CHRIS LAROSSA | MANAGER REGULATORY POLICY AND PROCEDURE | 973-896-7617 | christopher.larossa@pseg.com | AT APPROXIMATELY AT APPROXIMATELY 9:50 AM ON THE CORNER OF STELTON RD AND JESSE WAY IN PISCATAWAY A SUB-CONTRACTOR WORKING FOR LUCAS BROTHERS WAS MILLING OUTSIDE OF THE SCOPE OF THE MARK OUT AND HIT A DRIP RISER. POLICE AND FIRE ARE ON THE SCENE. · THE DAMAGE WAS LEAKING FROM WHEN IT WAS HIT AT 9:50 AM UNTIL APPROXIMATELY 10:43 AM. THE DAMAGE WAS PINNED IT OFF IT WAS SLIGHTLY MISTING UNTIL 11:50 PM WHEN COMPLETE REPAIR WAS MADE. · THE FINAL REPAIR STARTED WITH FINDING A SAFE DEPTH THAT WAS BELOW THE LEVEL OF SATURATION, WHICH DIDN'T REQUIRE SHORING, WE EXCAVATED A CLEARING TO THAT DEPTH, AN 1-1/4" STOP-OFF PLUG WAS INSERTED IN THE DAMAGED, 1-1/4" DRIP RISER, THE DAMAGED RISER WAS CUT AT A LOCATION THAT REVEALED GOOD PIPE CONDITION, AND AN 1- 1/4" DRESSER END CAP WAS INSTALLED OVER THE DRIP RISER AS THE FINAL REPAIR METHOD. · THE INITIAL ESTIMATE WAS A DISCHARGE OF 30 GALLONS, LATER UPGRADED TO APPROXIMATELY 50-60 GALLONS (THE CAPACITY OF THE POT). · THE LEAK LEFT OIL POOLED ON TOP OF THE SOIL IN THE AREA OF THE REMOVED ASPHALT. THE LEAK LEFT A VERY FINE INTERMITTENT OILY RESIDUE ON THE GRASS, SHRUBS AND TREES OF THE CONDOMINIUM DEVELOPMENT AS WELL AS SOME OF THE EXTERNAL WALLS OF THE BUILDINGS AND ONE VEHICLE. · THE STORM DRAIN GRATE IMMEDIATELY ADJACENT TO THE POT MANHOLE WAS ASSUMED IMPACTED BY THE SPILL. ESTIMATES INDICATE THAT ONLY A MINIMAL AMOUNT OF OIL WAS DISCHARGED TO THE DRAIN, SEVERAL OUNCES MAXIMUM. · LOCATION CLEAN-UP HAS BEEN COMPLETED, AREA SAMPLES ARE BEING TESTED TO VERIFY THAT THE AREAS AFFECTED ARE CLEAN AND NO FURTHER CLEANUP IS REQUIRED.
2025-03-31 10:13 | NO | NO | NO | 20190120 | 32854 | 2019-10-21 21:21 | ORIGINAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2019-09-29 07:52 |  |  | 2019 | 900 EAST WICKENBURG WAY | WICKENBURG | MARICOPA | AZ | 85390 | 33.9588 | -112.7118 | [9 empty] | 2019-09-29 10:05 | 1259711 |  | NATURAL GAS |  | 1070 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 8 | 2019-09-29 08:05 |  |  |  | 2019-09-29 08:05 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1996 | [8 empty] | STEEL |  |  |  | 0.154 | [6 empty] | OTHER | [8 empty] | DISTRICT REGULATOR STATION DAMAGED BY VEHICLE. | CLASS 3 LOCATION | 0 | 0 | 59371 | 67166.711769415521588 | 8000 | 9050.440352281824 | 0 | 0 |  |  | 1444 | 1618.341207349081364829396325459317585302 |  | 0 | 68815 | 33063.9189209635614084698162729658792651 | 77835.4933290464269528293963254593175853 | 12 | 0 | 80 |  |  |  |  | 255 | 255 | 275 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | SHAWN BRINK | ADMINISTRATOR DIVISION COMPLIANCE | shawn.brink@swgas.com | 602-484-5489 | 602-484-5322 |  |  |  | HENGAMEH NAJAFI | DIRECTOR CENTRAL SUPPORT | 602-484-5355 | hengameh.najafi@swgas.com | ARIZONA CORPORATION COMMISSION PIPELINE INCIDENT # VG - P/L # 2019-0028 SOUTHWEST GAS CORPORATION (SWG) RESPONDED TO A REPORT OF A VEHICLE STRIKING A DISTRICT REGULATOR STATION AND ELECTRICAL POWER POLE AT 900 EAST WICKENBURG WAY (U.S HWY 60) IN WICKENBURG. SWG WAS NOTIFIED OF THE INCIDENT ON SEPTEMBER 29, 2019 AT 07:52 BY THE WICKENBURG FIRE DEPARTMENT. EAST WICKENBURG WAY (US HWY 60) WAS CLOSED IN BOTH DIRECTIONS BY THE FIRE DEPARTMENT. SWG CREWS RESPONDED AND CONTROLLED THE FLOW OF GAS BY UTILIZING VALVES RESULTING IN AN OUTAGE OF 92 ACTIVE ACCOUNTS. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THE INCIDENT. SWG NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) ON SEPTEMBER 29, 2019 AT 10:05 AND WAS GIVEN NRC REPORT #1259711.
2025-03-31 10:13 | NO | YES | NO | 20190121 | 33472 | 2019-10-25 10:04 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2019-09-27 03:08 |  |  | 2019 | SALEM ST @ S BROADWAY | LAWRENCE | ESSEX | MA | 01843 | 42.6971 | -71.1633 | [9 empty] | 2019-09-27 06:00 | 1259504 |  | NATURAL GAS |  | 390 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 97 | 2019-09-27 03:08 |  |  |  | 2019-09-27 03:29 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2018 | [5 empty] | 2 | ASTM D2513 | PERFORMACE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | LEAK |  |  | OTHER | VALVE CLOSED ON INSERTED MAIN | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 1764026 | 1995651.511609287107928 | 81000 | 91635.708566853468 | 796491 | 901074.285828662784948 | CLAIMS PAID. CLAIMS CENTER ONSITE. POLICE, FOOD |  | 944 | 1057.973753280839895013123359580052493438 |  | 0 | 2642461 | 1238668.39845489764275965616797900262467 | 2989419.47975808420077101312335958005249 | 41 | 0 | 56 |  |  |  |  | 82 | 82 | 99 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | WATER DEPARTMENT CLOSED A GAS GATE VALVE ON AN ABANDONED CAST IRON GAS MAIN WITH A 2" PLASTIC MAIN LINE THAT WAS INSERTED THROUGH THE CAST IRON, SEVERING THE 2" PLASTIC MAIN | [154 empty] | KATHERINE SILVER | COMPLIANCE MANAGER | ksilver@nisource.com | 508-864-1836 |  |  |  |  | KATHERINE SILVER | COMPLIANCE MANAGER | 508-864-1836 | ksilver@nisource.com | IN THE EARLY MORNING OF FRIDAY, SEPTEMBER 27, 2019, WHILE CONDUCTING A CHECK OF WATER VALVES, CONTRACTORS WORKING FOR THE CITY OF LAWRENCE INADVERTENTLY CLOSED A LEGACY GAS VALVE THAT WAS CONNECTED TO AN ABANDONED GAS MAIN. THE ABANDONED GAS MAIN HAD WITHIN IT AN INSERTED, ACTIVE GAS MAIN. THE TURNING OF THE LEGACY VALVE SHEARED THE ACTIVE INSERTED MAIN. AT 03:08 AM, COLUMBIA GAS RECEIVED A GAS ODOR CALL AND DISPATCHED A TECH TO INVESTIGATE. EMERGENCY RESPONSE PROCEDURES WERE IMPLEMENTED. UPDATE: PART A: 16. CUSTOMER IMPACT NUMBER UPDATED TO INCLUDE CUSTOMER METERS THAT WERE TURNED OFF IN THE AREA BUT NOT ON THE IMPACTED MAIN. GENERAL PUBLIC EVACUATED IS NOT AVAILABLE AS EVACUATED BY FIRE AND POLICE EMERGENCY RESPONDERS. PART D: 2B. ADDITIONAL DOLLARS ADDED 3. CUSTOMER IMPACT NUMBER UPDATED TO INCLUDE CUSTOMER METERS THAT WERE TURNED OFF IN THE AREA BUT NOT ON THE IMPACTED MAIN.
2025-03-31 10:13 | NO | YES | NO | 20190122 | 32887 | 2019-10-31 14:09 | ORIGINAL FINAL | 18112 | SAN DIEGO GAS & ELECTRIC CO | 8326 CENTURY PARK COURT | SAN DIEGO | CA | 92123 | 2019-10-02 11:41 |  |  | 2019 | STRANDWAY AND YORK CT | SAN DIEGO | SAN DIEGO | CA | 92109 | 32.7892 | -117.2545 | [9 empty] | 2019-10-02 18:27 | 1260063 |  | NATURAL GAS |  | 268 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 67 | 2019-10-02 11:41 |  |  |  | 2019-10-02 12:11 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1959 | [5 empty] | 6.625 | API 5L GRADE B | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | OTHER | [8 empty] | 0.500" HOLE EXPOSED IN 6.625" MAIN DUE TO MECHANICAL DAMAGE TO 3/4" SERVICE NIPPLE. | CLASS 3 LOCATION | 0 | 0 | 123961 | 140237.704563650898108 | 12247 | 13855.092874299437316 | 0 | 0 |  |  | 1610 | 1804.383202099737532808398950131233595801 |  | 0 | 137818 | 65489.77535274067345641994750656167979 | 155897.1806400500729568083989501312335958 | 0 | 0 | 157 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | 192330149 | DIGALERT |  | CONTRACT LOCATOR | YES | YES | 8 | EXCAVATION ISSUE | EXCAVATOR FAILED TO PROTECT/SHORE/SUPPORT FACILITIES | [170 empty] | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | amatin@socalgas.com | 9099190463 |  |  |  |  | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 9099190463 | amatin@socalgas.com | ON 10/02/2019, SDG&E WAS NOTIFIED OF A THIRD-PARTY DAMAGE AT THE INTERSECTION OF STRANDWAY AND YORK CT, SAN DIEGO, CAUSING A RELEASE OF NATURAL GAS. CREWS RESPONDED AND WORKED WITH FIRE AND POLICE DEPARTMENTS TO SAFELY CONTROL THE GAS. THERE WERE NO INJURIES THAT RESULTED FROM THIS INCIDENT. THE CONTRACTOR WAS WORKING TO INSTALL AN 8-INCH WATER MAIN NEAR A 6-INCH STEEL GAS MAIN WHEN A SECTION OF CONCRETE COLLAPSED FROM THE PAVEMENT ONTO THE PIPE SHEARING OFF AN ABANDONED 0.75-INCH SERVICE TEE FROM THE 6-INCH MAIN. INVESTIGATION OF THE INCIDENT REVEALED THE CONTRACTOR FAILED TO PROPERLY PROTECT THE EXPOSED GAS FACILITIES DURING CONSTRUCTION ACTIVITIES. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE, MEDIA COVERAGE, AND ESTIMATED DAMAGE AMOUNT EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, CONTACT ALI MATIN AT (909) 919-0463.
2025-03-31 10:13 | NO | YES | NO | 20190123 | 33721 | 2019-10-31 15:01 | SUPPLEMENTAL FINAL | 22154 | WARNER ROBINS GAS SYSTEM | P.O. BOX 1488 | WARNER ROBINS | GA | 31099 | 2019-10-09 12:33 |  |  | 2019 | HWY 247 SPUR @ SANDBED RD. | Not Within a Municipality | HOUSTON | GA | 31047 | 32.4547 | -83.6203 | [9 empty] | 2019-10-09 15:20 | 1260677 |  | NATURAL GAS |  | 2300 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-10-09 13:20 |  |  |  | 2019-10-09 13:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 22 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1969 | [5 empty] | 8 | API 5L | UNKNOWN | STEEL |  | OTHER | WELDED | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 125000 | 141413.1305044035 | 8500 | 9616.092874299438 | 0 | 0 |  |  | 4000 | 4482.939632545931758530183727034120734908 |  | 0 | 137500 | 66698.7563804324674265091863517060367454 | 155512.1630112488697585301837270341207349 | 0 | 2 | 43 |  |  |  |  | 490 | 490 | 500 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | LEONARD AMMONS | CITY OF WARNER ROBINS GAS SUPERINTENDENT | lammons@wrga.gov | 478-951-2982 | 478-929-1964 |  |  |  | LEONARD AMMONS | CITY OF WARNER ROBINS GAS SUPERINTENDENT | 478-951-2982 | lammons@wrga.gov | ON OCTOBER 9TH 2019 AT APPROXIMATELY 12:30 A NORFOLK SOUTHERN TRAIN DERAILED ON HWY 247 SPUR @ SANDBED RD. POKING A HOLE IN THE 8" GAS MAIN BELONGING TO THE CITY OF WARNER ROBINS GA. THE WARNER ROBINS GAS DEPARTMENT RESPONDED TO THE 911 CALL AND PROCEEDED TO IMPLEMENT ITS EMERGENCY PLAN AND ESTABLISHED CONTACT WITH HOUSTON COUNTY FIRE DEPARTMENT'S INCIDENT COMMAND. DURING COORDINATION WITH INCIDENT COMMAND WARNER ROBINS GAS LOCATED ITS CLOSEST CRITICAL VALVES AND PROCEEDED TO SHUT DOWN THE DAMAGED SEGMENT. ALL CUSTOMERS AFFECTED WERE LOCKED OFF AND NOTIFIED OF THE TEMPORARY SHUTDOWN. AFTER DEPRESSURIZATION OCCURRED WARNER ROBINS GAS DEPARTMENT CONTACTED THEIR CONTRACTOR TO INSTALL A CAP OF THE LINE SEGMENT IN ORDER TO REESTABLISH ALL CUSTOMERS LOST DURING THE SHUTDOWN EXCEPT ONE INTERRUPTIBLE INDUSTRIAL CUSTOMER AT THE END OF THE LINE SEGMENT. THE UNDAMAGED LINE WAS THEN PURGED AND REINSTATED AND ALL CUSTOMERS WERE TURNED ON AND RELIT ACCORDING TO THE WARNER ROBINS RESTORATION OF SERVICE PROCEDURES IN APPENDIX M OF THE WARNER ROBINS EMERGENCY PLAN MANUAL. DURING NORFOLK SOUTHERNS' CLEAN UP AND REMOVAL OF THE 26 DERAILED CARS OTHER DAMAGES TO THE PIPELINE OCCURRED NECESSITATING 2000 FEET OF THE 8" MAIN BE REPLACED. AT THIS TIME, APPROXIMATELY 80% OF THE REPLACEMENT PROCESS HAS BEEN COMPLETED. THE CITY OF WARNER ROBINS EXPECTS REINSTATEMENT OF THE MAIN TO OCCUR ON OR ABOUT NOVEMBER 8TH 2019.
2025-03-31 10:13 | NO | YES | YES | 20190124 | 32890 | 2019-11-01 08:00 | ORIGINAL FINAL | 17570 | ROCHESTER GAS & ELECTRIC CORP | 180 SOUTH CLINTON AVENUE | ROCHESTER | NY | 14607 | 2019-08-21 17:17 |  |  | 2019 | 64 ILLINOIS ST | ROCHESTER | MONROE | NY | 14609 | 43.1578 | -77.5597 | [9 empty] | 2019-08-21 20:38 | 1255972 |  | NATURAL GAS |  | 0.9 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 14 | 2019-08-21 17:15 |  |  |  | 2019-08-21 17:31 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | 1996 | [8 empty] | OTHER | ALUMINUM (SERVICE REGULATOR) | [9 empty] | OTHER | [8 empty] | INTENTIONAL DISASSEMBLY OF THE SERVICE REGULATOR UPSTREAM OF THE METER BY THE BUILDING OCCUPANT/CUSTOMER. DISASSEMBLY OF THE SERVICE REGULATOR RESULTED IN A DIRECT RELEASE OF GAS INTO THE BASEMENT OF THE BUILDING | CLASS 3 LOCATION | 100000 | 113130.5044035228 | 2500 | 2828.26261008807 | 2500 | 2828.26261008807 | 0 | 0 | NO ADDITIONAL ESTIMATED COSTS |  | 21 | 23.53543307086614173228346456692913385827 |  | 0 | 105021 | 49219.7967402793920866141732283464566929 | 118810.5650567698061417322834645669291339 | 0 | 0 | 1 |  |  |  |  | 10 | 10 | 12 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FIRE DEPARTMENT IDENTIFICATION THAT THE SERVICE REGULATOR INSIDE THE BUILDING HAD VISIBLE SIGNS THAT IT HAD BEEN TAMPERED WITH AND WAS NOT IN IT'S NORMALLY EXPECTED CONFIGURATION. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [156 empty] | BARRY KACHMARYK | GAS ENGINEERING MANAGER | barry_kachmaryk@rge.com | 5857714143 |  |  |  |  | BARRY KACHMARYK | GAS ENGINEERING MANAGER | 5857714143 | barry_kachmaryk@rge.com | ON 8/21/2019 RGE WAS CALLED TO INVESTIGATE GAS ODOR BY A CUSTOMER AT 52 ILLINOIS ST, ROCHESTER NY. AFTER SURVEYING OUTSIDE AREA, THE RG&E CREW DETERMINED THE ODOR WAS ORIGINATING FROM 64 ILLINOIS ST. THE RG&E CREW KNOCKED ON DOOR OF 64 ILLINOIS ST HOWEVER NO-ONE ANSWERED THE DOOR TO PROVIDE THE COMPANY ACCESS TO THE BUILDING. THE RGE CREW REQUESTED FIRE DEPARTMENT ASSISTANCE TO GAIN BUILDING ACCESS. FIRE DEPT ARRIVED AND PRIOR TO BUILDING ENTRY AN EXPLOSION IN THE HOUSE OCCURRED. THE SINGLE FAMILY BUILDING AT 64 ILLINOIS ST, ROCHESTER, NY WAS DESTROYED AND THE EXPLOSION CAUSED EXTERIOR DAMAGE TO ADJACENT RESIDENTIAL BUILDING. FIRE DEPT. ACTIONS FOLLOWING THE EXPLOSION IDENTIFIED A HUMAN BODY IN THE BASEMENT OF 64 ILLINOIS ST. RGE AND FIRE DEPT PERSONNEL ON SCENE IDENTIFIED THAT THE SERVICE REGULATOR UPSTREAM OF THE COMPANY METER APPEARED TO HAVE BEEN INTENTIONALLY TAMPERED WITH/DISASSEMBLED THAT WOULD HAVE RELEASED NATURAL GAS INTO THE BUILDING. AS PART OF THE COMPANIES NORMAL CONTROL ROOM NOTIFICATION PROCEDURES, THE NRC WAS NOTIFIED ON 8/21/2019 (REPORT # 1255972) HOWEVER THE COMPANY DID NOT CONSIDER IT REPORTABLE TO PHMSA SINCE THERE WAS NO COMPONENT FAILURE OR CONTRIBUTING COMPANY CAUSE OF THE EVENT. SUBSEQUENT DISCUSSION WITH NYS PSC SAFETY STAFF SUGGESTED RG&E REQUEST CLARIFICATION FROM PHMSA (REQUEST SENT ON 10/10/2019, RESPONSE FROM MR. PETER KATCHMAR ON 10/16/2019). MR. KATCHMAR INDICATED THIS WAS A REPORTABLE EVENT.
2025-03-31 10:13 | NO | NO | NO | 20190125 | 32956 | 2019-11-04 08:33 | SUPPLEMENTAL FINAL | 13061 | NATIONAL FUEL GAS DISTRIBUTION CORP | 6363 MAIN ST. | WILLIAMSVILLE | NY | 14221 | 2019-10-05 08:05 |  |  | 2019 | STATE ROUTE 8 | CORNPLANTER TOWNSHIP | VENANGO | PA | 16301 | 41.5101 | -79.6991 | [9 empty] | 2019-10-05 08:05 | 1260300 |  | NATURAL GAS |  | 991 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 118 | 2019-10-05 03:35 |  |  |  | 2019-10-05 03:59 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | BLOWOFF RISER | 1955 | [8 empty] | STEEL |  |  |  | 0.154 | [6 empty] | LEAK |  |  | OTHER | UTV HIT RISER | [5 empty] | CLASS 3 LOCATION | 4212 | 4765.056845476380336 | 45896 | 51922.376301040824288 | 2691 | 3044.341873498798548 | 0 | 0 |  |  | 3723 | 4172.496062992125984251968503937007874016 |  | 0 | 56522 | 28598.9129263165711355984251968503937008 | 63904.271083008129156251968503937007874 | 0 | 0 | 0 |  |  |  |  | 217 | 217 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | OBSERVED PRESSURES AND FLOWS WERE WITHIN NORMAL OPERATING CONDITION LIMITS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | STEVEN M. MONNIE | ENGINEER II | monnies@natfuel.com | 814-871-8204 |  |  |  |  | KURT W. MEIGHEN | SUPERINTENDENT | 814-371-5870 | meighenk@natfuel.com | AT APPROXIMATELY 3:30 AM ON SATURDAY, OCTOBER 5, 2019, A SIDE-BY-SIDE ATV STRUCK AN ABOVE-GRADE FACILITY AT A REMOTE LOCATION ON A HIGH PRESSURE DISTRIBUTION MAIN RESULTING IN AN UNINTENTIONAL RELEASE OF NATURAL GAS. THERE WERE NO INJURIES REQUIRING INPATIENT HOSPITALIZATION OR FATALITIES. AT APPROXIMATELY 5:00 AM, HOMES IN CORNPLANTER AND ALONG STATE ROUTE 8 WERE EVACUATED, UNDER THE DIRECTION OF THE CORNPLANTER TOWNSHIP VOLUNTEER FIRE DEPARTMENT, UNTIL THE SITUATION WAS MADE SAFE AROUND 9:00 AM. DURING THIS TIME, A NATIONAL FUEL FIELD SERVICE REPRESENTATIVE MONITORED AIR QUALITY AT NEARBY HOMES TO ENSURE THAT THERE WAS NO DANGER TO PUBLIC SAFETY. INVESTIGATION INTO THE INCIDENT REVEALED THE IMPACT TO THE ABOVE-GRADE FACILITY CAUSED A 2" RISER TO SEPARATE FROM A BELOW-GRADE 2" VALVE RESULTING IN A LEAK. ALL ABOVE-GRADE FACILITIES WERE REMOVED AS PART OF THE REPAIR.
2025-03-31 10:13 | YES | NO | NO | 20190126 | 32987 | 2019-11-06 13:34 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2019-10-11 15:53 |  |  | 2019 | 2709 WALTERS PORT LN | EXCELSIOR | HENNEPIN | MN | 55331 | 44.9277 | -93.6041 | [9 empty] | 2019-10-11 21:19 | 1260908 |  | NATURAL GAS |  | 9.89 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2019-10-11 15:53 |  |  |  | 2019-10-11 16:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2019 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 100000 | 113130.5044035228 | 4520 | 5113.49879903923056 | 3407 | 3854.356285028021796 | 1207 | 1365.485188150520196 | COST FOR CREW TO AIR TEST SERVICE LINE ON 10/15/2019 |  | 87 | 97.50393700787401574803149606299212598425 |  | 0 | 109221 | 51225.2184676875665054015748031496062992 | 123561.348612748446567748031496062992126 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | AARON ABRAHAMSON | OPERATIONS SPECIALIST II | aaron.abrahamson@centerpointenergy.com | 612-321-5514 |  |  |  |  | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 612-321-5366 | dean.headlee@centerpointenergy.com | CNP WAS CALLED TO A FIRE INVOLVING A METER SET ON 10/11/2019 AT 2709 WALTER PORT LN. UPON ARRIVAL CNP SHUT OFF THE FLOW OF GAS TO THE METER SET AT 16:15 AND THE SERVICE WAS THEN SQUEEZED AND CAPPED AT 17:20. ON 10/15/2019 WITH MNOPS ON SITE, THE SERVICE LINE PASSED AIR TESTS PERFORMED TO COMPANY STANDARDS WITH ADAM RATZLAFF OF MINNESOTA OFFICE OF PIPELINE SAFETY(MNOPS) IN ATTENDANCE. IN AN EMAIL FROM JEFF BLACKWELL OF MNOPS, CNP WAS INFORMED THE FIRE WAS CAUSED BY A CONSTRUCTION WORKER DROPPING A CIGARETTE NEAR THE AREA WHERE THE FIRE WAS STARTED. "10-24-19: JRB SPOKE WITH SHAWN JOHNSON WITH THE CITY OF MINNETONKA FIRE INVESTIGATION AND HE SAID THAT WHITEMORE, THE INVESTIGATION COMPANY, WAS ABLE TO VIEW VIDEO TAPE FROM CAMERAS LOCATED ON SITE AND THE FOOTAGE SHOWED A CONSTRUCTION WORKER DROPPING A CIGARETTE BUTT IN THE AREA WHERE THE FIRE BEGAN. THIS HAS BEEN RULED THE CAUSE OF THE FIRE. THIS CASE WILL BE CLOSED." ANOTHER INVESTIGATION INVOLVING CNP WILL TAKE PLACE ON 11/13/2019 A SUPPLEMENTAL REPORT WILL BE PROVIDED AFTER. UPDATE 11/15/2019 NO NEW INFORMATION AFTER THE INVESTIGATION ON 11/13/2019. CAUSE OF INCIDENT WAS DUE TO A DROPPED CIGARETTE. CENTERPOINT ENERGY HAS TAKEN THE METER SET IN TO CUSTODY. THERE IS NO TIME TABLE AS OF 11/15/2019 OF WHEN SERVICE WILL BE RESTORED. AS REQUESTED BY ASHLEY HORTON OF PHMSA IN EMAIL SENT TO MNOPS ON 11/12/2019 THE TIME REPORTED TO THE NATIONAL RESPONSE CENTER HAS BEEN UPDATED AND THE TIME THE SERVICE LINE WAS CAPPED IS THE SAME AS WHEN THE LINE WAS SHUT DOWN. UPDATE 11/26/2019 UPDATED THE TIME THE SERVICE WAS CAPPED AS INSTRUCTED BY ASHLEY HORTON OF PHMSA. IT WAS NOT POSSIBLE TO ADD A DESCRIPTION AFTER SELECTING G4 NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE AND EXPLOSION AS THE PRIMARY CAUSE OF INCIDENT. VIDEO SURVEILLANCE CAMERAS CONFIRMED A DROPPED CIGARETTE WAS THE CAUSE OF THE FIRE THAT EVENTUALLY STARTED THE HOUSE AND METER SET ON FIRE.
2025-03-31 10:13 | NO | YES | YES | 20190127 | 32929 | 2019-11-07 18:29 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2019-10-11 10:38 |  |  | 2019 | 10315 MIDVALE AVE N | SEATTLE | KING | WA | 98133 | 47.7037 | -122.3433 | [9 empty] | 2019-10-11 14:57 | 1260896 |  | NATURAL GAS |  | 110.16 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 24 | 2019-10-11 10:38 |  |  |  | 2019-10-11 10:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2008 | [5 empty] | 2.375 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 5010 | 5667.83827061649228 | 3748 | 4240.131305044034544 | 0 | 0 |  |  | 980 | 1098.320209973753280839895013123359580052 |  | 0 | 9738 | 5119.594343541327207994750656167979002625 | 11006.2897856342801048398950131233595801 | 0 | 0 | 18 |  |  |  |  | 39.5 | 39.8 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INJURY OCCURRED DURING THE EMERGENCY RESPONSE TO DAMAGE CAUSED BY A THIRD PARTY CONTRACTOR WITH EXCAVATOR | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | DRAINAGE | YES | 19445690 |  |  | CONTRACT LOCATOR | YES | YES | 6 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | MIHAELA STEFANESCU | REGULATORY COMPLIANCE ANALYST | mihaela.stefanescu@pse.com | 425-457-5752 |  |  |  |  | KAAREN DAUGHERTY | MANAGER COMPLIANCE AND QUALITY MANAGEMENT | 425-462-3748 | kaaren.daugherty@pse.com | PSE RESPONDED TO A CALL FROM THE SEATTLE FIRE DEPARTMENT ON A BROKEN 2" PE GAS MAIN ON OCTOBER 11, 2019 AT 10:38. PSE'S GAS FIRST RESPONSE (GFR) PERSONNEL ARRIVED ONSITE AT 10:55 AND FOUND THAT A CONTRACTOR (SEATTLE PUBLIC UTILITIES) HAD DUG INTO THE 2"PE PIPELINE WITH EXCAVATOR. AT 11:07, WHILE GFR TECHNICIANS WERE IN THE PROCESS OF SQUEEZING THE PIPELINE TO STOP THE FLOW OF GAS, IGNITION OCCURRED. THREE FITTERS SUSTAINED BURNS AND WERE TAKEN TO HARBORVIEW MEDICAL CENTER AND ONE WAS ADMITTED TO THE HOSPITAL. ANOTHER GFR FITTER THAT WAS ALREADY ON SITE, CONTROLLED THE SITUATION AT 12:10 BY SQUEEZING THE PIPELINE IN A SEPARATE HOLE ON THE NORTH SIDE OF THE DAMAGED MAIN AND BY TURNING OFF THE VALVE ON THE SOUTH SIDE. AS A RESULT, 18 CUSTOMERS LOST SERVICE. APPROXIMATELY 24 PEOPLE WERE EVACUATED OUT OF 4 STRUCTURES. THE BUILDINGS WERE CLEARED FOR RE-ENTRY AT 13:13. PSE'S CONTRACTOR INFRASOURCE COMPLETED THE REPAIR AT 18:25. PSE NOTIFIED THE WASHINGTON UTILITIES AND TRANSPORTATION COMMISSION (WUTC) AT 11:44 ON 10/11/2019 AND THE NRC AT 14:57. A 48 HOUR FOLLOW UP CONTACT TO THE NRC WAS MADE ON 10/14/2019 AT 16:50 (NRC 1261117).
2025-03-31 10:13 | NO | YES | NO | 20190128 | 33005 | 2019-11-08 15:02 | SUPPLEMENTAL FINAL | 22763 | WISCONSIN GAS LLC DBA WE ENERGIES | 231 W. MICHIGAN STREET | MILWAUKEE | WI | 53203 | 2019-10-14 14:05 |  |  | 2019 | 136 W. ST GEORGE AVE | GRANTSBURG | BURNETT | WI | 54840 | 45.7758 | -92.6838 | [9 empty] | 2019-10-14 14:49 | 1261090 |  | NATURAL GAS |  | 195 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 15 | 2019-10-14 11:52 |  |  |  | 2019-10-14 12:30 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 34 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1991 | [5 empty] | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 3 | 2 | [7 empty] | CLASS 3 LOCATION | 125000 | 141413.1305044035 | 1300 | 1470.6965572457964 | 1400 | 1583.8270616493192 | 0 | 0 |  |  | 1100 | 1232.8083989501312335958005249343832021 |  | 0 | 128800 | 60974.589505375114579790026246719160105 | 145700.4625222487468335958005249343832021 | 0 | 0 | 1 |  |  |  |  | 50.3 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE FACILITY WAS DAMAGED BY A THIRD PARTY EXCAVATOR | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | NO | [5 empty] | YES | 5 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CLAUDE WILLIAMS JR | ENGINEER | claude.williams@we-energies.com | 414 221-5549 | 414 221-3027 |  |  |  | TIM STROMMEN | MANAGER GAS CODE COMPLIANCE | 414 221-5173 | tim.strommen@we-energies.com | AT 11:51 AM ON 10/14/19, WE ENERGIES WAS NOTIFIED OF A GAS MAIN DAMAGE AT 136 W. ST GEORGE AVE. IN GRANTSBURG, WI. A WE ENERGIES EMPLOYEE WAS DISPATCHED TO THE SCENE. UPON ARRIVAL THE EMPLOYEE FOUND THAT A 3RD PARTY EXCAVATOR HAD STRUCK THE MAIN, RESULTING IN A GAS RELEASE WHICH ALSO IGNITED. NO ONE WAS INJURED OR TRANSPORTED TO THE HOSPITAL; HOWEVER, THE NEARBY HOMES WERE DAMAGED BY THE FIRE CAUSING LOSSES BELIEVED TO EXCEED THE $50,000 FEDERAL REPORTING THRESHOLD. SEVERAL HOMES WERE EVACUATED AND THE GRANTSBURG FIRE DEPARTMENT WAS ALSO AT THE SCENE PUTTING OUT THE FIRE. AFTER CALLING IN THE 48 HOUR UPDATE, WE WERE PROVIDE WITH A NEW NRC NUMBER, 1261272. THE RELEASE OF GAS WAS STOPPED AT 13:08 BY USING A VALVE AND REMOTE SQUEEZE OF THE PE MAIN. THE PE MAIN IS 2 WAY FED WHICH ALLOWED THE ISOLATED SECTION TO BE CAPPED AND ONLY THE HOUSE AT 136 W ST GEORGE AVE. LEFT WITHOUT SERVICE. THIS PREMISE REMAINS UNINHABITABLE DUE TO THE FIRE DAMAGE. ON NOVEMBER 4, 2019 A FIELD INVESTIGATION WAS CONDUCTED AND THE CAUSE OF THE INCIDENT WAS CONFIRMED TO BE 3RD PARTY DAMAGE DURING EXCAVATION USING A BACKHOE. THE EXCAVATOR WILL RECEIVE A LETTER AS A RESULT OF THIS INCIDENT FROM WE ENERGIES FREQUENT DAMAGERS PROGRAM. EXCAVATOR WILL ALSO BE REFERRED TO THE WISCONSIN ONE CALL CENTER, DIGGERS HOTLINE, COMPLAINT PROCESS.
2025-03-31 10:13 | NO | NO | NO | 20190129 | 32907 | 2019-11-08 15:13 | ORIGINAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2019-10-12 03:40 |  |  | 2019 | DUNCAN CHAPEL ROAD | GREENVILLE | GREENVILLE | SC | 29617 | 34.92 | -82.4455 | [9 empty] | 2019-10-12 08:09 | 1260922 |  | NATURAL GAS |  | 1788 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-10-12 04:10 |  |  |  | 2019-10-12 04:35 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | DUCTILE IRON | [10 empty] | OTHER | [8 empty] | VALVE BROKEN OFF THREADED PIPE FITTING DUE TO BEING HIT BY A VEHICLE. | CLASS 3 LOCATION | 0 | 0 | 47000 | 53171.337069655716 | 0 | 0 | 0 | 0 |  |  | 13725 | 15382.0866141732283464566929133858267717 |  | 0 | 60725 | 36251.3038427242363228346456692913385827 | 68553.4236838289443464566929133858267717 | 1 | 1 | 315 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | N/A | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST II | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | A VEHICLE DROVE THROUGH THE FENCE OF A REGULATOR STATION STRIKING AND DAMAGING THE REGULATOR VALVE. THE DRIVER WAS TAKEN TO THE HOSPITAL. INJURIES SUSTAINED IN THE WRECK WERE NOT GAS RELATED.
2025-03-31 10:13 | NO | YES | NO | 20190130 | 34429 | 2019-11-13 17:41 | SUPPLEMENTAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2019-10-15 04:20 |  |  | 2019 | 1003 FAYETTEVILLE STREET | DURHAM | DURHAM | NC | 27701 | 35.984 | -78.8986 | [9 empty] | 2019-10-15 07:37 | 1261133 |  | NATURAL GAS |  | 6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2019-10-15 04:20 |  |  |  | 2019-10-15 05:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2017 | [8 empty] | OTHER | ALUMINUM | [9 empty] | LEAK |  |  | OTHER | DAMAGED BY FIRE | [5 empty] | CLASS 3 LOCATION | 320500 | 362583.266613290574 | 13 | 14.706965572457964 | 1514 | 1712.795836669335192 | 189 | 213.816653322658092 | ADMINISTRATION COSTS |  | 25 | 28.01837270341207349081364829396325459318 |  | 0 | 322241 | 151001.0696003873119065406824146981627297 | 364552.6044415584373214908136482939632546 | 1 | 0 | 0 |  |  |  |  | 60 | 60 | 66 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | OTHER | PROBABLE ARSON | [155 empty] | JERAMY FREE | ENGINEER IV - PIPELINE COMPLIANCE | jeramy.free@dominionenergy.com | 803-260-3602 |  |  |  |  | SCOTT SWINDLER | GENERAL MANAGER-OPERATIONS AND MAINTENANCE | 704-810-3230 | scott.swindler@dominionenergy.com | THIS IS A SUPPLEMENTAL/FINAL REPORT FOR INCIDENT REPORT NUMBER 20190130-32930 DOMINION ENERGY RESPONDED TO A CALL FROM DURHAM COUNTY 911 AT 4:20 AM ON 10/15/19 REPORTING A FIRE AT 1003 FAYETTEVILLE ST. IN DURHAM NC. OUR SERVICE TECH ARRIVED ON SCENE TO FIND THE BUILDING ON FIRE. WE WERE INFORMED BY THE FD THAT THERE HAD BEEN A FIRE AT THE SERVICE RISER. THE FD HAD TURNED OFF THE SERVICE CUTOFF TO PUT THE FIRE OUT AT THE RISER. THE BUILDING WAS FULLY INVOLVED AND WAS QUICKLY PUT OUT. THE GAS METER AND REGULATOR WERE DESTROYED IN THE FIRE. STEVE WOOD, WITH THE NCUC WAS NOTIFIED BY EMAIL AT 6:23 AM ON 10/15/19 AND A VOICEMAIL MESSAGE AT 6:33 AM. THE INITIAL NRC REPORT WITH USDOT BY PHONE AT 7:32 AM. THE SERVICE LINE WAS REPAIRED AND RETIRED AT 10:53 AM. THE APPARENT CAUSE WAS AN INTERIOR FIRE SET BY IGNITING TIRES AROUND METER SET. ACCORDING TO THE DURHAM FIRE DEPARTMENT FIRE MARSHAL, THE AVAILABLE EVIDENCE INDICATES THAT THIS FIRE WAS INTENTIONAL ARSON. HOWEVER, AN OFFICIAL CAUSE COULD NOT BE DETERMINED AND COULD NOT BE OFFICIALLY DOCUMENTED BY THE FIRE DEPARTMENT. NRC REPORT #1261133 AND LDF #276085 ORIGINAL PHMSA INCIDENT REPORT NUMBER: 20190130-32930
2025-03-31 10:13 | NO | NO | NO | 20190131 | 35768 | 2019-11-14 15:37 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2019-10-03 11:58 | EASTERN | NO | 2019 | 2600 COLLINS AVE | MIAMI BEACH | MAIMI - DADE | FL | 33140 | 25.8026 | -80.1265 | [5 empty] | YES |  |  |  | 2019-10-04 19:32 | 1260286 |  | NATURAL GAS |  | 114.36 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2019-10-04 00:08 |  |  |  | 2019-10-04 00:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 72 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2017 | [5 empty] | 6 | D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | MECHANICAL PUNCTURE | 2 | 3 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 40125 | 45393.6148919135235 | 21420 | 24232.55404323458376 | 0 | 0 |  | 76.495 | 8748 | 9804.188976377952755905511811023622047244 | 0 | 0 | 70293 | 37906.5198090230887602755905511811023622 | 79430.3579115260600159055118110236220472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 35 | 60 | 192.619(A)(2) | 2020-05-06 | PRESSURE DID NOT EXCEED MAOP | DRIP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS THE RESULT OF EXCAVATION DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | AUGER | ELECTRIC | YES | 274903389 |  |  | UTILITY OWNER | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | SANDRA PANOS | SUPERVISOR QUALITY ASSURANCE | sjpanos@tecoenergy.com | 813 205-3699 |  |  |  |  | SANDRA PANOS | SUPERVISOR QUALTY ASSURANCE | 813-205-3699 | sjpanos@tecoenergy.com | CONTRACTOR, MASTEC, STRUCK A 6" PE MAIN ON THE SECTION OF THE MAIN THAT RUNS EAST AND WEST, NORTH OF THE SIDEWALK ON INDIAN CREEK RD. THE MAIN WAS MARKED ACCURATELY AND MARKS WERE VISIBLE. CONTRACTOR WAS ATTEMPTING TO INSTALL A LIGHT BASE. NOTE: DUE TO COMPLEXITY OF THE EVENT, THE LOST GAS HAS NOT YET BEEN CALCULATED. (IT IS NOT ESTIMATED TO EXCEED ANY PHMSA REPORTING THRESHOLD.) ONCE COMPLETE A SUPPLEMENTAL REPORT WILL BE SUBMITTED. 12/03/2019 - SUPPLEMENTAL CREATED - ADDED LINE PUNCTURE INFORMATION AND LOST GAS TOTALS. WILL CLOSE THE REPORT WHEN PAVEMENT RESTORATION IS COMPLETE. 09/23/2020 - ADDED AMOUNT OF GAS LOST AND UPDATED COST INFORMATION. ALSO ADDED NEWLY REQUIRED FIELDS. 12/04/2019- ADDITIONAL QUESTIONS RESPONSE TO THE ONE CALL: PGS SENT A MARKED RESPONSE TO LOCATE TICKED 274903389. THE RESPONSE WAS SENT WITHIN THE REQUIRED TIMEFRAME. THE TRACER WIRE WAS AFFIXED TO THE TOP OF THE PIPELINE. EXCAVATOR CLEARANCE: MASTEC INDICATED THEY DISCOVERED A GREY PIPE WHILE SPOTTING THE GAS FACILITY AND ASSUMED IT WAS THE GAS MAIN. THEY MOVED TO A DIFFERENT LOCATION AND STRUCK THE ACTIVE LINE. SERVICES INTERRUPTED: THERE WERE NO CUSTOMERS ON THE ISOLATED SECTION OF MAIN. SQUEEZING OF THE LINE: THE LINE WAS SQUEEZED OFF AT 12:00 PM BY APPLYING TWO 6" MUSTANG SQUEEZE OFFS. THE DAMAGED SECTION WAS REPLACED WITH A 5' PIECE OF PRETESTED 6" PE PIPE.
2025-03-31 10:13 | NO | NO | NO | 20190132 | 33035 | 2019-11-15 14:28 | SUPPLEMENTAL FINAL | 1209 | COLUMBIA GAS OF MASSACHUSETTS | 4 TECHNOLOGY DRIVE | WESTBOROUGH | MA | 01581 | 2019-10-17 06:55 |  |  | 2019 | JACKSON ST | NORTHAMPTON | HAMPSHIRE | MA | 01060 | 42.3321 | -72.645 | [9 empty] | 2019-10-17 08:38 | 1261340 |  | NATURAL GAS |  | 11.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 8 | 2019-10-17 06:55 |  |  |  | 2019-10-17 07:22 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | OTHER | BRIDGE CROSSING |  |  | YES | YES | UNCASED | [9 empty] | PRIVATELY OWNED |  | MAIN |  | 1977 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 8200 | 9276.7013610888696 | 200 | 226.2610088070456 | 72000 | 81453.963170536416 | MAIN REPLACEMENT REQUIRED FOR SYSTEM INTEGRITY. |  | 28 | 31.38057742782152230971128608923884514436 |  | 0 | 80428 | 37700.6595092347069154855643044619422572 | 90988.3061178601527223097112860892388451 | 0 | 0 | 0 |  |  |  |  | 53 | 53 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | KATHERINE SILVER | COMPLIANCE MANAGER | ksilver@nisource.com | 508-864-1836 |  |  |  |  | KATHERINE SILVER | COMPLIANCE MANAGER | 508-864-1836 | ksilver@nisource.com | DURING A WIND STORM, OVERHEAD ELECTRICAL WIRES FELL AND ARCED THE 6" STEEL MAIN AT A BRIDGE CROSSING ON JACKSON STREET, RESULTING IN A FIRE. FIRE DEPARTMENT ARRIVED AND EVACUATED 8 CUSTOMERS FROM 2 HOMES ADJACENT TO THE BRIDGE. THE 6" STEEL MAIN GOING OVER THE BRIDGE WAS ABANDONED. ENGINEERING HAS EVALUATED THE LOCATION AND DETERMINED THAT A MAIN REPLACEMENT IS NECESSARY FOR SYSTEM INTEGRITY.
2025-03-31 10:13 | NO | YES | YES | 20190133 | 32973 | 2019-11-22 09:39 | ORIGINAL FINAL | 13820 | NORTHWEST ALABAMA GAS DISTRICT | 310 2ND ST SW | HAMILTON | AL | 35570 | 2019-10-26 15:00 |  |  | 2019 | INTERSECTION OF CO HWY 49 & TAYLOR SPRINGS RD | BEAVERTON | LAMAR | AL | 35544 | 33.908 | -88.0092 | [9 empty] | 2019-10-26 17:49 | 1262271 |  | NATURAL GAS |  | 1454 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO |  |  |  |  | NO | 0 | 2019-10-26 15:23 |  |  |  | 2019-10-26 16:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1977 | [5 empty] | 10 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | OTHER | [8 empty] | VEHICLE LOST CONTROL AND HIT 10" ABOVE-GROUND VALVE SETTING, BREAKING A 2" BLOW-DOWN COMPONENT OFF OF THE 10" PIPE FORCING A SHUT-DOWN OF THAT SECTION OF 10" MAIN. | CLASS 1 LOCATION | 15000 | 16969.57566052842 | 95140 | 107632.36188951159192 | 3657 | 4137.182546036828796 | 0 | 0 |  |  | 7270 | 8147.742782152230971128608923884514435696 |  | 0 | 121067 | 60857.0215913763701254304461942257217848 | 136886.8628782290716871286089238845144357 | 0 | 0 | 18 |  |  |  |  | 285 | 285 | 320 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JERRY DAVIS | OPERATIONS MANAGER | jerry.davis@nwagd.com | 2053951407 | 2059214752 |  |  |  | JERRY DAVIS | OPERATIONS MANAGER | 2053951407 | jerry.davis@nwagd.com | A PUBLIC OPERATED VEHICLE LOST CONTROL, RAN OFF THE ROAD, AND COLLIDED WITH AN ABOVE-GROUND 10" VALVE SETTING. THE VEHICLE BROKE A 2" BLOW-DOWN FROM ONE SIDE OF THE 10" VALVE SETTING FORCING A SHUT-DOWN OF THAT SECTION OF MAIN BETWEEN THIS 10" VALVE AND THE NEXT 10" MAIN-LINE VALVE FOR A DISTANCE OF 4.35 MILES. ONLY 18 CUSTOMERS WERE AFFECTED FOR A PERIOD OF TWO HOURS IN THIS RURAL AREA DURING WHICH TIME REPAIRS WERE BEING MADE.
2025-03-31 10:13 | NO | NO | NO | 20190134 | 32980 | 2019-11-22 19:14 | SUPPLEMENTAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2019-10-22 09:00 |  |  | 2019 | 710 N STRATFORD ROAD | MOSES LAKE | GRANT | WA | 98837-1569 | 47.1389 | -119.2785 | [9 empty] | 2019-11-08 12:11 | 1263446 |  | NATURAL GAS |  | 79 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 8 | 2019-10-22 09:00 |  |  |  | 2019-10-22 08:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 42 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.75 | [6 empty] | OTHER | [8 empty] | SERVICE TEE WAS PULLED OFF 6" MAIN LEAVING A 3/8" HOLE. THE SERVICE TEE WAS INSTALLED IN 1961. | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 30000 | 33939.15132105684 | 35279 | 39911.310648518808612 | SURFACE RESTORATION, TRAFFIC CONTROL, LIGHT TOWERS, BYPASS EQUIPMENT. |  | 356 | 398.981627296587926509186351706036745407 |  | 0 | 65635 | 30955.7278375631572084593175853018372703 | 74249.4435968722365385091863517060367454 | 3 | 0 | 0 |  |  |  |  | 40 | 40 | 47 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | UNKNOWN/OTHER | YES |  |  |  | UTILITY OWNER | NO | YES | 18 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO UNLOCATABLE FACILITY | [170 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.com | 208-377-6032 |  |  |  |  | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 208-377-6032 | greg.watkins@mdu.com | ORIGINAL NRC# 1263446 48-HOUR FOLLOW-UP NRC# 1263581 ON 10/17/19 AT 710 NORTH STRATFORD ROAD, MOSES LAKE, WA, A THIRD-PARTY CONTRACTOR USED A MINI EXCAVATOR ALONGSIDE A CNGC FIELD EMPLOYEE WITH A SHOVEL IN AN ATTEMPT TO LOCATE A LONG STUB SERVICE LINE THAT WAS UNLOCATABLE. THEY DUG 5.5 FEET DEEP, BUT WERE UNABLE TO LOCATE THE STUB. ON 10/18/19, TWO CNGC FIELD EMPLOYEES ATTEMPTED TO LOCATE THIS STUB SERVICE LINE WITH NO SUCCESS; THEY CONTACTED A CNGC CORROSION CONTROL TECHNICIAN FOR ASSISTANCE. ON 10/21/19, THE CORROSION CONTROL TECHNICIAN ATTEMPTED TO LOCATE THE STUB SERVICE LINE, AGAIN, WITH NO SUCCESS. MARKINGS PROVIDED BY CNGC WERE BASED ON MEASUREMENTS FROM FIELD DRAWINGS. ON 10/22/19, TWO CNGC FIELD EMPLOYEES WERE ON-SITE (SEE FIRST OPERATOR ARRIVAL) AT 8:30AM WORKING WITH THE THIRD-PARTY CONTRACTOR. AT 9:00AM, THE CONTRACTOR WAS DIGGING VERY SLOWLY WHEN HE STRUCK THE UNLOCATABLE STUB SERVICE LINE AND PULLED THE 3/4" AUTO PERF TEE AWAY FROM THE 6" STEEL MAIN CREATING A 3/8" HOLE. ONCE THE BLOWING GAS WAS UNDER CONTROL AND ON BYPASS, CNGC CREW DUG UP TO PERMANENTLY REPAIR THE DAMAGE. SYSTEM PRESSURE WAS 40PSIG AT THE TIME OF THE INCIDENT AND WAS LOWERED TO 27PSIG AT 2:50PM IN ORDER TO MITIGATE GAS LOSS. ALL AFFECTED SERVICE LINES WERE SHUT OFF AFTER NORMAL BUSINESS HOURS. CNG BECAME AWARE THE REPAIR COSTS WERE NEARING $50,000 ON NOVEMBER 8, 2019 AT WHICH TIME CNG CONTACTED THE NATIONAL RESPONSE CENTER.
2025-03-31 10:13 | NO | YES | NO | 20190135 | 32994 | 2019-11-27 07:06 | ORIGINAL FINAL | 13062 | NATIONAL FUEL GAS DISTRIBUTION CORP - NEW YORK | 6363 MAIN ST. | WILLIAMSVILLE | NY | 14221 | 2019-10-31 06:27 |  |  | 2019 | 7 MAPLE AVE | BLOOMFIELD | ONTARIO | NY | 14469-9312 | 42.9016 | -77.4197 | [9 empty] | 2019-10-31 06:27 | 1262706 |  | NATURAL GAS |  | 46 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2019-10-30 23:33 |  |  |  | 2019-10-30 23:56 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1982 | [8 empty] | OTHER | OUTSIDE METER/REGULATOR SET | [9 empty] | LEAK |  |  | OTHER | DAMAGE TO METER/REGULATOR SET | [5 empty] | CLASS 3 LOCATION | 135000 | 152726.18094475578 | 210 | 237.57405924739788 | 683 | 772.681345076060724 | 0 | 0 |  |  | 276 | 309.322834645669291338582677165354330709 |  | 0 | 136169 | 63959.1629047770531279291338582677165354 | 154045.7591837249078953385826771653543307 | 0 | 0 | 1 |  |  |  |  | 52 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | STEVEN M MONNIE | ENGINEER II | monnies@natfuel.com | 814-871-8204 |  |  |  |  | WILLIAM F SNYDER III | SUPERINTENDENT | 716-827-2327 | snyderw@natfuel.com | AT APPROXIMATELY 11:30 PM ON WEDNESDAY, OCTOBER 30, 2019, A TRUCK LEFT THE ROADWAY, SHEARED OFF A FIRE HYDRANT AND TELEPHONE POLE AND ROLLED SEVERAL TIMES PRIOR TO IMPACTING A SINGLE FAMILY RESIDENCE RESULTING IN A RELEASE OF NATURAL GAS FROM THE OUTDOOR METER. THE ACCIDENT RESULTED IN A STRUCTURE FIRE. THERE WERE NO FATALITIES, BUT THE DRIVER OF THE VEHICLE WAS TRANSPORTED VIA HELICOPTER TO STRONG MEMORIAL HOSPITAL IN ROCHESTER, NY, TREATED FOR MINOR INJURIES AND RELEASED THE SAME DAY. THE CURB VALVE TO THE RESIDENCE WAS CLOSED AT APPROXIMATELY 12:29 AM AND SUBSEQUENTLY THE SERVICE LINE WAS PERMANENTLY DISCONNECTED FROM THE RESIDENCE.
2025-03-31 10:13 | NO | YES | NO | 20190136 | 33030 | 2019-11-27 10:42 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2019-10-27 08:14 |  |  | 2019 | 2421 EAGLE DRIVE | AUGUSTA | RICHMOND | GA | 30906 | 33.4144 | -82.04 | [9 empty] | 2019-10-28 20:03 | 1262457 |  |  |  | 150 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-10-27 08:14 |  |  |  | 2019-10-27 09:15 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1966 | [5 empty] | 0.5 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | GAS PIPE FUSED TO WATER PIPE | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 139909 | 158279.757405924714252 | 25038 | 28325.615692554038664 | 0 | 0 |  |  | 900 | 1008.661417322834645669291338582677165354 |  | 0 | 165847 | 78219.4198564451324024645669291338582677 | 187614.0345158015875616692913385826771654 | 1 | 0 | 88 |  |  |  |  | 40 | 40 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | THE COMPANY INITIALLY RECEIVED A NATURAL GAS OUTAGE CALL AT 2421 EAGLE DRIVE, AUGUSTA GA WHERE UPON AN INVESTIGATION IT WAS DETERMINED THAT WATER WAS ENTERING THE NATURAL GAS SYSTEM. UPON INVESTIGATING FURTHER, IT APPEARS AN ELECTRICAL CHARGE ENTERED ONTO THE STEEL GAS PIPING AND STEEL WATER PIPING AS A RESULT OF A VEHICLE RUNNING INTO A UTILITY POLE AT 2401 EAGLE DRIVE. THE CURRENT APPEARS TO HAVE ENTERED ONTO THE GAS PIPING FROM THE HOUSE ACROSS THE STREET (3001 EAGLE DRIVE) FROM THE UTILITY POLE ACCIDENT AS THE UNION AT THE METER SET HAD A HOLE BURNED INTO IT. ADDITIONAL INVESTIGATION REVEALED THAT ELECTRICIANS AND PLUMBERS WERE ADDRESSING AN ELECTRICAL OUTAGE AND WATER PIPE LEAKS UNDER THE SAME ADDRESS AS IT APPEARS A LARGE AMOUNT OF CURRENT MAY HAVE TRAVELED THROUGH THE STRUCTURE. FOUR HOUSES DOWN FROM THE UTILITY POLE ACCIDENT (3010 EAGLE DRIVE) THE STEEL NATURAL GAS SERVICE PIPE WAS IN DIRECT CONTACT WITH THE STEEL WATER SERVICE PIPE TO SAME PROPERTY. THE ELECTRICAL CHARGE CAUSED THE TWO (2) PIPES TO FUSE TOGETHER CAUSING A LEAK IN BOTH RESULTING IN 60 PSIG WATER ENTERING THE 40 PSIG GAS SYSTEM AT THAT POINT. APPROXIMATELY 7,000 FEET OF NATURAL GAS MAIN WAS ISOLATED WITH ASSOCIATED SERVICES IN ORDER FOR THE WATER BE EXTRACTED FROM THE NATURAL GAS SYSTEM. APPROXIMATELY 139 NATURAL GAS METER SETS WERE AFFECTED DUE TO WATER ENTERING THE NATURAL GAS PIPING SYSTEM. DUE TO THE LENGTH OF TIME PERFORMING THE INVESTIGATION AND REPAIRS IT WAS DETERMINED THAT COSTS WOULD EXCEED THE $50,000 THRESHOLD FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. ADDITIONAL NRC REPORT NUMBER 1262686 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2025-03-31 10:13 | NO | YES | NO | 20190137 | 33001 | 2019-11-30 11:27 | ORIGINAL FINAL | 4350 | ELIZABETHTOWN GAS CO | 520 GREEN LANE | UNION | NJ | 07083 | 2019-10-30 09:40 |  |  | 2019 | 107 KING GEORGE ROAD | PENNINGTON | MERCER | NJ | 08534 | 40.3323 | -74.7888 | [9 empty] | 2019-10-30 12:34 | 1262632 |  | NATURAL GAS |  | 8.14 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 1 | 2019-10-30 09:53 |  |  |  | 2019-10-30 09:53 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | 1977 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | EXCAVATION DAMAGE TO THE EXTERIOR SERVICE LINE CAUSED THE INTERIOR PIPING TO PULL OUT AND BREAK CAUSING THE LEAKING GAS. | CLASS 3 LOCATION | 1000000 | 1131305.044035228 | 0 | 0 | 3780 | 4276.33306645316184 | 0 | 0 |  |  | 40 | 44.82939632545931758530183727034120734908 |  | 0 | 1003820 | 470365.2185930724649392650918635170603675 | 1135626.20649800662115758530183727034121 | 0 | 0 | 1 |  |  |  |  | 53 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | LANDSCAPING | YES | 192912670 |  |  | UTILITY OWNER | YES |  |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | MARC STUBEL | MANAGER OF SYSTEM INTEGRITY | mstubel@sjindustries.com | 9086628306 |  |  |  |  | MARC STUBEL |  | 9086628306 | mstubel@sjindustries.com | WHILE USING MECHANIZED EXCAVATION EQUIPMENT, LANDSCAPER PULLED ON THE SERVICE LINE TO HOUSE 107 KING GEORGE ROAD, PENNINGTON NJ, CAUSING THE INTERIOR PIPING TO BE PULLED. THE INTERIOR PIPING BROKE AT AN ELBOW CAUSING THE RELEASE OF GAS INTO THE BASEMENT, WHICH IGNITED CAUSING THE HOUSE TO BE DESTROYED BY EXPLOSION AND SUBSEQUENT FIRE.
2025-03-31 10:13 | NO | YES | NO | 20190139 | 33461 | 2019-12-11 17:23 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2019-11-11 11:06 |  |  | 2019 | 34368 RD 196 | WOODLAKE | TULARE | CA | 93286 | 36.4128 | -119.1335 | [9 empty] | 2019-11-11 21:27 | 1263704 |  | NATURAL GAS |  | 1534 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-11-11 11:06 |  |  |  | 2019-11-11 11:41 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1953 | [5 empty] | 1 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 175089 | 198079.068855084035292 | 200 | 226.2610088070456 | 0 | 0 |  |  | 9204 | 10315.244094488188976377952755905511811 |  | 0 | 184493 | 91674.3249094464164718976377952755905512 | 208620.573958379269868377952755905511811 | 0 | 0 | 0 |  |  |  |  | 170 | 170 | 175 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | GRADING | YES | 928800740 | NA |  | UTILITY OWNER | NO |  |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | BRYON WALSH | PIPELINE SAFETY AND COMPLIANCE ADVISOR | bwalsh@sdge.com | 619-992-1473 |  |  |  |  | BRYON WALSH | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 619-992-1473 | bwalsh@sdge.com | ON 11-11-19 AT APPROXIMATELY 11:06 AM, SOCALGAS WAS NOTIFIED OF A THIRD-PARTY DAMAGE AT 34368 ROAD 196, WOODLAKE. A THIRD-PARTY CONTRACTOR WAS GRADING AND PULLED ON A 1-INCH STEEL GAS SERVICE. THIS CAUSED A BREAK IN THE SERVICE AND A RELEASE OF GAS. SOCALGAS CREWS RESPONDED AND WERE ABLE TO CONTROL THE GAS BY WELDING ON A BYPASS AND PRESSURE CONTROL FITTINGS. NO INJURIES NOR FURTHER DAMAGE WERE REPORTED DUE TO THE RELEASE OF GAS. INVESTIGATION SHOWED THAT THE THIRD-PARTY CONTRACTOR HAD A VALID USA TICKET FOR THE WORK AREA AND THE LOCATOR FAILED TO MARK THE GAS LINE AS REQUIRED. THIS INCIDENT WAS REPORTED TO PHMSA AND THE CPUC DUE TO THE RELEASE OF GAS AND DAMAGES POTENTIALLY EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, CONTACT BRYON WALSH AT 619-992-1473. 03-13-20- UPDATED COSTS OF REPAIRS AND CLOSE OUT AS FINAL REPORT.
2025-03-31 10:13 | NO | YES | NO | 20190140 | 33374 | 2019-12-13 16:53 | SUPPLEMENTAL FINAL | 12350 | CENTERPOINT ENERGY RESOURCES CORP., DBA CENTERPOINT ENERGY MINNESOTA GAS | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2019-11-19 13:23 |  |  | 2019 | MINNIE ST & WASHBURNE AVE | PAYNESVILLE | STERNS | MN | 56362 | 45.3835 | -94.7133 | [9 empty] | 2019-11-19 18:43 | 1264370 |  | NATURAL GAS |  | 1455 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 40 | 2019-11-19 13:23 |  |  |  | 2019-11-19 13:25 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1970 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 198735 | 224829.90792634103658 | 915 | 1035.14411529223362 | 0 | 0 |  |  | 5823 | 6526.039370078740157480314960629921259843 |  | 0 | 205473 | 99583.4990617166209240157480314960629921 | 232391.0914117120103574803149606299212598 | 130 | 0 | 1277 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | 193110937 |  |  | UTILITY OWNER | YES | YES | 13 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | AARON ABRAHAMSON | OPERATION SPECIALIST II | aaron.abrahamson@centerpointenergy.com | 612-321-5514 |  |  |  |  | DEAN HEADLEE | PIPELINE SAFETY AND COMPLIANCE MANAGER | 612-321-5366 | dean.headlee@centerpointenergy.com | ON NOVEMBER 19, 2019 AT 13:23, A THIRD-PARTY CONTRACTOR INSTALLING SEWER AND WATER DAMAGED CENTERPOINT ENERGY'S 6" STEEL DISTRIBUTION MAIN WITH THEIR EXCAVATION EQUIPMENT. THE LINE HIT WAS ONE-WAY FEEDING THE ENTIRE TOWN OF PAYNESVILLE. DUE TO THE PROXIMITY OF RAILROAD TRACKS AND THE LOCATION OF THE DAMAGE, A BY-PASS WAS NOT A FEASIBLE OPTION AND THE ENTIRE SYSTEM WAS SHUT OFF AT THE TOWN-BORDER-STATION (TBS) IN PAYNESVILLE. SHUTTING DOWN THE SYSTEM FROM THE TBS STATION RESULTED IN THE LOSS OF GAS TO 1400 CUSTOMERS FOR APPROXIMATELY 13 HOURS AND 22 MINUTES. AFTER AN INVESTIGATION, IT WAS DETERMINED THE STEEL MAIN WAS MARKED CORRECTLY AND THE CONTRACTOR FAILED TO SPOT THE FACILITY BEFORE EXCAVATION CAUSING DAMAGE. GAS SERVICE WAS RESTORED AT ROUGHLY 02:45 ON NOVEMBER 20, 2019. 48 HOUR NRC 1264370
2025-03-31 10:13 | NO | YES | NO | 20190142 | 34601 | 2019-12-14 11:38 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2019-11-15 01:01 |  |  | 2019 | 28000 SHAKER BLVD | PEPPER PIKE | CUYAHOGA | OH | 44124 | 41.4794 | -81.4832 | [9 empty] | 2019-11-15 02:56 | 1263988 |  | NATURAL GAS |  | 13179 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 40 | 2019-11-15 01:01 |  |  |  | 2019-11-15 01:28 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 208 |  | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2019 | [5 empty] | 30 | API 5L | DURA-BOND | STEEL |  | OTHER | SAWL | 0.375 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 2902577 | 3283700.000800639982556 | 5032767 | 5693594.692554042315876 | 141295 | 159847.74619695754026 | 839928 | 950214.783026420983584 | CITY OF PEPPER PIKE IMPROVEMENT COSTS |  | 30838 | 34561.2230971128608923884514435695538058 |  | 0 | 8947405 | 4209851.98298481555147842257217847769029 | 10121918.44567517368316838845144356955381 | 0 | 0 | 0 |  |  |  |  | 193 | 193 | 249 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS LEAK IGNITED, BUT DID NOT CREATE ANY CONTROL ROOM AOC EVENTS THAT WARRANTED ACTIONS. THE VALVES USED TO ISOLATE THE LEAK WERE MANUAL VALVES. THE ACTIONS TAKEN BY THE CONTROL ROOM WAS AT THE DIRECTION OF GM&R TO ADJUST PRESSURES DURING THE EVENT THAT OPERATED BELOW MAOP. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BUTT WELD | MATERIAL/WELD/EQUIP FAILURE | BUTT WELD | MATERIAL FAILURE OF PIPE OR WELD | BUTT WELD | [146 empty] | BUTT WELD |  |  | PIPE | [26 empty] | YES | [10 empty] | YES |  |  |  | PROCEDURE NOT FOLLOWED |  |  | NO | [86 empty] | JEFFERY BURDETTE | SUPERVISOR PIPELINE COMPLIANCE | jeffery.l.burdette@dominionenergy.com | 3307545524 |  |  |  |  | REID HESS | MANAGER GAS OPERATIONS OHIO PIPELINE SAFETY | 8012459652 | reid.hess@dominionenergy.com | ON 11-15-19 DOMINION WAS NOTIFIED BY THE LOCAL FIRE DEPARTMENT AT 1:01 AM OF A FIRE ON OR NEAR THE OPERATORS PIPELINE. DEO CONFIRMED THAT THE FIRE WAS OCCURRING ON ITS FACILITIES AT APPROXIMATELY 1:45 AM BASED ON COMMUNICATIONS WITH FIELD OPERATIONS AND GAS CONTROL. THE LINE WAS ISOLATED AND FIRE EXTINGUISHED AT 3:30AM. THERE WERE NO INJURIES, FATALITIES, OR STRUCTURE DAMAGES. THE 30 INCH STEEL MAIN HAD BEEN RECENTLY INSTALLED, AND THE LOCATION OF THE RELEASE WAS AT A ROAD CROSSING AUGURED UNDER THE ROAD INSTALLED AT APPROXIMATELY 14.5FT. DEEP ON THE SOUTH END TO APPROXIMATELY 21FT. DEEP ON THE NORTH END. ON 11-24-19 THE FAILED SECTION WAS REMOVED AND CONFIRMED THAT THE RELEASE OF GAS HAD OCCURRED AT A GIRTH WELD FAILURE. IN COOPERATION WITH THE PUCO, THE FAILED SECTION OF THE PIPELINE (ALONG WITH ADDITIONAL SECTIONS IMMEDIATELY UPSTREAM AND DOWNSTREAM OF THE SECTION CONTAINING ADDITIONAL WELDS FOR TESTING) WERE EXTRACTED AND RETAINED BY DNV FOR METALLURGICAL ANALYSIS. THE PROTOCOLS FOR THE ANALYSIS WERE REVIEWED AND APPROVED BY DEO AND THE PUCO. DNV ISSUED ITS FINAL METALLURGICAL ANALYSIS REPORT ON 5-18-20, AND DEO HAS CONCLUDED ITS REVIEW OF THE INCIDENT. ANALYSIS OF THE INCIDENT INDICATES THAT THE FAILURE OCCURRED AS A RESULT OF AXIAL BENDING STRESSES ON THE PIPE STRING, LIKELY DUE TO THE PRESENCE OF A CAVERN OR VOID IN THE ROCK FORMATION THROUGH WHICH THE AUGER PASSED, WHICH CAUSED THE AUGER TO VEER OFF COURSE. THE BENDING STRESS CAUSED THE FIELD GIRTH WELD LOCATED AT THE EDGE OF THE CAVERN TO FAIL, PRIMARILY IN DUCTILE OVERLOAD. THIS ANALYSIS ALSO DETERMINED THAT A PRE-EXISTING HYDROGEN CRACK (FORMED PRIOR TO THE FINAL FAILURE) AND WELDING DEFICIENCIES CONTRIBUTED TO THE ELEVATED STRESS STATE ON THE GIRTH WELD.
2025-03-31 10:13 | NO | YES | NO | 20190143 | 33081 | 2019-12-16 15:00 | ORIGINAL FINAL | 18192 | SEVIER COUNTY UTIL DIST | 420 ROBERT HENDERSON RD | SEVIERVILLE | TN | 37862 | 2019-11-16 21:02 |  |  | 2019 | 604 WALNUT WAY | SEVIERVILLE | SEVIER | TN | 37862 | 35.8294 | -83.5934 | [9 empty] | 2019-11-16 23:00 | 1264126 |  | NATURAL GAS |  | 19.26 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2019-12-16 21:02 |  |  |  | 2019-12-16 21:25 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | 1993 | [8 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | OTHER | BROKE RISER FROM VEHICLE CRASH | [5 empty] | CLASS 3 LOCATION | 335000 | 378987.18975180138 | 250 | 282.826261008807 | 10000 | 11313.05044035228 | 0 | 0 | VALUE OF THE CABIN STRUCTURE & CONTENTS ~$275,000 & PICKUP TRUCK ~$60,000. |  | 149 | 166.989501312335958005249343832020997375 |  | 0 | 345399 | 161922.2670770037821502624671916010498688 | 390750.0559544748029580052493438320209974 | 0 | 0 | 88 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JAMES GREENE | VICE PRESIDENT OF ENGINEERING AND OPERATIONS | james.greene@scudgas.org | 865-453-3272 | 865-428-5055 |  |  |  | JAMES GREENE | VICE PRESIDENT OF ENGINEERING AND OPERATIONS | 865-453-3272 | james.greene@scudgas.org | ON SATURDAY, NOVEMBER 16, 2019 AT APPROXIMATELY 9:02 PM, SEVIER COUNTY UTILITY DISTRICT (SCUD) EMPLOYEES RECEIVED A PAGE FROM OUR ANSWERING SERVICE THAT A 'CAR RAN INTO CABIN AND HIT THE GAS LINES' AT 604 WALNUT WAY, SEVIERVILLE, TN. SCUD EMPLOYEES RECEIVED THE PAGE AND CONFIRMED THAT THEY WERE IMMEDIATELY RESPONDING. BOB TRENTHAM WAS THE FIRST SCUD EMPLOYEE ON THE SCENE AT APPROXIMATELY 9:25 PM. UPON ARRIVAL, THE SEVIERVILLE FIRE DEPARTMENT (SFD) AND SEVIERVILLE POLICE DEPARTMENT (SPD) ALONG WITH SURROUNDING FIRE DEPARTMENTS WERE ON THE SCENE AND PERFORMING FIRE SUPPRESSION OPERATIONS ON THE CABIN AND TRUCK THAT WERE BOTH ON FIRE. ADDITIONAL SCUD EMPLOYEES BEGAN ARRIVING SHORTLY AFTER BOB AND WE STARTED COORDINATION TO TURN THE GAS OFF. SPD SECURED THE SCENE AND WERE ONLY ALLOWING EMERGENCY PERSONNEL PAST A CHECKPOINT ~0.2 MILES FROM THE SCENE. SCUD GIS MAPS WERE REVIEWED TO ASSESS THE LOCATION OF THE GAS SERVICE LINE TO CABIN 4020, ALONG WITH THE GAS MAINS AND VALVES IMMEDIATELY UPSTREAM AND DOWNSTREAM OF THE METER. SCUD EMPLOYEES OPERATED COMBUSTIBLE GAS INDICATORS (CGI'S) TO MONITOR THE PRESENCE OF NATURAL GAS IN THE AIR AROUND THIS LOCATION. THE SUPPLY OF NATURAL GAS IS A 2'PE MAIN WITH A ONE-WAY SUPPLY OPERATING AT 45 PSIG. SCUD VALVE #71L 17 (LOCATED ~250' UPSTREAM OF THE CABIN) WAS OPERATED AT ~9:45 PM TO TURN THE GAS OFF. THE DOWNSTREAM SCUD VALVE #71L 6 (LOCATED ~1,550' DOWNSTREAM OF THE CABIN) WAS ALSO OPERATED TO LIMIT THE LOSS OF GAS AND IN HOPES OF MAINTAINING PRESSURE FOR THE 88 CUSTOMERS DOWNSTREAM OF VALVE #71L 17. THE 3/4' PE GAS SERVICE LINE TO 604 WALNUT WAY WAS EXPOSED BY HAND-DIGGING AND THE LINE WAS SQUEEZED OFF. THIS SERVICE LINE WAS INSTALLED ON 2-19-1993, SO THERE WAS NO EXCESS FLOW VALVE. THE 'LINEPACK' VOLUME OF GAS STORED IN THE PIPELINE DOWNSTREAM OF VALVE #71L 6 WAS CONSUMED BY THE DOWNSTREAM CUSTOMERS AND THE MAIN LINE WENT FLAT BEFORE THE GAS SERVICE ON THE MAIN COULD BE RESTORED. AT 11:20 PM, THE FIRE DEPARTMENTS REPORTED THAT THE FIRE IS CONTAINED. GAS SERVICE WAS RESTORED ON THE 2'PE MAIN AT APPROXIMATELY 11:30 PM. THE TEMPERATURE WAS 35F AND CUSTOMERS NEEDED HEAT FOR THE NIGHT. ADDITIONAL SCUD PERSONNEL WAS CALLED IN TO ASSIST WITH THE RESTORATION OF SERVICE AND LIGHT-UPS OF THE GAS APPLIANCES. NATURAL GAS SERVICE WAS RESTORED TO ALL OF THE 88 AFFECTED HOMES (EXCEPT TWO UNOCCUPIED CABINS) WHEN SCUD EMPLOYEES LEFT THE SCENE EARLY SUNDAY MORNING. JAMES GREENE CALLED TENNESSEE PUBLIC UTILITY COMMISSION'S (TPUC) GAS PIPELINE SAFETY DIVISION (GPSD) DEPUTY DIRECTOR TRAVIS ASLINGER TO NOTIFY HIM OF THE INCIDENT AT 10:47 PM ON SATURDAY, NOVEMBER 16. AFTER THAT CONVERSATION, JAMES CALLED THE NATIONAL RESPONSE CENTER (NRC) AT 10:55 PM TO FILE AN INITIAL REPORT FOR THE INCIDENT (REPORT #1264126). ON MONDAY, NOVEMBER 18, JAMES CALLED THE NRC PROVIDE A 48-HOUR UPDATE (REPORT #1264233). ACCORDING TO THE SPD INCIDENT REPORT, CASE NUMBER 2019037915, 'OFFICERS WERE DISPATCHED TO 604 WALNUT WAY REGARDING A CABIN FIRE THAT WAS STARTED BY A VEHICLE CRASH. UPON ARRIVAL, THE CABIN WAS ENGULFED IN FLAMES. A WHITE PICKUP TRUCK HAD ROLLED BACKWARDS DOWN THE HILL OFF OF THE ROAD AND SMASHED INTO THE SIDE OF THE HOUSE, BREAKING THE GAS LINE AND CAUSING AN EXPLOSION.' THERE WERE FOUR FEMALE OCCUPANTS IN THE CABIN THAT WERE ABLE TO EVACUATE THE CABIN. WHEN SPD ARRIVED, THE MAN ADMITTED HE WAS THE DRIVER OF THE TRUCK AND HE HAD BEEN HEAVILY DRINKING. HE WAS SUBSEQUENTLY PLACED UNDER ARREST FOR DUI AND IMPLIED CONSENT AND TRANSPORTED TO JAIL. SCUD HAD 18 EMPLOYEES ON THE SCENE AT SOME POINT SATURDAY AND SUNDAY. ON SUNDAY, SCUD EMPLOYEES WENT BACK TO THE SCENE TO ASSESS THE SITUATION DURING DAYLIGHT. THEY OBSERVED THE BURNT TRUCK WHERE IT CRASHED INTO THE HOUSE AND KNOCKED A HOLE IN THE CRAWLSPACE. THE TRUCK STRUCK THE GAS METER (WHICH WAS UNDER THE BACKSIDE OF THE TRUCK), BROKE THE TOP PART OF THE RISER OFF, AND BENT THE BOTTOM PART OF THE BROKEN RISER INTO THE CRAWLSPACE OF THE CABIN.
2025-03-31 10:13 | NO | YES | YES | 20190145 | 35237 | 2019-12-17 17:38 | SUPPLEMENTAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2019-11-18 00:39 | MOUNTAIN | NO | 2019 | 814 S 28TH STREET | BILLINGS | YELLOWSTONE | MT | 59101 | 45.7728 | -108.4972 | [5 empty] | YES |  |  |  | 2019-11-18 02:12 | 1264173 | 1264344 | NATURAL GAS |  | 299.38 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 2019-11-18 00:39 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 4 | 2019-11-18 00:39 |  |  |  | 2019-11-18 01:13 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 32 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1982 | [5 empty] | 1.25 | UNKNOWN | DUPONT ALDYAL-A | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 10 |  |  | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 100000 | 113130.5044035228 | 15000 | 16969.57566052842 | 2500 | 2828.26261008807 | 0 | 0 |  | 3.71 | 1111 | 1245.136482939632545931758530183727034121 | 0 | 0 | 118611 | 56206.756982138674796587926509186351706 | 134173.4791570789225459317585301837270341 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1982-06-24 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 20 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | EVIDENCE OF FOREIGN BACKFILL. | [154 empty] | DANNY L HOOD | MGR POLICY AND PROCEDURE | danny.hood@mdu.com | 7015162749 |  | DEBBIE BUCK | debbie.buck@mdu.com | 4068964210 | DANNY L. HOOD | MGR POLICY AND PROCEDURE | 7015162749 | danny.hood@mdu.com | AT 00:39 ON NOVEMBER 18, 2019, EMERGENCY RESPONDERS CONTACTED MONTANA-DAKOTA UTILITIES CALL CENTER TO REPORT A HOUSE FIRE WITH POSSIBLE EXPLOSION. A LOCAL SERVICE TECHNICIAN WAS DISPATCHED IMMEDIATELY UPON NOTIFICATION. UPON ARRIVAL THE SERVICE TECH MADE THE AREA SAFE AND STARTED TO ASSESS THE SCENE. IT WAS CONFIRMED THAT AN EXPLOSION HAD OCCURRED AT A PRIVATE RESIDENCE AND TWO OCCUPANTS WERE TAKEN TO THE HOSPITAL. VERBAL COMMUNICATION FROM THE BILLINGS FIRE DEPARTMENT INDICATED TWO OCCUPANTS WERE TAKEN TO THE BILLINGS HOSPITAL AND THEN FLOWN TO A HOSPITAL IN DENVER. A LEAK INVESTIGATION OUTSIDE THE RESIDENCE WAS COMPLETED, GAS WAS INDICATED AT THE RISER OF THE RESIDENCE WITH HIGHEST CONCENTRATION OF GAS AT THE INTERSECTION OF TWO 1982 VINTAGE 1 1/4" PLASTIC MAINS ACROSS THE ALLEY. THE MAINS FEEDING THE TEE WERE ISOLATED, SECURING THE LEAK AT 05:50 ON NOVEMBER 18, 2019. THE MAIN WAS EXCAVATED AND A CRACK WAS DISCOVERED AT THE INTERFACE OF THE PIPE AT A SOCKET TEE CONNECTING THE MAINS. FACTORS THAT CAUSED THE GAS TO BE CONTROLLED AT 5:50 WERE THE TIME REQUIRED TO COMPLETE A LEAK INVESTIGATION TO ENSURE THE SAFETY OF THE SURROUNDING STRUCTURES, PINPOINT THE SUSPECTED SOURCE OF THE GAS, GET EMERGENCY LOCATES COMPLETED, EXCAVATE THE LOCATION OF THE HIGHEST CONCENTRATION OF GAS TO ENSURE THE LOCATION OF LEAK, AND EXCAVATE TWO LOCATIONS FOR SHUT OFF OF THE GAS DUE TO THE AREA BEING SERVED FROM TWO LOCATIONS. UPON EXCAVATION, THE PIPE AT THE TEE LOCATION, HAD A DEFLECTION FROM THE MAIN LINE WHICH WOULD BE INCONSISTENT WITH THE STANDARD INSTALLATION OF THE PIPE. THIS DEFLECTION MAY HAVE BEEN CAUSED FROM IMPROPER SUPPORT DURING THIRD PARTY EXCAVATION OR IMPROPER BACKFILL METHODS POST THIRD PARTY EXCAVATION THAT OCCURRED SOMETIME AFTER MONTANA-DAKOTA'S INITIAL INSTALLATION OF THE PIPE. FURTHER INDICATION THAT OUTSIDE FORCES CAUSED THE CRACK INCLUDE BACKFILL MATERIAL SURROUNDING THE PIPE AND TEE THAT APPEARED TO BE FOREIGN FROM NATIVE MATERIALS THAT WOULD HAVE BEEN USED AT TIME OF INITIAL INSTALLATION. 4/8/2021 - THE PE PIPE MATERIAL WAS REVISED TO CORRECT FROM PE 2406 TO PE 2306. 4/19/2021 - THE NUMBERS FOR GAS RELEASED (PG. 1 ITEMS 7) AND GAS CONSUMED (PG. 2 ITEM 21C) ARE NOT KNOWN. PHMSA FORM F 7100.1 REQUIRES A NUMERICAL ENTRY EVEN THOUGH AN ESTIMATED VALUE IS UNABLE TO BE DETERMINED. 5/3/2021 - ADDED THE PIPE MANUFACTURER AND UPDATED NRC REPORT NUMBERS. VOLUME OF GAS UNINTENTIONALLY RELEASED CALCULATED USING AND ESTIMATED OPENING OF 0.05 SQUARE INCHES AND A PRESSURE OF 55 PSIG. FOR PURPOSES OF PROVIDING AND ILLUSTRATIVE CALCULATION OF GAS LOSS, AN ESTIMATED TIME OF 3 MONTHS WAS UTILIZED.
2025-03-31 10:13 | YES | NO | NO | 20190146 | 33748 | 2019-12-18 16:53 | SUPPLEMENTAL FINAL | 2128 | CASCADE NATURAL GAS CORP | 8113 W. GRANDRIDGE BLVD | KENNEWICK | WA | 99336 | 2019-11-25 06:50 |  |  | 2019 | 908 EAST FULTON ST. | MOUNT VERNON | SKAGIT | WA | 98273 | 48.4228 | -122.3292 | [9 empty] | 2019-11-25 08:25 | 1264834 |  | NATURAL GAS |  | 92 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 2 | 2019-11-25 06:37 |  |  |  | 2019-11-25 07:37 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1967 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | AN EXPLOSION OCCURRED INSIDE THE STRUCTURE WHICH FORCED PART OF THE STRUCTURE INTO THE METER SET ASSEMBLY RESULTING IN A BREAK AT THE THREADED CONNECTION OF THE VALVE AND SERVICE LINE RISER. | CLASS 3 LOCATION | 630000 | 712722.17774219364 | 15000 | 16969.57566052842 | 9500 | 10747.397918334666 | 0 | 0 |  |  | 414 | 463.984251968503937007874015748031496063 |  | 0 | 654914 | 307096.9023057467933503937007874015748032 | 740903.1355730252299370078740157480314961 | 0 | 0 | 2 |  |  |  |  | 58 | 58 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | GREG WATKINS | MANAGER OF POLICY AND PROCEDURE | greg.watkins@mdu.com | 208-377-6032 |  |  |  |  | GREG WATKINS | MANAGER OF POLICY AND PROCEDURE | 208-377-6032 | greg.watkins@mdu.com | UPDATED QUESTION 12E TO 1 PERSON. AFTER FURTHER INVESTIGATION, 1 PERSON WAS TRANSPORTED TO SKAGIT VALLEY HOSPITAL FOR INJURIES AND THE SECOND PERSON WAS TREATED AND RELEASED AT THE SCENE. 48-HOUR FOLLOW-UP NOTIFICATION MADE TO NRC ON 11/26/2019. (NRC# 1264973) ON 11/25/2019 AT 6:14AM, AN EXPLOSION OCCURRED INSIDE A HOME AT 908 EAST FULTON STREET, MOUNT VERNON, WA. THE EXPLOSION CAUSED CASCADE NATURAL GAS CORPORATION'S (CNGC) RISER TO BREAK BELOW THE METER STOP ON A TWO-METER MANIFOLD THAT WAS SERVING THE ADDRESS (DUPLEX), WHICH RESULTED IN THE UNINTENTIONAL IGNITION OF JURISDICTIONAL NATURAL GAS. THE DUPLEX AND MULTIPLE VEHICLES WERE DESTROYED DUE TO THE FIRE. CNGC FIRST RESPONDERS ASSISTED THE MOUNT VERNON FIRE DEPARTMENT BY SHUTTING OFF GAS TO THE BUILDING AT THE MAIN. THE BUREAU OF ALCOHOL, TOBACCO, FIREARMS, AND EXPLOSIVES IS CURRENTLY WORKING WITH THE FIRE DEPARTMENT TO DETERMINE THE CAUSE OF THE INCIDENT; DETAILS HAVE NOT YET BEEN RELEASED. FOLLOWING THE INCIDENT, ON 11/26/2019, CNGC PERFORMED SUCCESSFUL LEAK TESTS ON THE SERVICE LINE TO 908 EAST FULTON STREET AND ON THE ADJACENT MAIN. THE SERVICE LINE LEAK TEST HELD FOR ONE HOUR AND FIVE MINUTES, AND THE MAIN LEAK TEST HELD FOR ONE HOUR; BOTH AT 58PSIG. ADDITIONAL INFORMATION REGARDING PART A 12 E: THE FIRST INJURED PERSON WAS HOSPITALIZED WITH 6% BURNS TO THEIR BODY. THE SECOND PERSON HAD MINOR INJURIES AND DROVE THEIR SELF TO THE HOSPITAL. ADDITIONAL INFORMATION REGARDING PAR A 13: THE RELEASE OF GAS WAS CONTROLLED AT THE SERVICE LINE TO MAIN CONNECTION AT 8:30 A.M. AND THE SERVICE LINE WAS ABANDONED AT THAT 10:00 A.M.
2025-03-31 10:13 | NO | YES | NO | 20190147 | 33485 | 2019-12-20 08:35 | SUPPLEMENTAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2019-12-12 15:30 |  |  | 2019 | 506 GRAND AVE. | NORTH BERGEN | BERGEN | NJ | 07047 | 40.7589 | -74.0483 | [9 empty] | 2019-12-12 18:13 | 1266273 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2019-12-12 15:30 |  |  |  | 2019-12-12 15:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2019 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | OTHER | [8 empty] | EXCESSIVE PRESSURE | CLASS 4 LOCATION | 175000 | 197978.3827061649 | 0 | 0 | 1209 | 1367.747798238590652 | 0 | 0 |  |  | 0 | 0 |  | 0 | 176209 | 82563.188595320750493 | 199346.130504403490652 | 0 | 0 | 1 |  |  |  |  | 5 | 0.25 | 0.25 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 8 | 0 | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [222 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED |  |  |  |  | YES | SERVICE WAS MISSED TO A STRUCTURE | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ROGER GUNNELS | PRINCIPAL REGULATOR SPECIALIST | roger.gunnels@pseg.com | 973-365-5326 |  |  |  |  | CHRIS LAROSSA | MANAGER REGULATORY POLICY AND PROCEDURE. | 9738967617 | christopher.larossa@pseg.com | ON THURSDAY 12/12/19 AT 506 GRAND AVE. NORTH BERGEN, WHILE PERFORMING AN UP-RATE ON SECAUCUS AVE. AN ACCIDENTAL IGNITION OCCURRED CAUSING DAMAGE TO THE PROPERTY. THE EXCESS PRESSURE CAUSED PILOTS OR BURNERS FLAMES TO ESCAPE THEIR NORMAL BOUNDARIES AND IGNITE COMBUSTIBLES IN THE AREA. THE FIRE DEPARTMENT AND ADDITIONAL PSE&G ARRIVED ON SITE. AT THIS TIME GAS IS OFF, FIRE IS OUT AND THE AREA HAS BEEN MADE SAFE. 506 GRAND AVE IS SERVICED FROM SECAUCUS AVE. 506 GRAND AVE IS NOT VISIBLE FROM SECAUCUS AVE. IT IS LOCATED BEHIND OTHER STRUCTURES IN THE AREA. THE SERVICE TO 506 GRAND AVE. DID NOT HAVE A REGULATOR INSTALLED AS IT WAS A UTILIZATION PRESSURE SYSTEM. THE SERVICE RECORDS FOR SECAUCUS AVE.WERE SOMEWHAT AMBIGUOUS, THE INDICATION OF A SERVICE TO BE CHECKED PRIOR TO THE UP-RATE WAS MISSED. DUE TO THE BRIEFNESS OF THE GAS EXPANSION AND THE SPEEDY SHUT DOWN THE AMOUNT OF GAS RELEASED CANNOT BE DETERMINED.
2025-03-31 10:13 | NO | YES | YES | 20190148 | 34280 | 2019-12-20 14:28 | SUPPLEMENTAL FINAL | 32513 | AMEREN ILLINOIS COMPANY | 10 EXECUTIVE DR. | COLLINSVILLE | IL | 62234 | 2019-11-22 23:35 |  |  | 2019 | 2368 E LOCUST ST | DECATUR | MACON | IL | 62521 | 39.8568 | -88.9227 | [9 empty] | 2019-11-23 00:30 | 1264676 |  | NATURAL GAS |  | 0 |  | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2019-11-22 23:14 |  |  |  | 2019-11-22 23:35 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1963 | [8 empty] | OTHER | ABOVE GRADE METER SET PIPING | [9 empty] | OTHER | [8 empty] | A THIRD PARTY PASSENGER VEHICLE CRASHED THROUGH A GAS METER SET AT A RESIDENTIAL STRUCTURE, SHEARING THE GAS METER SET AND INTO THE ADJACENT RESIDENTIAL STRUCTURE. | CLASS 3 LOCATION | 34860 | 39437.29383506804808 | 2911 | 3293.228983186548708 | 186 | 210.422738190552408 | 0 | 0 |  |  | 21 | 23.53543307086614173228346456692913385827 |  | 0 | 37978 | 17806.6234460884649756141732283464566929 | 42964.4809895160153377322834645669291339 | 0 | 0 | 1 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO CONTROL ROOM VISIBILITY TO SINGLE RESIDENTIAL GAS SERVICE DAMAGE ON DISTRIBUTION SYSTEM | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JOHN BOZARTH | DIRECTOR PIPLINE SAFETY AND QUALITY MANAGEMENT | jbozarth@ameren.com | 217-625-6854 |  |  |  |  | JOHN BOZARTH | DIRECTOR PIPLINE SAFETY AND QUALITY MANAGEMENT | 217-625-6854 | jbozarth@ameren.com | UPDATE 9/16/2020 - REPORT REVISED TO SHOW RESTART TIME WHICH IS EQUAL TO THE SHUTDOWN TIME SINCE THE SERVICE TO THIS STRUCTURE WAS ABANDONED AT THIS TIME. A THIRD PARTY PASSENGER VEHICLE DROVE OFF OF A RESIDENTIAL ROAD AND CRASHED THROUGH A NATURAL GAS METER SET AND INTO THE SIDE OF A HOME, WITH THE VEHICLE COMING TO A STOP COMPLETELY INSIDE THE RESIDENTIAL STRUCTURE. THE GAS METER SET WAS INSTALLED IMMEDIATELY ADJACENT TO THE STRUCTURE. GAS BEGAN LEAKING AND IGNITED. A FIRE ENSUED WHICH RESULTED IN A FATALITY TO A RESIDENT OF THE IMPACTED HOME WHO WAS INSIDE AT THE TIME, DAMAGE TO THE STRUCTURE AND CONTENTS, AND DAMAGE TO THE PUBLIC VEHICLE. THE DRIVER OF THE VEHICLE HAD FLED THE SCENE AND WAS LATER IDENTIFIED AND CHARGED WITH DRIVING UNDER THE INFLUENCE OF ALCOHOL AT THE TIME OF THE ACCIDENT. THE DRIVER WAS INJURED IN THE ACCIDENT. DAMAGE TO AMEREN ILLINOIS NATURAL GAS FACILITIES WAS LIMITED TO THE ABOVE GROUND METER SET PIPING. THE GAS SERVICE FEEDING THE IMPACTED HOME WAS ISOLATED TO CONTROL THE GAS LEAK AND THE GAS SERVICE WAS SUBSEQUENTLY RETIRED DUE TO DAMAGE TO THE HOME, AND THEREFORE NOT RETURNED TO SERVICE.
2025-03-31 10:13 | NO | YES | NO | 20190149 | 34979 | 2019-12-20 14:37 | SUPPLEMENTAL FINAL | 621 | ARKANSAS OKLAHOMA GAS CORP | 10825 E. GEDDES AVE, SUITE 410 | CENTENNIAL | CO | 80112 | 2019-11-25 11:49 | CENTRAL | NO | 2019 | ARKANSAS RIVER | LAVACA | SEBASTIAN | AR | 72941 | 35.3556 | -94.2088 |  | YES | [7 empty] | 2019-12-03 17:18 | 1265416 |  | NATURAL GAS |  | 3836 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2019-11-25 11:49 | YES | OPERATOR | 2020-09-16 22:13 | 2019-11-25 11:49 |  | NO | PUBLIC PROPERTY | UNDERGROUND | OTHER | UNDERWATER | 144 | NO | YES | [6 empty] | YES | BORED/DRILLED | ARKANSAS RIVER | 27 | BELOW WATER, PIPE IN BORED/DRILLED CROSSING | INVESTOR OWNED |  | MAIN |  | 1969 | [5 empty] | 10 | GRADE B | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.307 | [6 empty] | OTHER | [8 empty] | PIPE IS CURRENTLY SUBMERGED IN RIVER CROSSING, RELEASE TYPE CURRENTLY UNKNOWN. | CLASS 1 LOCATION | 0 | 0 | 1924269 | 2176935.225780624148332 | 0 | 0 | 0 | 0 | COSTS ASSOCIATED WITH DAMAGE, REPAIRS, AND OTHER COSTS ARE CURRENTLY UNKNOWN. | 2.6336 | 10102 | 11321.664041994750656167979002624671916 | 0 | 0 | 1934371 | 912094.4833914380999213989501312335958005 | 2188256.88982261889898816797900262467192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 137 | 165 | 192.619(A)(3) | 1969-06-01 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CAUSE OR CONTRIBUTING FACTORS TO THE INCIDENT ARE CURRENTLY UNDETERMINED. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | INVESTIGATION COMPLETE. CAUSE OF INCIDENT UNKNOWN DUE TO BELOW WATER PIPE LOCATION AND IN-PLACE ABANDONMENT. | [45 empty] | TYLER DAVIS | REGULATORY AFFAIRS SUPERVISOR | tdavis@summitutilitiesinc.com | 207-781-1200 |  |  |  |  | STANWOOD GIVEN | DIRECTOR OF PIPELINE SAFETY | 207-660-5982 | sgiven@summitutilitiesinc.com | A LEAK ON A 10 INCH HPD LINE CROSSING THE ARKANSAS RIVER IN APPROXIMATELY 27 FEET OF WATER WAS IDENTIFIED BY A THIRD PARTY AND REPORTED TO AOG DISPATCH. FOLLOWING NOTIFICATION THE PRESSURE IN THE LINE WAS REDUCED, FOLLOWED BY ISOLATION OF THE CROSSING SEGMENT, WHICH SUCCESSFULLY STOPPED THE LEAK. DUE TO THE LOCATION OF THE LEAK IN THE BOTTOM OF THE RIVER, THE CAUSE OF THE LEAK IS UNDETERMINED AT THIS TIME. THE LINE WAS REPLACED WITH FINAL TIE IN OF THE NEW LINE COMPLETED ON 10/6/2020.
2025-03-31 10:13 | NO | YES | NO | 20190150 | 33823 | 2019-12-20 18:09 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2019-09-04 18:32 |  |  | 2019 | 45581 ECORSE ROAD | VAN BUREN TOWNSHIP | WAYNE | MI | 48111 | 42.248 | -83.4869 | [9 empty] | 2019-09-07 14:09 | 1257534 |  | NATURAL GAS |  | 4810 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-09-04 11:00 |  |  |  | 2019-09-04 11:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | FOUND A LEAKING PLUG IN FLANGE ON STOPPLE | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 150000 | 169695.7566052842 | 75000 | 84847.8783026421 | 0 | 0 |  |  | 13468 | 15094.0577427821522309711286089238845144 |  | 0 | 238468 | 119387.2266106849365485564304461942257218 | 269637.6926507084522309711286089238845144 | 0 | 0 | 0 |  |  |  |  | 289 | 289 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [8 empty] | YES | [74 empty] | FRENAE SMITH | MANAGER CODES AND STANDARDS | frenae.smith@dteenergy.com | 313-389-7762 |  |  |  |  | FRENAE SMITH | MANAGER CODES AND STANDARDS | 313-389-7762 | frenae.smith@dteenergy.com | DTE GAS EMPLOYEES IDENTIFIED A LEAK ON THE 36-INCH VAN BORN PIPELINE DURING ROUTINE MAINTENANCE WORK ON 9/4/2019. THE PRESSURE WAS INITIAL LOWERED TO 215 PSIG AND MONITORED CONTINUOUSLY UNTIL A BLOW DOWN PROCEDURE WAS EXECUTED. IT WAS DETERMINED AFTER EXCAVATING THAT LEAK WAS ON PLUG IN FLANGE ON STOPPLE. IT APPEARED THAT THE COMPLETION PLUG INSIDE IS LEAKING AND POSSIBLY UNSEATED. THE REPAIR WAS MADE AND THE PIPE WAS RETURN TO SERVICE ON 9/16/19.
2025-03-31 10:13 | NO | YES | NO | 20190151 | 34421 | 2019-12-30 16:01 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2019-11-30 17:48 |  |  | 2019 | 20912 LE FEVER | WARREN | MACOMB | MI | 48091 | 42.45 | -83.0585 | [9 empty] | 2019-11-30 22:09 | 1265212 |  | NATURAL GAS |  | 0.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 0 | 2019-11-30 17:48 |  |  |  | 2019-11-30 18:12 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1959 | [5 empty] | 2 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 158454 | 179259.809447558017512 | 26883 | 30412.873498799034324 | 278 | 314.502802241793384 | 0 | 0 |  |  | 0 | 0 |  | 0 | 185615 | 86970.394537852556355 | 209987.18574859884522 | 0 | 0 | 1 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 4192905737 |  |  |  |  | JASON PIONK | GAS COMPLIANCE LEAD | 989-791-5749 | jason.pionk@cmsenergy.com | ON NOVEMBER 30, 2019 AT APPROXIMATELY 17:48 HOURS CONSUMERS ENERGY (CE) WAS NOTIFIED OF A HOME EXPLOSION AT 20912 LE FEVER AVENUE, WARREN, MICHIGAN (MACOMB COUNTY). A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 18:12 HOURS. THE GSW SHUT-OFF THE GAS AT THE CURB VALVE AT APPROXIMATELY 19:00 HOURS. AN INVESTIGATION WAS PERFORMED BY CE SERVICE DEPARTMENT PERSONNEL AT THE INCIDENT LOCATION AND THE SURROUNDING AREA AND NO GAS READS WERE DISCOVERED. CE DISTRIBUTION EMPLOYEES ARRIVED ONSITE AT APPROXIMATELY 20:15 HOURS TO CUT AND CAP THE SERVICE LINE. AN ON-SCENE INVESTIGATION WITH THE MICHIGAN PUBLIC SERVICE COMMISSION (MPSC) WAS SCHEDULED FOR DECEMBER 2, 2019. ON DECEMBER 2, 2019 DURING AN INCIDENT INVESTIGATION WITH THE MPSC, GAS READS WERE DISCOVERED ALONG THE 2" STEEL MEDIUM PRESSURE MAIN. FURTHER INVESTIGATION DETERMINED A PINHOLE CORROSION LEAK LOCATED ON THE MAIN. A MALLEABLE IRON CLAMP WAS INSTALLED AS A TEMPORARY REPAIR. THERE IS NO EVIDENCE THE LEAK DISCOVERED DURING ON DECEMBER 2, 2019 INVESTIGATION WAS THE SOURCE OR CONTRIBUTED TO THE HOME EXPLOSION THAT OCCURRED. ON DECEMBER 16, 2019 A JOINT SCENE INVESTIGATION WAS PERFORMED, THE LOCATION WAS CAREFULLY EXCAVATED AND EVIDENCE (GAS APPLIANCES AND ASSOCIATED PIPING) WAS REMOVED, EXAMINED AND TRANSPORTED TO NEDERVELD, INC. LABORATORIES FOR FURTHER INVESTIGATION. FOLLOWING A SERIES OF INVESTIGATION ACTIVITIES THAT INCLUDED EVIDENCE EVALUATION AND LABORATORY ANALYSIS, SOIL SAMPLING AND TESTING OF EXEMPLARS TO DETERMINE THE POSITIONING OF THE UNCAPPED GAS VALVE DISCOVERED AT THE SITE. CONSUMERS ENERGY FOUND NO CONCLUSIVE EVIDENCE THE EXPLOSION AND FIRE AT 20912 LEFEVER WAS THE RESULT OF A RELEASE AND/OR MIGRATION OF CONSUMERS ENERGY'S REGULATED GAS PIPELINE OR GAS FACILITIES. THE SOURCE OF THE NATURAL GAS COULD NOT BE DETERMINED BECAUSE SEVERAL POTENTIAL SOURCES WERE IDENTIFIED DURING THE INVESTIGATION, THE UNCAPPED NATURAL GAS VALVE, THE GAS DRYER AND THE CORROSION LEAK DISCOVERED ON THE PIPELINE SERVING THE RESIDENCE. HOWEVER, OF THE THREE POTENTIAL SOURCES IDENTIFIED, THE LEAST PLAUSIBLE SOURCE OF NATURAL GAS WAS THE CORROSION LEAK FOUND ON THE NATURAL GAS PIPELINE BECAUSE THERE WAS NO EVIDENCE FOUND DURING THE INVESTIGATION TO INDICATE THAT GAS MIGRATED FROM THE PIPELINE TO THE STRUCTURE.
2025-03-31 10:13 | NO | YES | YES | 20200001 | 33943 | 2020-01-02 11:51 | SUPPLEMENTAL FINAL | 15755 | PONTOTOC, CITY OF | 116 NORTH MAIN ST ; PO BOX 158 | PONTOTOC | MS | 38863 | 2019-09-09 10:00 |  |  | 2019 | 380 CLARK STREET | PONTOTOC | PONTOTOC | MS | 38863 | 34.2558 | -88.9763 | [9 empty] | 2019-09-10 09:10 | 1257779 |  | NATURAL GAS |  | 0 |  | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2019-09-09 10:00 |  |  |  | 2019-09-09 10:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 24 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 32300 | 36541.1529223378644 | HOSPITAL BILLS |  | 0 | 0 |  | 0 | 32300 | 15134.2496219197671 | 36541.1529223378644 | 0 | 0 | 0 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | INCORRECT OPERATION | INCORRECT EQUIPMENT | [222 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED |  |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | DAVID OWEN | OPERATOR | davidowen68@icloud.com | 6625092905 |  |  |  |  | DAVID OWEN | OPERATOR | 6625092905 | davidowen68@icloud.com | ON SEPTEMBER 9,2019 AT APPROXIMATELY 10 AM EMPLOYEES WERE REPAIRING A GAS LEAK BY ATTEMPTING TO INSTALL A BOLT ON LEAK CLAMP WITH A BATTERY POWERED IMPACT WRENCH WHEN GAS IGNITED. WHILE TIGHTENING THE BOLTS IGNITION OCCURRED BURNING TWO EMPLOYEES. BOTH EMPLOYEES WERE TRANSPORTED TO A HOSPITAL; ONE EMPLOYEE WAS TREATED AND RELEASED; THE OTHER EMPLOYEE WAS ADMITTED TO A BURN CENTER OVERNIGHT. AN ACCIDENT INVESTIGATION REVEALED ERRORS WERE MADE AND PROCEDURES WERE NOT FOLLOWED DURING THE GAS LEAK REPAIR ATTEMPT. SPECIFICALLY THE BOLT ON REPAIR CLAMP WAS THE WRONG SIZE FOR THE PIPE BEING REPAIRED ; PROCEDURES PROHIBIT THE USE OF SPARK GENERATING EQUIPMENT IN A HAZARDOUS ATMOSPHERE; AND EMPLOYEES WERE NOT WEARING PROPER PPE CLOTHING.
2025-03-31 10:13 | NO | YES | NO | 20200002 | 35469 | 2020-01-03 10:21 | SUPPLEMENTAL FINAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDENCE BLVD | VIRGINIA BEACH | VA | 23452 | 2019-10-17 09:07 | EASTERN | NO | 2019 | INTERSECTION OF PATRIOTS LANDING DRIVE AND PATRIOTS LANDING PLACE | NEW KENT | NEW KENT | VA | 23141-1642 | 37.5079 | -77.1842 | [5 empty] | YES |  |  |  | 2019-10-22 18:20 | 1261895 |  | NATURAL GAS |  | 818 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2019-10-17 09:07 |  |  |  | 2019-10-17 09:32 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 43 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2007 | 2006 |  |  |  |  | 4 | ASTM D2513 | DRISCOPLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 3 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 105140 | 118945.41232986387192 | 71558 | 80953.926341072845224 | 2200 | 2488.8710968775016 | MEALS AND HOTELS FOR CREWS TO RELIGHT CUSTOMERS. | 7.1516 | 5850 | 6556.299212598425196850393700787401574803 | 0 | 0 | 184748 | 89888.0872200823277885196850393700787402 | 208944.5089804126439408503937007874015748 | 0 | 0 | 365 | 0 | 0 | 365 | 0 | 60 | 60 | 60 | 192.619(A)(2) | 2007-04-27 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | BACKHOE/TRACKHOE | WATER | YES | B927000126 |  |  | CONTRACT LOCATOR | NO | YES | 31 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | JONATHAN HEATH | DIRECTOR - COMPLIANCE AND SYSTEM INTEGRITY | jbheath@southernco.com | (757) 298-5729 |  |  |  |  | JONATHAN HEATH | DIRECTOR - COMPLIANCE AND SYSTEM INTEGRITY | (757) 298-5729 | jbheath@southernco.com | CONTRACTOR DAMAGED A 4"PL MAIN NEAR THE INTERSECTION OF PATRIOTS LANDING DR AND PATRIOTS LANDING PLACE IN NEW KENT, VIRGINIA, 23141, ON OCTOBER 17, 2019 WITH A TRACKHOE. THE MAIN WAS MARKED TO 7FT NORTH OF THE SOUTH CURB OF PATRIOTS LANDING PL WITH AN ARROW. THE MAIN WAS DAMAGED 19' PASSED THE ARROW; THUS OUTSIDE THE AREA MARKED AND OUTSIDE OF THE SCOPE OF THE MISS UTILITY TICKET.
2025-03-31 10:13 | NO | YES | YES | 20200003 | 34511 | 2020-01-03 14:26 | SUPPLEMENTAL FINAL | 15469 | PHILADELPHIA GAS WORKS | 800 W. MONTGOMERY AVENUE | PHILADELPHIA | PA | 19122 | 2019-12-19 11:45 |  |  | 2019 | 1435 S. 8TH STREET | PHILADELPHIA | PHILADELPHIA | PA | 19147 | 39.9308 | -75.1579 | [9 empty] | 2019-12-19 15:47 | 1266865 |  | NATURAL GAS |  | 10 |  | YES | 0 | 0 | 0 | 0 | 2 | 2 | NO | [5 empty] | 0 | YES |  |  |  |  | YES | 60 | 2019-12-19 11:45 |  |  |  | 2019-12-19 11:49 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 32 |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1928 | [5 empty] | 6 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 20 | 0.1 |  | CLASS 4 LOCATION | 1375900 | 1556562.6100880702052 | 1000 | 1131.305044035228 | 40000 | 45252.20176140912 | 0 | 0 |  |  | 20 | 22.41469816272965879265091863517060367454 |  | 0 | 1416920 | 663912.9420071494242396325459317585301837 | 1602968.5315916772828587926509186351706 | 0 | 0 | 5 |  |  |  |  | 0.25 | 0.25 | 0.5 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | A LARGE UNDERGROUND CAVITY CAUSED GROUND MOVEMENT WHICH RESULTED IN THE RUPTURE OF THE SIX INCH CAST IRON MAIN. | [154 empty] | JOSEPH HAWKINSON | VP OF FIELD OPERATIONS | joseph.hawkinson@pgworks.com | 2672496768 |  |  |  |  | JOSEPH HAWKINSON | VP OF FIELD OPERATIONS | 2672496768 | joseph.hawkinson@pgworks.com | ON THURSDAY, DECEMBER 19TH 2019, AT 11:45 AM PGW RECEIVED A CALL FROM THE PHILADELPHIA FIRE DEPARTMENT (PFD) REPORTING A POSSIBLE EXPLOSION ON THE 1400 BLOCK OF SOUTH 8TH STREET. PGW IMMEDIATELY DISPATCHED FIRST RESPONDERS TO INVESTIGATE. THE FIRST PGW EMPLOYEE ARRIVED ON LOCATION AT 11:49 AM. UPON ARRIVAL THREE PROPERTIES WERE ON FIRE (1433, 1435, & 1437 S. 8TH STREET) AND THE DEBRIS FIELD WAS CONSISTENT WITH A POTENTIAL EXPLOSION. WITH THE ASSISTANCE OF THE PFD, PGW PERFORMED HOUSE CHECKS AND THE PFD EVACUATED APPROXIMATELY 60 PEOPLE DURING THE EVENT. A 6" CAST IRON GAS MAIN SUPPLIED THE GAS SERVICES TO THE PROPERTIES ON FIRE. IN ORDER TO SHUT DOWN THE GAS MAIN AND SERVICES TO THESE PROPERTIES PGW UTILIZED GREASE INJECTED THROUGH THE SERVICES OF 1421 AND 1441 S. 8TH STREET. THE MAIN AND SERVICES WERE SHUT DOWN AT 13:27. THE PERMANENT CUT AND CAPS OF THE 6" CAST IRON MAIN WERE COMPLETED AT 17:30. ON 12/19/19 AT 23:00 PGW INSERTED A CAMERA INSIDE THE ABANDONED 6" CAST IRON GAS MAIN AND IDENTIFIED A POTENTIAL BROKEN MAIN LOCATION. THE CAMERA VIEW WAS HINDERED DUE TO THE MAIN BEING FILLED WITH WATER. ON 12/21/19 (AFTER THE WATER HAD BEEN DRAINED FROM THE MAIN) PGW INSERTED THE CAMERA AGAIN AND IDENTIFIED A CLEAR CIRCUMFERENTIAL BREAK WHERE THE MAIN HAD DROPPED. THE LOCATION OF THE BROKEN MAIN WAS 136 FEET NNCL OF DICKINSON STREET. ON 12/22/19 PGW WAS GIVEN ACCESS TO EXCAVATE AND RETRIEVE THE 6" CAST IRON BROKEN MAIN FOR EVIDENCE. THE FOOTWAY AND ROADWAY PAVEMENT WAS UNDERMINED AT THIS LOCATION AND A LARGE CAVITY EXISTED IN THE INTERSECTION OF 1400 S. 8TH STREET AND 800 WILDER STREET. A 6" STAINLESS STEEL SLEEVE WAS INSTALLED ON THE BROKEN MAIN AND THIS SECTION OF MAIN WAS MARKED AND REMOVED FOR EVIDENCE. THE TESTING AND METALLURGICAL ANALYSIS HAS NOT BEEN COMPLETED DUE TO THE CURRENT WORK STOPPAGE CAUSED BY THE COVID-19 PANDEMIC. THE TESTING WILL BE RESCHEDULED AFTER THE PANDEMIC RESTRICTIONS HAVE BEEN LIFTED. THE TESTING AND METALLURGICAL ANALYSIS IS SCHEDULED TO TAKE PLACE ON 6/24/2020 AT AFFILIATED ENGINEERING LABORATORIES, INC. 777 NEW DURHAM ROAD, EDISON NJ 08817. ON SEPTEMBER 30, 2020 THE TESTING ANALYSIS WAS PROVIDED TO PGW AND THE PENNSYLVANIA PUBLIC UTILITY COMMISSION. THE SUMMARY OF THE FINDINGS CONCLUDED EXTERNAL STRESSES APPLIED TO A GRAPHITIZED GAS MAIN INDUCED A CIRCUMFERENTIAL CRACK WHEREBY GAS WAS ALLOWED TO ESCAPE. THERE WAS NO EVIDENCE OF A PRE-EXISTING BREACH OR LEAK LOCATION OBSERVED ON THE FRACTURE SURFACE.
2025-03-31 10:13 | NO | YES | NO | 20200004 | 33149 | 2020-01-03 15:18 | ORIGINAL FINAL | 22476 | ATMOS ENERGY CORPORATION - KY/MID-STATES (KENTUCKY) | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2019-12-05 10:19 |  |  | 2019 | 8070 CARNEAL RD | WEST PADUCAH | MCCRACKEN | KY | 42086 | 37.1272 | -88.7576 | [9 empty] | 2019-12-06 12:15 | 1265688 |  | NATURAL GAS |  | 3.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 1 | 2019-12-05 10:19 |  |  |  | 2019-12-05 10:55 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 43 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1968 | [5 empty] | 8 | ASTM | UNKNOWN | STEEL |  |  |  | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 31 | 6 | [7 empty] | CLASS 2 LOCATION | 1800 | 2036.3490792634104 | 60000 | 67878.30264211368 | 21685 | 24532.34987990391918 | 0 | 0 | THIRD PARTY DAMAGE TO 8" TRANSMISSION PIPE LINE |  | 15225 | 17063.1889763779527559055118110236220472 |  | 0 | 98710 | 54901.5642890515621402755905511811023622 | 111510.1905776589623359055118110236220472 | 1 | 0 | 0 |  |  |  |  | 340 | 360 | 395 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROL ROOM WAS ONLY MONITORING PRESSURE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | TRENCHER | TELECOMMUNICATIONS | YES | 19120220175 |  |  | CONTRACT LOCATOR | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | JACK M. SANDERS | MANAGER OF COMPLIANCE | jack.sanders@atmosenergy.com | 615-771-8387 |  |  |  |  | RYAN R AUSTIN | VP TECHNICAL SERVICES | 270 929-3803 | ryan.austin@atmosenergy.com | WHILE INSTALLING TELEPHONE CABLE FOR AT&T, STAR CONSTRUCTION PLOWED INTO AN 8" STEEL TRANSMISSION MAIN. STAR HAD CALLED IN THE FOLLOWING 5 TICKETS: OCTOBER 10TH, 1910250115, 1910250123, 1910250125, 1910250126, AND 1910250128. ATMOS CONTRACT LOCATOR LOCATED THESE TICKETS 10/29/19. ON 11/6/2019, MITCHELL BAUMGARDNER, ATMOS DAMAGE PREVENTION TECH, SPOKE TO GEORGE OLIVER, STAR CONSTRUCTION, BY PHONE, OF THE HIGH-PRESSURE TRANSMISSION AND ADVISED HIM THAT AN ATMOS REPRESENTATIVE MUST BE THERE IF DIGGING IS OCCURRING AROUND THE TRANSMISSION LINE. ACCORDING TO KORWEB NOTIFICATION, MR. OLIVER WAS SENT POSITIVE RESPONSE OF THE HIGH-PRESSURE LINE FOR EACH TICKET. NO WORK WAS PERFORMED TO OUR KNOWLEDGE ON THESE TICKETS. ON 12/2/2019, STAR CALLED IN THESE TICKETS AGAIN ON 12/2/19: 19120220175, 0179, 0183, 0186. AGAIN, ACCORDING TO KORWEB NOTIFICATION, MR. OLIVER WAS SENT POSITIVE RESPONSE FOR EACH TICKET. ON 12/4/2019, ATMOS'S CONTRACT LOCATOR REFRESHED THE MARKS. ON 12/5/2019, WITHOUT PROVIDING THE REQUIRED NOTICE TO ATMOS, STAR CONSTRUCTION BEGAN PLOWING IN THEIR CABLE AND CUT THE 8" STEEL TRANSMISSION LINE. AFTER GAS WAS SHUT OFF, DAMAGE PREVENTION SPECIALIST MIKE COLEMAN, MITCHELL BAUMGARDNER AND ATMOS CONTRACT LOCATOR SUPERVISOR ANDREW TUCKER WOULD TIE ON TO THE WIRE AT THE TEST STATION USED BY THE ATMOS LOCATORS AND REPLICATED THE SAME MARKS & FLAGS. MARKS WERE OFF APPROXIMATELY 6' TO 12' THE LENGTH OF THE PROJECT. THOUGH A SMALL SECTION OF THE TRANSMISSION LINE WAS SHUT DOWN, SERVICE WAS NOT INTERRUPTED BECAUSE THIS WAS PART OF A TWO-WAY FEED. THE DAMAGE AREA WAS ISOLATED AND REPAIRED BY INSTALLING 23 FEET OF 8' STEEL PRE-TESTED PIPE.
2025-03-31 10:13 | NO | NO | NO | 20200005 | 33935 | 2020-01-08 09:20 | SUPPLEMENTAL FINAL | 13635 | NORTHEAST OHIO NATURAL GAS CORP | 5640 LANCASTER NEWARK RD NE | PLEASANTVILLE | OH | 43148 | 2019-11-27 15:00 |  |  | 2019 | CORNER OF SR 57 & PLEASANT HOME RD | RITTMAN | WAYNE | OH | 44270 | 40.9165 | -81.7632 | [9 empty] | 2019-11-27 20:28 | 1265043 |  | NATURAL GAS |  | 683.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-11-27 15:30 |  |  |  | 2019-11-27 15:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | ERW | 0.216 | [6 empty] | OTHER | [8 empty] | DRIVER HIT STATION AND SHEARED THE DUMP VALVE OFF OF THE VERTICAL SEPARATOR. | CLASS 3 LOCATION | 0 | 0 | 58264 | 65914.357085668524192 | 2000 | 2262.610088070456 | 0 | 0 |  |  | 3836 | 4299.139107611548556430446194225721784777 |  | 0 | 64100 | 32213.8104646446985495223097112860892388 | 72476.1062813505287484304461942257217848 | 0 | 0 | 0 |  |  |  |  | 428 | 428 | 575 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | KELLI ALBANESE | PIPELINE SAFETY COMPLIANCE MANAGER | kalbanese@egas.net | 740-400-4314 | 740-862-6330 |  |  |  | KELLI ALBANESE | PIPELINE SAFETY COMPLIANCE MANAGER | 740-400-4314 | kalbanese@egas.net | CAR WAS PASSING AT AN INTERSECTION. CAR THEY ATTEMPTED TO PASS WAS TURNING LEFT. CAR SWERVED TO AVOID HITTING THE CAR THAT WAS PASSING THEM, WENT OFF ROAD AND HIT OUR STATION. 48 HOUR UPDATE INCIDENT REPORT # 1265125 REPLACED ALL DAMAGED PIPE AND FITTINGS WITH NEW PIPE AND FITTINGS THE MEET THE PRESSURE REQUIREMENTS OF THE STATION. ALL FACILITIES TESTED TO THE REQUIREMENTS OF PART 192
2025-03-31 10:13 | NO | NO | NO | 20200006 | 33315 | 2020-01-08 14:13 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2019-12-10 09:26 |  |  | 2019 | 1100 N. COUNCIL AVE. | BLANCHARD | MCCLAIN | OK | 73010 | 35.1469 | -97.6528 | [9 empty] | 2019-12-10 11:11 | 1265991 |  | NATURAL GAS |  | 62 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 50 | 2019-12-10 09:26 |  |  |  | 2019-12-10 09:28 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1985 | [5 empty] | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | MECHANICAL PUNCTURE | 6.5 | 2 | [7 empty] | CLASS 2 LOCATION | 60000 | 67878.30264211368 | 61 | 69.009607686148908 | 1245 | 1408.47477982385886 | 0 | 0 |  |  | 189 | 211.818897637795275590551181102362204724 |  | 0 | 61495 | 28921.0317958654059415275590551181102362 | 69567.6059272614830435905511811023622047 | 2 | 0 | 6 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | TRENCHER | TELECOMMUNICATIONS | YES | 19112712331518 |  |  | CONTRACT LOCATOR | YES | YES | 5 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | SETH SLIFER | SR. COMPLIANCE SPECIALIST | seth.slifer@onegas.com | 405-248-7018 |  |  |  |  | MEGHAN BOOKER | DIRECTOR OF ENGINEERING | 405-239-0573 | meghan.booker@onegas.com | UNDERGROUND SOLUTIONS TRENCHED INTO ONG'S 2" PE MAIN WHILE INSTALLING A FIBER OPTIC LINE. IGNITION OF THE GAS OCCURRED FROM THE OPERATOR ACTIVATING AN ELECTRIC SHUT-OFF SWITCH TO THE TRENCHER. REPAIRS COMPLETE AND SERVICE RESTORED SAME DAY.
2025-03-31 10:13 | NO | NO | NO | 20200007 | 33187 | 2020-01-15 12:40 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2019-10-16 14:52 |  |  | 2019 | 1204 W. 6TH ST & S. MACARTHUR BLVD. | IRVING | DALLAS | TX | 75060 | 32.8085 | -96.9602 | [9 empty] | 2019-12-20 12:13 | 1266914 |  | NATURAL GAS |  | 555 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 30 | 2019-10-16 14:52 |  |  |  | 2019-10-16 15:19 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 33 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1996 | [5 empty] | 2 | PE2306 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | MECHANICAL PUNCTURE | 2 | 0.6 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 55206 | 62454.826261008796968 | 13125 | 14848.3787029623675 | 0 | 0 |  |  | 2989 | 3349.87664041994750656167979002624671916 |  | 0 | 71320 | 35115.501089585598415083989501312335958 | 80653.0816043911119745616797900262467192 | 1 | 0 | 2 |  |  |  |  | 23 | 30 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 1977701310 | TEXAS811 |  | CONTRACT LOCATOR | UNKNOWN/OTHER | YES | 9 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO UNLOCATABLE FACILITY | [170 empty] | BRUCE MISERENDINO | OPERATIONS SUPERVISOR | bruce.miserindino@atmosenergy.com | 214-2062387 | 972-579-1269 |  |  |  | MARLO SUTTON | VICE PRESIDENT - TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON OCTOBER 16, 2019, A 2" PE MAIN WAS STRUCK BY THIRD PARTY CONTRACTOR PERFORMING DIRECTIONAL BORING TO INSTALL COMMUNICATIONS. ATMOS ENERGY'S CONTRACT LOCATOR HAD NOT COMPLETED THE LOCATE TICKET DUE TO DIFFICULTIES LOCATING THE LINE AND NOTIFIED THE THIRD-PARTY CONTRACTOR THAT THE TICKET WAS IN TROUBLE STATUS. THE THIRD-PARTY CONTRACTOR CHOSE TO CONTINUE WORK BEFORE LOCATES WERE COMPLETED AND DID NOT EXPOSE THE GAS FACILITY WITH EXISTING LOCATE MARKS. INITIALLY, ATMOS ENERGY DID NOT EXPECT THE DAMAGES ASSOCIATED WITH THIS INCIDENT TO EXCEED $50,000. HOWEVER, DUE TO THE COMPLEXITIES INVOLVED, THE COST OF CONTRACTOR WORKFORCE AND RESTORATIONS OF PROPERTIES ULTIMATELY WERE HIGHER THAN ORIGINALLY ESTIMATED. WHEN ATMOS ENERGY DISCOVERED THIS, THE INCIDENT WAS REPORTED PURSUANT TO PART 191.3.
2025-03-31 10:13 | NO | NO | NO | 20200009 | 33450 | 2020-01-15 15:33 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2019-12-06 12:59 |  |  | 2019 | 1194 UNIVERSITY DR | CORAL SPRINGS | DADE-BROWARD | FL | 33071 | 26.246 | -80.2533 | [9 empty] | 2019-12-10 21:36 | 1266059 |  | NATURAL GAS |  | 635 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-12-06 12:59 |  |  |  | 2019-12-06 13:21 |  | NO | PUBLIC PROPERTY | UNDERGROUND | OTHER | UNDER A WATER CANAL | 300 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2002 | [5 empty] | 6 | SDR 11.5 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 83388 | 94337.265012009592464 | 8870 | 10034.67574059247236 | 648 | 733.085668534827744 | EQUIPMENT CHARGES |  | 5541 | 6209.992125984251968503937007874015748031 |  | 0 | 98447 | 49275.9560011964337871968503937007874016 | 111315.018547121144536503937007874015748 | 0 | 0 | 0 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS DUE TO EXCAVATION. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | OTHER | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | NO | [5 empty] | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | SANDRA PANOS | SUPERVISOR QUALITY ASSURANCE | sjpanos@tecoenergy.com | 813-275-3730 |  |  |  |  | SANDRA PANOS | SUPERVISOR QUALITY ASSURANCE | 813-275-3730 | sjpanos@tecoenergy.com | CONTRACTOR, JM POWER, STRUCK A 6" PE MAIN WHILE BORING UNDER A CANAL. JM POWER DID NOT SUBMIT AN UNDERWATER TICKET AS REQUIRED BY FS CHAPTER 556; THEREFORE, THE CANAL WAS NOT MARKED WITH BUOYS. TWO 2" BYPASSES WERE BUILT TO CONTINUE GAS FLOW, 6 INCH PIPE WAS SQUEEZED AFTER. CREWS, VERIFIED NO PRESSURE DROPS AFTER BYPASS WAS INSTALLED. TO MAKE FINAL REPAIRS, A PIECE OF 4" PE WAS INSERTED INTO THE DAMAGED AREA. 6" X 4" REDUCERS WERE INSTALLED ON EITHER SIDE OF THE INSERTED PIPE. COST INFORMATION IS DOES NOT INCLUDE RESTORATION (WHICH SHOULD BRING THE COSTS TO OVER $50K); WILL UPDATE WITH A SUPPLEMENTAL WHEN FINAL COSTS ARE RECEIVED. SUPPLEMENTAL CREATED: ADDED TOTALS OF RESTORATION AND ADDITIONAL CONTRACTOR CHARGES.. COSTS ARE FINAL.
2025-03-31 10:13 | NO | YES | NO | 20200010 | 33443 | 2020-01-17 17:11 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2019-12-15 00:45 |  |  | 2019 | OX RD. & CLARA BARTON DR. | FAIRFAX STATION | FAIRFAX COUNTY | VA | 22015 | 38.7967 | -77.3253 | [9 empty] | 2019-12-15 12:53 | 1266505 |  |  |  | 239 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-12-15 00:48 |  |  |  | 2019-12-15 01:29 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2002 | [8 empty] | STEEL |  |  |  | 0.28 | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 450000 | 509087.2698158526 | 1000 | 1131.305044035228 | 0 | 0 |  |  | 621 | 695.976377952755905511811023622047244094 |  | 0 | 451621 | 211961.0504606661222755905511811023622047 | 510914.5512378405839055118110236220472441 | 0 | 0 | 0 |  |  |  |  | 225 | 225 | 280 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE BY VEHICLE WAS TO INLET SIDE OF STATION AND DUE TO SIZE OF LEAK, IT WOULD NOT CREATE AN ALARM. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | RICHARD W. FITZPATRICK | DOT PIPELINE SAFETY SUPERVISOR | richardfitzpatrick@washgas.com | 703-639-7825 |  |  |  |  | KRISTOPHER KELLEY | DIRECTOR SAFETY QUALITY PIPELINE COMPLIANCE | 703-750-7710 | kristopherkelley@washgas.com | 48HR FOLLOW-UP NRC # 1266661 ON, 12/15/19 AT APPROXIMATELY 0045 HRS., WASHINGTON GAS WAS NOTIFIED BY FAIRFAX COUNTY FIREBOARD OF DAMAGED FACILITY NEAR THE INTERSECTION OF OX RD. & CLARA BARTON DR. FAIRFAX, VA. WASHINGTON GAS IDENTIFIED THE FACILITY TO BE STATION #390, DAMAGED BY A VEHICLE THAT HAD TRAVELLED THROUGH THE SAFETY BOLLARDS AND SECURITY ENCLOSURE BOX. WASHINGTON GAS SECURED THE STATION BY CLOSING THE STATION VALVES, ISOLATING THE DAMAGED FACILITIES. THERE WERE NO CUSTOMERS AFFECTED, AS AREA WAS A TWO-WAY FEED. THE AREA OF GAS RELEASE WAS ON 6"X4" REDUCER AND 4" STRAINER. OTHER PARTS OF THE FACILITY PIPING WERE BENT DUE TO IMPACT.
2025-03-31 10:13 | NO | YES | NO | 20200012 | 33448 | 2020-01-21 08:49 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2019-11-22 15:09 |  |  | 2019 | SR 436 AT LYNCHFIELD AVE | ALTAMONTE SPRINGS | SEMINOLE COUNTY | FL | 32714 | 28.6616 | -81.3989 | [9 empty] | 2019-12-19 14:25 | 1266857 |  | NATURAL GAS |  | 931 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-11-22 15:09 |  |  |  | 2019-11-22 15:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 168 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1999 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 98026 | 110897.308246597259928 | 24152 | 27323.279423538826656 | 12204 | 13806.446757405922512 | EQUIPMENT CHARGES |  | 8117 | 9097.005249343832020997375328083989501312 |  | 0 | 142499 | 71380.3006310560636638687664041994750656 | 161124.0396768858411169973753280839895013 | 8 | 0 | 129 |  |  |  |  | 125 | 125 | 137 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DAMAGE WAS DUE TO EXCAVATION | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 311907253 |  |  | UTILITY OWNER | YES | YES | 12 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | SANDRA PANOS | SUPERVISOR OF QUALITY ASSURANCE | sjpanos@tecoenergy.com | 813-275-3730 |  |  |  |  | SANDRA PANOS | SUPERVISOR OF QUALITY ASSURANCE | 813-275-3730 | sjpanos@tecoenergy.com | THIRD PARTY CONTRACTOR STRUCK PGS' PROPERLY MARKED 4" STEEL MAIN WHILE INSTALLING TELECOMMUNICATIONS CONDUIT. THE DAMAGE OCCURRED ON A 4 LANE HIGHWAY AT A DEPTH OF 13 TO 14 FEET. THE AREA WAS MADE SAFE, TEMPORARILY, BY TURNING OFF THE VALVE. TO RESTORE SERVICE 400 FEET OF STEEL PIPE WAS INSERTED THROUGH THE DAMAGED LINE. ONCE PERMITS ARE OBTAINED, PGS PLANS TO RETIRE THE DAMAGED SECTION OF MAIN AND REPLACE IT WILL A NEW INSTALLATION. THIS WORK SHOULD COMMENCE WITHIN 3 OR 4 MONTHS.
2025-03-31 10:13 | NO | NO | NO | 20200013 | 33237 | 2020-01-28 12:00 | ORIGINAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2019-12-26 12:25 |  |  | 2019 | 1210 HALF ST | Not Within a Municipality | Not Within a County or Parish | DC | 20003 | 38.8761 | -77.0106 | [9 empty] | 2019-12-26 14:47 | 1267331 |  |  |  | 91.51 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 15 | 2019-12-26 12:41 |  |  |  | 2019-12-26 12:41 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 29 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2019 | [5 empty] | 4 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | MECHANICAL PUNCTURE | 1.2 | 1.2 | [7 empty] | CLASS 4 LOCATION | 320 | 362.01761409127296 | 133 | 150.463570856685324 | 7797 | 8820.785428342672716 | 383 | 433.289831865492324 | ADMIN COSTS |  | 239 | 267.855643044619422572178477690288713911 |  | 0 | 8872 | 4292.796919600424669608923884514435695538 | 10034.4120882007427465721784776902887139 | 6 | 0 | 0 |  |  |  |  | 20 | 20 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DUE TO THE SIZE OF DAMAGE AREA, SCADA WOULD NOT OF DETECTED THE MINIMUM GAS LOSS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | MILLING | NO |  |  |  | CONTRACT LOCATOR | YES | YES | 6 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | RICHARD FITZPATRICK | DOT PIPELINE SUPERVISOR | richardfitzpatrick@washgas.com | 7037506941 |  |  |  |  | KRISTOPHER KELLEY | DIRECTOR SAFETY QUALITY PIPELINE COMPLIANCE | 7037507710 | kristopherkelley@washgas.com | PAVING CONTRACTOR ANDERSON COMPANY, WORKING FOR THE DISTRICT OF COLUMBIA USED AN EXCAVATOR AND HIT A 2" PLASTIC SERVICE TEE. NRC NOTIFICATION WAS MADE DUE TO SHUT DOWN OF NAVY YARD BALLPARK METRO STATION BY DC FIRE DEPARTMENT. THE STATION WAS MONITORED BY DC FD & WG. NO INDICATIONS OF NATURAL GAS WERE FOUND. 48HR FOLLOW UP NRC # 1267452
2025-03-31 10:13 | NO | YES | YES | 20200014 | 34540 | 2020-01-29 11:38 | SUPPLEMENTAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2020-01-10 17:44 |  |  | 2020 | 3152 KENNEDY BLVD | JERSEY CITY | HUDSON | NJ | 07306 | 40.7407 | -74.0611 | [9 empty] | 2020-01-10 21:57 | 1268403 |  | NATURAL GAS |  | 11346 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | YES | 2 | 2020-01-10 17:44 |  |  |  | 2020-01-10 18:11 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | MAIN |  | 1952 | [5 empty] | 36 | UNKNOWN | UNKNOWN | CAST/WROUGHT IRON | [10 empty] | LEAK |  |  | OTHER | LEAKING AT JOINTS | [5 empty] | CLASS 4 LOCATION | 100000 | 111640.7690281801 | 449363 | 501672.308928100942763 | 234961 | 262312.267316302244761 | 0 | 0 |  |  | 9863 | 12278.4285714285714285714285714285714286 |  | 0 | 794187 | 374016.022131686295219591836734693877551 | 887903.7738440118589525714285714285714286 | 2 | 0 | 1 |  |  |  |  | 15 | 15 | 20 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | OTHER PIPE, WELD, OR JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | OTHER PIPE/WELD/JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | OTHER PIPE/WELD/JOINT FAILURE | [146 empty] | OTHER PIPE, WELD, OR JOINT FAILURE | [26 empty] | BELL JOINTS WERE FOUND TO BE LEAKING | [11 empty] | YES | NATURAL CAUSES |  | YES |  |  |  | OTHER | NATURAL CAUSES | NO | [86 empty] | ROGER GUNNELS | PRINCIPAL REGULATOR SPECIALIST | roger.gunnels@pseg.com | 973-365-5326 |  |  |  |  | CHRIS LAROSSA | MANAGER REGULATORY POLICY AND PROCEDURE. | 9738967617 | christopher.larossa@pseg.com | ON FRIDAY 1/10/2020 1744 HRS AT 3152 KENNEDY BLVD, JERSEY CITY, ACCIDENTAL IGNITION OCCURRED AND SUBSEQUENT EXPLOSION/RAPID EXPANSION OCCURRED RESULTING IN ONE PERSON BEING TRANSPORTED TO THE HOSPITAL. THE FIRE DEPARTMENT AND PSE&G ARRIVED ON SITE. GAS WAS FOUND TO BE MIGRATING FROM MULTIPLE LEAKS ON A 36" 15 PSI MAIN THROUGH A 4" ELECTRICAL CONDUIT COMING FROM THE STREET AND EXTENDING INTO THE BASEMENT OF THE STRUCTURE. PSE&G IS UNABLE TO DETERMINE THE VOLUME OF GAS THAT LEAKED OUT. MULTIPLE ENCAPSULATIONS WERE PERFORMED ON THE 36" MAIN TO STOP THE LEAKS. THE SERVICE TO THE STRUCTURE WHILE NOT BEING THE SOURCE OF THE RELEASE OF GAS WAS SHUT OFF OUT OF AN ABUNDANCE OF CAUTION AND REMAINS SHUT OFF AT THIS TIME. REPAIRS TO THE PIPE INCLUDED ENCAPSULATION OF TEES, BELL JOINTS, AND MECHANICAL SLEEVES AS WELL AS REPLACEMENT OF CAST IRON UP MAIN. LOCATED NEAR THE 36' MAIN IS A 12 IN MAIN, OUT OF AN ABUNDANCE OF CAUTION A SECTION OF THIS MAIN WAS ALSO REPLACED. WE WERE ABLE TO DETERMINE APPROXIMATELY HOW MUCH GAS WOULD HAVE BEEN IN THE CONDUIT AND INSIDE THE STRUCTURE. I USED THE WIDTH OF JFK BLVD. TO DETERMINE THE ESTIMATED LENGTH OF THE CONDUIT, THE DIAMETER OF THE CONDUIT AND THE LENGTH AND WIDTH OF THE HOUSE AND A BLANKET OF GAS ALONG THE CEILING OF AT LEAST 6' (THE RAFTERS ARE 2X6'S AND THAT AREA WOULD HAVE FILLED FIRST WITH NO MERCAPTAN BEING DETECTED IN THE HOUSE BY THE OCCUPANTS).
2025-03-31 10:13 | NO | YES | NO | 20200016 | 33252 | 2020-01-30 16:06 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2019-12-31 13:42 |  |  | 2019 | 1878 KENNY RD | COLUMBUS | FRANKLIN | OH | 43212 | 39.9977 | -83.0346 | [9 empty] | 2019-12-31 15:19 | 1267682 |  | NATURAL GAS |  | 2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2019-12-31 13:52 |  |  |  | 2019-12-31 13:52 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1997 | [8 empty] | OTHER | METER SETTING&REGULATOR W/ PLASTIC RISER | [9 empty] | LEAK |  |  | OTHER | VEHICLE DAMAGE-FIRE DAMAGE | [5 empty] | CLASS 4 LOCATION | 242000 | 273775.820656525176 | 1200 | 1357.5660528422736 | 3000 | 3393.915132105684 | 0 | 0 |  |  | 5 | 5.60367454068241469816272965879265091864 |  | 0 | 246205 | 115362.8387399333981349081364829396325459 | 278532.9055160138160146981627296587926509 | 0 | 0 | 0 |  |  |  |  | 43.5 | 43.5 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | A THIRD PARTY VEHICLE LOST CONTROL AND CAUSED THE INCIDENT THE CONTROLLERS ACTIONS HAD NO BEARING ON THE SITUATION. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | ROB R. SMITH | MANAGER OF COMPLIANCE | rrsmith@nisource.com | 614-460-5491 |  |  |  |  | ROB R. SMITH | MANAGER OF COMPLIANCE | 614-460-5491 | rrsmith@nisource.com | THIRD-PARTY DRIVER FAILED TO CONTROL A VEHICLE AND VEERED OFF THE ROADWAY APPROXIMATELY 20' AND STRUCK A DOMESTIC METER SETTING LOCATED ON THE SIDE OF THE HOUSE. A FIRE ENSUED AND DAMAGED BOTH THE STRUCTURE AND THE VEHICLE. PLEASE CONSIDER THIS A FINAL REPORT.
2025-03-31 10:13 | NO | YES | NO | 20200017 | 33266 | 2020-02-03 15:27 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2020-01-07 13:59 |  |  | 2020 | 2483 MEMORIAL DRIVE SE | ATLANTA | DEKALB | GA | 30317 | 33.7472 | -84.306 | [9 empty] | 2020-01-07 15:15 | 1268149 |  | NATURAL GAS |  | 2779 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2020-01-07 13:59 |  |  |  | 2020-01-07 14:06 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1993 | [5 empty] | 6 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 3.5 | 3.5 | [7 empty] | CLASS 3 LOCATION | 325000 | 362832.499341585325 | 92000 | 102709.507505925692 | 14000 | 15629.707663945214 | 0 | 0 |  |  | 5839 | 7268.959183673469387755102040816326530612 |  | 0 | 436839 | 206011.1059892558981924198250728862973761 | 488440.6736951297003877551020408163265306 | 3 | 3 | 4 |  |  |  |  | 45 | 45 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 11219400202 |  |  | CONTRACT LOCATOR | YES | YES | 12 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A 6-INCH PLASTIC NATURAL GAS MAIN WAS RUPTURED BY A CONTRACT CREW WHILE INSTALLING TELECOMMUNICATIONS CONDUIT BY DIRECTIONAL DRILLING. THE ESCAPING GAS IGNITED CAUSING DAMAGE TO A NEARBY STRUCTURE AND VEHICLE. ONCE THE INCIDENT WAS MADE SAFE IT WAS IDENTIFIED THAT DAMAGE TO THE SURROUNDING STRUCTURES AND REPAIRS TO THE AFFECTED PIPELINE WOULD EXCEED THE $50,000 THRESHOLD FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. NOTIFICATION TO THE ONE-CALL CENTER WAS MADE WHERE THE MAIN WAS CORRECTLY LOCATED, HOWEVER, THE EXCAVATOR FAILED TO POTHOLE WHERE THE FACILITY WAS DAMAGED. ADDITIONAL NRC REPORT NUMBER 1268226 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2025-03-31 10:13 | NO | NO | NO | 20200018 | 34374 | 2020-02-05 12:32 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2020-01-06 16:30 |  |  | 2020 | E. MAIN AND S. CROWLEY RD. | CROWLEY | TARRANT | TX | 76036 | 32.5785 | -97.3531 | [9 empty] | 2020-01-07 18:21 | 1268177 |  | NATURAL GAS |  | 66.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-01-06 16:30 |  |  |  | 2020-01-06 18:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 132 |  | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 2006 | [5 empty] | 6 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 80780 | 90183.41322096388478 | 0 | 0 | 0 | 0 |  |  | 300 | 373.469387755102040816326530612244897959 |  | 0 | 81080 | 37696.7460833612750157434402332361516035 | 90556.882608718986820816326530612244898 | 2 | 0 | 0 |  |  |  |  | 25 | 25 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | NATURAL GAS | YES | 2050249433 | TEXAS811 |  | CONTRACT LOCATOR | YES | YES | 1 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | TONY MARLOW | OPERATIONS SUPERVISOR | tony.marlow@atmosenergy.com | 817-207-2870 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | AT 4:30 PM ON JANUARY 6, 2020, A 2ND PARTY CONTRACTOR WAS BORING A HOLE AT THE INTERSECTION OF E. MAIN ST. AND S. CROWLEY RD. IN CROWLEY, TX. THE CONTRACTOR EXPOSED THE WRONG FACILITY, WHICH RESULTED IN BORING INTO AN ATMOS ENERGY 6" POLY MAIN. ATMOS ENERGY, USING SQUEEZE TOOLS AND LINE STOPPERS, WAS ABLE TO SHUT DOWN THE LINE AT 9:20 AM ON JANUARY 7, 2020. THE COST OF REPAIRS FOR THIS LINE HAS EXCEEDED $50,000. THE FACILITY WAS PLACED BACK IN SERVICE ON APRIL 9, 2020.
2025-03-31 10:13 | NO | YES | YES | 20200019 | 34434 | 2020-02-06 07:30 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2020-01-04 19:33 |  |  | 2020 | 14406 EVERGREEN | DETROIT | WAYNE | MI | 48223 | 42.3926 | -83.2367 | [9 empty] | 2020-01-04 21:09 | 1267969 |  | NATURAL GAS |  | 2 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 6 | 6 | YES |  |  |  |  | YES | 6 | 2020-01-04 19:33 |  |  |  | 2020-01-04 19:55 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | 1943 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.145 | [6 empty] | LEAK |  |  | OTHER | LEAK CAUSE DUE TO A GUN SHOT | [5 empty] | CLASS 3 LOCATION | 21087 | 23541.688964972337687 | 3703 | 4134.057677113509103 | 5000 | 5582.038451409005 | 131 | 146.249407426915931 | SUPPORT SERVICES COST: CUSTOMER SERVICE & GAS DISPATCH SERVICES |  | 299 | 372.224489795918367346938775510204081633 |  | 0 | 30220 | 14179.2787042504199016909620991253644315 | 33776.2589907176860883469387755102040816 | 0 | 0 | 2 |  |  |  |  | 2 | 2 | 2 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [156 empty] | FRENAE F. SMITH | MANAGER CODES AND STANDARDS | frenae.smith@dteenergy.com | 313-389-7762 |  |  |  |  | FRENAE F. SMITH | MANAGER CODES AND STANDARDS | 313-389-7762 | frenae.smith@dteenergy.com | ON JANUARY 4, 2020, DTE GAS DISPATCH RECEIVED A CALL FROM 911 AT 19:33 OF AN EXPLOSION AT 14404 & 14406 EVERGREEN STREET IN DETROIT, MICHIGAN. THIS IS A RESIDENCE THAT IS CONSIDERED A 2-FAMILY FLAT (ONE STRUCTURE WITH TWO RESIDENCES). DTE GAS FIRST RESPONDERS ARRIVED ON-SITE AT 19:55 TO INVESTIGATE AND TERMINATE GAS SERVICE. THERE WERE 6 INDIVIDUALS TAKING TO THE HOSPITAL, ONE WITH BURNS AND 5 WITH SMOKE INHALATION. WORKING WITH DETROIT FIRE & ARSON, DTE GAS'S INTERNAL INVESTIGATION TEAM AND THE MICHIGAN PUBLIC SERVICE COMMISSION, IT WAS DETERMINED THAT THE CAUSE OF THIS INCIDENT WAS DUE TO AN AK 47 GUN THAT WAS SHOT IN THE HOUSE WHICH PENETRATED THE SERVICE LINE JUST BELOW THE METER & REGULATOR ASSEMBLY. THE CASE HAS BEEN TURNED OVER TO DETROIT POLICE FOR FURTHER INVESTIGATION.
2025-03-31 10:13 | NO | YES | NO | 20200020 | 33502 | 2020-02-06 15:24 | SUPPLEMENTAL FINAL | 18112 | SAN DIEGO GAS & ELECTRIC CO | 8326 CENTURY PARK COURT | SAN DIEGO | CA | 92123 | 2019-08-22 08:05 |  |  | 2019 | 2920 ZOO DRIVE | SAN DIEGO | SAN DIEGO | CA | 92101 | 32.7342 | -117.1483 | [9 empty] | 2020-01-15 08:50 | 1268754 |  | NATURAL GAS |  | 300 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-08-22 08:05 |  |  |  | 2019-08-22 08:26 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 1935 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1.2 | 1.2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 5717 | 6467.670936749398476 | 200 | 226.2610088070456 | 429846 | 486286.947958366614888 | CUSTOMER CLAIM FOR LOSS OF BUSINESS REVENUE |  | 1800 | 2017.322834645669291338582677165354330709 |  | 0 | 437563 | 206044.0370262965751179291338582677165354 | 494998.2027385687282553385826771653543307 | 30 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  | NO |  |  | YES | YES | [8 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | GRADING | YES | 191341234 | DIGALERT |  | CONTRACT LOCATOR | UNKNOWN/OTHER | YES | 4 | NOTIFICATION ISSUE | EXCAVATOR PROVIDED INCORRECT NOTIFICATION INFORMATION | [170 empty] | AUSTIN WALKER | PIPELINE SAFETY COMPLIANCE ADVISOR | awalker4@socalgas.com | (323) 513-4998 |  |  |  |  | AUSTIN WALKER | PIPELINE SAFETY COMPLIANCE ADVISOR | 8186328407 | awalker4@socalgas.com | ON AUGUST 22, 2019, AT 2920 ZOO DRIVE IN SAN DIEGO, SAN DIEGO COUNTY, A THIRD PARTY CONTRACTOR DAMAGED A 1.25 INCH STEEL NATURAL GAS SERVICE WHILE EXCAVATING CAUSING A GAS LEAK. CREWS RESPONDED AND CONTROLLED THE GAS. THERE WERE NO INJURIES OR FURTHER DAMAGE RESULTED FROM THIS INCIDENT. ALL REPAIRS WERE COMPLETED AND THE AFFECTED CUSTOMERS WERE RESTORED. INVESTIGATION OF THE INCIDENT SHOWED THERE WAS A NOTIFICATION FOR A USA TICKET, BUT IT WAS NOT SUFFICIENT AS THE CONTRACTOR DAMAGED THE 1.25 INCH SERVICE 300 FEET OUTSIDE THE DESCRIBED WORK AREA AS NOTED ON THE USA TICKET. ON JANUARY 15, 2020, SDG&E WAS MADE AWARE OF A CLAIM FROM THE SAN DIEGO ZOO FOR THE AMOUNT OF $429,846.57 AND SUBSEQUENTLY REPORTED THIS INCIDENT TO THE DOT DUE TO GAS RELEASE AND DAMAGES POTENTIALLY EXCEEDING $50,000. SDG&E'S INVESTIGATION REVEALED THAT SDG&E WAS NOT THE PRIMARY CAUSE OF THE INCIDENT AND WILL BE CLOSING THIS INCIDENT REPORT AS FINAL.
2025-03-31 10:13 | NO | NO | NO | 20200021 | 33327 | 2020-02-12 19:27 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2020-01-13 09:43 |  |  | 2020 | 642 S ALVARADO STREET | LOS ANGELES | LOS ANGELES | CA | 90057 | 34.058 | -118.2758 | [9 empty] | 2020-01-14 09:04 | 1268662 |  | NATURAL GAS |  | 561 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 120 | 2020-01-13 09:43 |  |  |  | 2020-01-13 09:43 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 57 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1933 | [5 empty] | 8 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | CORROSION ON BAND. | [5 empty] | CLASS 4 LOCATION | 0 | 0 | 26000 | 29026.599947326826 | 14000 | 15629.707663945214 | 15000 | 16746.115354227015 | PAVING COSTS. |  | 3366 | 4190.326530612244897959183673469387755102 |  | 0 | 58366 | 29307.3394268350944606413994169096209913 | 65592.7494961112998979591836734693877551 | 1 | 0 | 35 |  |  |  |  | 35 | 35 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | PRELIMINARY INDICATION IS STRAY CURRENT. |  |  | YES |  |  |  | YES | NO |  | NO | NO | [8 empty] | NO | COAL TAR | [21 empty] | 2019-09-16 | NO | [227 empty] | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | amatin@socalgas.com | 909-919-0463 |  |  |  |  | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-919-0463 | amatin@socalgas.com | ON 01/13/2020, SOCALGAS WAS NOTIFIED OF A GAS LEAK AT 642 S ALVARADO STREET, LOS ANGELES. SOCALGAS CREWS WERE SENT TO THE SCENE TO PERFORM LEAK INVESTIGATION AND CENTERED LEAK OVER AN 8-INCH STEEL MAIN. THE LEAK WAS ISOLATED BY OPERATING TWO MAINLINE VALVES AND GAS WAS CONTROLLED AT 05:25 ON 01/14/2020. THE LEAK WAS PERMANENTLY REPAIRED ON 01/14/2020 BY WELDING ON A WELD PATCH. ALL CUSTOMER RESTORES WERE COMPLETED ON 01/15/2020. THERE WERE NO INJURIES OR FURTHER DAMAGES RESULTING FROM THE RELEASE OF GAS. FURTHER INVESTIGATION SHOWS THE CAUSE OF LEAK WAS CORROSION ON BOTTOM OF MAIN. A CATHODIC PROTECTION MITIGATION PLAN WAS DEVELOPED TO MONITOR THE BELL HOLE LOCATION UNTIL FURTHER REMEDIATION IS DETERMINED. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE AND DAMAGES EXCEEDING $50,000. FOR ANY FURTHER QUESTIONS, PLEASE CONTACT ALI MATIN AT (909) 919-0463.
2025-03-31 10:13 | NO | YES | NO | 20200023 | 33615 | 2020-02-17 09:12 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2020-01-11 12:56 |  |  | 2020 | INTERSECTION OF HANLEY AND SR42 | MANSFIELD | RICHLAND | OH | 44903 | 40.6958 | -82.5626 | [9 empty] | 2020-01-11 17:22 | 1268463 |  | NATURAL GAS |  | 38597 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-01-11 12:56 |  |  |  | 2020-01-11 12:56 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1958 | [5 empty] | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.27 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | 80000 | 89312.61522254408 | 244135 | 272554.191466947487135 | 7112 | 7939.891493284168712 | 0 | 0 | 0 |  | 96493 | 120123.9387755102040816326530612244897959 |  | 0 | 427740 | 264284.5197699681778657725947521865889213 | 489930.6369582859399286326530612244897959 | 12 | 0 | 984 |  |  |  |  | 95 | 95 | 115 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | WE RECEIVED NUMEROUS REPORTS FROM THE PUBLIC AT THE SAME TIME LOW PRESSURE ALARM WAS RECEIVED VIA GAS CONTROLS SCADA SYSTEM UPON PRESSURE DROPPING FROM 96 PSIG TO 4.2 PSIG. THE GAS CONTROLLER EVALUATED OTHER SCADA INDICATIONS AND NOTICED A CORRESPONDING INCREASE IN FLOW, PROMPTING THEM TO CALL-OUT TO THE OPERATIONS LEADER. THE OPERATIONS LEADER INFORMED THE GAS CONTROLLER THEY HAD BEEN NOTIFIED OF THE INCIDENT FROM OTHER PARTIES AS WELL AND THAT TECHNICIANS WERE RESPONDING. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | MECHANICAL JOINT FAILURE | MATERIAL/WELD/EQUIP FAILURE | MECHANICAL JOINT FAILURE | MATERIAL FAILURE OF PIPE OR WELD | JOINT/FITTING/COMPONENT | [146 empty] | MECHANICAL JOINT FAILURE | [8 empty] | BOLTED |  | COUPLING |  | DRESSER |  | OTHER | MATERIALS JOINED: 1ST STEEL, 2ND STEEL | [22 empty] | YES | N/A |  |  | YES |  |  |  |  | NO | [86 empty] | ROB SMITH | MANAGER OF COMPLIANCE | rrsmith@nisource.com | 6144605491 |  |  |  |  | ROB SMITH | MANAGER OF COMPLIANCE | 6144605491 | rrsmith@nisource.com | COLUMBIA GAS OF OHIO, INC. (COLUMBIA) WAS NOTIFIED BY ITS SCADA AND BY THE GENERAL PUBLIC OF A LEAK AT THE INTERSECTION OF SR42 AND HANLEY RD. COLUMBIA FOUND A 12" STEEL MAIN LINE LEAK WHERE A SHORT BARRELED BOLTED COUPLING WITHOUT PULL OUT RESTRAINT FAILED. COLUMBIA SHUT OFF THE LINE FOR SAFETY AND MADE PERMANENT REPAIRS. THIS EVENT RESULTED IN A SERVICE DISRUPTION TO 996 CUSTOMERS. PLEASE CONSIDER THIS REPORT FINAL.
2025-03-31 10:13 | NO | YES | NO | 20200024 | 33869 | 2020-02-17 17:20 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2020-01-22 12:00 |  |  | 2020 | 100 E CLARENDON DR | DALLAS | DALLAS | TX | 75203 | 32.7345 | -96.8226 | [9 empty] | 2020-01-23 07:58 | 1269346 |  | NATURAL GAS |  | 2163 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 33 | 2020-01-22 12:00 |  |  |  | 2020-01-22 11:44 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2019 | [5 empty] | 12 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 1.159 |  | 4710 | MECHANICAL PUNCTURE | 2.5 | 2.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 80883 | 90298.403213062910283 | 43408 | 48461.025019752417808 | 0 | 0 |  |  | 9731 | 12114.1020408163265306122448979591836735 |  | 0 | 134022 | 68676.2472357466699646647230320699708455 | 150873.5302736316546216122448979591836735 | 4 | 0 | 0 |  |  |  |  | 24 | 24 | 55 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 2050939705 | TEXAS811 |  | CONTRACT LOCATOR | NO | YES | 19 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | PATRICK MCGRATH | MANAGER OF OPERATIONS | patrick.mcgrath2@atmosenergy.com | 2144267082 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 2142062033 | marlo.sutton@atmosenergy.com | ON THE MORNING OF JANUARY 22, 2020, PRO BORE CONSTRUCTION WAS DIRECTIONAL BORING FOR TELECOMMUNICATIONS AND HIT A 12-INCH POLY MAIN. THE EXCAVATOR HAD A VALID LOCATE TICKET, 2050941166 AND ALTHOUGH THE DAMAGE OCCURRED IN THE SCOPE OF THE LOCATE TICKET, THE GAS LINES IN THE INTERSECTION WERE NOT MARKED. ATMOS ENERGY WAS NOTIFIED OF THE DAMAGE BY THE FIRE DEPARTMENT AT 10:55 AM. TECH ARRIVED ONSITE AROUND 11:44 AM. ASSISTANCE ARRIVED AT 1:30 PM. THE VALVE ON THE 12-INCH LINE IN THE SW CORNER OF THE INTERSECTION WAS TURNED TO THE OFF POSITION AROUND 1:50 PM. THE 4-INCH POLY LINE NORTH OF THE INTERSECTION WAS SQUEEZED OFF AROUND 3:45 PM. AROUND 6:00 PM, THE CONTRACTOR ARRIVED ONSITE TO BEGIN PROCESS OF APPLYING SHORT STOP TO THE 12-INCH STEEL LINE EAST OF THE INTERSECTION. ON JANUARY 23, 2020, THE CONDITION WAS ELIMINATED AROUND 7:11 AM. GAS SERVICE WAS RESTORED TO THE SYSTEM AFTER REPAIRS AROUND 12:00 PM ON JANUARY 24, 2020. *48-HOUR UPDATE: NRC # 1269535.
2025-03-31 10:13 | NO | NO | NO | 20200025 | 33973 | 2020-02-19 12:55 | SUPPLEMENTAL FINAL | 8160 | INTERMOUNTAIN GAS CO | 555 SOUTH COLE ROAD | BOISE | ID | 83709 | 2020-01-16 15:32 |  |  | 2020 | BROADWAY ST. AND I-15 SOUTHBOUND ONRAMP | IDAHO FALLS | BONNEVILLE | ID | 83402 | 43.4966 | -112.0548 | [9 empty] | 2020-01-31 14:10 | 1270059 |  | NATURAL GAS |  | 34 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-01-16 15:32 |  |  |  | 2020-01-16 15:50 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 34 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1958 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 42686 | 47654.978667368957486 | 16157 | 18037.799051883058757 | 2780 | 3103.61337898340678 | TRAFFIC CONTROL FOR ROAD CLOSURE. |  | 133 | 165.571428571428571428571428571428571429 |  | 0 | 61756 | 28646.5651615399759289795918367346938776 | 68961.9625268068515944285714285714285714 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2019-05-23 | NO | [12 empty] | NO | YES | INTERSTATE HIGHWAY | [12 empty] | UNKNOWN/OTHER | UNKNOWN/OTHER | UNKNOWN/OTHER | NO | [5 empty] | NO |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | ASSUME DAMAGE OCCURRED DURING INSTALLATION OF GUARDRAIL | [169 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.com | 208-377-6032 |  |  |  |  | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 208-377-6032 | greg.watkins@mdu.com | AT 15:32 ON JANUARY 16, 2020, THE IDAHO FALLS FIRE DEPARTMENT REPORTED A NATURAL GAS LEAK NEAR THE SOUTHBOUND ON-RAMP OF I-15 AND BROADWAY ST. IN IDAHO FALLS, ID. INTERMOUNTAIN GAS COMPANY (IGC) FIRST RESPONDERS ARRIVED AT 15:50 AND CONFIRMED AN UNDERGROUND GAS LEAK. ONCE THE EXACT LOCATION WAS PINPOINTED BY IGC CONSTRUCTION AND LEAK SURVEY PERSONNEL, THE SECTION OF PIPELINE WAS SHUTDOWN UTILIZING LINE STOPPER EQUIPMENT AT 12:30 ON JANUARY 17,2020. THE SECTION OF PIPELINE WHERE THE LEAK WAS PINPOINTED WAS REPLACED VIA HORIZONTAL DIRECTION BORE. AFTER REPAIRS AND ONCE THE DAMAGE WAS PHYSICALLY EXPOSED, IGC DISCOVERED A SMALL SECTION OF COAL TAR WRAP HAD BEEN KNOCKED OFF AND RE-WRAPPED WITH A FIELD APPLIED COATING. BASED ON THE VINTAGE OF FIELD WRAP, THE ORIGINAL COATING DAMAGE OCCURRED PRIOR TO 1993. THERE IS NO EVIDENCE OF DAMAGE (I.E. DENT, SCRATCH OR WALL LOSS) TO THE PIPELINE. THE OXIDATION (CORROSION) OCCURRED DUE TO A POOR APPLICATION OF THE FIELD WRAP. ON JANUARY 31, 2020, THE TO DATE REPAIR COST WAS $45,000. IGC WILL INCUR A MINIMUM OF $5,000 IN ADDITIONAL COSTS THIS SPRING WHEN THE TEMPORARY ASPHALT IS REPLACED WITH PERMANENT ASPHALT, AT WHICH TIME THE TOTAL REPAIR COSTS WILL EXCEED $50,000. THE NRC REPORT NUMBER OF THE 48-HOUR CONFIRMATION CALL IS 1270070. 6/29/2020 - CORRECTED PART A - 7 FROM EST TO MST. UPDATED PART D - 2B. TO INCLUDE PERMANENT ASPHALT REPAIR COSTS.
2025-03-31 10:13 | NO | YES | NO | 20200026 | 33791 | 2020-02-21 14:33 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2020-01-24 13:00 |  |  | 2020 | MINGO CREEK, 11TH AND MINGO | TULSA | TULSA | OK | 74128 | 36.1481 | -95.872 | [9 empty] | 2020-01-24 19:00 | 1269516 |  | NATURAL GAS |  | 85162 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-01-24 13:13 |  |  |  | 2020-01-24 13:25 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | YES | [6 empty] | YES | UNCASED | MINGO CREEK | 1 |  | PRIVATELY OWNED |  | MAIN |  | 1976 | [5 empty] | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | ERW | 0.375 | [6 empty] | MECHANICAL PUNCTURE | 5 | 12 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 118391 | 132172.622860152702191 | 0 | 0 |  |  | 269966 | 336080.1224489795918367346938775510204082 |  | 0 | 388357 | 365635.7264407248740113119533527696793003 | 468252.7453091322940277346938775510204082 | 7 | 0 | 3 |  |  |  |  | 120 | 120 | 125 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | N/A | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | STATE HIGHWAY | [12 empty] | MUNICIPALITY | GRADER/SCRAPER | GRADING | NO | [5 empty] | YES | 8 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | SETH SLIFER | SR. COMPLIANCE SPECIALIST | seth.slifer@onegas.com | 4052487018 |  |  |  |  | MEGHAN BOOKER | DIRECTOR OF ENGINEERING | 4052390573 | meghan.booker@onegas.com | THE CITY OF TULSA DAMAGED ONG'S 12" DM 100 WITH A BULLDOZER GRADER WHILE PERFORMING A SILT REMOVAL PROCESS IN MINGO CREEK AS REQUIRED BY THE ARMY CORP OF ENGINEERS. ONG SHUT VALVES AT 11TH AND MEMORIAL AND 11TH AND MINGO. ONG ISOLATED AND CAPPED THE PIPE ON THE EAST AND WEST SIDE OF MINGO CREEK. REPAIRS COMPLETE AND SERVICE RESTORED NEXT DAY AT 10:30AM.
2025-03-31 10:13 | NO | NO | NO | 20200027 | 34053 | 2020-02-22 23:03 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2020-01-23 13:40 |  |  | 2020 | INTERSECTION OF WEST WILMINGTON STREET AND HIGHWAY 53 | BURGAW | PENDER | NC | 28425 | 34.5516 | -77.9253 | [9 empty] | 2020-01-23 17:37 | 1269410 |  | NATURAL GAS |  | 812 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 3 | 2020-01-23 12:30 |  |  |  | 2020-01-23 13:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  |  |  | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | OTHER | PNG SERVICE | MAIN |  | 2009 | [5 empty] | 6 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 2 | 7 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 54228 | 60540.556228601504628 | 0 | 0 | 0 | 0 |  |  | 16000 | 19918.3673469387755102040816326530612245 |  | 0 | 70228 | 43499.7386735423181196501457725947521866 | 80458.9235755402801382040816326530612245 | 0 | 0 | 13 |  |  |  |  | 60 | 60 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  | YES |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 200072306 |  |  | CONTRACT LOCATOR | YES | YES | 7 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | A CONTRACTOR CAME IN CONTACT WITH A 6" MAIN WHILE DIRECTIONAL BORING. DUE TO NOT POTHOLING THE GAS LINE PRIOR TO BORING, THE PIPELINE WAS DAMAGED. DUE TO THE DEPTH OF COVER, THE PIPELINE WAS ABANDONED BENEATH A DOT STATE ROAD. NEW PIPELINE WAS INSTALLED.
2025-03-31 10:13 | NO | NO | NO | 20200028 | 33370 | 2020-02-25 13:14 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2020-01-28 11:08 |  |  | 2020 | LINKWOOD RD AT MARTIN LUTHER KING JR RD | ATLANTA | FULTON | GA | 30311 | 33.7546 | -84.4818 | [9 empty] | 2020-01-28 14:16 | 1269775 |  | NATURAL GAS |  | 162.2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-01-28 11:08 |  |  |  | 2020-01-28 11:22 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2011 | [5 empty] | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 2500 | 2791.0192257045025 | 1500 | 1674.6115354227015 | 0 | 0 |  |  | 340 | 423.26530612244897959183673469387755102 |  | 0 | 4340 | 2241.075520467413177842565597667638483965 | 4888.89606724965297959183673469387755102 | 0 | 0 | 1 |  |  |  |  | 45 | 45 | 45 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 10309400026 |  |  | CONTRACT LOCATOR | YES | YES | 6 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A 4-INCH PLASTIC NATURAL GAS MAIN WAS RUPTURED BY A CONTRACT CREW WHILE INSTALLING TELECOMMUNICATIONS CONDUIT BY DIRECTIONAL DRILLING. ONCE THE INCIDENT WAS MADE SAFE IT WAS IDENTIFIED THAT THE FIRE DEPARTMENT HAD STOPPED THE RAILROAD FOR MORE THAN THE 20-MINUTE THRESHOLD THE COMPANY HAS IN ITS OPERATIONS PROCEDURE MANUAL (OPM) FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. NOTIFICATION TO THE ONE-CALL CENTER WAS MADE, HOWEVER, IT APPEARS THE LOCATE TICKET HAD EXPIRED AND THE MARKS AT THE JOB SITE WERE FADED. IN ADDITION, THE FADED MARKS APPEARED TO BE MIS-LOCATED BY APPROXIMATELY 6-INCHES WHERE THE EXCAVATOR HAD FAILED TO POTHOLE TO DETERMINE THE PROXIMITY OF THE PIPELINE. ADDITIONAL NRC REPORT NUMBER 1269835 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2025-03-31 10:13 | NO | NO | NO | 20200029 | 33372 | 2020-02-25 17:33 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2020-01-11 04:15 |  |  | 2020 | 601 N. VERMILLLION ST. | LEXINGTON | MCLEAN | IL | 61753 | 40.6464 | -88.7748 | [9 empty] | 2020-01-11 10:05 | 1268426 |  | NATURAL GAS |  | 11.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2020-01-11 02:49 |  |  |  | 2020-01-11 04:15 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 24 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1979 | [5 empty] | 0.625 | ASTM D2513 | SAMUEL MOORE & CO. | OTHER | PLASTIC/ALUMINUM COMPOSITE PIPE | [9 empty] | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 0.6 | 0.6 |  | CLASS 3 LOCATION | 75000 | 83730.576771135075 | 100 | 111.6407690281801 | 500 | 558.2038451409005 | 0 | 0 |  |  | 31 | 38.59183673469387755102040816326530612245 |  | 0 | 75631 | 34991.8229636562664956268221574344023324 | 84439.0132220388494775510204081632653061 | 0 | 0 | 1 |  |  |  |  | 52 | 52 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | DIRECT HIT |  |  | NO | [218 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | lquezad@southernco.com | [5 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QUALITY ASSURANCE | 6303882316 | lquezad@southernco.com | A LIGHTNING STRIKE HIT A 5/8" SERVICE LINE, IGNITING THE GAS AND CAUSING A FIRE WHICH IGNITED THE METER SET AND THE STRUCTURE TO WHICH IT IS CONNECTED.
2025-03-31 10:13 | NO | YES | YES | 20200030 | 33445 | 2020-02-26 16:35 | SUPPLEMENTAL FINAL | 1800 | KEYSPAN ENERGY DELIVERY - NY CITY | 2 HANSON PLACE | BROOKLYN | NY | 11217 | 2020-01-28 10:00 |  |  | 2020 | BAY RIDGE PARKWAY & 19TH AVENUE | BROOKLYN | KINGS | NY | 11204 | 40.6122 | -73.9936 | [9 empty] | 2020-01-28 11:45 | 1269757 |  | NATURAL GAS |  | 21.5 |  | NO | [5 empty] | 0 | YES | 0 | 2 | 0 | 0 | 0 | 2 | YES |  |  |  |  | NO | 0 | 2020-01-28 10:00 |  |  |  | 2020-01-28 10:26 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2017 | [5 empty] | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.375 | [6 empty] | MECHANICAL PUNCTURE | 0.2 | 0.2 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 14139 | 15784.888332894384339 | 5463 | 6098.935212009478863 | 0 | 0 |  |  | 94 | 117.020408163265306122448979591836734694 |  | 0 | 19696 | 9171.874115747351280932944606413994169096 | 22000.8439530671285081224489795918367347 | 0 | 0 | 25 |  |  |  |  | 0.3 | 0.32 | 0.43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS RELATED TO EVENTS THAT OCCURRED AT THE EXCAVATION SITE. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER GAS WORK METHODS | corinne.byrnes@nationalgrid.com | 6317703549 |  |  |  |  | CORINNE BYRNES | PRINCIPAL PROGRAM MANAGER GAS WORK METHODS | 6317703549 | corinne.byrnes@nationalgrid.com | GAS FIELD OPERATIONS SENIOR SUPERVISOR REPORTED THAT A CONTRACTOR CREW WAS PREPPING A WORK LOCATION FOR A LP MAIN TIE IN SCHEDULED FOR JANUARY 29, 2020. WHILE CONTRACTOR (HALLEN) FOREMAN AND OPERATOR WERE WORKING IN THIS EXCAVATION WITH A LIVE GAS MAIN DRILLING A TAP HOLE, AN IGNITION OCCURRED RESULTING IN BOTH EMPLOYEES SUSTAINING SECOND DEGREE BURNS. FDNY, EMS, NYPD, PSC, GAS FIELD OPERATIONS (GFO) AND INCIDENT COMMAND RESPONDED TO THE LOCATION. THE CMS SUPERVISOR REPORTED (AS PER FDNY CHIEF DONADIO, ENGINE 318) THAT THE 2 CONTRACTORS WERE TAKEN TO STATEN ISLAND BURN CENTER FOR FURTHER EVALUATION AND WE WERE INFORMED THEY WERE KEPT OVERNIGHT. THE CONTRACTORS WERE NOT DRUG TESTED DUE TO THEIR INJURIES. GFO SENIOR SUPERVISOR REPORTED THAT AT 14:48, THE 12" LP ST MAIN WAS SECURED BY SECURING 2 LP VALVES AND SQUEEZING OFF A SECTION OF THE MAIN. CMS REPORTED THAT THE ISOLATION AND REPAIR WORK PERFORMED BY GFO RESULTED IN THE INTERRUPTION OF GAS TO 6 SERVICES SUPPLYING 25 CUSTOMERS. THESE CUSTOMERS WERE SECURED AS A PRECAUTION PRIOR TO THE REPAIR WORK. CMS AND GFO CREWS REMAINED ON SITE UNTIL REPAIRS ARE COMPLETED AND TURNED OVER FOR THE RELIGHT PROCESS.
2025-03-31 10:13 | NO | NO | NO | 20200031 | 33814 | 2020-02-28 13:00 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2020-01-31 11:31 |  |  | 2020 | D STREET, 3126 FEET WEST OF 15TH STREET | BURNS HARBOR | PORTER | IN | 46304 | 41.6372 | -87.1206 | [9 empty] | 2020-02-01 20:23 | 1270144 |  | NATURAL GAS |  | 1497.8 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-01-31 11:21 |  |  |  | 2020-01-31 11:21 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1983 | [8 empty] | STEEL |  |  |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | 1/2" NIPPLE | [5 empty] | CLASS 1 LOCATION | 0 | 0 | 41000 | 45772.715301553841 | 1000 | 1116.407690281801 | 36000 | 40190.676850144836 | OUTSIDE SERVICES, LABOR/MATERIAL FOR A BYPASS THAT WAS NOT USED. |  | 2737 | 3407.285714285714285714285714285714285714 |  | 0 | 80737 | 39217.7802292894840816326530612244897959 | 90487.0855562661922857142857142857142857 | 0 | 0 | 0 |  |  |  |  | 60 | 60 | 75 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK WAS MINOR IN TERMS OF VOLUME BASED ON STATION FLOW AND COULD NOT BE DETECTED BY SCADA. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | [197 empty] | THREADED CONNECTION FAILURE | [12 empty] | PIPE NIPPLE | [70 empty] | RICK SMITH | MANAGER OF GAS OPERATIONS COMPLIANCE | ricksmith@nisource.com | 219-252-4057 |  |  |  |  | RICK SMITH | MANAGER OF GAS OPERATIONS COMPLIANCE | 219-252-4057 | ricksmith@nisource.com | STATION LOCATED INSIDE METAL BUILDING ON THE CUSTOMER'S PROPERTY (ARCELOR MITTAL STEEL). TAP CONNECTED TO 1/2" WELDED HALF COUPLING WAS DAMAGED. THE PIPE NIPPLE BROKE AT THE THREADED POINT WHERE IT ENGAGED INTO THE HALF COUPLING. THERE WAS A VIBRATION AT THE STATION THAT CAUSED THE NIPPLE TO CRACK. THE NIPPLE HAD A CAP ON THE OUTLET SIDE OF THE FITTING, WHICH WAS REPLACED WITH A PIPE PLUG. THE PLUG IS THICKER AT THE THREADED POINT AND WILL SERVE THE SAME PURPOSE.
2025-03-31 10:13 | NO | YES | NO | 20200032 | 33772 | 2020-02-28 15:51 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2019-12-09 13:03 |  |  | 2019 | 604 WEST GRAUWYLER LANE | IRVING | DALLAS | TX | 75061-4515 | 32.8294 | -96.9521 | [9 empty] | 2020-01-30 14:25 | 1269972 |  | NATURAL GAS |  | 556.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 1 | 2019-12-09 13:03 |  |  |  | 2019-12-09 13:11 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 144 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2002 | [5 empty] | 8 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 115 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 7413 | 8386.364291433145164 | 185340 | 209676.07686148915752 | 45757 | 51765.124899919927596 | 0 | 0 |  |  | 2758 | 3090.986876640419947506561679790026246719 |  | 0 | 241268 | 114613.829198091698645328083989501312336 | 272918.5529294826502275065616797900262467 | 0 | 0 | 3 |  |  |  |  | 22 | 20 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES |  | YES | [7 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | BORING | CABLE TV | YES | 1982263553 | TEXAS811 |  | CONTRACT LOCATOR | NO | YES | 15 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | BRUCE MISERENDINO | OPERATIONS SUPERVISOR | No Email Address | 2142062387 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 2142062033 | marlo.sutton@atmosenergy.com | ON DECEMBER 9, 2019 A THIRD PARTY EXCAVATOR DAMAGED AN 8-INCH PE MAIN NEAR 604 W. GRAUWYLER LANE IN IRVING, TEXAS. THE EXCAVATOR HAD A VALID LOCATE TICKET AT THE TIME OF DAMAGE. HOWEVER, THE LINE WAS NOT MARKED. UPON DAMAGING THE LINE, THE EXCAVATOR NOTIFIED THE FIRE DEPARTMENT. AN ATMOS ENERGY REPRESENTATIVE ARRIVED ONSITE AT APPROXIMATELY 12:30 PM. AROUND 4:00 PM, THE COMPANY CONTRACTOR SQUEEZED THE LINE EAST OF THE CUT. THE CONDITION WAS ELIMINATED AT 7:00 PM. THE LINE WAS PLACED BACK IN SERVICE BY 6:00 PM ON JANUARY 3RD, 2020. 48-HOUR NRC UPDATE: 1270228 SUPPLEMENTAL: UPDATED ESTIMATED COST OF PUBLIC AND NON-OPERATOR PRIVATE PROPERTY DAMAGE. SECOND SUPPLEMENTAL: CORRECTED INITIAL NRC REPORT TIME FROM EASTERN TIME ZONE TO CENTRAL TIME ZONE. ADJUSTED COSTS TO THE APPROPRIATE LINE ITEM. 2A INCLUDES TREE REMOVAL AND DISPOSAL AS WELL AS INSTALLATION OF BED PLANTS, GRADING AND INSTALLING SOD. 2B INCLUDES CONTRACT LABOR, TRENCH SAFETY, STREET PLATES, AND OTHER MATERIALS, BACKFILL AND REBUILDING RETAINING WALL AS WELL AS TRAFFIC CONTROL AND PAVEMENT REPAIRS FROM EMERGENCY THROUGH PERMANENT REPAIRS. 2C INCLUDES CONTRACT LABOR FOR EMERGENCY RESPONSE.
2025-03-31 10:13 | NO | YES | YES | 20200034 | 37023 | 2020-03-11 10:38 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2020-02-17 06:30 | MOUNTAIN | NO | 2020 | 621 W FRANCIS ST | ASPEN | PITKIN | CO | 81611 | 39.1921 | -106.8263 | [7 empty] | YES | USED THE NO-BLOW MACHINE TO STOP THE FLOW OF GAS. | 2020-02-17 07:06 | 1271384 |  | NATURAL GAS |  | 10.52 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2020-02-16 10:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 2 | 2020-02-17 10:55 |  |  |  | 2020-02-16 11:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE RISER |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 300 | 334.9223070845403 | 2100 | 2344.4561495917821 | 0 | 0 |  | 4.943 | 52 | 64.73469387755102040816326530612244897959 | 0 | 0 | 2452 | 1169.601580502022250728862973760932944606 | 2744.11315055387342040816326530612244898 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 38 | 38 | 40 | 192.619(A)(1) | 2020-02-16 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 3.2 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | SNOW/ICE IMPACT OR ACCUMULATION | NATURAL FORCE DAMAGE | DAMAGE FROM SNOW/ICE | [56 empty] | SNOW/ICE IMPACT OR ACCUMULATION | [5 empty] | NO | [218 empty] | STONEY DAVIDSON | COMPLIANCE COORDINATOR | stoney.davidson@blackhillscorp.com | 7193590586 |  | TODD ELLSWORTH | todd.ellsworth@blackhillscorp.com | 970 989-7046 | STONEY DAVIDSON | PIPELINE SAFETY PROFESSIONAL | 719 359-0586 | stoney.davidson@blackhillscorp.com | INITIAL BHE TECHNICIAN THAT RESPONDED HEARD A LEAK AT AT THE METER SET BY DETACHED GARAGE STRUCTURE. LEAK WAS FOUND ON THE INLET RISER. POSSIBLE CAUSE WAS DUE TO SNOW/ICE FALLING FROM ROOF ONTO THE METER SET. A NO-BLO TOOL WAS USED TO STOP THE GAS AT THE GARAGE (METER SET).. NOTE THERE WAS NO GAS SERVICE TO THE DETACHED GARAGE STRUCTURE. AFD MADE AREA SAFE. BHE REBULT METER SET AND TURNED GAS SERVICE BACK ON TO RESIDENCE.
2025-03-31 10:13 | NO | YES | NO | 20200035 | 33498 | 2020-03-13 16:04 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2020-02-14 18:02 |  |  | 2020 | INTERSECTION NEAR 46515 HARRY BYRD HWY | POTOMAC FALLS | LOUDOUN COUNTY | VA | 20164 | 39.025 | -77.3917 | [9 empty] | 2020-02-14 11:35 | 1271263 |  | NATURAL GAS |  | 7593.9 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 20 | 2020-02-14 11:35 |  |  |  | 2020-02-14 11:52 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 54 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1995 | [5 empty] | 8 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2406 | MECHANICAL PUNCTURE | 5 | 5 | [7 empty] | CLASS 3 LOCATION | 38000 | 42423.492230708438 | 15841 | 17685.014221754009641 | 109062 | 121757.655517513780662 | 6923 | 7728.890439820908323 | OVERHEAD |  | 862 | 1073.102040816326530612244897959183673469 |  | 0 | 170688 | 79517.2667122757479932361516034985422741 | 190668.1544506134631566122448979591836735 | 9 | 0 | 0 |  |  |  |  | 20 | 20 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA EQUIPMENT MEASURES PRESSURE IN THE AREA OF THE STATION AND DOES NOT MEASURE FLOW AS THERE IS NOT A METERING STATION NEAR THE DAMAGED FACILITY. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 4300525 |  |  | CONTRACT LOCATOR | YES | NO |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | OLD TICKET NO LONGER VALID | [169 empty] | RICHARD W. FITZPATRICK | DOT PIPELINE SAFETY SUPERVISOR | richardfitzpatrick@washgas.com | 703-639-7825 |  |  |  |  | KRISTOPHER KELLEY | DIRECTOR SAFETY QUALITY PIPELINE COMPLIANCE | 703-750-7710 | kristopherkelley@washgas.com | NRC 48HR UPDATE #1271349 ATLANTIC CONSTRUCTION COMPANY 516 JACK ENDERS BLVD. UNIT A BERRYVILLE, VA 22611 DIRECTIONAL DRILLING HIT A 8" PLASTIC NATURAL GAS MAIN ON FEBRUARY 14, 2020. WASHINGTON GAS CONTRACT LOCATOR FAILED TO MARK TICKET B002801077 IN ITS ENTIRETY (56-265. 19A) THE EXCAVATOR HAD INITIATED A REMARK ON 2/12/20 A004300525 DUE TO WEATHER. THAT NOTIFICATION HAD NOT BEEN MARKED AND CLEARED THROUGH THE CALL CENTER, AND THEREFORE THE EXCAVATOR DID NOT POSSESS A VALID TICKET (56-265.17 D). PIPELINE REPAIRS ARE COMPLETE.
2025-03-31 10:13 | NO | YES | YES | 20200038 | 33747 | 2020-03-25 16:00 | SUPPLEMENTAL FINAL | 2364 | DUKE ENERGY OHIO | 139 EAST FOURTH STREET PO BOX 960 - ROOM 460-ANNEX | CINCINNATI | OH | 45202 | 2020-02-25 19:08 |  |  | 2020 | 9948 PRINCETON GLENDALE ROAD | WEST CHESTER | BUTLER | OH | 45246 | 39.3101 | -84.4648 | [9 empty] | 2020-02-25 23:27 | 1272092 |  | NATURAL GAS |  | 260 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES |  |  |  |  | NO | 0 | 2020-02-25 21:36 |  |  |  | 2020-02-25 22:30 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | UNKNOWN | [10 empty] | OTHER | [8 empty] | STRUCK BY TRACTOR TRAILER. CIRCUMFERENTIAL DAMAGE. | CLASS 3 LOCATION | 0 | 0 | 2155 | 2405.858572557281155 | 0 | 0 | 20000 | 22328.15380563602 | PROPERTY DAMAGE COST OF THE VEHICLE. |  | 67 | 83.40816326530612244897959183673469387755 |  | 0 | 22222 | 10321.2435550238701615160349854227405248 | 24817.4205414586072774489795918367346939 | 1 | 0 | 0 |  |  |  |  | 135 | 135 | 480 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST II | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | A TRACTOR TRAILER HIT A FIRST STAGE REGULATOR ON A SERVICE. THE TRACTOR TRAILER AND FIRST STAGE REGULATOR CAUGHT ON FIRE. THE DRIVER WAS TRANSFERRED TO THE HOSPITAL WITH BURNS TO THE FACE AND ARMS. 48-HOUR UPDATE TO THE NRC: #1272222 ON 2/27/2020 AT 10:55AM.
2025-03-31 10:13 | NO | YES | YES | 20200039 | 36031 | 2020-03-27 09:49 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2020-02-14 12:21 | EASTERN | NO | 2020 | NE 25TH ST & NE 36TH AVE | OCALA | MARION | FL | 34470 | 29.2126 | -82.086 |  | YES | [7 empty] | 2020-02-14 13:43 | 1271245 |  | NATURAL GAS |  | 80.53 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES | 2020-02-14 12:21 | OPERATOR/CONTRACTOR |  | 72 | NO | 0 | 2020-02-14 12:21 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-02-14 12:30 | 2020-02-14 12:39 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 12 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2008 | [5 empty] | 2 | ASTM D2513 | DRISCOL PLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 1738 | 1940.316565709770138 | 2893 | 3229.767447985250293 | 798 | 890.893336844877198 | EQUIPMENT | 7.8977 | 636 | 791.755102040816326530612244897959183673 | 0 | 0 | 6065 | 3242.694866772472337376093294460641399417 | 6852.732452580713955530612244897959183673 | 2 | 0 | 0 | 0 | 1 | 0 | 3 | 52 | 52 | 60 | 192.619(A)(2) | 1993-12-31 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EXCAVATION DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | GRADER/SCRAPER | ROAD WORK | NO | [5 empty] | YES | 6 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | SANDRA PANOS | MANAGER SAFETY MGMT SYSTEM AND QUALITY ASSURANCE | sjpanos@tecoenergy.com | [5 empty] | SANDRA PANOS | MANAGER SAFETY MGMT SYSTEM AND QUALITY ASSURANCE | 813-205-3699 | sjpanos@tecoenergy.com | ROAD CONSTRUCTION CONTRACTOR, SEMA CONSTRUCTION, STRUCK A 2" PE MAIN WHILE MIXING THE NEW ROAD BED. CONTRACTOR INITIALLY STRUCK THE LINE GOING EAST AND PROCEEDED TO WORK AS THEY WERE UNAWARE THE LINE WAS DAMAGED. CONTRACTOR THEN REVERSED COURSE, HEADING WEST, COMPLETELY SEVERING THE LINE. THE GAS THEN IGNITED AND EQUIPMENT CAUGHT ON FIRE RESULTING IN THIRD DEGREE BURNS TO THE WORKER. THE WORKER WAS TRANSPORTED TO THE HOSPITAL AND SUBSEQUENTLY ADMITTED. TO MAKE REPAIRS, THE DAMAGED SECTION WAS CUT OUT AND 40' OF PRETESTED PIPE WAS FUSED IN IT'S PLACE USING A BUTT FUSION PROCESS. NOTES: 1. INPUTS FOR LENGTH AND WIDTH OF DAMAGED AREA (1 X 1) ARE INACCURATE. THE DAMAGED LINE WAS COMPLETELY SEVERED AND HAS A 1.943 INNER DIAMETER. 2. THE DEPTH OF COVER (12 INCHES) IS ESTIMATE BECAUSE THE LINE WAS PULLED UP BY THE INCIDENT AND GROUND COVER HAD PREVIOUSLY BEEN REMOVED DURING THE EXCAVATION MAKING THE GROUND IN THE AREA WELL BELOW GRADE. 3. DID GAS LINE EXPLODE IS ANSWERED AS NO. IT IS UNKNOWN IF THE GAS LINE EXPLODED. 4. THE AMOUNT OF GAS IGNITED, 72.477, IS AN ESTIMATE BASED ON 90% OF THE ESTIMATED VOLUME OF GAS RELEASED. THE PHMSA PORTAL WOULD NOT ALLOW FOR DECIMAL ENTRIES SO A VALUE OF 72 WAS ENTERED .
2025-03-31 10:13 | NO | NO | NO | 20200040 | 33528 | 2020-03-27 17:34 | ORIGINAL FINAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2020-02-26 08:10 |  |  | 2020 | 245 BRIAR RIDGE COURT | OZARK | CHRISTIAN | MO | 65714 | 37.0443 | -93.2539 | [9 empty] | 2020-02-26 18:03 | 1272179 |  | NATURAL GAS |  | 6224 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-02-26 08:10 |  |  |  | 2020-02-26 08:25 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 3 | 1.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 15813 | 17653.754806426119213 | 500 | 558.2038451409005 | 0 | 0 |  |  | 25640 | 31919.1836734693877551020408163265306122 |  | 0 | 41953 | 37069.960774873924585539358600583090379 | 50131.1423250364074681020408163265306122 | 0 | 0 | 1 |  |  |  |  | 225 | 226 | 275 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | NO | NO | NO | NO | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER(S) ACTIONS DID NOT CAUSE OR CONTRIBUTE TO THIS INCIDENT. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | UNKNOWN/OTHER | DRIVEWAY | NO | [5 empty] | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY | nicole.christianer@spireenergy.com | 314-349-2929 |  |  |  |  | CRAIG HOEFERLIN | VP OPERATION SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | A THIRD PARTY CONTRACTOR DAMAGED A 4-INCH STEEL FEEDER LINE. THERE WERE NO LOCATES REQUESTED FOR THE SITE. GAS WAS MADE SAFE ON FEBRUARY 26, 2020 AT 14:44 BY WELDING TWO 4-INCH SHORT STOPS ON THE MAIN AND SHUTTING IT DOWN. A 4-INCH PUMPKIN WAS WELDED OVER THE DAMAGE TO COMPLETE THE REPAIR. THE AMOUNT OF GAS LOSS EXCEEDED THE 3 MILLION CUBIC FEET THRESHOLD FOR A FEDERAL REPORTABLE INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20200041 | 34100 | 2020-04-03 18:05 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2020-03-05 09:30 |  |  | 2020 | 2707 US HWY 190 | COPPERAS COVE | CORYELL | TX | 76522 | 31.121 | -97.8713 | [9 empty] | 2020-03-05 11:51 | 1272777 |  | NATURAL GAS |  | 51 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-03-05 09:30 |  |  |  | 2020-03-05 10:00 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2020 | [8 empty] | OTHER | BRASS BALL VALVE TO STEEL PIPE NIPPLE | [9 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 412485 | 460501.426125888685485 | 0 | 0 |  |  | 187 | 232.795918367346938775510204081632653061 |  | 0 | 412672 | 190941.2294960497938478134110787172011662 | 460734.2220442560324237755102040816326531 | 270 | 0 | 4067 |  |  |  |  | 30 | 30 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT NOT RELATED TO CONTROL ROOM OPERATION | [12 empty] | YES | 2 | 0 | YES | 8 | 0 | EQUIPMENT FAILURE | THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | THREADED CONNECTION/COUPLING FAILURE | EQUIPMENT FAILURE | THREADED CONNECTION/COUPLING FAILURE | [197 empty] | THREADED CONNECTION FAILURE | [12 empty] | THREADED FITTING | [70 empty] | DALE GAMBRELL | COMPLIANCE SUPERVISOR | dale.gambrell@atmosenergy.com | 512-844-8270 | 512-310-3880 |  |  |  | MARLO SUTTON | VICE PRESIDENT TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | AT 9:30 AM ON MARCH 5, 2020, A THREADED FITTING FAILED AT A CONNECTION POINT WITH A 2" BRASS BALL VALVE AT GROUND LEVEL ON A RECENTLY INSTALLED TEMPORARY BYPASS AT THE COPPERAS COVE CITY GATE STATION, CAUSING AN INTERRUPTION IN SERVICE. THE FAILURE OF THE THREADED CONNECTION ON THE TEMPORARY BYPASS VALVE OCCURRED DURING SUPPORT CRIBBING ADJUSTMENT. ATMOS ENERGY IDENTIFIED ADDITIONAL POTENTIAL CONTRIBUTING FACTORS AS THE VALVE MATERIAL AND POSSIBLE UNDER-TORQUEING OF THE THREADED CONNECTION. AN INITIAL ESTIMATE OF THE COPPERAS COVE SYSTEM BASED ON THE FACTS AVAILABLE AT THAT TIME RESULTED IN AN UNDERESTIMATION OF THE TOTAL NUMBER OF CUSTOMERS AND THE COST OF RELIGHTS. HOWEVER, A SUBSEQUENT REVIEW OF OUTAGE REPORTS WHEN REFINING THAT ESTIMATE INDICATED THAT THE CUSTOMER OUTAGE WAS MORE EXTENSIVE THAN ORIGINALLY ANTICIPATED. AT 12:30 PM, THE RELIGHT COSTS WERE ESTIMATED TO BE GREATER THAN $50,000, AND A TELEPHONIC REPORT WAS MADE TO THE NATIONAL RESPONSE CENTER AT 12:51 PM. GAS SERVICE WAS INTERRUPTED TO 270 COMMERCIAL AND 4067 RESIDENTIAL CUSTOMERS. THE APPROPRIATE REPAIRS WERE MADE AND THE FACILITY WAS RESTARTED AT 12:12 AM ON MARCH 6, 2020. SERVICE HAS BEEN RESTORED TO ALL AFFECTED CUSTOMERS. 48 HR. NRC # 1272905
2025-03-31 10:13 | NO | NO | NO | 20200042 | 34179 | 2020-04-07 16:25 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2020-03-03 15:00 |  |  | 2020 | 111 W OAK AVE | TAMPA | HILLSBOROUGH | FL | 33602 | 27.9618 | -82.4616 | [9 empty] | 2020-03-03 17:06 | 1272627 |  | NATURAL GAS |  | 124 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2020-03-03 15:08 |  |  |  | 2020-03-03 15:17 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2019 | [5 empty] | 1.25 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 26 | 29.026599947326826 | 1350 | 1507.15038188043135 | 0 | 0 |  |  | 981 | 1221.244897959183673469387755102040816327 |  | 0 | 2357 | 1765.96146592125660548104956268221574344 | 2757.421879786941849469387755102040816327 | 0 | 0 | 0 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INCIDENT WAS NOT RELATED TO CONTROL ROOM EVENTS | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | DAMAGE WAS BY A MATERIAL THAT WAS SOLDERING A COPPER LINE IN CLOSE PROXIMITY TO THE FACILITY. | [154 empty] | SANDRA PANOS | SUPERVISOR QUALITY ASSURANCE | sjpanos@tecoenergy.com | 8032053699 |  |  |  |  | SANDRA PANOS | SUPERVISOR QUALITY ASSURANCE | 8132053699 | sjpanos@tecoenergy.com | A PLUMBER (I.E. BERNHARD MECHANICAL CONTRACTORS) WAS SOLDERING A COPPER LINE IN CLOSE PROXIMITY TO A 1 1/4' PE GAS SERVICE LINE WHEN THE LINE IGNITED. THE PLUMBER WAS TAKEN TO THE HOSPITAL AND LATER RELEASED. THE SERVICE LINE THAT WAS DAMAGED HAD BEEN PREVIOUSLY LOCATED FOR ANOTHER THIRD-PARTY UNRELATED TO BERNHARD. BERNARD HAD ALREADY EXPOSED THE GAS LINE AND WAS DOING WORK ON A WATER LINE WHEN THEY DAMAGED THE GAS LINE. NUMBER OF EVACUEES IS UNKNOWN AS THE FIRE DEPARTMENT HAD EVACUATED THE SCENE. FACILITY IS STILL SHUT DOWN. PGS WILL CREATE A SUPPLEMENTAL WHEN THE LINE IS REINSTATED. SERVICE LINE HAS BEEN REINSTALLED LOCATION OF INCIDENT WAS INCORRECT IN PGS' LEAK MANAGEMENT SYSTEM. (CORRECT ADDRESS IS ACROSS THE STREET FORM ORIGINALLY NOTED LOCATION.) UPDATED ADDRESS AND LAT/LONG COORDINATES. ADDED DATE SERVICE WAS REINSTALLED.
2025-03-31 10:13 | NO | YES | NO | 20200043 | 33575 | 2020-04-09 13:24 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2020-03-10 08:52 |  |  | 2020 | 1144 N STEMMONS FWY | LEWISVILLE | DENTON | TX | 75067 | 33.0569 | -97.0113 | [9 empty] | 2020-03-10 09:39 | 1273124 |  | NATURAL GAS |  | 15.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2020-03-09 07:15 |  |  |  | 2020-03-09 07:38 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1978 | [8 empty] | OTHER | METER INSTALLATION | [9 empty] | OTHER | [8 empty] | VEHICLE DAMAGED METER SET AND ASSOCIATED 2" POLY SERVICE RISER | CLASS 1 LOCATION | 125489 | 140096.884645772925689 | 1914 | 2136.804319199367114 | 3030 | 3382.71530155385703 | 0 | 0 |  |  | 56 | 69.71428571428571428571428571428571428571 |  | 0 | 130489 | 60374.4372105439164269387755102040816327 | 145686.1185522404355472857142857142857143 | 1 | 0 | 0 |  |  |  |  | 30 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | JEFF BROWN | OPERATIONS SUPERVISOR | jeffrey.brown@atmosenergy.com | 972-360-4404 |  |  |  |  | MARLO SUTTON | VP TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON MARCH 9, 2020, DRIVER LOST CONTROL OF HIS VEHICLE ON THE NORTHBOUND SERVICE ROAD OF INTERSTATE 35-E IN LEWISVILLE, TEXAS, RAN THROUGH AN EXISTING BARRICADE HITTING THE GAS METER FOR A CAR DEALERSHIP AT 1144 N. STEMMONS. THE DAMAGE RESULTED IN IGNITION OF NATURAL GAS AND THE DRIVER-OWNED VEHICLE AS WELL AS EXISTING NEW VEHICLES ON THE DEALERSHIP LOT WERE DAMAGED BY HEAT AND FLAMES. EXTENT OF DAMAGE TO THE DEALERSHIP-OWNED VEHICLES WAS UNKNOWN UNTIL THE MORNING OF MARCH 10, 2020. WE RECEIVED NOTIFICATION OF THE DAMAGE ON MARCH 9, 2020 AT 7:15 AM AND THE HAZARD WAS ELIMINATED AND AREA MADE SAFE AT AROUND 9:50 AM. 48-HR UPDATE: 1273324
2025-03-31 10:13 | NO | NO | NO | 20200044 | 33617 | 2020-04-17 17:39 | ORIGINAL FINAL | 12876 | DOMINION ENERGY UTAH/WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2020-03-24 07:00 |  |  | 2020 | W 7800 S AND REDWOOD ROAD | WEST JORDAN | SALT LAKE COUNTY | UT | 84084 | 40.6096 | -111.9375 | [9 empty] | 2020-03-24 11:34 | 1274123 |  | NATURAL GAS |  | 3827.25 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 6 | 2020-03-24 11:15 |  |  |  | 2020-03-24 03:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2013 | [5 empty] | 8 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 4 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 172 | 192.022122728469772 | 13598 | 15180.911772451929998 | 3348 | 3737.732947063469748 | OTHER COSTS INCLUDE MATERIAL AND SERVICES FOR ROADWAY CUTTING AND REPAIRS. |  | 15692 | 19534.9387755102040816326530612244897959 |  | 0 | 32810 | 25986.027150481694111486880466472303207 | 38645.6056177540735996326530612244897959 | 6 | 0 | 0 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | A00730537 |  |  | CONTRACT LOCATOR | YES | YES | 5 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | LAUREN L SKUFCA | ENGINEER | lauren.l.skufca@dominionenergy.com | 2166338865 |  |  |  |  | REID HESS | MANAGER | 8013243374 | reid.hess@dominionenergy.com | ON MARCH 24, 2020 AT 03:00 DOMINION ENERGY UTAH (DEU) WAS NOTIFIED OF A DAMAGED GAS LINE NEAR REDWOOD ROAD AND W 7800 S IN WEST JORDAN, UTAH. DEU TECHNICIANS ARRIVED ON-SITE AND DISCOVERED THAT A 3RD PARTY CONTRACTOR HAD HIT A NATURAL GAS MAIN WITH DRILLING EQUIPMENT. COMPANY BEGAN IMMEDIATE RESPONSE TO SECURE THE DAMAGED SECTION OF MAIN. THE DAMAGED SECTION OF MAIN WAS SECURED AT 08:15. DEU ENGINEERING PERFORMED GAS LOSS ESTIMATION CALCULATIONS BASED ON INFORMATION OBTAINED ON-SITE. ONCE THE DAMAGE HOLE SIZE WAS OBSERVED AT 11:15, DEU DETERMINED THAT GAS LOSS WAS HIGHER THAN ANTICIPATED AND THE EVENT MET INCIDENT CRITERIA. COMPANY REPORTED THE INCIDENT AFTER DETERMINATION. THE DAMAGED SECTION OF MAIN WAS CUT OUT AND REPLACED. THE NATURAL GAS MAIN WAS LOCATED AND MARKED ACCURATELY. THE CONTRACTOR DID NOT POT HOLE TO VERIFY LOCATION OF THE FACILITIES PRIOR TO DRILLING.
2025-03-31 10:13 | NO | YES | YES | 20200045 | 33800 | 2020-04-22 10:32 | SUPPLEMENTAL FINAL | 22435 | WEST TEXAS GAS INC | 303 VETERANS AIRPARK LANE | MIDLAND | TX | 79705 | 2020-04-20 18:30 |  |  | 2020 | COUNTY RD 220 AND COUNTY RD 43 | Not Within a Municipality | FLOYD COUNTY | TX | 79235 | 34.0213 | -101.527 | [9 empty] | 2020-04-20 19:18 | 1275739 |  | NATURAL GAS |  | 50 |  | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 1 | 0 | 1 | YES |  |  |  |  | NO | 0 | 2020-04-20 16:40 |  |  |  | 2020-04-20 16:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 2 | ASTM | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 17 |  |  | 3406 | MECHANICAL PUNCTURE | 4.5 | 2 | [7 empty] | CLASS 1 LOCATION | 35000 | 39074.269159863035 | 3500 | 3907.4269159863035 | 1500 | 1674.6115354227015 | 0 | 0 |  |  | 150 | 186.73469387755102040816326530612244898 |  | 0 | 40150 | 18668.0438344117411078717201166180758017 | 44843.042305149591020408163265306122449 | 0 | 0 | 1 |  |  |  |  | 27 | 30 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | UNKNOWN/OTHER | TRENCHER | LIQUID PIPELINE | YES | 2060709496 | TEXAS 811 |  | UTILITY OWNER | NO | YES | 21 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | RAY REED | DIRECTOR OF IM | rreed@westtexasgas.com | 8063581321 |  |  |  |  | RICHARD HATCHETT | PRESIDENT | 4326824349 | rhatchett@westtexasgas.com | WTG RECEIVED A LINE LOCATE REQUEST FOR THE AREA OF THE INCIDENT FROM A CONTRACTOR INSTALLING A WATER PIPELINE. WTG EMPLOYEE WHO IS QUALIFIED TO LOCATE PIPELINE MET THE CONTRACTOR ON SITE APRIL 20, 2020. OUR PIPELINE IN THIS SPECIFIC LOCATION IS POLY WITH NO TRACER WIRE. THE DISCUSSION BETWEEN THE WTG EMPLOYEE AND CONTRACTOR CONCLUDED: WTG WOULD BE ON SITE FIRST THING APRIL 21, 2020 TO FOLLOW WTG'S DAMAGE PREVENTION PROCEDURES FOR PIPELINES WITHOUT TRACER WIRE AND ASSIST IN LOCATING OUR PIPELINE. APPROXIMATELY TWO HOURS AFTER THIS ON-SITE MEETING BETWEEN THE WTG EMPLOYEE AND THE CONTRACTOR, WE RECEIVED NOTIFICATION FROM THE CONTRACTOR THAT HE HAD DUG INTO OUR PIPELINE.
2025-03-31 10:13 | NO | NO | NO | 20200046 | 33722 | 2020-05-05 18:12 | SUPPLEMENTAL FINAL | 22784 | ALLIANT ENERGY - WISCONSIN POWER & LIGHT CO | 4902 N BILTMORE LANE | MADISON | WI | 53718 | 2020-04-08 09:30 |  |  | 2020 | PRAIRIE AVENUE, APPROXIMATELY 0.1 MILES NORTH OF E. INMAN PARKWAY | BELOIT | ROCK | WI | 53511 | 42.5555 | -89.0113 | [9 empty] | 2020-04-08 09:40 | 1275027 |  | NATURAL GAS |  | 291 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-04-07 19:16 |  |  |  | 2020-04-07 19:44 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2009 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.28 | [6 empty] | OTHER | [8 empty] | VEHICLE STRUCK REGULATOR STATION DAMAGING INLET, OUTLET, AND STATION PIPING. | CLASS 3 LOCATION | 15000 | 16746.115354227015 | 51000 | 56936.792204371851 | 21000 | 23444.561495917821 | 0 | 0 |  |  | 495 | 616.224489795918367346938775510204081633 |  | 0 | 87495 | 40797.3284302245456559766763848396501458 | 97743.6935443126053673469387755102040816 | 8 | 0 | 103 |  |  |  |  | 54 | 54 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA IS NOT INCORPORATED INTO THE FACILITIES THAT WERE DAMAGED. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | RICHARD A. SUBLETT | SR. MGR. COMPLIANCE AND OPERATIONAL PERFORMANCE | richardsublett@alliantenergy.com | 319-786-4008 |  |  |  |  | RICHARD A. SUBLETT | SR. MANAGER COMPLIANCE AND OPERATIONAL PERFORMANCE | 319-786-4008 | richardsublett@alliantenergy.com | ON TUESDAY, APRIL 7, 2020, AT APPROXIMATELY 7:10 P.M., A WISCONSIN POWER AND LIGHT COMPANY (WPL) PRESSURE REGULATION STATION LOCATED ON PRAIRIE AVENUE IN BELOIT, WISCONSIN, WAS STRUCK AND DAMAGED BY A VEHICLE. PRAIRIE AVENUE IS A TWO-WAY NON-DIVIDED ROAD WITH A POSTED SPEED LIMIT OF 40 MPH. THE STATION IS LOCATED APPROXIMATELY 35 FEET EAST OF THE ROAD AND THE STRETCH OF ROAD IS STRAIGHT. A 2008 FORD F350 PICKUP TRUCK TRAVELING NORTH ON PRAIRIE AVENUE AT A HIGH RATE OF SPEED LOST CONTROL, HIT THE CURB, LEFT THE ROAD AND STRUCK THE STATION'S TRAFFIC BARRIER AND PRESSURE REGULATION STATION. THE TRUCK SUBSEQUENTLY OVERTURNED SEVERAL TIMES AND ENDED UP NORTH OF THE PRESSURE REGULATION STATION. AS A RESULT OF THE MOTOR VEHICLE ACCIDENT, THE DRIVER OF THE VEHICLE WAS FATALLY INJURED AND ANOTHER OCCUPANT WAS INJURED AND TRANSPORTED TO A LOCAL HOSPITAL. THE POLICE REPORT NOTES THAT THE DRIVER WAS EXCEEDING THE SPEED LIMIT AND THEIR SPEED WAS TOO FAST FOR CONDITIONS. THE DAMAGE FROM THE VEHICLE CAUSED LEAKS ON THE PRESSURE REGULATING STATION PIPING. WPL'S CUSTOMER SERVICE CENTER (CSC) WAS NOTIFIED AT APPROXIMATELY 7:16 P.M. BY THE 911 DISPATCH CENTER OF THE INCIDENT. THE CSC EMPLOYEE NOTIFIED WPL'S DISTRIBUTION SYSTEM OPERATIONS (DSO) OF THE ACCIDENT AT 7:21 P.M. WPL FIELD PERSONNEL WERE DISPATCHED TO THE SITE AT APPROXIMATELY 7:30 P.M. AND ARRIVED AT THE SITE AT APPROXIMATELY 7:44 P.M. WPL FIELD PERSONNEL CLOSED THE STATION INLET VALVE AND THE STATION OUTLET VALVE AT APPROXIMATELY 8:00 P.M. THIS SHUT OFF GAS FLOW TO THE STATION AND RESULTED IN THE LOSS OF GAS SERVICE TO 111 CUSTOMERS. WPL FIELD PERSONNEL BEGAN SHUTTING RISER VALVES FOR THE CUSTOMERS THAT LOST SERVICE SHORTLY AFTER THE FLOW OF GAS TO THE STATION WAS STOPPED. REPAIRS TO THE REGULATION STATION STARTED SHORTLY BEFORE MIDNIGHT AND WERE COMPLETED BY APPROXIMATELY 6:00 A.M. ON APRIL 8, 2020. THE RESTORATION OF GAS SERVICE TO CUSTOMERS STARTED AT APPROXIMATELY 8:00 A.M. ON APRIL 8, 2020. AT THE TIME OF THE INCIDENT, THE PRESSURE REGULATION FACILITY AT PRAIRIE AVENUE AND E. INMAN PARKWAY WAS OPERATING AT: 105 PSIG INLET PRESSURE (115 PSIG MAOP) AND 54 PSIG OUTLET PRESSURE (60 PSIG MAOP). NOTE: THE FATALITY TO THE DRIVER AND HOSPITALIZATION OF THE PASSENGER WERE A RESULT OF INJURIES SUSTAINED DURING THE MOTOR VEHICLE ACCIDENT. THEY WERE NOT RELATED TO THE RELEASE OF NATURAL GAS FROM THE DAMAGED PRESSURE REGULATION STATION. INITIAL NATIONAL RESPONSE CENTER REPORT NUMBER: 1275027 48 HOUR UPDATED NATIONAL RESPONSE CENTER REPORT NUMBER: 1275113 UPDATES ON SUPPLEMENTAL REPORT: 05/08/2020 - GPS COORDINATES UPDATED - LOCATION DESCRIPTION REVISED: THE ABOVEGROUND STATION IS LOCATED ON PRAIRIE AVENUE APPROXIMATELY 0.1 MILES NORTH OF E. INMAN PARKWAY AND APPROXIMATELY 35 FEET EAST OF PRAIRIE AVENUE ON EASEMENT.
2025-03-31 10:13 | NO | YES | NO | 20200047 | 33972 | 2020-05-13 15:35 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2020-03-12 09:30 |  |  | 2020 | 1713 CRESTDALE DRIVE | CHARLOTTE | MECKLENBURG | NC | 28216 | 35.2694 | -80.8474 | [9 empty] | 2020-03-12 19:57 | 1273376 |  | NATURAL GAS |  | 0.01 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-03-12 12:24 |  |  |  | 2020-03-12 12:44 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 14 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | PUNCTURE WAS THE SIZE OF A PINHOLE. PINHOLE IS TOO SMALL TO DETERMINE THE SIZE. | CLASS 3 LOCATION | 0 | 0 | 209962 | 234403.191466947501562 | 0 | 0 | 0 | 0 |  |  | 0 | 0 |  | 0 | 209962 | 97082.77183741545112 | 234403.191466947501562 | 0 | 0 | 0 |  |  |  |  | 150 | 150 | 150 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | ROAD WORK | NO | [5 empty] | NO |  | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 7047314680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 7047314618 | farris.berry@duke-energy.com | WHILE ROAD WORK WAS BEING DONE AROUND A 14" MAIN BY A SOFT DIG CREW IN A CUL-DE-SAC, A GAS ODOR WAS DETECTED. A CREW BEGIN DRILLING HOLES IN THE ASPHALT TO PINPOINT WHERE THE LEAK WAS COMING FROM. A PINHOLE SIZE LEAK WAS FOUND IN THE STEEL GAS LINE AND WAS HIT BY A BORE. THE USE OF MECHANIZED EQUIPMENT IN THE TOLERANCE ZONE & EXCAVATOR FAILED TO SUPPORT AND PROTECT FACILITIES.
2025-03-31 10:13 | NO | NO | NO | 20200048 | 34093 | 2020-05-14 16:32 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2020-04-14 13:00 |  |  | 2020 | 209TH W. AVE. AND W. ARCHER ST. | SAND SPRINGS | TULSA | OK | 74063 | 36.1615 | -96.226 | [9 empty] | 2020-04-15 09:45 | 1275436 |  | NATURAL GAS |  | 193.64 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-04-14 13:12 |  |  |  | 2020-04-14 14:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1968 | [5 empty] | 6.625 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.18 | [6 empty] | MECHANICAL PUNCTURE | 6 | 7 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 13190 | 14725.41743481695519 | 72182 | 80584.539899920959782 | 0 | 0 |  |  | 505 | 628.673469387755102040816326530612244898 |  | 0 | 85877 | 40056.0856205080111165014577259475218659 | 95938.6308041256700740408163265306122449 | 6 | 0 | 554 |  |  |  |  | 10 | 38 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | UTILITY | GRADER/SCRAPER | ELECTRIC | YES | 20040310061015 |  |  | CONTRACT LOCATOR | NO | YES | 56 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | SETH SLIFER | SR. COMPLIANCE SPECIALIST | seth.slifer@onegas.com | 4052487018 |  |  |  |  | MEGHAN BOOKER | DIRECTOR OF ENGINEERING | 4052390573 | meghan.booker@onegas.com | ON APRIL 14, 2020, UTILITY LINE CONSTRUCTION ELECTRIC COMPANY DAMAGED ONG'S 6" MAIN WHILE BUILDING A PAD WITH A BULLDOZER FOR A CRANE. THE 3RD PARTY ELECTRICAL CONTRACTOR WAS INSTALLING NEW STEEL ELECTRIC POLES. THE DAMAGE RESULTED IN AN OUTAGE TO 554 RESIDENTIAL CUSTOMERS. REPAIRS COMPLETE AND SERVICE RESTORED TO MOST CUSTOMERS BY 12:00 PM ON APRIL 17, 2020.
2025-03-31 10:13 | NO | NO | NO | 20200049 | 35184 | 2020-05-15 22:24 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2020-05-13 13:30 | CENTRAL | NO | 2020 | 1014 W PIKE ST | GOSHEN | ELKHART | IN | 46526 | 41.5887 | -85.8489 | [6 empty] | YES |  |  | 2020-05-14 15:43 | 1277275 |  | NATURAL GAS |  | 9983.75 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 900 | 2020-05-13 12:00 | YES | OPERATOR | 2020-05-13 12:00 | 2020-05-13 12:05 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1961 | UNKNOWN |  |  |  |  | 8 | API 5L PSL2 X42 | UNKNOWN | STEEL |  | OTHER | ERW | 0.219 | [6 empty] | LEAK |  |  | OTHER | STOPPLE EQUIPMENT FAILURE | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 23000 | 25677.376876481423 | 10000 | 11164.07690281801 | 10000 | 11164.07690281801 | OUTSIDE SERVICES COST | 2.11 | 21066 | 26225.0204081632653061224489795918367347 | 0 | 0 | 64066 | 44142.1303581442251895043731778425655977 | 74230.5510902807083061224489795918367347 | 0 | 0 | 4 | 0 | 0 | 100 | 15 | 190 | 190 | 200 | 192.619(A)(2) | 1961-11-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | STOPPLE EQUIPMENT FAILED WHILE EMPLOYEES WERE ONSITE. | [12 empty] | NO |  |  | YES | 2 | 0 | INCORRECT OPERATION | WRONG EQUIPMENT SPECIFIED OR INSTALLED | INCORRECT OPERATION | INCORRECT EQUIPMENT | INCORRECT OPERATION | INCORRECT EQUIPMENT | [222 empty] | WRONG EQUIPMENT SPECIFIED OR INSTALLED |  | YES |  | YES |  |  | DECOMMISSIONING | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [45 empty] | YES |  |  |  | RICK SMITH | MANAGER OF GAS OPERATIONS COMPLIANCE | ricksmith@nisource.com | 2192524057 |  | RICK SMITH | ricksmith@nisource.com | 2192524057 | RICK SMITH | MANAGER OF GAS OPERATIONS COMPLIANCE | 2192524057 | ricksmith@nisource.com | WHILE STOPPING THE DEAD END OF A PIPELINE FOR SCHEDULED WORK, TDW SHORTSTOPP II PLUGGING SYSTEM FAILED, CAUSING A RELEASE OF GAS. THERE WERE NO INJURIES, FATALITIES, OR PROPERTY DAMAGE AS A RESULT OF THE RELEASE OF GAS. THE FIRE DEPARTMENT EVACUATED APPROXIMATELY 900 RESIDENTS ON A VOLUNTARY BASIS. I WILL BE PROVIDING UPDATES EVERY 30 DAYS. 6/12/2020 UPDATE: AT THIS TIME, THE INVESTIGATION INTO THIS INCIDENT IS STILL ONGOING. I WILL PROVIDE AN UPDATE IN 30 DAYS OR ONCE ALL THE FACTS ARE KNOWN, WHICHEVER COMES FIRST. 7/13/2020 UPDATE: AT THIS TIME, THE INVESTIGATION INTO THIS INCIDENT IS STILL ONGOING. WE ARE EXPECTING INITIAL RESULTS FROM A 3RD PARTY TESTING FACILITY WITHIN THE NEXT 14 DAYS. I WILL PROVIDE AN UPDATE IN 30 DAYS OR ONCE ALL THE FACTS ARE KNOWN, WHICHEVER COMES FIRST. 8/13/2020 UPDATE: AT THIS TIME, WE HAVE RECEIVED RESULTS FROM A 3RD PARTY VENDOR AND ARE IN THE FINAL STAGES OF THE INVESTIGATION. I WILL PROVIDE AN UPDATE IN 30 DAYS OR ONCE ALL THE FACTS OR KNOWN, WHICHEVER COMES FIRST. 4/16/2021 FINAL UPDATE: THE WRONG TOOLING WAS SELECTED FOR THE PURPOSES OF THE JOB. THE STOPPLE EQUIPMENT USED WAS RATED FOR 150 PSI AND THE PIPE WAS OPERATING AT 190 PSI. THIS WAS A RESULT OF CONFUSING LANGUAGE IN THE MANUFACTURES EQUIPMENT LISTING TABLE , HUMAN ERROR, AND GAPS IN A TOOL SELECTION PROCESS.
2025-03-31 10:13 | NO | YES | NO | 20200050 | 34820 | 2020-05-18 18:26 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2020-04-18 12:30 | CENTRAL | NO | 2020 | 3051 E. MAYFIELD & WATSON RD (HWY 360) | GRAND PRAIRIE | TARRANT | TX | 75052-7330 | 32.6915 | -97.0611 | YES |  |  |  |  | YES |  |  |  | 2020-04-18 13:02 | 1275628 |  | NATURAL GAS |  | 3140.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-04-18 10:53 | ALLOWED TO BURN OUT |  | 2643.1 | NO | 0 | 2020-04-18 10:53 |  |  |  | 2020-04-18 12:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 45 | NO | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1977 | [5 empty] | 6 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 18.8 | 2 |  | CLASS 3 LOCATION | 175867 | 196339.271266789496467 | 38000 | 42423.492230708438 | 14133 | 15778.189886752693533 | 32336 | 36100.159072952317136 | FIRE DEPARTMENT HAZMAT RESPONSE. | 3.85 | 12091 | 15052.0612244897959183673469387755102041 | 0 | 0 | 272427 | 134298.869961273130928513119533527696793 | 305693.1736816927410543673469387755102041 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 31 | 35 | 50 | 192.619(A)(2) | 1977-09-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 1977 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [7 empty] | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | BRUCE MISERENDINO | OPERATIONS SUPERVISOR | bruce.miserendino@atmosenergy.com | 214-206-2387 |  | BRUCE MISERENDINO | bruce.miserendino@atmosenergy.com | 214-206-2387 | MARLO SUTTON | V.P. TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON APRIL 18, 2020, THE GRAND PRAIRIE FIRE DEPARTMENT NOTIFIED ATMOS ENERGY OF A NATURAL GAS LEAK IN FRONT OF 3051 E. MAYFIELD IN GRAND PRAIRIE, TEXAS. THE FIRE DEPARTMENT SECURED THE SCENE AND CLOSED OFF TRAFFIC NEAR THE LEAK. WHILE ATMOS CREWS WERE EN ROUTE, A VEHICLE ENTERED THE SECURED AREA AND PARKED OVER THE LEAK RESULTING IN AN IGNITION OF THE GAS. THE GRAND PRAIRIE POLICE DEPARTMENT MOVED THE VEHICLE AWAY FROM THE LEAK. THE CITY OF GRAND PRAIRIE EMERGENCY MANAGEMENT CONDUCTED EVACUATIONS VIA TEXT AND EMAIL AND THEREFORE IS UNABLE TO PROVIDE AN ESTIMATE OF THE NUMBER OF GENERAL PUBLIC EVACUATED. A CURRENT ESTIMATE OF THIRD PARTY PROPERTY DAMAGE AND OPERATOR COSTS HAS BEEN INCLUDED IN PART D. HOWEVER, ALL COSTS ASSOCIATED WITH THIS INCIDENT ARE STILL IN THE PROCESS OF BEING COMPILED. ATMOS ENERGY CREWS BEGAN WORK TO ISOLATE AND REPAIR THE LEAK. THE LEAK WAS SECURED AT 6:30 PM AND THE PIPELINE WAS PLACED BACK IN SERVICE AT 4:00 PM ON MONDAY, APRIL 20, 2020. 48-HOUR UPDATE NRC# 1275699.
2025-03-31 10:13 | NO | YES | NO | 20200052 | 34663 | 2020-05-29 15:30 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2020-04-29 09:40 | EASTERN | NO | 2020 | 111 JEFFERSON STREET | ROBINSON | INDIANA | PA | 15949 | 40.3995 | -79.1459 | YES | [8 empty] | 2020-04-30 16:58 | 1276429 |  | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-04-29 09:40 | YES | OPERATOR | 2020-04-29 12:05 | 2020-04-29 09:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1981 | UNKNOWN | [7 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | OVER PRESSURIZATION. NO RELEASE OF GAS. | CLASS 2 LOCATION | 47958 | 53540.680010534612358 | 0 | 0 | 101840 | 113694.95917829861384 | 0 | 0 |  | 7.7621 | 0 | 0 | 0 | 0 | 149798 | 69263.98612940036648 | 167235.639188833226198 | 2 | 0 | 219 | 0 | 0 | 219 | 2 | 1.63 | 0.5 | 1 | 192.623 | 2015-11-23 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | INJECTION PUMP |  | 0.7 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | NO |  |  | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [222 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED |  |  |  | YES |  |  | ROUTINE MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | DANIEL P. KUEHN | MANAGER PROCESS WORK MANAGEMENT | daniel.kuehn@peoples-gas.com | 724-444-3251 |  | DANIEL P. KUEHN | daniel.kuehn@peoples-gas.com | 724-444-3251 | JOSEPH A. GREGORINI | SR. VICE PRESIDENT RATES - REGULATORY AFFAIRS | 412-208-7905 | joseph.a.gregorini@peoples-gas.com | DURING A ROUTINE ANNUAL INSPECTION OF DISTRICT REGULATOR STATION LS-260, PEOPLES EMPLOYEES NEEDED TO ISOLATE THE REGULATOR FROM THE SYSTEM IN ORDER TO INSPECT IT. IN ORDER TO ISOLATE THAT REGULATOR, THE STATION BY-PASS NEEDS TO BE MANUALLY OPERATED TO MAINTAIN OUTLET PRESSURE. THE EMPLOYEES PLACED A GAUGE ON THE RELIEF VALVE PIPING, WHICH WAS UPSTREAM AND NOW ISOLATED FROM THE OUTLET/DOWNSTREAM PIPING. WHILE MANUALLY OPERATING THE STATION'S BY-PASS THEY WERE UNABLE TO MONITOR THE OUTLET PRESSURE, RESULTING IN AN OVER PRESSURIZATION OF THE DOWNSTREAM SYSTEM IN THE TOWN OF ROBINSON, PA. SUPPLEMENTAL QUESTION ASKED BY NRC: WERE THE EMPLOYEES INVOLVED WITH THIS INCIDENT RE-QUALIFIED ON THE TASKS THAT LED TO THE OVER PRESSURIZATION? ON APRIL 29, 2020, THERE WERE THREE EMPLOYEES ON SITE PERFORMING THE ANNUAL INSPECTION OF DISTRICT REGULATOR STATION LS-260, ROBINSON, PA WHEN THE OVER PRESSURIZATION OCCURRED. ALL THREE INDIVIDUALS WERE RE-QUALIFIED ON JUNE 23, 2020 ON THE TASKS THAT LED TO THAT OVER PRESSURIZATION. DURING THE TIME PERIOD FROM 4/29/2020 UNTIL THEIR RE-QUALIFICATION ON 6/23/2020, NONE OF THESE INDIVIDUALS WERE PERMITTED TO PERFORM ANNUAL DISTRICT REGULATOR INSPECTIONS INDEPENDENTLY, BUT WERE ASSIGNED TO WORK WITH SENIOR DISTRICT REGULATOR OQ CERTIFIED SPECIALISTS.
2025-03-31 10:13 | NO | NO | NO | 20200053 | 34121 | 2020-06-05 12:33 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2020-05-08 10:53 |  |  | 2020 | 8424 SANTA MONICA BLVD | WEST HOLLYWOOD | LOS ANGELES | CA | 90069 | 34.0904 | -118.3744 | [9 empty] | 2020-05-08 22:03 | 1276942 |  | NATURAL GAS |  | 24.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-05-08 10:53 |  |  |  | 2020-05-08 11:19 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 45 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1983 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS | SEAMLESS | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 0.3 | 0.3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 3000 | 3349.223070845403 | 53900 | 60174.3745061890739 | 0 | 0 |  |  | 145 | 180.510204081632653061224489795918367347 |  | 0 | 57045 | 26476.5514652378737376093294460641399417 | 63704.1077811161095530612244897959183673 | 0 | 0 | 0 |  |  |  |  | 35 | 35 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | A201040862 | DIGALERT |  | UTILITY OWNER | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | amatin@socalgas.com | 909-919-0463 |  |  |  |  | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-919-0463 | amatin@socalgas.com | ON MAY 8, 2020, A THIRD-PARTY CONTRACTOR DAMAGED A 6-INCH STEEL GAS MAIN WHILE BORING TO INSTALL CONDUIT. SOCALGAS CREWS RESPONDED AND CONTROLLED THE GAS WITH PRESSURE CONTROL EQUIPMENT. THERE WERE NO INJURIES OR FURTHER DAMAGE RESULTING FROM THIS INCIDENT. THE 6-INCH MAIN WAS REPAIRED BY WELDING A WEDDING BAND. INVESTIGATION OF THE INCIDENT SHOWED THAT THERE WAS A VALID USA TICKET, HOWEVER, THE 6-INCH MAIN WAS NOT MARKED OUT BY THE LOCATOR. TICKET HAD BEEN LEFT OPEN IN "PROJECT" STATUS BY THE LOCATOR TO RETURN ON A LATER DATE TO COMPLETE. THE LOCATOR DID NOT ADDRESS THE TICKET BEFORE THE DUE DATE UPON HIS RETURN TO WORK FROM HIS TIME OFF (7 DAYS). THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE AND ESTIMATED PROPERTY DAMAGE OF $50,000 OR MORE. FOR ANY FURTHER QUESTIONS, CONTACT ALI MATIN AT (909) 919-0463.
2025-03-31 10:13 | NO | YES | NO | 20200054 | 33866 | 2020-06-05 14:35 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2020-05-05 10:50 |  |  | 2020 | 13086 AVENUE 384 | CUTLER | TULARE | CA | 93615 | 36.4867 | -119.2803 | [9 empty] | 2020-05-07 17:57 | 1276850 |  | NATURAL GAS |  | 503 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-05-05 10:50 |  |  |  | 2020-05-05 10:50 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 28 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1940 | [5 empty] | 4 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.178 | [6 empty] | OTHER | [8 empty] | 0.500" HOLE IN 4" MAIN DUE TO MECHANICAL DAMAGE. | CLASS 1 LOCATION | 0 | 0 | 10540 | 11766.93705557018254 | 90708 | 101267.108770081605108 | 0 | 0 |  |  | 3018 | 3757.102040816326530612244897959183673469 |  | 0 | 104266 | 50290.8510959370515703790087463556851312 | 116791.1478664681141786122448979591836735 | 0 | 0 | 0 |  |  |  |  | 170 | 170 | 175 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR (FIRST PARTY) | [14 empty] | NO | YES | STATE HIGHWAY | [12 empty] | UTILITY | BACKHOE/TRACKHOE | NATURAL GAS | YES | X012200988 | USA NORTH |  | UTILITY OWNER | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | amatin@socalgas.com | 909-919-0463 |  |  |  |  | ALI MATIN | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 909-919-0463 | amatin@socalgas.com | ON MAY 5, 2020, SOCALGAS CREW WAS WORKING ON A SERVICE ABANDONMENT JOB AND DAMAGED A 1-INCH SERVICE TEE WITH A BACKHOE. THE SERVICE WAS FED FROM A 4-INCH STEEL HIGH PRESSURE MAIN. GAS WAS CONTROLLED BY COLD PINCHING THE 4-INCH HIGH PRESSURE STEEL MAIN AT TWO LOCATIONS TO THE EAST AND WEST OF THE DAMAGE. THERE WERE NO INJURIES OR FURTHER DAMAGE RESULTING FROM THIS INCIDENT. THE 4-INCH MAIN WAS REPAIRED BY WELDING ON PRESSURE CONTROL FITTINGS, STOPPING THE MAIN WITH PRESSURE CONTROL EQUIPMENT, CUTTING OUT THE COLD SQUEEZES, AND REPLACING A SECTION OF THE PIPE. INVESTIGATION OF THE INCIDENT SHOWED THAT THERE WAS A VALID USA TICKET AND THE 4-INCH MAIN WAS PROPERLY MARKED. SOCALGAS CREW FAILED TO USE HAND TOOLS WHERE REQUIRED. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE AND ESTIMATED PROPERTY DAMAGE OF $50,000 OR MORE. FOR ANY FURTHER QUESTIONS, CONTACT ALI MATIN AT (909) 919-0463.
2025-03-31 10:13 | NO | NO | NO | 20200055 | 34403 | 2020-06-09 15:17 | SUPPLEMENTAL FINAL | 14210 | OKLAHOMA NATURAL GAS COMPANY, A DIVISION OF ONE GAS, INC. | 401 N. HARVEY AVE | OKLAHOMA CITY | OK | 73102 | 2020-05-12 18:05 |  |  | 2020 | SW 19TH AND PENNSYLVANIA AVE. | OKLAHOMA CITY | OKLAHOMA | OK | 73108 | 35.4468 | -97.548 | [9 empty] | 2020-05-12 22:40 | 1277133 |  | NATURAL GAS |  | 1673.43 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 7 | 2020-05-12 18:05 |  |  |  | 2020-05-12 18:20 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 204 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1965 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 2246 | 2507.451672372925046 | 69736 | 77853.806689491674536 | 0 | 0 |  |  | 4535 | 5645.612244897959183673469387755102040816 |  | 0 | 76517 | 38505.7449367345991479883381924198250729 | 86006.8706067625587656734693877551020408 | 0 | 0 | 541 |  |  |  |  | 48 | 48 | 54 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | DRAINAGE | YES | 20042014533512 |  |  | CONTRACT LOCATOR | NO | YES | 31 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | SETH SLIFER | SR. COMPLIANCE SPECIALIST | seth.slifer@onegas.com | 4053139363 |  |  |  |  | MEGHAN BOOKER | DIRECTOR OF ENGINEERING | 405-239-0573 | meghan.booker@onegas.com | YOUNG'S CONTRACTING WAS PERFORMING WORK FOR THE CITY OF OKLAHOMA CITY AND STRUCK ONG'S 2" SERVICE THAT THEREBY DAMAGED ONG'S 8" CS MAIN WHILE INSTALLING A CONCRETE CHANNEL FOR DRAINAGE. THE LOCATE TICKET WAS OUT OF COMPLIANCE AND EXPIRED. THE DAMAGE RESULTED IN AN OUTAGE OF 541 CUSTOMERS. REPAIRS COMPLETE AND SERVICE RESTORED TO CUSTOMERS BY 6:15 AM ON 5/14/20. AS A RESULT OF THIS INCIDENT, ONG WILL REBUILD THE 8" CS MAIN AND NOT REINSTALL THE 2" BRANCH SERVICE.
2025-03-31 10:13 | NO | YES | NO | 20200056 | 34317 | 2020-06-11 16:53 | SUPPLEMENTAL FINAL | 31636 | NORTHERN STATES POWER CO OF MINNESOTA | 414 NICOLLET MALL | MINNEAPOLIS | MN | 55402 | 2020-05-11 17:00 |  |  | 2020 | VALLEY CREEK DRIVE AND TOWER DRIVE | WOODBURY | WASHINGTON | MN | 55125 | 44.92 | -92.9442 | [9 empty] | 2020-05-11 17:00 | 1277068 |  | NATURAL GAS |  | 1405 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-05-08 15:13 |  |  |  | 2020-05-08 15:25 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 300 |  | YES |  |  |  |  | YES | BORED/DRILLED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2018 | [5 empty] | 12 | API 5L | TENARIS | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY | HIGH FREQUENCY WELD | 0.375 | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 50000 | 55820.38451409005 | 1500000 | 1674611.5354227015 | 3737 | 4172.015538583090337 | 0 | 0 |  |  | 3204 | 3988.653061224489795918367346938775510204 |  | 0 | 1556941 | 722110.6645692096661841399416909620991254 | 1738592.58853659913013291836734693877551 | 0 | 0 | 0 |  |  |  |  | 196 | 200 | 220 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | YES | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE WAS CAUSED BY 3RD PARTY EXCAVATOR | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | YES | [7 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | WATER | YES | 201135196 |  |  | CONTRACT LOCATOR | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO UNLOCATABLE FACILITY | [170 empty] | LISA KALLBERG | PRINCIPAL CONSULTANT GAS STANDARDS | elisabeth.m.kallberg@xcelenergy.com | 651-229-2282 |  |  |  |  | CHRISTOPHER AKINS | MANAGER GAS STANDARDS | 303-571-3298 | christopher.a.akins@xcelenergy.com | ON MAY 8, 2020, NORTHERN STATES POWER COMPANY, MINNESOTA (NSPM) WAS NOTIFIED REGARDING A BLOWING GAS SITUATION. THE INVESTIGATION REVEALED THAT AN ABANDONED SIX INCH STEEL, COAL TAR COATING PIPELINE WAS LOCATED. AN EXISTING 12 INCH STEEL FBE COATED HIGH PRESSURE DISTRIBUTION LINE WAS NOT LOCATED. REVIEW OF THE BORE PROFILE DETERMINED THE 12 INCH MAIN THAT WAS INSTALLED IN 2018 WAS APPROXIMATELY 25 FEET AT THE POINT OF DAMAGE. NSPM ATTEMPTED TO EXCAVATE THE MAIN AT THE POINT OF DAMAGED AND LATER DETERMINED DUE TO DEPTH, IT WAS SAFER TO NOT EXPOSE THE MAIN AT THE POINT OF DAMAGE AND INSTALL APPROXIMATELY 1100 FEET OF NEW 12 INCH STEEL. ESTIMATED GAS LOSS WAS CALCULATED FROM SCADA DATA AT THE TIME OF THE DAMAGE. POINT OF DAMAGE WAS NOT EXPOSED SO SIZE OF PUNCTURE IS NOT KNOWN FOR PART D: QUESTION 2.D REVIEW OF EXISTING DAMAGE PREVENTION PROCESSES WAS CONDUCTED AND FOUND THAT THE INDIVIDUAL RESPONSIBLE FOR VERIFYING THE SIZE AND TYPE OF PIPE THAT WAS EXPOSED DID NOT FOLLOW THOSE PROCESSES.
2025-03-31 10:13 | NO | YES | YES | 20200057 | 34645 | 2020-06-18 11:49 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2020-05-28 14:03 | CENTRAL | YES | 2020 | 401 WEST MCNEESE ST | LAKE CHARLES | CALCASIEU | LA | 70605 | 30.1759 | -93.2244 | [5 empty] | YES |  |  |  | 2020-05-28 15:10 | 1278310 | 1278572 | NATURAL GAS |  | 11 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2020-05-28 13:42 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 11 | NO | 0 | 2020-05-28 14:15 |  |  |  | 2020-05-28 14:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2012 |  | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | NIPPLE ABOVE STOPCOCK SHEARED. | [5 empty] | CLASS 3 LOCATION | 72000 | 80381.353700289672 | 1200 | 1339.6892283381612 | 615 | 686.590729523307615 | 0 | 0 |  | 3.5455 | 39 | 48.55102040816326530612244897959183673469 | 0 | 0 | 73854 | 34175.6828814523480880466472303206997085 | 82456.1846785593040803061224489795918367 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 26 | 26 | 60 | 192.619(A)(1) | 2012-04-16 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | NO | UNKNOWN | PASSENGER CAR | ROADWAY | 50 | NO | [142 empty] | JAMES TODD HEBERT | OPERATIONS SPECIALIST | james.hebert@centerpointenergy.com | 337-256-2161 | 337-373-1520 |  |  |  | SCOTT FAULK | REGIONAL OPERATIONS DIRECTOR | 337-373-1518 | scott.faulk@centerpointenergy.com | VEHICLE LEFT THE ROADWAY AND MADE IMPACT TO CENTERPOINT ENERGY FACILITY AND CUSTOMERS HOME, WHICH RESULTED IN GAS LEAKAGE, IGNITION AND DRIVER FATALITY. CENTERPOINT ENERGY WAS NOTIFIED, TECHNICIAN RESPONDED AND SQUEEZED 1" SERVICE LINE TO SECURE LEAK. FIRE WAS THEN EXTINGUISHED BY FIRE DEPT. UPON INVESTIGATION BY TECHNICIAN IT WAS DETERMINED THAT THE NIPPLE ABOVE THE STOPCOCK HAD BEEN SHEARED BY THE VEHICULAR IMPACT. PER CITY OF LAKE CHARLES POLICE REPORT #2005280378, SEVERAL WITNESSES STATED THAT THE VEHICLE WAS DRIVING AT A HIGH RATE OF SPEED, SWERVING IN AND OUT OF TRAFFIC PASSING OTHER VEHICLES PRIOR TO INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20200058 | 34698 | 2020-06-18 15:31 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-05-19 22:41 | EASTERN | YES | 2020 | M-30 HIGHWAY AND CEDAR STREET | EDENVILLE TOWNSHIP | MIDLAND | MI | 48628 | 43.8058 | -84.3861 | [5 empty] | YES | YES |  |  | 2020-05-21 20:02 | 1277809 | 1277853 | NATURAL GAS |  | 447 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-05-19 22:41 |  |  |  | 2020-05-19 22:16 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | NO | YES | YES | UNCASED | [9 empty] | PRIVATELY OWNED |  | MAIN |  | 1968 | [5 empty] | 4 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | SEVERED-EROSION/DEBRIS | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 3965252 | 4426837.826705291978852 | 996 | 1111.942059520673796 | 0 | 0 |  | 2 | 894 | 1112.938775510204081632653061224489795918 | 0 | 0 | 3967142 | 1834953.52755807066148291545189504373178 | 4429062.7075403228567296326530612244898 | 26 | 0 | 450 | 0 | 0 | 450 | 26 | 55 | 55 | 60 | 192.619(A)(2) | 1968-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | WASHOUTS/SCOURING |  |  |  | YES |  |  |  | YES | CONSIDERABLE RAINFALL OVER MULTIPLE DAYS CAUSED A LEVEE BREACH RESULTING IN SIGNIFICANT FLOODING IN MID-MICHIGAN AREA. | [213 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 4192905737 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON MONDAY, MAY 19, 2020 AT APPROXIMATELY 22:41HOURS CONSUMERS ENERGY (CE) WAS NOTIFIED OF AN ODOR OF GAS NEAR M-30 HIGHWAY AND CEDAR ROAD, EDENVILLE TOWNSHIP, MICHIGAN. A DISTRIBUTION CREW WAS DISPATCHED AND ARRIVED ON-SITE AT APPROXIMATELY 23:16 HOURS. DUE TO EXTREME WEATHER CONDITIONS AND FLOODING IN THE AREA, CE PERSONNEL WAS STAGED THROUGHOUT THE AREA TO ASSESS NATURAL GAS FACILITIES AND RESPOND TO GAS EMERGENCIES. AN INVESTIGATION CONFIRMED A 4" STEEL MP PIPELINE DAMAGED. THE PIPELINE WAS SEVERED WHEN SIGNIFICANT FLOODING IN THE AREA CAUSED A ROAD WASH-OUT. A MUELLER FITTING WAS INSTALLED TO CONTAIN THE BLOWING GAS. BECAUSE THE PIPELINE WAS A ONE FEED, A LOSS OF SERVICE TO APPROXIMATELY 360 CUSTOMERS OCCURRED. A PLAN WAS DEVELOPED TO UTILIZE COMPRESSES NATURAL GAS (CNG) TO PROVIDE TEMPORARY SERVICE TO THE MAJORITY OF THE IMPACTED CUSTOMERS UNTIL A PERMANENT PLAN COULD BE COORDINATED WITH THE GLADWIN AND MIDLAND COUNTY ROADWAY COMMISSIONS. ON JUNE 16, 2020 SERVICE WAS REINSTATED TO THE MAJORITY OF IMPACTED CUSTOMERS BY COMPLETING THE INSTALLATION OF APPROXIMATELY 6.25 MILES OF NEW GAS DISTRIBUTION MAIN. ADDITIONAL MAIN INSTALLATION IS NEEDED TO REINSTATE THE REMAINING CUSTOMERS (APPROXIMATELY EIGHT CUSTOMER REMAINING). THE ANTICIPATED COMPLETION DATE IS JULY, 15, 2020. THE PIPELINE CONSTRUCTION NECESSARY TO SERVE THE REMAINING EIGHT CUSTOMERS WAS COMPLETED ON JULY 24, 2020.
2025-03-31 10:13 | NO | YES | NO | 20200059 | 33931 | 2020-06-21 09:10 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2020-05-22 11:35 |  |  | 2020 | 102 ANGELA COURT | WOODSTOCK | CHEROKEE | GA | 30311 | 34.1099 | -84.5245 | [9 empty] | 2020-05-22 20:06 | 1277906 |  | NATURAL GAS |  | 796 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 3 | 2020-05-22 11:37 |  |  |  | 2020-05-22 11:50 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2017 | [5 empty] | 4 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2708 | MECHANICAL PUNCTURE | 2.2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 69000 | 77032.130629444269 | 34000 | 37957.861469581234 | 0 | 0 |  |  | 4909 | 6111.204081632653061224489795918367346939 |  | 0 | 107909 | 53278.6275966423033236151603498542274052 | 121101.1961806581560612244897959183673469 | 0 | 0 | 355 |  |  |  |  | 50 | 50 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | STORM DRAIN/CULVERT | YES | 05150259025 |  |  | CONTRACT LOCATOR | NO | YES | 6 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A 4-INCH PLASTIC NATURAL GAS MAIN WAS RUPTURED BY A BACKHOE WHILE A CONTRACT CREW WAS INSTALLING A STORM DRAINAGE SYSTEM. ONCE THE INCIDENT WAS MADE SAFE IT WAS IDENTIFIED THAT NATURAL GAS SERVICE WAS LOSS TO APPROXIMATELY 355 CUSTOMERS AND COSTS ASSOCIATED WITH THE INCIDENT WOULD EXCEED THE $50,000 THRESHOLD FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. NOTIFICATION TO THE ONE-CALL CENTER WAS MADE, HOWEVER, IT APPEARS THE FACILITY WAS NOT LOCATED PROPERLY. ADDITIONAL NRC REPORT NUMBER 1278001 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2025-03-31 10:13 | NO | NO | NO | 20200060 | 34034 | 2020-06-26 14:06 | SUPPLEMENTAL FINAL | 13635 | NORTHEAST OHIO NATURAL GAS CORP | 5640 LANCASTER NEWARK RD NE | PLEASANTVILLE | OH | 43148 | 2020-05-29 11:26 |  |  | 2020 | 9347 SR 45 | BLOOMFIELD TOWNSHIP | TRUMBULL | OH | 44450 | 41.2836 | -80.5277 | [9 empty] | 2020-05-29 11:26 | 1278361 |  | NATURAL GAS |  | 97 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 1 | 2020-05-29 06:11 |  |  |  | 2020-05-29 06:45 |  | NO | PRIVATE PROPERTY | TRANSITION AREA | SOIL/AIR INTERFACE |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | VEHICLE DAMAGE CAUSED BY AN INTOXICATED DRIVER. | CLASS 3 LOCATION | 0 | 0 | 12439 | 13886.995259415322639 | 9653 | 10776.683434290225053 | 0 | 0 | NA |  | 473 | 588.836734693877551020408163265306122449 |  | 0 | 22565 | 10759.6644727193655468221574344023323615 | 25252.5154283994252430204081632653061224 | 0 | 1 | 1 |  |  |  |  | 200 | 200 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | KELLI ALBANESE | PIPELINE SAFETY COMPLIANCE MANAGER | kalbanese@egas.net | 740-400-4314 | 740-862-6330 |  |  |  | KELLI ALBANESE | PIPELINE SAFETY COMPLIANCE MANAGER | 6149805858 | kalbanese@egas.net | FRIDAY, MAY 29, 2020 6:11 AM RECEIVED A CALL FROM OUR AFTER HOURS CALL SERVICER ABOUT DAMAGE FROM A VEHICLE ACCIDENT THAT RESULTED IN BLOWING GAS. 6:45 ARRIVE ON SCENE TO FIND A FARM TAP IN PIECES AN BLOWING GAS AND THAT ST RT 45 IS CLOSED TO THRU TRAFFIC. BOTH TRUMBULL COUNTY SHERIFF AND OHIO STATE HIGHWAY PATROL ARE ON SCENE. HE FOUND OUT THAT THE HOMEOWNER HAD SHUT THE BLOWING VALVE ON THE 1" STEEL RISER BUT COULD STILL HEAR GAS BLOWING. 6:55 SECOND EMPLOYEE ARRIVES ON SCENE. IDENTIFIES THAT THE DAMAGE IS TO THE TAP FEEDING A FARM TAP THAT IS ON OUR LINE KNOWN AS MCFLOW, A 3" COATED STEEL MAINLINE HE IDENTIFIES THE VALVE TO THE SOUTH AT THE BLOOMFIELD TBS AND TO THE NORTH, HANIES RD. AND FLAGG RD. AS THE VALVES NEEDED TO ISOLATE THE DAMAGED TAP. 7:15 THE OCCUPANTS OF 9347 PAINESVILLE HAVE LEFT THE PROPERTY. 8:30 THE TAP IS EXPOSED AND WE CAN SEE THE SIZE OF THE CRACK IN THE RISER. 12:15 PM GAS HAS STOPPED BLOWING AT DAMAGED TAP. WHILE THIS IS ALL GOING ON BUCKEYE PIPELINE IS CONTACTED AND IS REQUESTED TO SEND A WELDER AND CREW TO ASSIST IN THE REPAIR. 1:15 PM CONTRACT CONSTRUCTION PERSONNEL START ARRIVING ON SCENE. AN ATTEMPT IS MADE TO TURN IN THE TAP CUTTER HEAD WITH THE IDEA OF SEALING UP THE TAP. BUT THE HOLE IN THE MAINLINE THAT IS NORMALLY MADE WITH THE TAP CUTTING HEAD WAS BURNED IN BY A TORCH AT THE TIME THE MAINLINE WAS BUILT AND THEREFORE IT WAS LARGER THAN THE CUTTING HEAD AND WOULD NOT LINE UP AND SEAL. ULTIMATELY IT WAS DECIDED THAT ADDITIONAL MATERIAL WOULD BE NEEDED TO CUT OUT THE TAP AND REPLACE A SECTION OF MAINLINE. THE RISER WAS SEALED WITH A PLUG AND THE TAP CAP WAS SEALED, THE EXCAVATION WAS BACKFILLED FOR THE NIGHT TO BE CONTINUED IN THE MORNING WITH THE FINAL REPAIR. SATURDAY, MAY 30, 2020 7:00 THE SECTION OF PIPE BETWEEN THE BLOOMFIELD TBS TO THE SOUTH AND FLAGG ROAD TBS TO THE WEST AND PVP / PENNIMAN RD. TO THE EAST IS BLOWN DOWN TO PREPARE FOR THE TAP REPAIR. 7:30 AM BUCKEYE PIPELINE BEGINS WELDING ON FOUR TAPS, TWO ON EITHER SIDE OF THE DAMAGED TAP TO BE USED AS AIR MOVERS. A 15' PIECE OF THE 3" MAIN CONTAINING THE TAP IS CUT OUT AND IS REPLACED. TAPS ARE TURNED IN AND SEALED. THE VALVE AT THE BLOOMFIELD STATION IS CRACKED OPEN SO THE SECTION OF MAINLINE CAN BE PURGED AT THE FLAGG RD. TBS AS WELL AS AT PVP INDUSTRIES. THE WELDS ARE SOAPED TO CHECK FOR LEAKS AND THE ENTIRE SECTION OF PIPE IS COATED AND WRAPPED. 1:00 PM THE DAMAGED SECTION OF MAINLINE IS PUT BACK IN SERVICE.
2025-03-31 10:13 | NO | YES | YES | 20200062 | 34129 | 2020-07-09 10:48 | SUPPLEMENTAL FINAL | 603 | CENTERPOINT ENERGY RESOURCES CORP. | 10825 E GEDDES AVE SUITE 410 | CENTENNIAL | CO | 80112 | 2020-06-18 10:17 |  |  | 2020 | EDGEWOOD DR & WINDWOOD LN | MAUMELLE | PULASKI | AR | 72113 | 34.8664 | -92.4054 | [9 empty] | 2020-06-18 13:25 | 1279885 |  | NATURAL GAS |  | 1177 |  | NO | [5 empty] | 0 | YES | 2 | 0 | 0 | 0 | 0 | 2 | YES |  |  |  |  | NO | 1 | 2020-06-18 10:17 |  |  |  | 2020-06-18 10:22 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 |  | NO | [11 empty] | OTHER | PUBLICLY TRADED LDC | MAIN |  | 1978 | [5 empty] | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2306 | OTHER | [8 empty] | COMPLETE SEPARATION | CLASS 3 LOCATION | 3000 | 3349.223070845403 | 58472 | 65278.590466157468072 | 10208 | 11396.289702396624608 | 0 | 0 |  |  | 4413 | 5493.73469387755102040816326530612244898 |  | 0 | 76093 | 38225.6097699247321935860058309037900875 | 85517.837933277046700408163265306122449 | 0 | 0 | 14 |  |  |  |  | 35 | 35 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 8 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 2006040605 |  |  | CONTRACT LOCATOR | YES | YES | 56 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | VERNON MCNULLY | DISTRICT OPERATIONS MANAGER | vernon.mcnully@centerpointenergy.com | 501-377-4633 |  |  |  |  | KEITH KITTINGER | REGIONAL OPERATIONS DIRECTOR | 501-377-4669 | keith.kittinger@centerpointenergycom | CONTRACTOR INSTALLING COMMUNICATIONS CABLE WAS BORING PERPENDICULAR TO 2 INCH PLASTIC GAS MAIN. EXCAVATOR (SUBCONTRACTOR) DID NOT HAVE A VALID TICKET IN THEIR NAME. ARKUPS (CONTRACT LINE LOCATOR) HAD NOTED THAT FURTHER LOCATE ACTIVITY SHOULD BE PERFORMED ON 2 INCH PLASTIC PRIOR TO EXCAVATION AND LEFT A SIGN AT THE LOCATION TO BE CALLED BEFORE EXCAVATING IN THE AFFECTED AREA. EXCAVATOR (SUBCONTRACTOR) POT-HOLED ON MARKS TO VERIFY THAT GAS LINE WAS LOCATED WHERE MARKS INDICATED, BUT MIS-IDENTIFIED A DIFFERENT CABLE AS GAS PIPING. BORING HEAD DAMAGED PIPE RESULTING IN SEPARATION OF 2 INCH PLASTIC MAIN. CNP REPAIR CREWS WERE EXCAVATING IN REMOTE LOCATION TO ISOLATE SYSTEM AND REPLACE DAMAGED MAIN WHEN IGNITION OCCURRED. ADDITIONAL CNP CREWS WERE CALLED TO THE SITE TO ISOLATE THE SYSTEM AND SHUT OFF GAS FEED TO THE 2 INCH PLASTIC MAIN. THE INVESTIGATION IS ONGOING.
2025-03-31 10:13 | NO | YES | YES | 20200063 | 36851 | 2020-07-13 17:11 | SUPPLEMENTAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2020-06-13 09:30 | EASTERN | NO | 2020 | 1347 COURTLAND DRIVE | RALEIGH | WAKE | NC | 27604 | 35.7995 | -78.6303 | [7 empty] | YES | RAN DOWN TAPPING TEE CUTTER | 2020-06-13 12:52 | 1279507 |  | NATURAL GAS |  | 295.43 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2020-06-13 09:30 | OTHER | NO SUSTAINED FIRE - ONLY AN EXPLOSION. FINDINGS SUGGEST IGNITION OF A DISCRETE AMOUNT GASEOUS FUEL. | 1 | YES | 14 | 2020-06-13 09:30 |  |  |  | 2020-06-13 09:48 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 2020 |  | SINGLE FAMILY RESIDENTIAL | YES | NO | NO | 0.75 | ASTM D2513-12AE1 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2708 | OTHER | [8 empty] | UNDETERMINED WHETHER: THIRD-PARTY DAMAGE, IMPROPER INSTALLATION, OR MATERIAL FAILURE | CLASS 3 LOCATION | 690209 | 770554.635501711586409 | 63136 | 70485.515933631787936 | 0 | 0 | 64257 | 71737.008954437686857 | LABOR/TRANSP ($37,064) & INVESTIGATION (AIR LAB: $4,400; CORE SAMPLE $22,793 | 4.64 | 1371 | 1706.755102040816326530612244897959183673 | 0 | 0 | 818973 | 379623.772810512315245947521865889212828 | 914483.9154918218775285306122448979591837 | 0 | 0 | 3 | 0 | 0 | 5 | 0 | 55 | 55 | 60 | 192.621 M | 2020-01-27 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 4.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | SEE PART H NARRATIVE | [45 empty] | MARK NOAH | MANAGER-GAS OPERATIONS | mark.noah@dominionenergy.com | 414-788-2462 |  | CURTIS RICE | curtis.rice@dominionenergy.com | 919-268-7962 | SCOTT SWINDLER | DIRECTOR - GAS OPERATIONS | 704-810-3230 | scott.swindler@dominionenergy.com | THIS SUPPLEMENTAL AND FINAL REPORT WAS SUBMITTED ON JULY 13, 2022. AT APPROXIMATELY 9:30 AM, ON JUNE 13, 2020, DOMINION ENERGY NORTH CAROLINA RECEIVED A 911-CALL REPORTING AN EXPLOSION AT 1347 COURTLAND DRIVE IN RALEIGH, NC. 911 REPORTED TO DENC THAT AN EXPLOSION OCCURRED IN THE CRAWL SPACE OF THE HOME AT 1347 COURTLAND. DENC CREWS DID NOT OBSERVE ANY FIRE AT THE HOUSE. A CONTRACTOR WORKING FOR THE HOMEOWNER OF 1347 COURTLAND WAS REPORTEDLY INJURED AT THE SCENE WHEN THE EXPLOSION OCCURRED. AT THE TIME OF THE EXPLOSION, THE CONTRACTOR WAS IN THE CRAWL SPACE UNDERNEATH THE HOME PERFORMING WORK ON THE HOMEOWNER'S HVAC SYSTEM. THE CONTRACTOR WAS REPORTEDLY BURNED BY THE EXPLOSION AND TRANSPORTED TO THE LOCAL BURN HOSPITAL. FOUR NEIGHBORING HOMES, ALONG WITH 1347 COURTLAND, WERE ALL EVACUATED (I.E., 1345, 1347, 1349, 1401, 1403 COURTLAND). THE RESIDENTS OF 1401 AND 1403 COURTLAND WERE ALLOWED TO RETURN TO THEIR HOMES WITHIN DAYS OF THE INCIDENT. AS OF AUGUST 2020, THE RESIDENTS OF 1345 AND 1349 COURTLAND HAD RETURNED TO THEIR HOMES. THE HOME AT 1347 COURTLAND SUSTAINED STRUCTURAL DAMAGE AND IS NOT HABITABLE. ON THE DAY OF THE INCIDENT, DENC DISCOVERED A NATURAL GAS LEAK NEAR THE TRANSITION BETWEEN THE STEEL TAPPING TEE AND THE PLASTIC SERVICE LINE THAT SERVED 1345 COURTLAND. THE RESPONDING DENC CREW STOPPED THE LEAK BY RUNNING THE TAPPING TEE CUTTER DOWN. AS A PRECAUTION, THE TAPPING TEE AT 1347 COURTLAND WAS ALSO SHUT OFF BY RUNNING DOWN THE TAPPING TEE PERFORATOR/STOP FOR THE SERVICE LINE. BOTH SERVICES WERE LATER DISCONNECTED, AND STEEL CAPS WERE WELDED ON. SUBSEQUENTLY, DENC EXPOSED THE MAIN IN FRONT OF 1345, 1347 AND 1349 COURTLAND AND VERIFIED THERE WERE NO LEAKS. A PORTION OF THE STEEL TAPPING TEE AND PLASTIC SERVICE LINE TO 1345 COURTLAND WITH THE VERIFIED LEAK WAS REMOVED AND PRESERVED FOR FURTHER TESTING. A LEAK FLOW TEST USING COMPRESSED AIR WAS PERFORMED ON THE SUBJECT PIPE IN A LABORATORY SETTING ON NOVEMBER 5, 2020. AT 60.0 PSI, THE LEAK RATE WAS 66 SCFH OF AIR, WHICH CONVERTS TO APPROXIMATELY 89.2 SCFH OF NATURAL GAS. USING THIS LEAK RATE, DENC ESTIMATES THE AMOUNT OF LOST GAS TO BE 295.43 MCF AND THE COST OF LOST GAS TO BE $1,371. DENC RETAINED INVESTIGATORS WHO EXAMINED THE SCENE. THESE INVESTIGATORS OBSERVED OXY-ACETYLENE TANKS LAYING ON THEIR SIDE IN THE CRAWL SPACE OF 1347 COURTLAND AFTER THE INCIDENT. THE INVESTIGATORS ASSESSED BLAST DYNAMICS AND OBSERVED ISOLATED BURN DAMAGE. SPECIFICALLY, THEY FOUND LITTLE TO NO FLAME PROPAGATION. THE PHOTOGRAPHS AFTER THE INCIDENT DEMONSTRATE THAT NEITHER THE WOOD JOISTS IN THE CRAWL SPACE NOR THE FOAM INSULATION WERE BURNED. THESE FINDINGS SUGGEST IGNITION OF A DISCRETE AMOUNT OF GASEOUS FUEL. WHILE THE EXACT AMOUNT OF GAS CONSUMED IN THE INCIDENT IS INDETERMINABLE, DENC ESTIMATES THAT IT WAS LESS THAN 1 MCF. (NOTE: PART A.21C WILL ONLY ALLOW A MINIMUM OF 1 MCF TO BE ENTERED). THE INVESTIGATORS' GAS MIGRATION MODELING SUGGESTS THAT NEAR-ZERO GAS FLOW WOULD MIGRATE FROM THE SERVICE LINE FRACTURE TO THE FOUNDATION WALL OF THE HOME, EVEN WITH THE HIGHEST SIMULATED PERMEABILITY VALUES (I.E., 1.0X10-3 CM2). IN LIGHT OF THE PHYSICAL FINDINGS AND GAS MIGRATION MODELING RESULTS, INVESTIGATORS QUESTIONED WHETHER OTHER POTENTIAL CONTRIBUTING FACTORS MAY HAVE LED TO THIS INCIDENT. SPECIFICALLY, THE OXY-ACETYLENE TANKS AND RELATED EQUIPMENT, WHICH WERE IN THE CRAWL SPACE WHEN THE INVESTIGATORS FIRST ARRIVED ON SCENE AND IN USE BY THE HVAC CONTRACTOR AT THE TIME OF THE INCIDENT, LATER WENT MISSING AS OF AUGUST 3, 2020 AND HAVE NOT BEEN RECOVERED TO DATE. THE HVAC CONTRACTOR'S EMPLOYER CONFIRMED THAT THEY DID NOT MAINTAIN RECORDS FOR THE MISSING TANKS AND RELATED EQUIPMENT. DENC CLASSIFIES THE APPARENT CAUSE OF THIS INCIDENT AS UNKNOWN (PART G8). THIS CONCLUDES DENC'S INVESTIGATION INTO THIS INCIDENT. INITIAL NRC INCIDENT REPORT #1279507, WAS MADE ON 06/13/20 AT 12:52 ET 48-HOUR UPDATE NRC #1279640, WAS MADE ON 06/15/20 16:51 ET LDF 1345/306401 & 1347/306389
2025-03-31 10:13 | NO | YES | NO | 20200064 | 34040 | 2020-07-15 15:20 | ORIGINAL FINAL | 18408 | DOMINION ENERGY SOUTH CAROLINA, INC. | 601 TAYLOR ROAD MAIL CODE J48 | CAYCE | SC | 29033 | 2020-06-19 17:00 |  |  | 2020 | OKATIE HWY (SC HWY 46) AT INTERSECTION OF NEW RIVER TRAIL | BLUFFTON | BEAUFORT | SC | 29910 | 32.2444 | -81 | [9 empty] | 2020-06-25 14:39 | 1280381 |  | NATURAL GAS |  | 6996.1 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-06-19 17:00 |  |  |  | 2020-06-19 17:33 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OTHER | VALVE STATION | 2016 | [8 empty] | STEEL |  | OTHER | ERW | 0.28 | [6 empty] | OTHER | [8 empty] | A TREE FELL ON A 2-IN TITAN Y CLASS 600 STRAINER, WHICH CAUSED THE GAS TO RELEASE FROM TWO LOCATIONS (UPSTREAM AND DOWNSTREAM) FROM TWO, APPROXIMATELY 2 INCH, PIPE OPENINGS. | CLASS 3 LOCATION | 0 | 0 | 85000 | 94894.653673953085 | 2500 | 2791.0192257045025 | 14500 | 16187.9115090861145 | TO RETIRE STATION: MATERIAL $2000 LABOR $5000 TREE REMOVAL: $7500 |  | 14000 | 17428.5714285714285714285714285714285714 |  | 0 | 116000 | 63285.4724191493567346938775510204081633 | 131302.1558373151305714285714285714285714 | 0 | 0 | 0 |  |  |  |  | 300 | 300 | 587 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO INVESTIGATION WAS NEEDED, AS THE CONTROL ROOM WAS FUNCTIONING PROPERLY AND WAS ABLE TO CONFIRM THE ORIGINAL NOTIFICATION WHICH WAS INITIATED BY OPERATIONS PERSONNEL. THE CONTROL ROOM DID NOT HAVE REMOTE CONTROL OVER THE VALVE STATION - ONLY MONITORING CAPABILITIES. THERE WERE NO CONTRIBUTING FACTORS FROM THE CONTROL ROOM THAT IMPACTED THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | NATURAL FORCE DAMAGE | HIGH WINDS | [56 empty] | HIGH WINDS |  |  |  |  | ,,, | NO | [218 empty] | JERAMY FREE | ENGINEER IV PIPELINE COMPLIANCE | jeramy.free@dominionenergy.com | 8032603602 |  |  |  |  | GREG MCGLOHORN | GM OF CONSTRUCTION AND OPERATIONS AND MAINTENANCE | 8032177346 | greg.mcglohorn@dominionenergy.com | ON JUNE 19, 2020, AT APPROXIMATELY 5:00 PM LOCAL TIME, IN OKATIE, SC, A SEVERE THUNDERSTORM WITH HIGH WINDS CAUSED TWO TREES TO FALL ONTO THE HWY 46 VALVE STATION. THE DAMAGE SEVERED AN ABOVE-GROUND 2-IN STEEL STRAINER ON THE VALVE STATION. IT IS ESTIMATED THAT APPROXIMATELY 6996.1 MCF OF NATURAL GAS WAS LOST DURING THE LEAK. THE LEAK WAS STOPPED AT APPROXIMATELY 9:42 PM, AND TEMPORARY REPAIRS WERE MADE TO THE STATION. DURING THIS TIME OKATIE HWY (SC HWY 46) WAS CLOSED IN BOTH DIRECTIONS. THE INITIAL NRC INCIDENT REPORT NUMBER WAS 1280381. ON, JUNE 26, 2020 A FOLLOW-UP REPORT WAS MADE TO THE NRC TO GIVE CORRECTIONS TO THE INFORMATION CAPTURED IN THE ORIGINAL NRC REPORT (#1280485). THE STATION WAS PLACED INTO SERVICE IN 2016. AFTER THE INCIDENT OF JUNE 19, 2020. AN ENGINEERING COST ANALYSIS WAS PERFORMED FOR THE STATION AND IT WAS DETERMINED THAT THE STATION IS NO LONGER NEEDED FOR SYSTEM RELIABILITY. THUS THE PRELIMINARY PLAN IS TO RETIRE THE STATION. A NEW STATION MAY BE CONSTRUCTED AT THE LOCATION IF FUTURE OPERATIONAL NEEDS REQUIRE IT.
2025-03-31 10:13 | NO | NO | NO | 20200066 | 35216 | 2020-07-24 17:52 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2020-06-24 09:04 | MOUNTAIN | YES | 2020 | 4337 SILVER DOLLAR AVENUE | LAS VEGAS | CLARK | NV | 89102 | 36.1382 | -115.1985 | [7 empty] | YES | CLOSED FITTING AT MAIN-TO-SERVICE CONNECTION | 2020-06-24 14:33 | 1280311 | 1280402 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-06-24 10:13 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 14 | 2020-06-24 09:04 | YES | OPERATOR | 2020-06-24 10:13 | 2020-06-24 09:04 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 28 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1973 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO | 0.5 | ASTM D1785 | UNKNOWN | PLASTIC |  |  |  |  | POLYVINYL CLORIDE (PVC) |  |  | 0.109 |  |  | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 43000 | 48005.530682117443 | 6000 | 6698.446141690806 | 5500 | 6140.2422965499055 | 0 | 0 |  | 1 | 1 | 1.24489795918367346938775510204081632653 | 0 | 0 | 54501 | 25201.002362869962274052478134110787172 | 60845.4640183173381734693877551020408163 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 39 | 43 | 43 | 192.619(A)(2) | 1973-08-11 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 3 | 0 | YES | 3 | 1 | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | EROSION OF SUPPORT DUE TO HOUSELINE WATER LEAK. | [154 empty] | MICHAEL ROSS | SUPERVISOR ENGINEERING | michael.ross@swgas.com | (702) 365-2361 |  |  |  |  | ANTHONY HILLS | DIRECTOR GAS OPERATIONS | (702) 365-2049 | anthony.hills@swgas.com | WHILE CONDUCTING AN ANNUAL PVC LEAK SURVEY PURSUANT TO SOUTHWEST GAS' DIMP PLAN ON JUNE 24, 2020, SOUTHWEST GAS' LEAK SURVEY CONTRACTOR CONTACTED SOUTHWEST GAS AT 09:04 PDT AND REPORTED GAS READS OF 1 LEL NEAR THE LAUNDRY ROOM RISER AND ZERO READS INSIDE THE LAUNDRY ROOM LOCATED AT 4337 SILVER DOLLAR AVENUE IN LAS VEGAS, NV. SOUTHWEST GAS CREWS ARRIVED AT 09:35 PDT AND OBTAINED GAS READS OF 4 LEL BY THE RISER TO THE LAUNDRY FACILITY, TURNED OFF THE METER, CONFIRMED ZERO GAS READS INSIDE THE UNOCCUPIED BUILDING, AND CONDUCTED FURTHER LEAK INVESTIGATION. AT 10:13 PDT, IGNITION OF FUGITIVE NATURAL GAS OCCURRED WITHIN THE DETACHED, UNOCCUPIED LAUNDRY FACILITY STRUCTURE RESULTING IN A FIRE AND PROPERTY DAMAGE. POST IGNITION LEAK SURVEY RESULTS DISCOVERED INCREASING GAS READINGS AND LEAK SPREAD RESULTING IN AN EVACUATION OF 14 PEOPLE FROM SOME UNITS OF THE ADJACENT, SEPARATE APARTMENT BUILDING. A LEAK ON A PVC SERVICE LINE COUPLING CONNECTION FITTING WAS REVEALED DURING A LEAK TEST OF THE PVC SERVICE DURING A POST INCIDENT INVESTIGATION. ADDITIONALLY, A LEAK TEST PERFORMED ON THE CUSTOMER'S HOUSELINE FAILED DURING THE POST INCIDENT INVESTIGATION. PART A4: BASED ON COMMUNICATIONS THAT THE PUBLIC UTILITIES COMMISSION OF NEVADA'S REGULATORY OPERATIONS STAFF HAD WITH THE PIPELINE AND HAZARDOUS MATERIALS SAFETY ADMINISTRATION'S ACCIDENT INVESTIGATION DIVISION, "LOCAL TIME AND DATE OF THE INCIDENT" REFLECTS THE TIME SOUTHWEST GAS WAS NOTIFIED OF A LEAK ON THE PIPELINE. AT THAT TIME, NO INCIDENT REPORTING CRITERIA WAS MET. PART A6: SOUTHWEST GAS NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) TELEPHONICALLY OF THE INCIDENT ON JUNE 24, 2020 AT 14:33 PDT. THE NRC ISSUED REPORT NUMBER 1280311 FOR THE INCIDENT. SOUTHWEST GAS PROVIDED A 48-HOUR UPDATE TELEPHONICALLY TO THE NRC ON JUNE 25, 2020 AT 15:28 PDT. THE NRC ISSUED REPORT NUMBER 1280402 FOR THE UPDATED REPORT. SUPPLEMENTAL RESPONSE: CHANGED PART G TO UPDATE THE APPARENT CAUSE FROM PART G5 TO G8. THE CAUSE OF THE LEAK REMAINS UNDER INVESTIGATION. CURRENT EVIDENCE SUGGESTS THE CAUSE MAY BE G3, G4, OR G5. THE SAMPLE HAS BEEN SENT TO A THIRD-PARTY MATERIALS TESTING LABORATORY FOR ANALYSIS AND THE RESULTS OF THE ANALYSIS WILL BE PROVIDED IN A SUPPLEMENTAL RESPONSE. THE LEAK WAS ORIGINALLY BELIEVED TO BE DUE TO A SOLVENT CEMENT JOINT, BUT A CRACK WAS FOUND WHEN ASSESSED IN SOUTHWEST GAS'S MATERIALS TESTING LABORATORY. THE CRACK APPEARS TO BE A CIRCUMFERENTIAL CRACK IN THE PIPE NEAR THE LOCATION OF THE PIPE TO COUPLING JOINT. SUPPLEMENTAL RESPONSE 2: FOLLOWING THE INCIDENT, THE SERVICE LINE WAS DISCONNECTED AT THE MAIN. ON MARCH 30, 2021, THE SERVICE TO THE CUSTOMER WAS REPLACED. PART C, 3 AND 4 - CHANGED THE PIPE SIZE AND WALL THICKNESS TO 0.5-INCH AND 0.109-INCH RESPECTIVELY BASED ON 3RD PARTY LABORATORY ANALYSIS. CHANGED PART G FROM G8 - OTHER INCIDENT CAUSE TO G4 - OTHER OUTSIDE FORCE DAMAGE, WITH A SUB-CAUSE AS OTHER OUTSIDE FORCE DAMAGE. AN INDEPENDENT LABORATORY'S MATERIAL INVESTIGATION CONCLUDED THAT THE ROOT CAUSE OF THE FAILURE WAS SUSTAINED EXTERNAL BENDING LOADS LEADING TO SLOW CRACK GROWTH AND CREEP RUPTURE. THE FIELD INVESTIGATION DETERMINED THAT THE PROBABLE CAUSE OF THE BENDING LOADS WAS A CUSTOMER HOUSELINE WATER LEAK WHICH ERODED THE SUPPORT FROM UNDER THE SERVICE LINE'S TRANSITION FITTING.
2025-03-31 10:13 | NO | YES | YES | 20200067 | 39792 | 2020-07-28 16:06 | SUPPLEMENTAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2020-07-02 10:26 | EASTERN | NO | 2020 | 120 MERRISON ST. | TEANECK | BERGEN | NJ | 07666 | 40.8871 | -74.0115 |  | YES | [7 empty] | 2020-07-02 11:45 | 1280892 | 1281075 | NATURAL GAS |  | 4.32 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2020-07-02 10:15 | OPERATOR/CONTRACTOR |  | 4.3 | NO | 0 | 2020-07-02 10:26 | YES | OPERATOR | 2020-07-02 10:26 | 2020-07-02 10:26 | 2020-07-02 10:26 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 40 | NO | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN |  | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 1000 | 1116.407690281801 | 0 | 0 |  | 7.26 | 31 | 38.59183673469387755102040816326530612245 | 0 | 0 | 1031 | 498.082291195570495626822157434402332362 | 1154.999527016494877551020408163265306122 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0.25 | 0.25 | 0.25 | 192.619(A)(1) | 1928-06-05 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 2 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | INCORRECT TOOLING USED DURING THE CUT AND CAP OF A SERVICE. |  |  | YES |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ROGER GUNNELS | PRINCIPAL REGULATORY SPECIALIST | roger.gunnels@pseg.com | 973-513-2474 |  |  |  |  | CHRIS LAROSSA | MANAGER REGULATORY POLICY AND PROCEDURE | 973-896-7617 | christopher.larossa | ON 7/2/20 AT 120 MERRISON ST. IN TEANECK, WHILE CONDUCTING A LEAK REPAIR ON A 1 1/4 A STEEL UTILITY PRESSURE SERVICE A PSE&G EMPLOYEE USED THE INCORRECT CUTTING TOOL AND AN ACCIDENTAL IGNITION OCCURRED CAUSING A FLASH INJURING TWO PSE&G EMPLOYEES. FIRST RESPONDERS ARRIVED ON SITE AND TRANSPORTED THE EMPLOYEES TO THE HOSPITAL. ONE EMPLOYEE REMAINED OVERNIGHT, THE OTHER WAS TREATED AND RELEASED.
2025-03-31 10:13 | NO | YES | NO | 20200068 | 34253 | 2020-07-28 23:51 | SUPPLEMENTAL FINAL | 22189 | PUGET SOUND ENERGY | 355 110TH AVE NE | BELLEVUE | WA | 98004 | 2020-06-30 02:05 |  |  | 2020 | 210 S MERIDIAN | PUYALLUP | PIERCE | WA | 98371 | 47.1908 | -122.2938 | [9 empty] | 2020-06-30 14:11 | 1280754 |  | NATURAL GAS |  | 913.32 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-06-30 02:05 |  |  |  | 2020-06-30 02:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 74 |  | YES |  |  |  |  | YES | UNCASED | [5 empty] | PRIVATELY OWNED |  | MAIN |  | 1997 | [5 empty] | 4 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 4 | 1 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 472016 | 526962.292336054580816 | 85574 | 95535.471688174838774 | 0 | 0 |  |  | 7964 | 9914.36734693877551020408163265306122449 |  | 0 | 565554 | 266991.2745728110389539358600583090379009 | 632412.1313711681951002040816326530612245 | 46 | 0 | 1 |  |  |  |  | 55.8 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | INITIAL INFORMATION INDICATED THAT THE CAUSE OF THE MAIN BREAK ORIGINATED FROM 3RD PARTY DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 20251307 |  |  | CONTRACT LOCATOR | NO | YES | 15 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | MIHAELA STEFANESCU | REGULATORY COMPLIANCE ANALYST | mihaela.stefanescu@pse.com | 425-457-5752 |  |  |  |  | KAAREN DAUGHERTY | MANAGER COMPLIANCE AND QUALITY MANAGEMENT | 425-766-2409 | kaaren.daugherty@pse.com | PSE RESPONDED TO A CALL FROM PIERCE COUNTY FIRE DEPARTMENT OF A BROKEN AND BLOWING 4" PE GAS MAIN AT THE INTERSECTION OF S MERIDIAN STREET AND W PIONEER AVENUE IN PUYALLUP ON JUNE 30, 2020 AT 02:05. THE GAS FIRST RESPONSE (GFR) TECHNICIAN FIRST ARRIVED ONSITE AT 02:40 AND FOUND THAT A CONTRACTOR (SEFNCO) HAD DAMAGED THE 4" PE GAS MAIN WHILE DIRECTIONAL DRILLING ACROSS MERIDIAN STREET TO INSTALL NEW TELECOMMUNICATION CABLE. THE GFR TECHNICIAN ASSESSED THE SITUATION AND REQUESTED ADDITIONAL SUPPORT. THE FIRE DEPARTMENT HAD BLOCKED ACCESS TO APPROXIMATELY ONE BLOCK RADIUS SURROUNDING THE DAMAGE. PSE'S ELECTRIC FIRST RESPONSE WAS CONTACTED TO DE-ENERGIZE CUSTOMERS IN THE IMMEDIATE VICINITY AS A PRECAUTION. IN ORDER TO ISOLATE AND SHUT DOWN THE GAS LEAK, A COMBINATION OF PIPE SQUEEZES AND VALVE CLOSURES WERE REQUIRED. THE BREAK WAS JUST SOUTH OF A TWO-WAY CONNECTION TO A 2" PE MAIN THAT RUNS PERPENDICULAR (EAST/WEST) TO THE 4" PE MAIN. VALVES ON THE 2" MAIN, IN CLOSE PROXIMITY TO THE DAMAGED 4" MAIN, WERE NOTED BY GAS FIRST RESPONSE PERSONNEL AS REQUIRING EXCAVATION TO OPERATE. BECAUSE OF THE GAS READS IN THE AREA, SQUEEZE LOCATIONS ON THE 2" MAIN FURTHER FROM THE DAMAGED 4" WERE SELECTED AS ALTERNATES TO EXCAVATING AND OPERATING THE VALVES. SQUEEZING OF THE 4" PE MAIN NORTH AND SOUTH OF THE DAMAGE WAS NOT FEASIBLE AS THE DEPTH OF MAIN WAS DETERMINED TO BE 6 TO 7 FEET DEEP. INSTEAD, MULTIPLE VALVE CLOSURES WERE INCORPORATED INTO THE ISOLATION PLAN. IN THE COURSE OF OPERATING ONE OF THE SELECTED VALVES, THE VALVE ADAPTER BROKE AND SO AN ADDITIONAL SQUEEZE NORTH OF THE VALVE WAS MADE. SHUT DOWN OF THE 4" PE MAIN WAS ACHIEVED AT 11:10. A TOTAL OF 47 CUSTOMER OUTAGES WERE IDENTIFIED. THE FINAL REPAIR WAS COMPLETED ON JULY 1, 2020 AT APPROXIMATELY 02:00; THE SYSTEM WAS RE-PRESSURIZED AND THE CUSTOMER RELIGHTS BEGAN. THE CONTRACTOR HAD REQUESTED LOCATES; IT WAS DISCOVERED DURING THE EMERGENCY RESPONSE THAT THE LOCATE MARKS DID NOT COVER THE FULL SCOPE OF THE LOCATE TICKET AND WERE NON-EXISTENT IN THE AREA OF THE DAMAGED MAIN. THIS INCIDENT WAS REPORTED TO NRC DUE TO PROPERTY DAMAGE EXCEEDING $50,000. NRC # 1280754 SUBMITTED ON JUNE 30, 2020 AT 14:11 NRC # 1280940 SUBMITTED ON JULY 2, 2020 AT 13:39 (48 HOURS PHMSA REQUIRED UPDATE).
2025-03-31 10:13 | NO | NO | NO | 20200069 | 34105 | 2020-07-30 14:18 | SUPPLEMENTAL FINAL | 13730 | NORTHERN INDIANA PUBLIC SERVICE CO | 801 E 86TH AVENUE | MERRILLVILLE | IN | 46410 | 2020-06-23 15:42 |  |  | 2020 | 9501 SEA PINES WAY | FORT WAYNE | ALLEN | IN | 46819 | 40.9969 | -85.1451 | [9 empty] | 2020-06-23 17:35 | 1280230 |  | NATURAL GAS |  | 21.57 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2020-06-23 15:42 |  |  |  | 2020-06-23 16:01 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 26 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1979 | [5 empty] | 0.625 | PE 2306 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 7 |  |  | 2306 | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 100 | 111.6407690281801 | 1000 | 1116.407690281801 | 0 | 0 | NO OTHER COSTS |  | 12 | 14.93877551020408163265306122448979591837 |  | 0 | 1112 | 522.44008299734328862973760932944606414 | 1242.987234820185181632653061224489795918 | 0 | 0 | 1 |  |  |  |  | 40 | 40 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES |  |  | YES | PRIVATE LANDOWNER | [10 empty] | OCCUPANT | AUGER | FENCING | NO | [5 empty] | YES | 5 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | RICK SMITH | MANAGER OF GAS OPERATIONS COMPLIANCE | ricksmith@nisource.com | 219-252-4057 |  |  |  |  | RICK SMITH | MANAGER OF GAS OPERATIONS COMPLIANCE | 219-252-4057 | ricksmith@nisource.com | HOMEOWNER FAILED TO NOTIFY 811 AND STRUCK AN UNMARKED 5/8 INCH PLASTIC GAS SERVICE LINE WITH A POWER AUGUR RESULTING IN THE RELEASING GAS TO IGNITE AND CAUSE MINOR BURNS TO ONE OF THE OPERATORS OF THE AUGUR. DUE TO HIPAA LAWS, THERE IS NO UPDATE ON THE INDIVIDUAL. THE GAS LEAK WAS VERY SMALL FROM A VOLUME PERSPECTIVE. THE SERVICE DAMAGED SERVICE WAS REPLACED. THE NEW SERVICE WAS PRESSURE TESTED AND THE CUSTOMER WAS PLACED BACK IN SERVICE THE SAME DAY.
2025-03-31 10:13 | NO | NO | NO | 20200070 | 34090 | 2020-07-31 13:23 | ORIGINAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2020-07-02 17:24 |  |  | 2020 | 5111 DAFFODILL LANE | CONCORD | CABARRUS | NC | 28025 | 35.3476 | -80.5608 | [9 empty] | 2020-07-02 21:05 | 1280964 |  | NATURAL GAS |  | 156 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-07-02 17:51 |  |  |  | 2020-07-02 18:18 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 52 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2001 | [5 empty] | 4 | ASTM D2513 | PERFORMANCE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.391 |  | 2406 | OTHER | [8 empty] | DAMAGE BY DIRECTIONAL BORE. THE DAMAGE AREAS WERE NOT EXCAVATED DUE TO THE PRO. | CLASS 3 LOCATION | 0 | 0 | 44362 | 49526.077956281255962 | 26268 | 29325.797208322348668 | 0 | 0 |  |  | 722 | 898.816326530612244897959183673469387755 |  | 0 | 71352 | 33489.5395449274006658892128279883381924 | 79750.6914911342168748979591836734693878 | 0 | 0 | 147 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE GAS LOSS FROM THE DAMAGE DID NOT CAUSE A PRESSURE REDUCTION THAT TRIGGERED ANY SCADA ALARMS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | BORING | CABLE TV | YES | A201751026 |  |  | CONTRACT LOCATOR | YES | YES | 15 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | RALPH EUCHNER | MANAGER - REGIONAL OPERATIONS | ralph.euchner@dominionenergy.com | 704-810-3331 |  |  |  |  | SCOTT SWINDLER | GENERAL MANAGER - OPERATIONS AND MAINTENANCE | 704-810-3230 | scott.swindler@dominionenergy.com | ON JULY 2ND DOMINION ENERGY OF NC RECEIVED AN ODOR CALL AT 5111 DAFFODIL LANE IN CONCORD. DENC FIRST RESPONDER ARRIVED AT THE SCENE AT 5:51PM AND DETERMINED THAT THIS WAS AN UNDERGROUND DAMAGED MAIN OR SERVICE. SUBSEQUENTLY, RESPONDING DENC OPERATIONS AND MAINTENANCE PERSONNEL DISCOVERED THAT THE MAIN WAS LEAKING IN SEVERAL LOCATIONS ALONG 500-FOOT LONG COMMUNICATIONS CONDUIT BORE PATH. GAS WAS BLOWING IN IN THE ROADWAY AND DUE TO SAFETY CONCERNS THE VOLUNTEER FIRE DEPARTMENT DECIDED TO CUT OFF THE 4" PLASTIC VALVE OFF LOCATED ABOUT 100' UPSTREAM FROM THE DAMAGED AREA. THE MAIN WAS DAMAGED BY DIRECTIONAL BORE IN MULTIPLE LOCATIONS. THE DAMAGED AREAS WERE NOT EXCAVATED DUE TO THE PROXIMITY OF THE MAIN IN RELATION TO OTHER UTILITIES, ROAD AND SIDEWALKS. THE DECISION WAS MADE TO REPLACE THE ENTIRE SECTION ON THE OTHER SIDE OF THE ROAD. THE MAIN WAS A ONE-WAY FEED AND A TEMPORARY BY-PASS WAS INSTALLED TO SUPPORT THE DOWNSTREAM CUSTOMERS UNTIL THE REPLACEMENT MAIN COULD BE INSTALLED. THE WORK ON THE BY-PASS EXTENDED INTO JULY 3RD AND THE DOWNSTREAM SYSTEM WAS PLACED BACK INTO SERVICE. 147 DOWNSTREAM CUSTOMERS HAD TO BE RESTORED. THE FINAL AND PERMANENT REPLACEMENT OF THIS SECTION OF MAIN HAS BEEN COMPLETED AND THE COSTS ARE INCLUDED IN THIS REPORT. LOCATING MARKS FOR THE NATURAL GAS MAIN THAT WERE PRESENT AT THE SCENE WERE DETERMINED TO BE OUTSIDE OF THE TOLERANCE ZONE. ROOT CAUSE OF INCIDENT IS INACCURATE FACILITY MARKING. THE LOCATE WAS PERFORMED BY DOMINION ENERGY'S THIRD-PARTY LOCATER ON JUNE 24TH. NOTE: PART C, QUESTION 5 - THE MAIN WAS DAMAGED BY DIRECTIONAL BORE IN MULTIPLE LOCATIONS. THE DAMAGED AREAS WERE NOT EXCAVATED DUE TO THE PROXIMITY OF THE MAIN IN RELATION TO OTHER UTILITIES, ROAD AND SIDEWALKS, THEREFORE, ACCURATE DIMENSIONS OF THE DAMAGED AREAS COULD NOT BE DETERMINED. THE DECISION WAS MADE TO REPLACE THE ENTIRE SECTION ON THE OTHER SIDE OF THE ROAD. LDF-309434
2025-03-31 10:13 | NO | NO | NO | 20200071 | 36477 | 2020-07-31 16:05 | SUPPLEMENTAL FINAL | 30769 | SPIRE MISSOURI INC. WEST | 700 MARKET STREET | SAINT LOUIS | MO | 63101 | 2020-07-01 15:32 | CENTRAL | YES | 2020 | MO 169 HIGHWAY AND BARRY ROAD | KANSAS CITY | CLAY | MO | 64118 | 39.2445 | -94.5903 | [6 empty] | YES |  |  | 2020-07-01 19:00 | 1280866 | 1281146 | NATURAL GAS |  | 100.59 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-07-01 15:32 | YES | OPERATOR | 2020-07-01 18:42 | 2020-07-01 15:40 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 53 | NO | YES |  |  |  |  | YES | CASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1957 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 8.3 | 0.1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 64783 | 72324.239399525914183 | 500 | 558.2038451409005 | 0 | 0 |  | 4.1157 | 414 | 515.387755102040816326530612244897959184 | 0 | 0 | 65697 | 30662.4859974615365377259475218658892128 | 73397.8309997688554993265306122448979592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 128 | 128 | 150 | 192.619(A)(3) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE VOLUME OF GAS RELEASED WAS NOT DETECTABLE BY THE SCADA SYSTEM AND THE CONTROLLER(S) TOOK NO ACTIONS THAT WOULD HAVE CONTRIBUTED TO OR CAUSED THE INCIDENT. | [12 empty] | NO |  |  | YES | 2 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | AUGER | POLE | YES | 201833282 |  |  | CONTRACT LOCATOR | NO | NO |  | EXCAVATION ISSUE | MARKS FADED OR NOT MAINTAINED | [170 empty] | NICOLE CHRISTIANER | MANAGER PIPELINE SAFETY DISTRIBUTION | nicole.christianer@spireenergy.com | 314-349-2929 |  | NICOLE CHRISTIANER | nicole.christianer@spireenergy.com | 314-349-2929 | CRAIG HOEFERLIN | VP OPERATIONS SERVICES | 314-349-2972 | craig.hoeferlin@spireenergy.com | A THIRD PARTY CONTRACTOR WAS INSTALLING GUARD RAILS FOR THE HIGHWAY DEPARTMENT IN THE MEDIAN OF MISSOURI 169 HIGHWAY JUST SOUTH OF BARRY ROAD OVERPASS. WHILE AUGURING A HOLE FOR A SUPPORT POST THE 12-INCH MAIN WAS STRUCK RESULTING IN A LEAK. WHILE THE NORTHBOUND LANE OF HIGHWAY 169 WAS ALREADY CLOSED DUE TO THE GUARD RAIL CONSTRUCTION WORK, THE SOUTHBOUND LANE WAS ALSO CLOSED TEMPORARILY DUE TO THE DAMAGE AND THE GAS RELEASE. STOPPER FITTINGS WERE INSTALLED TO ISOLATE THE SECTION OF MAIN FOR COMPLETING THE REPAIR WITH A REINFORCEMENT SLEEVE. THE CONTRACTOR WAS NOT WORKING UNDER A VALID LOCATE AT THE TIME OF THE DAMAGE. A LOCATE WAS REQUESTED BY THE CONTRACTOR ON MAY 28TH FOR THE AREA BEING WORKED. THE LOCATOR DID NOT COMPLETE A PROPER LOCATE AT THAT TIME, AND THE ORIGINAL LOCATE HAD EXPIRED BEFORE THE WORK BEGAN AND WAS NOT RENEWED. NRC INCIDENT REPORT WAS UPDATED ON JULY 5, 2020 AT 10:12 PM, REPORT NUMBER 1281146.
2025-03-31 10:13 | NO | YES | NO | 20200072 | 35421 | 2020-08-06 11:08 | SUPPLEMENTAL FINAL | 31636 | NORTHERN STATES POWER CO OF MINNESOTA | 414 NICOLLET MALL | MINNEAPOLIS | MN | 55402 | 2020-07-06 20:20 | CENTRAL | NO | 2020 | 800 SIBLEY MEMORIAL HIGHWAY | MENDOTA HEIGHTS | DAKOTA | MN | 55118 | 44.9031 | -93.131 | YES | [8 empty] | 2020-07-06 20:20 | 1281226 | 1281391 | NATURAL GAS |  | 298 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-07-06 07:55 | ALLOWED TO BURN OUT |  | 298 | NO | 0 | 2020-07-06 08:20 | YES | OPERATOR | 2020-07-06 08:24 | 2020-07-06 08:10 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1979 | UNKNOWN | [7 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 2 LOCATION | 0 | 0 | 146000 | 162995.522781142946 | 5853 | 6534.334211219381253 | 0 | 0 |  | 0.44 | 0 | 0 | 0 | 0 | 151853 | 70214.18233693262828 | 169529.856992362327253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 175 | 720 | 192.619(A)(2) | 1979-09-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | FIRE WAS DETERMINED TO BE CAUSED TO LIGHTNING. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | YES |  |  |  | YES | THUNDERSTORM | [213 empty] | ELISABETH KALLBERG | KALLBERG | elisabeth.m.kallberg@xcelenergy.com | 651-229-2282 |  |  |  |  | CHRISTOPHER AKINS | MANAGER PIPELINE COMPLIANCE AND STANDARDS | 303-571-3298 | christopher.a.akins@xcelenergy.com | ON JULY 6, 2020, AT APPROXIMATELY 0800 A THUNDERSTORM MOVED THRU THE MENDOTA HEIGHTS AREA WHERE THE SIBLEY PROPANE PLANT IS LOCATED. PERSONNEL REPORTED HEARING A LIGHTNING STRIKE AND APPROXIMATELY 15 MINUTES LATER REPORTED A FIRE AT THE EXTERIOR WALL OF THE VAPORIZER BUILDING. FIRE WAS CONTAINED TO THE NORTH EXTERIOR WALL OF THE BUILDING.
2025-03-31 10:13 | NO | NO | NO | 20200073 | 34269 | 2020-08-07 14:52 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2019-03-09 07:27 |  |  | 2019 | WESTERN AVENUE | MOON TOWNSHIP | ALLEGHENY | PA | 15108 | 40.5488 | -80.2455 | [9 empty] | 2019-03-09 11:38 | 1239662 |  | NATURAL GAS |  | 113 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2019-03-09 07:27 |  |  |  | 2019-03-09 08:07 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2018 | [8 empty] | STEEL |  | OTHER | ERW | 0.28 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 2 LOCATION | 0 | 0 | 4618 | 5224.366693354682904 | 63388 | 71711.164131305032464 | 0 | 0 |  |  | 459 | 514.417322834645669291338582677165354331 |  | 0 | 68465 | 32340.2556088615615265669291338582677165 | 77449.9481474943610372913385826771653543 | 0 | 0 | 980 |  |  |  |  | 33 | 33 | 40 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | HEAVY RAINS/FLOODS | [56 empty] | HEAVY RAINS/FLOODS |  | OTHER |  |  | ,,,,,SEVERAL DAYS OF HEAVY RAINS PRIOR TO THE INCIDENT, SATURATED THE SOIL, CAUSING AN OVER BURDEN ON THE INLET PIPE. SEE PART H.,,,,,,,,,, | NO | [218 empty] | DANIEL P. KUEHN | MANAGER COMPLIANCE PROCESS | daniel.kuehn@peoples-gas.com | 724-444-3251 |  |  |  |  | JOSEPH A. GREGORINI | PRESIDENT OF PEOPLES | 412-208-5244 | joseph.a.gregorini@peoples-gas.com | ON 03/09/2019 AT APPROXIMATELY 07:27, THE INLET PIPE TO THE WESTERN AVENUE METERING SITE EXPERIENCED A SEPARATION OF THE 6 INCH INLET PIPING. DUE TO LONG TERM, HEAVY RAINS THAT OCCURRED OVER A PERIOD OF SEVERAL DAYS PRIOR TO THIS INCIDENT, THE SATURATED SOIL CREATED A HEAVY OVERBURDEN ON THE INLET PIPING, AND THAT STRAIN CAUSED THE STEEL PORTION OF THAT PIPING TO SEPARATE AT THE COUPLER. THE FIRST RESPONDERS ON SITE DETERMINED TO SHUT THE SYSTEM DOWN FOR SAFETY, MAKE REPAIRS AND RESTORE SERVICE. PERMANENT REPAIRS RENEWED THAT COUPLED PIPE, REPLACING IT WITH ALL WELDED STEEL PIPING. NRC FOLLOW UP QUESTIONS: GIVEN THAT THIS WAS A RELATIVELY NEW INSTALLATION (2018), IS IT POSSIBLE THERE WERE SOME WORKMANSHIP ISSUES THAT MAY HAVE CONTRIBUTED TO THE FAILURE? WAS THE PIPING INSTALLED IN A BIND? HOW FAR DID IT SEPARATE WHEN IT PULLED APART? WERE THE CONSTRUCTION SPECIFICATIONS ADHERED TO? PEOPLES FOLLOW UP ANSWERS: AN INTERNAL INVESTIGATION WAS CONDUCTED AFTER THIS INCIDENT OCCURRED AND NO POOR WORKMANSHIP ISSUES WERE FOUND THAT CONTRIBUTED TO THIS INCIDENT, WITH ALL CONSTRUCTION SPECIFICATIONS BEING ADHERED TO. AT THE TIME THAT THIS INCIDENT OCCURRED, THE PIPING HAD SEPARATED APPROXIMATELY 3 INCHES AND SHOWED NO SIGNS OF MISALIGNMENT AND WAS STILL IN LINE WITH THE INLET RISER IT HAD SEPARATED FROM, INDICATING THAT THE PIPE WAS NOT INSTALLED IN A BIND. THE NUTS ON THE COUPLING BOLTS WERE FOUND IN THE POSITION OF HAVING BEEN TIGHTENED WELL INTO THE FINAL TORQUED TIGHTENED PHASE. ALL INDICATIONS POINT TO THE FACT THAT SEVERAL DAYS OF HEAVY RAINS WAS THE PRIMARY FACTOR THAT INITIATED THIS INCIDENT.
2025-03-31 10:13 | NO | NO | NO | 20200074 | 34588 | 2020-08-10 20:39 | SUPPLEMENTAL FINAL | 15462 | PECO ENERGY CO | 2301 MARKET STREET, S9-1 | PHILADELPHIA | PA | 19103 | 2020-07-10 11:00 |  |  | 2020 | 824 BELVOIR ROAD | PLYMOUTH MEETING | MONTGOMERY | PA | 19462 | 40.1212 | -75.3071 | [9 empty] | 2020-07-16 14:52 | 1282095 |  | NATURAL GAS |  | 71 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2020-07-10 11:23 |  |  |  | 2020-07-10 11:30 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1971 | [8 empty] | OTHER | CAST ALUMINUM GAS METER | [9 empty] | LEAK |  |  | OTHER | ELECTRIC FAULT AT METER SET | [5 empty] | CLASS 3 LOCATION | 75000 | 83730.576771135075 | 200 | 223.2815380563602 | 1500 | 1674.6115354227015 | 0 | 0 |  |  | 150 | 186.73469387755102040816326530612244898 |  | 0 | 76850 | 35637.4846209976331078717201166180758017 | 85815.204538491687720408163265306122449 | 0 | 0 | 1 |  |  |  |  | 15 | 15 | 25 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A SINGLE SERVICE, THE CONTROL ROOM WOULD NOT HAVE NOTICED THE EVENT | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | MATTHEW MARINZOLI | SENIOR ENGINEER | matthew.marinzoli@exeloncorp.com | 267.533.1169 |  |  |  |  | RYAN LEWIS | MANAGER GAS ASSET MANAGEMENT AND PERFORMANCE | 215.841.5719 | ryan.lewis@exeloncorp.com | THE EVENT APPEARS TO HAVE BEEN CAUSED BY A FAILED SLEEVE ON A PRIMARY ELECTRIC CABLE, CAUSING THE CABLE TO FALL AND MAKE CONTACT WITH THE GAS METER. THE ARCING BURNED 2 HOLES IN THE METER SET: 1 ON THE METER (6 "WC) AND 1 ON THE INLET TO THE SERVICE REGULATOR (15 PSIG). THE GAS IGNITED AND FED A FIRE. THERE WAS DAMAGE TO THE EXTERIOR VINYL SIDING. THE ELECTRIC PANEL AND SOME HOUSE WIRING WILL NEED TO BE REPLACED. WALLS IN THE DINING ROOM AND LIVING ROOM WERE VENTED BY THE FIRE DEPARTMENT AND WILL REQUIRE RESTORATION. THERE WAS MINOR SMOKE AND WATER DAMAGE.
2025-03-31 10:13 | NO | YES | NO | 20200075 | 34194 | 2020-08-11 12:10 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2020-07-13 12:30 |  |  | 2020 | 15TH AND NAISMITH | LAWRENCE | DOUGLAS | KS | 66045 | 38.9571 | -95.2522 | [9 empty] | 2020-07-13 14:50 | 1281787 |  | NATURAL GAS |  | 750 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2020-07-13 12:35 |  |  |  | 2020-07-13 12:35 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1959 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  |  |  | 0.203 | [6 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 110000 | 122804.84593099811 | 15000 | 16746.115354227015 | 5000 | 5582.038451409005 | 0 | 0 |  |  | 3750 | 4668.36734693877551020408163265306122449 |  | 0 | 133750 | 64428.2488758323276967930029154518950437 | 149801.3670835729055102040816326530612245 | 13 | 0 | 0 |  |  |  |  | 30 | 30 | 34 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | INCORRECT OPERATION | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR | [222 empty] | DAMAGE BY OPERATOR OR OPERATOR'S CONTRACTOR NOT RELATED TO EXCAVATION AND NOT DUE TO MOTORIZED VEHICLE/EQUIPMENT DAMAGE |  |  |  | YES |  |  | CONSTRUCTION | YES | NO, BUT THEY WERE PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | RON HENNING | COMPLIANCE COORDINATOR | ron.henmning@blackhillscorp.com | 316.215.4569 |  |  |  |  | RON HENNING | COMPLIANCE COORDINATOR | 316.215.4569 | ron.henmning@blackhillscorp.com | WHILE WORKING ON A 6" STEEL LINE, CONTRACTOR TRIED TO MAKE AN ADJUSTMENT TO THE STOPPLING EQUIPMENT. THIS ADJUSTMENT CAUSED GAS TO ESCAPE AND WAS IGNITED BY A NEARBY WELDERS FLAME. A PARALLEL 6" PE LINE ADJACENT TO THE 6" STEEL LINE MELTED FROM THE FIRE. ONCE THE PE LINE WAS COMPROMISED IT FUELED THE FIRE FURTHER.
2025-03-31 10:13 | NO | YES | NO | 20200076 | 34151 | 2020-08-14 16:00 | ORIGINAL FINAL | 18112 | SAN DIEGO GAS & ELECTRIC CO | 8326 CENTURY PARK COURT | SAN DIEGO | CA | 92123 | 2020-07-16 09:14 |  |  | 2020 | 4256 ORANGE AVENUE | SAN DIEGO | SAN DIEGO | CA | 92105-1227 | 32.7533 | -117.1035 | [9 empty] | 2020-07-16 15:47 | 1282118 |  | NATURAL GAS |  | 1500 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-07-16 09:14 |  |  |  | 2020-07-16 09:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 45 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1930 | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 711026 | 793794.894390307837826 | 16361 | 18265.546220700546161 | 0 | 0 |  |  | 9000 | 11204.0816326530612244897959183673469388 |  | 0 | 736387 | 346695.511198933660592303206997084548105 | 823264.5222436614452114897959183673469388 | 0 | 0 | 3278 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ELECTRIC | YES | A200350160 | DIGALERT |  | UTILITY OWNER | YES | YES | 15 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | ALEXANDER HUGHES | SR PIPELINE SAFETY AND COMPLIANCE ADVISOR | ahughes@socalgas.com | 9496972539 |  |  |  |  | ALEXANDER HUGHES | SR PIPELINE SAFETY AND COMPLIANCE ADVISOR | 9496972539 | ahughes@socalgas.com | ON 07/16/2020, A CONTRACTOR WAS EXCAVATING TO INSTALL ELECTRICAL CONDUITS ON ORANGE AVENUE IN SAN DIEGO AND STRUCK A FITTING ATTACHED TO A 6-INCH MEDIUM PRESSURE STEEL GAS MAIN, CAUSING A RELEASE OF GAS. SDG&E GAS CREWS RESPONDED AND CONTROLLED THE LEAK BY UTILIZING MAINLINE VALVES IN THE VICINITY. FURTHER INVESTIGATION FOUND THAT THE MAIN WAS MARKED CORRECTLY AND THE CONTRACTOR WAS NOT USING HAND TOOLS TO FULLY EXPOSE THE GAS LINES. THERE WERE NO INJURIES RESULTING FROM THIS INCIDENT. THE INCIDENT WAS FIRST REPORTED TO THE CPUC WHEN SDG&E BECAME AWARE OF MEDIA COVERAGE, AND LATER REPORTED TO THE DOT WHEN SDG&E DETERMINED THAT CUSTOMER RESTORE COSTS WOULD RESULT IN TOTAL EXPENSES EXCEEDING $50,000.
2025-03-31 10:13 | NO | NO | NO | 20200077 | 34520 | 2020-08-21 18:35 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2020-07-22 11:13 |  |  | 2020 | N TRYON STREET & 16TH STREET | CHARLOTTE | MECKLENBURG | NC | 28206 | 35.2368 | -80.8294 | [10 empty] | NRC NOTIFICATION REQUIRED BUT NOT MADE |  | NATURAL GAS |  | 4870 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-07-22 11:21 |  |  |  | 2020-07-22 12:31 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 6 | 6 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 43053 | 48064.700289702378453 | 0 | 0 | 0 | 0 |  |  | 14700 | 18300 |  | 0 | 57753 | 36835.5287633093688514285714285714285714 | 66364.700289702378453 | 0 | 0 | 0 |  |  |  |  | 70 | 70 | 70 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  | NO |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DRILLING | ROAD WORK | YES | C201761729 |  |  | CONTRACT LOCATOR | YES | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 7047314680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 7047314618 | farris.berry@duke-energy.com | ON 7/22/20, CONTRACTOR WAS DRILLING (SHORING) WHILE PERFORMING ROAD WORK WHEN A 6" STEEL MAIN WAS STRUCK. IT WAS DETERMINED THAT THE CONTRACTOR WAS EXCAVATING ON AN EXPIRED LOCATE TICKET AND FAILED TO PERFORM AN ADDITIONAL CALL TO THE ONE CALL CENTER TO UPDATE THEIR LOCATE TICKET.
2025-03-31 10:13 | NO | NO | NO | 20200078 | 34204 | 2020-08-27 14:29 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2020-07-28 16:45 |  |  | 2020 | 1100 S. ELLSWORTH AVE. | SALEM | COLUMBIANA | OH | 44460 | 40.8925 | -80.8569 | [9 empty] | 2020-07-28 17:21 | 1283027 |  | NATURAL GAS |  | 3464 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-07-28 16:45 |  |  |  | 2020-07-28 10:42 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 32 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | [5 empty] | 10 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.218 | [6 empty] | MECHANICAL PUNCTURE | 7 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 30100 | 33603.8714774822101 | 10500 | 11722.2807479589105 | 0 | 0 | 0 |  | 7852 | 9774.938775510204081632653061224489795918 |  | 0 | 48452 | 27815.1235298287918600583090379008746356 | 55101.0910009513246816326530612244897959 | 0 | 7 | 0 |  |  |  |  | 40 | 40 | 47 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | OTHER | INSPECTOR OVERSEEING CITY SEWER PROJECT |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS THE RESULT OF A THIRD PARTY EXCAVATOR WHO DAMAGED A 10 INCH STEEL PIPELINE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | A020600345 | OHIO UTILITIES PROTECTION SERVICE (OUPS) |  | CONTRACT LOCATOR | YES | YES | 20 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | ROB SMITH | MANAGER OF COMPLIANCE | rrsmith@nisource.com | 6144605491 | 6144608442 |  |  |  | ROB SMITH | MANAGER OF COMPLIANCE | 6144605491 | rrsmith@nisource.com | ON JULY 28, 2020 AT APPROXIMATELY 10:35 AM, A CONTRACTOR WORKING FOR THE CITY OF SALEM INSTALLING SEWER LINES EXPOSED AN OLD ABANDONED STEEL GAS LINE AT 1100 S. ELLSWORTH AVENUE IN SALEM, OH. THE CONTRACTOR ASSUMED IT WAS THE ACTIVE LINE IN THE AREA. THE CONTRACTOR CONTINUED DIGGING AND DAMAGED THE ACTIVE 10-INCH STEEL-TREATED MEDIUM PRESSURE (MP) MAIN. THE ACTIVE MAIN WAS CORRECTLY MARKED. THE MARKS WERE CLEAR AND VISIBLE. REPAIRS WERE MADE AND THE MAIN WAS PLACED BACK IN SERVICE AT 12:05 AM ON JULY 29,2020.
2025-03-31 10:13 | NO | YES | NO | 20200079 | 34229 | 2020-08-31 17:48 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2020-08-01 13:21 |  |  | 2020 | 2214 CAMBRIA ST | CAMBRIA | SAN LUIS OBISPO | CA | 93428 | 35.5637 | -121.0824 | [9 empty] | 2020-08-01 14:59 | 1283445 |  | NATURAL GAS |  | 88.23 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 1 | 2020-08-01 13:21 |  |  |  | 2020-08-01 13:50 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2011 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | SEVERED | CLASS 3 LOCATION | 100000 | 111640.7690281801 | 11542 | 12885.577561232547142 | 200 | 223.2815380563602 | 0 | 0 |  |  | 529 | 658.551020408163265306122448979591836735 |  | 0 | 112271 | 52276.7528113468668937609329446064139942 | 125408.1791478771706073061224489795918367 | 10 | 0 | 1 |  |  |  |  | 43 | 43 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | BRYON WALSH | PIPELINE SAFTEY AND COMPLIANCE ADVISOR | bwalsh@sdge.com | 6199921473 |  |  |  |  | KHOA LE | SR PIPELINE SAFETY AND COMPLIANCE ADVISOR | 6268934536 | kle2@socalgas.com | ON 08/01/20, SOCALGAS WAS NOTIFIED OF A VEHICLE INCIDENT AT 2214 MAIN ST, CAMBRIA. A VEHICLE TRAVELING AT A HIGH RATE OF SPEED IN A PARKING LOT, LOST CONTROL, CRASHING INTO THE LEFT CORNER OF THE BUSINESS. THE IMPACT OF THE CRASH, BENT THE BOLLARDS PROTECTING THE METER SET ASSEMBLY, BREAKING A NIPPLE DOWNSTREAM OF THE SERVICE VALVE, THUS CAUSING A GAS RELEASE AND IGNITION. SOCALGAS CREW RESPONDED TO THE SCENE AND SAFELY CONTROLLED THE GAS. THERE WERE NO REPORTED INJURIES CAUSED BY THE RELEASE OF GAS. THIS WAS REPORTED TO CPUC AND DOT (#1283445) DUE TO A RELEASE OF GAS AND DAMAGES EXCEEDING $50,000.
2025-03-31 10:13 | NO | YES | NO | 20200081 | 34237 | 2020-09-01 17:48 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2020-08-02 07:26 |  |  | 2020 | 324 IDAHO AVE | SANTA MONICA | LOS ANGELES | CA | 90403 | 34.0228 | -118.5035 | [9 empty] | 2020-08-02 15:11 | 1283494 |  | NATURAL GAS |  | 37.61 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-08-02 07:26 |  |  |  | 2020-08-02 08:15 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 29 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1970 | [5 empty] | 2 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 91770 | 102452.73373716087777 | 78230 | 87336.57361074529223 | 0 | 0 |  |  | 226 | 281.346938775510204081632653061224489796 |  | 0 | 170226 | 78865.3014565997539358600583090379008746 | 190070.6542866816802040816326530612244898 | 2 | 0 | 264 |  |  |  |  | 39 | 39 | 43 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | BRYON WALSH | PIPELINE SAFETY AND COMPLIANCE ADVISOR | bwalsh@sdgecom | 6199921473 |  |  |  |  | BRYON WALSH | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 6199921473 | bwalsh@sdge.com | ON 08/02/20, SOCALGAS WAS NOTIFIED OF WATER IN GAS SERVICES IN THE VICINITY OF 1045 3RD ST, SANTA MONICA. CREW INVESTIGATED AND CENTERED THE LEAK TO BE AT 324 IDAHO AVE, SANTA MONICA. CREWS WERE ABLE TO MITIGATE THE ISSUE BY ISOLATING A SECTION OF THE AFFECTED MAIN. INVESTIGATION DISCOVERED EDISON HAD AN EQUIPMENT ARC ON SATURDAY 8/1/20 AROUND 3:00PM. THE EDISON POLE IS LOCATED AT THE N/E CORNER OF IDAHO ST / 4TH ST. ABOUT 10FT FROM WHERE THE WATER SERVICE & GAS MAIN ARE LOCATED. THE WATER SERVICE WAS FOUND TO BE ON TOP OF THE 2 INCH STEEL GAS MAIN. THE ARCING INCIDENT OF THE EDISON EQUIPMENT LIKELY CAUSED THE WATER SERVICE AND THE GAS MAIN TO ARC ON EACH OTHER. THIS CAUSED A HOLE IN THE WATER SERVICE AND GAS MAIN AT (324 IDAHO ST.) CAUSING WATER TO ENTER INTO THE GAS MAIN. NO INJURIES WERE REPORTED DUE TO THIS INCIDENT. THIS WAS INITIALLY REPORTED TO THE CPUC AND DOT DUE TO THE RELEASE OF NATURAL GAS AND ASSOCIATED DAMAGES TO EXCEEDING 50,000 DOLLARS. THIS INCIDENT DID MEET GO 112-F REPORTING CRITERIA DUE TO AN UNDER-PRESSURE EVENT. 09-04-20 UPDATED SECTION FOR DEPTH OF PIPE AND REMOVED ' AFTER 10 IN THE SUMMARY. ADDED FT AFTER THE 10.
2025-03-31 10:13 | NO | NO | NO | 20200082 | 34226 | 2020-09-03 13:50 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2020-08-23 05:54 |  |  | 2020 | 1910 E 52ND STREET | SAVANNAH | CHATHAM | GA | 31404 | 32.0356 | -81.0724 | [9 empty] | 2020-08-23 09:51 | 1285317 |  | NATURAL GAS |  | 1.75 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2020-08-23 05:54 |  |  |  | 2020-08-23 06:19 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1994 | [5 empty] | 0.5 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | RUPTURE |  |  |  |  | OTHER | LIGHTNING STRIKE TO TREE TRAVELED TO AND ARCED A HOLE INTO PLASTIC SERVICE | 0.1 | 0.1 |  | CLASS 3 LOCATION | 70000 | 78148.53831972607 | 100 | 111.6407690281801 | 200 | 223.2815380563602 | 0 | 0 |  |  | 5 | 6.22448979591836734693877551020408163265 |  | 0 | 70305 | 32511.2535841681393702623906705539358601 | 78489.6851166065286673469387755102040816 | 0 | 0 | 0 |  |  |  |  | 43 | 43 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | NATURAL FORCE DAMAGE | LIGHTNING | [56 empty] | LIGHTNING |  |  | SECONDARY IMPACT SUCH AS RESULTING NEARBY FIRES |  |  | YES |  |  |  | YES | THUNDERSTORM | [213 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A 1/2-INCH PLASTIC NATURAL GAS SERVICE WAS RUPTURED BY LIGHTNING DURING A STORM. THE LIGHTNING HAD STRUCK A TREE AND TRAVELED DOWN TO A CHAIN LINK FENCE CONNECTED TO THE HOUSE AND TRAVELED DOWN TO THE PIPE. THE ESCAPING GAS IGNITED WHERE FIRE ASSOCIATED WITH THE LIGHTNING STRIKE CAUSED EXTENSIVE DAMAGE TO THE HOUSE. ONCE THE INCIDENT WAS MADE SAFE IT WAS IDENTIFIED THAT COSTS ASSOCIATED WITH THE INCIDENT WOULD EXCEED THE $50,000 THRESHOLD FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. ADDITIONAL NRC REPORT NUMBER 1285508 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2025-03-31 10:13 | NO | YES | NO | 20200083 | 34871 | 2020-09-03 17:51 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2020-08-03 23:59 | PACIFIC | YES | 2020 | 230 DESERT BREEZE DRIVE | CALIFORNIA CITY | KERN | CA | 93505 | 35.1343 | -117.9294 | [5 empty] | YES |  |  |  | 2020-08-04 16:30 | 1283697 | 1283886 | NATURAL GAS |  | 47.1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-08-03 23:59 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 47.1 | NO | 3 | 2020-08-03 23:59 |  |  |  | 2020-08-04 01:03 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1970 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | DUE TO STRUCTURE FIRE, METER AND REG MELTED | CLASS 3 LOCATION | 200000 | 223281.5380563602 | 275 | 307.012114827495275 | 44007 | 49129.753226231216607 | 0 | 0 |  | 6.0085 | 283 | 352.306122448979591836734693877551020408 | 0 | 0 | 244565 | 113277.6458671657978768513119533527696793 | 273070.6095198678914738367346938775510204 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 55 | 55 | 60 | 192.619(A)(2) | 1970-09-01 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | THE IGNITION SOURCE AND FIRST FUEL IGNITED COULD NOT BE DETERMINED. | [45 empty] | EDWIN BAIRES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | ebaires2@socalgas.com | 213-326-1831 |  |  |  |  | EDWIN BAIRES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 213-326-1831 | ebaires2@socalgas.com | ON 08-03-20, SOCALGAS WAS NOTIFIED OF A STRUCTURE FIRE AT 230 DESERT BREEZE DR, CALIFORNIA CITY. SOCALGAS PERSONNEL RESPONDED AND SAFELY CONTROLLED THE GAS. THE METER SET ASSEMBLY WAS DESTROYED BY THE FIRE. THE CAUSE OF THE FIRE IS UNDER INVESTIGATION. SOCALGAS IS AWAITING THE FINAL INVESTIGATION REPORT FROM THE FIRE DEPT. ON THE ACTUAL CAUSE. THIS WAS REPORTED TO DOT (#1283697) AND CPUC DUE TO A RELEASE OF GAS AND DAMAGES EXCEEDING $50,000. 2-10- 21 UPDATE THE FINAL INVESTIGATION SHOWED THE FIRE ORIGINATED INSIDE THE DOUBLE WIDE MOBILE HOME AT 230 DESERT BREEZE DRIVE, CALIFORNIA CITY. THE IGNITION SOURCE AND FIRST FUEL IGNITED COULD NOT BE DETERMINED. DAMAGE TO THE SOCALGAS METER SET ASSEMBLY WAS DUE TO THE FIRE ORIGINATING INSIDE THE DOUBLE WIDE MOBILE HOME.
2025-03-31 10:13 | NO | NO | NO | 20200084 | 34313 | 2020-09-04 14:58 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2020-08-06 20:00 |  |  | 2020 | W PARKER RD AT RANCHERO RD | PLANO | COLLIN | TX | 75093 | 33.0427 | -96.8054 | [9 empty] | 2020-08-06 20:27 | 1283939 |  | NATURAL GAS |  | 927.3 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-08-06 11:22 |  |  |  | 2020-08-06 11:22 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 60 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1973 | [5 empty] | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 7560 | 8440.04213853041556 | 19392 | 21649.377929944684992 | 23108 | 25797.948907031857508 | 0 | 0 |  |  | 4582 | 5704.122448979591836734693877551020408163 |  | 0 | 54642 | 28423.5193223231453084548104956268221574 | 61591.4914244865498967346938775510204082 | 0 | 0 | 1 |  |  |  |  | 148 | 155 | 175 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | DUE TO THE FACT THAT THIS WAS A THIRD PARTY EXCAVATION DAMAGE AND THE OPERATING PRESSURE AT THE TIME OF THE INCIDENT WAS BELOW THE MAOP. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 2071713728 | TEXAS811 |  | CONTRACT LOCATOR | NO | YES | 16 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | QUINT NANCE | OPERATIONS SUPERVISOR | quint.nance@atmosenergy.com | 469-426-6575 |  |  |  |  | MARLO SUTTON | V.P. TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON AUGUST 6, 2020, A THIRD-PARTY EXCAVATOR INSTALLING TELECOMMUNICATIONS FIBER-OPTIC CABLE BORED INTO AN END CAP ON A 12-INCH HIGH PRESSURE STEEL LINE RESULTING IN MECHANICAL PUNCTURE. CREWS INITIALLY THOUGHT A 6-INCH POLY LINE IN THE VICINITY WAS HIT AND SQUEEZED OFF THAT LINE AT 4:15 PM ON THE SAME DAY, AUGUST 6, 2020. ONE RESIDENTIAL CUSTOMER LOST SERVICE AT THAT TIME. WHEN THE LEAK DID NOT STOP AFTER SQUEEZING OFF THE 6-INCH POLY LINE, CREWS REALIZED THE 12-INCH STEEL LINE HAD BEEN HIT. AT APPROXIMATELY 10:35 PM ON AUGUST 6, 2020, THE LEAK ON THE 12-INCH STEEL LINE WAS ISOLATED USING VALVES. AT 8:00 AM ON AUGUST 7, 2020, GAS WAS RESTORED TO THE CUSTOMER THAT LOST SERVICE WHEN THE 6-INCH WAS SQUEEZED OFF. THE GAS TO THE 12-INCH STEEL LINE WAS REINSTATED AT 4:04 PM ON AUGUST 7, 2020. INTERNAL INVESTIGATION INDICATED THAT THE LINE LOCATOR FAILED TO PROPERLY LOCATE THE LINE RESULTING IN A PORTION OF THE LINE NOT BEING MARKED. NRC UPDATE # 1284052.
2025-03-31 10:13 | YES | NO | NO | 20200085 | 34933 | 2020-09-10 15:10 | SUPPLEMENTAL FINAL | 2704 | CONSOLIDATED EDISON CO OF NEW YORK | 4 IRVING PLACE | NEW YORK | NY | 10003 | 2020-08-12 15:30 | EASTERN | NO | 2020 | 551 E 179 STREET | BRONX | BRONX | NY | 10457 | 40.8489 | -73.8937 |  |  | YES | [6 empty] | 2020-08-12 16:00 | 128439 |  | NATURAL GAS |  | 10 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-08-12 15:30 | OPERATOR/CONTRACTOR |  | 10 | NO | 0 | 2020-08-12 12:47 |  |  |  | 2020-08-12 13:00 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | INSIDE METER/REGULATOR SET |  | 1998 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | YES |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | OTHER | SECONDARY IGNITION GAS METER | [5 empty] | CLASS 4 LOCATION | 50000 | 55820.38451409005 | 0 | 0 | 800 | 893.1261522254408 | 0 | 0 |  | 1 | 10 | 12.44897959183673469387755102040816326531 | 0 | 0 | 50810 | 23500.5512382160307405247813411078717201 | 56725.9596459073275346938775510204081633 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0.25 | 0.25 | 0.5 | 192.623 | 1998-01-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SECONDARY IGNITION AT GAS METER SET DURING ONGOING BUILDING FIRE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | OSCAR LEON | OPERATIONS MANAGER | leono@coned.com | 718-319-2310 | 718-904-4607 | OSCAR LEON | operations manager | 718-319-2310 | OSCAR LEON | OPERATIONS MANAGER | 718-319-2310 | leono@coned.com | AT 12:47 ON AUGUST 12, 2020, NEW YORK CITY EMERGENCY MANAGEMENT (NYCEM) CALLED CON EDISON'S GAS EMERGENCY RESPONSE CENTER (GERC) AND REPORTED A FIRE INSIDE A WAREHOUSE LOCATED AT 551 EAST 179TH STREET IN THE BRONX. THE GERC IMMEDIATELY DISPATCHED CON EDISON GAS DISTRIBUTION SERVICES (GDS) AND GAS EMERGENCY RESPONSE GROUP (ERG) PERSONNEL TO THE LOCATION. THE GERC ALSO NOTIFIED CON EDISON'S ELECTRIC OPERATIONS DEPARTMENT. THE BUILDING IS SUPPLIED BY A 2-INCH LOW-PRESSURE POLYETHYLENE GAS SERVICE (INSTALLED IN 1998) AND AN UNDERGROUND ELECTRIC SERVICE. CON EDISON GDS ARRIVED AT 13:00, BEGAN TO INVESTIGATE AND REPORTED THAT NO GAS ODORS OR READINGS WERE DETECTED. AT 15:30, THE FIRE DEPARTMENT OF THE CITY OF NEW YORK (FDNY) BOROUGH COMMANDER CHIEF BOYLE REPORTED THAT A SECONDARY NATURAL GAS IGNITION HAD OCCURRED AND WAS ONGOING AT THE INDOOR METER SET. ADDITIONAL CON EDISON GDS AND EMERGENCY RESPONSE FORCE (ERF)/CONSTRUCTION PERSONNEL WERE DISPATCHED TO THE LOCATION BY THE GERC. AT 15:37, GDS CLOSED THE CURB VALVE ON THE GAS SERVICE SUPPLYING THE WAREHOUSE, THEREBY EXTINGUISHING THE SECONDARY IGNITION AT THE GAS METER SET. AT 17:03, GDS REPORTED THAT THE FDNY EXTINGUISHED THE STRUCTURAL FIRE. FDNY BOROUGH COMMANDER CHIEF BOYLE REPORTED THAT THE PRIMARY CAUSE OF THE FIRE WAS UNKNOWN. A SPECIAL GAS LEAK SURVEY WAS PERFORMED BY CON EDISON AND NO GAS ODORS OR READINGS WERE DETECTED. PRESSURE AND ODORANT READINGS WERE CHECKED AT 4290 3RD AVE AND WERE WITHIN THE ACCEPTABLE RANGES (8.0 INCHES W.C. AND 0.28 % GAS-IN-AIR, RESPECTIVELY). A CON EDISON ERF/CONSTRUCTION CREW CUT AND CAPPED THE GAS SERVICE AT THE MAIN. THERE WERE NO REPORTED INJURIES. MULTIPLE MEDIA OUTLETS WERE ON LOCATION. THE DAMAGE WAS REPORTED TO BE MORE THAN $50,000. NYSDPS, USDOT, AND NYCDEP WERE NOTIFIED.
2025-03-31 10:13 | NO | YES | NO | 20200087 | 34538 | 2020-09-18 16:14 | SUPPLEMENTAL FINAL | 12876 | DOMINION ENERGY UTAH/WYOMING/IDAHO | 333 SOUTH STATE STREET P.O. BOX 45360 | SALT LAKE CITY | UT | 84111 | 2020-08-19 05:33 |  |  | 2020 | 257 E CLARK STREET | GRANTSVILLE | TOOELE | UT | 84029 | 40.6027 | -112.4547 | [9 empty] | 2020-08-19 08:43 | 1284932 |  |  |  | 6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 4 | 2020-08-19 08:15 |  |  |  | 2020-08-19 06:06 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1992 | [8 empty] | OTHER | ALUMINUM (METER) | [9 empty] | OTHER | [8 empty] | METER MELTED DURING FIRE | CLASS 3 LOCATION | 200000 | 223281.5380563602 | 300 | 334.9223070845403 | 2194 | 2449.398472478271394 | 0 | 0 |  |  | 19 | 23.65306122448979591836734693877551020408 |  | 0 | 202513 | 93651.5791759797586469970845481049562682 | 226089.5118971475014899183673469387755102 | 0 | 0 | 1 |  |  |  |  | 45 | 45 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | [46 empty] | LAUREN SKUFCA | ENGINEER PIPELINE COMPLIANCE | lauren.l.skufca@dominionenergy.com | 2166338865 |  |  |  |  | REID HESS | MANAGER COMPLIANCE | 8013243374 | reid.hess@dominionenergy.com | ON AUGUST 19, 2020 DOMINION ENERGY UTAH (DEU) WAS NOTIFIED OF A HOUSE FIRE AT 257 E CLARK STREET, GRANTSVILLE, UTAH. DEU SENT A TECHNICIAN TO THE SITE. UPON ARRIVAL THE TECHNICIAN NOTED THAT THE FIRE DEPARTMENT HAD CLOSED THE SERVICE VALVE AND THAT THE METER WAS DAMAGED AND MELTED DUE TO THE FIRE. THE FIRE DEPARTMENT NOTED THAT THE DAMAGE TO THE STRUCTURE WAS ESTIMATED TO BE $200,000. DEU MADE THE NRC NOTIFICATION DUE TO THE ESTIMATED COST OF DAMAGES. DEU CREWS LEAK SCREENED THE AREA AND PRESSURE TESTED THE SERVICE LINE WITH NO LEAKS FOUND. DEU THEN RETIRED THE SERVICE LINE TO THE RESIDENCE. THIS EVENT IS BELIEVED TO BE A FIRE FIRST EVENT, HOWEVER THE CAUSE WAS UNABLE TO BE DETERMINED THROUGH DEU AND STATE FIRE MARSHALL INVESTIGATION. AT THIS TIME, THE CAUSE OF THE FIRE IS UNKNOWN AND THE INVESTIGATION IS COMPLETE.
2025-03-31 10:13 | NO | YES | NO | 20200088 | 35086 | 2020-09-23 11:29 | SUPPLEMENTAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY | CANONSBURG | PA | 15317 | 2020-08-27 13:34 | EASTERN | NO | 2020 | 2249 3RD AVE | NEW BRIGHTON | BEAVER | PA | 15066 | 40.1753 | -80.2985 | YES |  |  |  |  | YES |  |  |  | 2020-08-27 13:35 | 1285738 |  | NATURAL GAS |  | 2765 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-08-27 01:30 |  |  |  | 2020-08-27 02:12 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1985 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | A PASSENGER VEHICLE RAN INTO THE DISTRICT REGULATOR STATION AND SHEARED OFF THE SPOOL PIECE A PART OF THE MONITOR, CAUSING THE RELEASE OF GAS. | CLASS 3 LOCATION | 0 | 0 | 327500 | 365623.5185672898275 | 8150 | 9098.72267579667815 | 0 | 0 |  | 1.4799 | 4092 | 5094.122448979591836734693877551020408163 | 0 | 0 | 339742 | 159911.0754129710794227405247813411078717 | 379816.3636920660974867346938775510204082 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 70 | 80 | 192.619(A)(1) | 2013-12-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A VEHICULAR DAMAGE TO A DISTRICT REGULATOR. GAS CONTROL ONLY ASSISTED WITH CONFIRMATION OF TIME OF THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  | YES |  |  |  | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 75 | YES | [5 empty] | YES | THE REGULATOR STATION WAS INSIDE A FENCE | [135 empty] | RICHARD W BURKE | OPERATIONS COMPLIANCE MANAGER | rburke@nisource.com | 724-321-7155 |  |  |  |  | MICHAEL J DAVIDSON | VP AND GENERAL MANAGER | 724-416-6308 | mdavids@nisource.com | NEW BRIGHTON POLICE DEPARTMENT REPORTED THEY WERE IN PURSUIT OF A MALE IN A VEHICLE. THE VEHICLE IN QUESTION DROVE INTO THE PROPERTY AT 2249 3RD AVENUE NEW BRIGHTON. THE VEHICLE CONTINUED TO THE BACK OF THE PROPERTY WHERE IT RAN INTO THE OUTLET SIDE OF OUR DISTRICT REGULATOR STATION AND SHEARED OFF BOTH A SPOOL PIECE AND A SECTION OF THE MONITOR REGULATOR CAUSING A RELEASE OF GAS. THE REGULATOR STATION WAS PROTECTED BY A FENCE. ESTIMATED COST TO REBUILD THE DISTRICT REGULATOR STATION WILL BE GREATER THAN $50,000. UPDATE 11-24-2020 - COST OF COMPANY REPAIR - ESTIMATE OF $299,000 FOR A TOTAL COST OF $307,150
2025-03-31 10:13 | NO | NO | NO | 20200089 | 34306 | 2020-09-25 10:42 | ORIGINAL FINAL | 15938 | PUBLIC SERVICE CO OF NORTH CAROLINA | 800 GASTON ROAD | GASTONIA | NC | 28056 | 2020-08-27 12:15 |  |  | 2020 | 7520 NC HWY 751 | DURHAM | DURHAM | NC | 27713 | 35.9082 | -78.9604 | [9 empty] | 2020-08-27 13:20 | 1285735 |  | NATURAL GAS |  | 3484.68 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 3 | 2020-08-27 12:15 |  |  |  | 2020-08-27 12:27 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2017 | [5 empty] | 12 | API 5L | UNKNOWN | STEEL |  | OTHER | ELECTRIC RESISTANCE | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 1.3 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 7750 | 8652.15959968395775 | 0 | 0 | 34469 | 38481.456676323398669 | $22,869 COMPANY LABOR $11,600 CONTRACTOR LABOR |  | 15019 | 18697.1224489795918367346938775510204082 |  | 0 | 57238 | 36817.2632053385604341690962099125364431 | 65830.7387249869482557346938775510204082 | 2 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE WERE NO ACTIONS BY THE CONTROL ROOM WHICH INITIATED THE EVENT. FURTHERMORE, THE PRESSURE DROP CAUSED BY THE LINE DAMAGE WAS NOT LARGE ENOUGH TO TRIGGER ANY ALARMS IN THE CONTROL ROOM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY | 2017-12-12 | NO |  |  | YES | YES | [8 empty] | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | C20225257100C |  |  | CONTRACT LOCATOR | NO | YES | 9 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | EXCAVATOR WORKED BEYOND THE LOCATED AND MARKED AREA | [169 empty] | JERAMY FREE | ENGINEER IV - PIPELINE COMPLIANCE | jeramy.free@dominionenergy.com | (803)260-3602 |  |  |  |  | SCOTT SWINDLER | GENERAL MANAGER - OPERATIONS AND MAINTENANCE | (704)810-3230 | scott.swindler@dominionenergy.com | DOMINION ENERGY NORTH CAROLINA DISPATCH RECEIVED A CALL FROM 911 AT 12:15 ON AUGUST 27, 2020 TO RESPOND TO A HIT LINE AT 7520 NC HWY 751. THE EMERGENCY ORDER WAS DISPATCHED AND THE COMPANY FIRST RESPONDER ARRIVED ON SITE AT 12:27 PM. UPON ARRIVAL, THE DURHAM FIRE DEPARTMENT HAD EVACUATED THE NEARBY GAS STATION AND THE FIRE DEPARTMENT BLOCKED NC HWY 751 IN BOTH DIRECTIONS AND HAD CLOSED THE WEST BOUND ON RAMP FOR US INTERSTATE 40 WESTBOUND. A CONTRACTOR DIRECTIONAL DRILLING COMPANY (FIBER OPTIC CONTRACTOR), WAS BORING UNDER THE ROAD FOR FIBER OPTIC CABLE. DURING THE BORING PROCESS THEY HIT DOMINION'S 12-IN STEEL MAIN, OPERATING AT 55 PSIG, AND CAUSED A LEAK. GAS WAS SHUT OFF AT 11:28 PM AND DOMINION CREWS BEGAN WORKING ON REPAIRS. AFTER REPAIRS WERE COMPLETE, GAS WAS RESTORED ON AUGUST 28, 2020 AT 8:42 AM. THE DENC LDF MASTER LEAK ID NUMBER IS 316682. THE GAS LINE WAS MARKED CORRECTLY BASED ON THE DESCRIPTION ON THE LOCATE REQUEST. HOWEVER, THE EXCAVATOR WORKED BEYOND THE LOCATED AND MARKED AREA. ALSO, THERE WERE PIPELINE MARKERS IN THE IMMEDIATE AREA BEYOND THE GROUND MARKINGS.
2025-03-31 10:13 | NO | YES | NO | 20200091 | 34722 | 2020-10-02 14:06 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-09-04 14:35 | EASTERN | YES | 2020 | 8580 W. GRAND RIVER AVENUE | BRIGHTON | LIVINGSTON | MI | 48116 | 42.5415 | -83.787 |  | YES |  |  |  |  | YES |  |  | 2020-09-04 15:27 | 1286526 | 1286634 | NATURAL GAS |  | 841 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-09-03 08:45 | YES | OPERATOR | 2020-09-04 14:35 | 2020-09-03 09:01 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 54 | NO | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | BOLTED FLANGE | 1957 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 614407 | 685928.699762970507007 | 3289 | 3671.864893336843489 | 0 | 0 |  | 2.2592 | 1900 | 2365.306122448979591836734693877551020408 | 0 | 0 | 619596 | 287799.9184758668096597084548104956268222 | 691965.8707787563300878367346938775510204 | 13 | 0 | 0 | 0 | 0 | 0 | 13 | 340 | 355 | 355 | 192.619(C) | 1969-11-25 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | CONTRACTOR WORKING FOR THE OPERATOR | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | MATERIAL/WELD/EQUIP FAILURE | NON-THREADED CONNECTION FAILURE | EQUIPMENT FAILURE | NON-THREADED CONNECTION FAILURE | [197 empty] | NON-THREADED CONNECTION FAILURE | [14 empty] | GASKET | [68 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON SEPTEMBER 3, 2020 AT APPROXIMATELY 08:45 HOURS CONSUMERS ENERGY WAS NOTIFIED BY THE LEAK SURVEY CONTRACTOR OF A POSSIBLE GAS LEAK ON W. GRAND RIVER AVENUE, BETWEEN HILTON AND CHALLIS BRIGHTON, MICHIGAN (LIVINGSTON COUNTY). A GAS SERVICE WORKER (GSW) ARRIVED ONSITE AT 09:01 HOURS AND BEGAN A LEAK INVESTIGATION. DURING THE INVESTIGATION, MULTIPLE UNDERGROUND READS WERE DISCOVERED AS WELL AS READS IN NEARBY MANHOLES. THE GSW REQUESTED ADDITIONAL RESOURCES, GAS SERVICE AND GAS DISTRIBUTION, TO ASSIST WITH LEAK PROSPECTING AND TO CHECK NEARBY STRUCTURES TO ENSURE PUBLIC SAFETY. THE GAS DISTRIBUTION CREW ARRIVED ONSITE AT 10:40 HOURS AND BEGAN VENTING TRAFFIC SIGNAL MANHOLES WHERE GAS READS WERE DISCOVERED AND PROCEEDED WITH LEAK PROSPECTING TO IDENTIFY THE SOURCE OF THE GAS RELEASE. TRAFFIC CONTROL WAS SET UP AND EMERGENCY RESPONDERS (POLICE AND FIRE) WERE ONSITE TO ASSIST WITH TRAFFIC CONTROL. THERE WERE NO FATALITIES OR INJURIES AS A RESULT OF THE INCIDENT. THE DISTRIBUTION CREW CONTINUED EXPOSING A 6" STEEL HIGH-PRESSURE PIPELINE AND LEAK PINPOINTING THROUGH THE NIGHT DISCOVERING A FROST BALL ON THE PIPELINE NEAR 8580 W. GRAND RIVER AVENUE. GAS OPERATIONS ISOLATED THE HIGH-PRESSURE PIPELINE FROM THE VALVE CLUSTER AT HOWELL RS 402 (HILTON ROAD) BY CLOSING DESIGNATED VALVE H140 AND ENSURING H138 WAS OPEN. THIS RESULTED IN A LOSS OF SERVICE TO 13 CUSTOMERS. THE GAS MECHANICS PROCEEDED TO CLOSED IN BOTH HP STATIONS TO ISOLATE THE LINE. THE VALVE STOPPAGE WAS UNSUCCESSFUL AND REQUIRED THE INSTALLATION OF CONTROL FITTINGS TO OBTAIN A COMPLETE SHUT-DOWN. THE PIPELINE WAS ISOLATED, CUT AND CAPPED ON SEPTEMBER 5, 2020 AT APPROXIMATELY 21:30 THE SOURCE OF THE LEAK WAS DETERMINE TO BE A 4" HP BOLTED FLANGE FITTING OFF OF A MUELLER HP BOTTOM-OUT FITTING. THE FLANGE GASKET FAILED CAUSING GAS TO BE RELEASED. ON SEPTEMBER 10, 2020, APPROXIMATELY 390'-2" PLASTIC MEDIUM-PRESSURE PIPELINE WAS INSTALLED AND SERVICE RESTORE TO THE 13 CUSTOMERS PREVIOUSLY SERVED BY THE HP PIPELINE. THE ISOLATED SEGMENT OF THE HIGH-PRESSURE PIPELINE HAS BEEN SCHEDULE FOR REPLACED AT A LATER DATE. A CONSTRUCTION PROJECT REPLACING 884 FEET OF 6-INCH STEEL HIGH PRESSURE PIPELINE WAS COMPLETED AND NORMAL OPERATIONS RESUMED ON NOVEMBER 20, 2020.
2025-03-31 10:13 | NO | NO | NO | 20200092 | 34366 | 2020-10-05 11:10 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2020-09-04 15:08 |  |  | 2020 | 321 EAST MONTGOMERY STREET | GAFFNEY | CHEROKEE | SC | 29340 | 35.0685 | -81.6482 | [9 empty] | 2020-09-04 19:36 | 1286547 |  | NATURAL GAS |  | 13.49 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 2 | 2020-09-04 15:16 |  |  |  | 2020-09-04 15:16 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1976 | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 2 LOCATION | 0 | 0 | 100000 | 111640.7690281801 | 500 | 558.2038451409005 | 0 | 0 |  |  | 150 | 186.73469387755102040816326530612244898 |  | 0 | 100650 | 46642.1900902277211078717201166180758017 | 112385.707567198551520408163265306122449 | 0 | 0 | 1 |  |  |  |  | 65 | 65 | 120 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | NATURAL FORCE DAMAGE | OTHER NATURAL FORCE DAMAGE | [56 empty] | OTHER NATURAL FORCE DAMAGE |  |  |  |  | ,,,,,,LARGE DEAD OAK TREE BROKE OFF AND FELL ACROSS THE OVERHEAD POWER LINES AND ON TO THE GAS METER SET. THIS BROKE THE PIPE NIPPLE AT THE GAS SERVICE RISER SHUT OFF DAMAGING IT. THE POWER LINE BEING CARRIED ONTO THE GAS SERVICE IGNITED THE ESCAPING GAS AND IGNITED THE STRUCTURE. | NO | [218 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 7047314680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 7047314618 | farris.berry@duke-energy.com | LARGE DEAD OAK TREE BROKE OFF AND FELL ACROSS THE OVERHEAD POWER LINES AND ON TO THE GAS METER SET. THIS BROKE THE PIPE NIPPLE AT THE GAS SERVICE RISER SHUT OFF DAMAGING IT. THE POWER LINE BEING CARRIED ONTO THE GAS SERVICE IGNITED THE ESCAPING GAS AND IGNITED THE STRUCTURE.
2025-03-31 10:13 | NO | YES | NO | 20200093 | 34802 | 2020-10-05 17:37 | SUPPLEMENTAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2020-09-04 23:48 | EASTERN | NO | 2020 | 101 BROOKSIDE DRIVE | ANNA | SHELBY | OH | 45302 | 40.3954 | -84.1844 |  |  | YES | [6 empty] | 2020-09-05 03:36 | 1286567 |  | NATURAL GAS |  | 77 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-09-04 23:48 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 77 | NO | 4 | 2020-09-04 23:48 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-09-04 23:48 | 2020-09-05 00:20 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2005 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | YES | NO | YES |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2408 | OTHER | [8 empty] | SOURCE OF RELEASE STILL UNDER INVESTIGATION | CLASS 3 LOCATION | 343000 | 382927.837766657743 | 5000 | 5582.038451409005 | 1000 | 1116.407690281801 | 0 | 0 |  | 3.6883 | 284 | 353.551020408163265306122448979591836735 | 0 | 0 | 349284 | 161698.5767701112458309037900874635568513 | 389979.8349287567122653061224489795918367 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 51 | 51 | 60 | 192.619(A)(2) | 2005-10-31 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 8 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | STILL UNDER INVESTIGATION, CAUSE OF INCIDENT TO BE DETERMINED* (*SUPPLEMENTAL REPORT REQUIRED) | [46 empty] | JEFFERY BURDETTE | SUPERVISOR - PIPELINE COMPLIANCE | jeffery.l.burdette@dominionenergy.com | 330-754-5524 |  |  |  |  | CAROL HAGER | MANAGER GAS OPERATIONS PIPELINE SAFETY | 330-266-2152 | carol.m.hager@dominionenergy.com | AN APARTMENT FIRE AT 101 BROOKSIDE DRIVE, ANNA OHIO WAS REPORTED TO DOMINION. UPON ARRIVAL THE FIRE WAS ALREADY OUT, AND THE GAS TO THE METER SETTING WAS TURNED OFF BY THE FIRE DEPARTMENT. THE DOMINION RESPONDER CHECKED THE AREA FOR ANY LEAKING NATURAL (NO LEAKS FOUND) AND SHUT OFF THE METER SET VALVE. IT WAS NOT IMMEDIATELY DISCUSSED THAT THE METER SET WAS A POSSIBLE SOURCE OF THE FIRE ON THE SCENE. ONCE IT WAS DETERMINED TO BE A POSSIBILITY, DOMINION MADE THE REQUIRED NOTIFICATIONS AND STARTED THE INVESTIGATION PROCESS. THIS EVENT IS STILL UNDER INVESTIGATION, AND NATURAL GAS HAS NOT YET BEEN DETERMINED TO BE THE SOURCE OF THE HOUSE FIRE, OR THE LEAKING NATURAL GAS WAS A SECONDARY EVENT AS A RESULT OF THE HOUSE FIRE.
2025-03-31 10:13 | YES | NO | NO | 20200094 | 34610 | 2020-10-08 16:01 | SUPPLEMENTAL FINAL | 31232 | AVISTA CORP | 1411 EAST MISSION (PO BOX 3727, 99220-3727) | SPOKANE | WA | 99202 | 2020-09-09 17:00 |  |  | 2020 | UNKNOWN | TALENT | JACKSON | OR | 97540 | 42.2219 | -122.8173 | [9 empty] | 2020-09-09 17:30 | 1287140 |  | NATURAL GAS |  | 16.67 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 5600 | 2020-09-08 11:00 |  |  |  | 2020-09-08 11:15 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | RISERS AND METERS |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | [8 empty] | OTHER | ALUMINUM METERS AND ASSOCIATED RISERS | [9 empty] | OTHER | [8 empty] | FIRE CONSUMED OUTSIDE METER SET ASSEMBLIES | CLASS 3 LOCATION | 0 | 0 | 438063 | 489056.902027916591463 | 169242 | 188943.070318672564842 | 0 | 0 |  |  | 73 | 90.87755102040816326530612244897959183673 |  | 0 | 607378 | 280891.3214667708378058309037900874635569 | 678090.8498976095644682653061224489795918 | 100 | 0 | 1400 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | OTHER | LOCAL AND STATE OFFICIALS MONITORING FIRES |  | YES, SPECIFY INVESTIGATION RESULT(S): (SELECT ALL THAT APPLY) |  |  |  |  | YES | [8 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | BRIAN SCHULTZ | PIPELINE INTEGRITY PROGRAM MANAGER | brian.schultz@avistacorp.com | 509-495-2162 |  |  |  |  | ELIZABETH FREDERIKSEN | MANAGER OF PIPELINE INTEGRITY AND COMPLIANCE | 5094958215 | elizabeth.frederiksen@avistacorp.com | ON 9/8/20, AVISTA BECAME AWARE OF SEVERAL FIRES IN THE MEDFORD, OREGON AREA. AS A PRECAUTION, AVISTA OPERATIONS DECIDED TO CLOSE 34 VALVES AND PERFORM MULTIPLE CUT AND CAPS WHERE NECESSARY TO ISOLATE CUSTOMERS LOCATED IN HIGH FIRE-RISK AREAS IN ASHLAND, TALENT, PHOENIX AND MEDFORD, OREGON. ON 9/9/20 AVISTA NOTIFIED THE NATIONAL RESPONSE CENTER (NRC) SINCE AVISTA'S RESPONSE TO THE FIRES WERE DECIDED (PER THE DEFINITION OF CONFIRMED DISCOVERY) TO MEET THE DEFINITION OF AN "INCIDENT" AS DEFINED IN 49 CFR 191.3, SPECIFICALLY, THAT THERE WAS A RELEASE OF GAS AND AN ANTICIPATED ESTIMATED PROPERTY DAMAGE OF GREATER THAN $50,000. BEGINNING ON 9/10/20 AVISTA BEGAN ASSESSING ALL METERS AND RISERS WITHIN THESE ZONES, CONSISTING OF 1,368 INDIVIDUAL INSPECTION SITES, OF WHICH 1,300 WERE ASSOCIATED TO AN ACTIVE CUSTOMER ACCOUNT. OF THOSE ASSESSED, 904 METER POINTS WERE IDENTIFIED AS A TOTAL LOSS WHICH HAD AN ACTIVE CUSTOMER ACCOUNT ASSOCIATED TO THEM AND 396 POINTS WITH ACTIVE ACCOUNTS WERE ASSESSED AS OK TO RELIGHT. ON 9/19/20 AVISTA PERFORMED A METER SAFETY CHECK ON 748 METERS AND RISERS OUTSIDE OF THE KNOWN SHUT DOWN ZONES, RESULTING IN IDENTIFYING 84 ADDITIONAL METERS AS A TOTAL LOSS WHICH WERE CONNECTED TO AN ACTIVE CUSTOMER ACCOUNT. AN ADDITIONAL EIGHT METERS WERE IDENTIFIED AS OK TO RELIGHT. THROUGHOUT THE EVENT AVISTA WORKED TO RELIGHT ALL CUSTOMERS WITH ACTIVE ACCOUNTS WHO WERE EITHER IDENTIFIED AS OK TO RELIGHT OR REQUIRED REPAIRS BEFORE RELIGHT. ANY CUSTOMER NOT HOME DURING THE INITIAL VISIT RECEIVED A DOOR HANGER AND ONCE READY, AVISTA HAS RETURNED TO SAFELY RELIGHT THEIR APPLIANCES. REMAINING CUSTOMERS ARE BEING HANDLED ON AN INDIVIDUAL CASE BY CASE BASIS, AS APPLICABLE, BY THE MEDFORD CONSTRUCTION DEPARTMENT TO ADDRESS EACH UNIQUE CIRCUMSTANCE SO NATURAL GAS CAN BE RESTORED WHEN APPROPRIATE. REBUILDING AND FUTURE PLANS FOR DEMOLITION AND NEW CONSTRUCTION WILL BE ONGOING FOR THE FORESEEABLE FUTURE IN THE AREAS AFFECTED. IF ESTIMATED PROPERTY DAMAGE EXCEEDS 20% OF THE AMOUNT INDICATED ON LINE D2E, A SUPPLEMENTAL REPORT WILL BE SUBMITTED. A SUPPLEMENTAL FINAL REPORT WAS SUBMITTED ON 12/10/2020 DUE TO AN INCREASE IN PROPERTY DAMAGE EXCEEDING 20% OF THE PREVIOUSLY SUBMITTED AMOUNT.
2025-03-31 10:13 | NO | NO | NO | 20200095 | 34359 | 2020-10-09 19:23 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2020-09-11 03:03 |  |  | 2020 | 2200 W FLORIDA AVE | HEMET | RIVERSIDE | CA | 92545 | 33.7474 | -116.9961 | [9 empty] | 2020-09-11 11:45 | 1287114 |  | NATURAL GAS |  | 100.5 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-09-11 03:03 |  |  |  | 2020-09-11 06:05 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 48 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1965 | [5 empty] | 6 | GRADE X42, MILL TEST PRESS 1790 | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | LEAK |  |  | OTHER | DAMAGE SIZE 3.0IN X 0.25IN | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 358 | 399.673953120884758 | 74436 | 83100.922833816139236 | 0 | 0 |  |  | 313 | 389.653061224489795918367346938775510204 |  | 0 | 75107 | 34943.8947885561352184256559766763848397 | 83890.2498481615137899183673469387755102 | 2 | 0 | 113 |  |  |  |  | 365 | 365 | 400 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | THE CAUSE OF THE GAS LEAK WAS DUE TO A WATER MAIN LEAK. | [154 empty] | EDWIN BAIRES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | ebaires2@socalgas.com | 2133261831 |  |  |  |  | EDWIN BAIRES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 2133261831 | ebaires2@socalgas.com | SOCALGAS WAS NOTIFIED OF A GAS LEAK AT 2200 W FLORIDA AVE, HEMET, CA. SOCALGAS DISCOVERED A 6" HIGH PRESSURE DISTRIBUTION SUPPLY LINE 41-22 TO BE LEAKING. GAS WAS CONTROLLED AT 10:30 ON 09/11/20. 115 CUSTOMERS WERE TEMPORARILY OUT OF GAS SERVICE. A SECTION OF THE MAIN WAS REPLACED AND WELDED. GAS WAS RESTORED AT 13:00 ON 09/12/2020. THERE WERE NO REPORTED FATALITIES OR INJURIES DUE TO THE GAS RELEASE. INVESTIGATION SHOWS THE CAUSE OF THE GAS LEAK WAS DUE TO PRESSURIZED WATER LEAKING FROM A NEARBY WATER MAIN. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO A GAS RELEASE AND POTENTIAL DAMAGES TO EXCEEDING $50,000
2025-03-31 10:13 | NO | NO | NO | 20200096 | 34390 | 2020-10-12 12:28 | SUPPLEMENTAL FINAL | 14200 | OKALOOSA COUNTY GAS DISTRICT | 364 VALPARAISO PKWY | VALPARAISO | FL | 32580 | 2020-09-16 12:29 |  |  | 2020 | 3742 E. HIGHWAY 90 | CRESTVIEW | OKALOOSA | FL | 32539 | 30.75 | -86.4813 | [9 empty] | 2020-10-09 07:10 | 1289340 |  | NATURAL GAS |  | 3.6 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2020-09-16 12:29 |  |  |  | 2020-09-16 13:29 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | OTHER | SPECIAL UTILITY DISTRICT | OUTSIDE METER/REGULATOR SET |  | 2007 | [8 empty] | STEEL |  | OTHER | UNKNOWN | 0.133 | [6 empty] | OTHER | [8 empty] | ELECTRICAL ARC | CLASS 1 LOCATION | 39000 | 43539.899920990239 | 1000 | 1116.407690281801 | 600 | 669.8446141690806 | 0 | 0 |  |  | 8 | 9.95918367346938775510204081632653061224 |  | 0 | 40608 | 18781.9456872631941924198250728862973761 | 45336.1114091145899877551020408163265306 | 0 | 0 | 1 |  |  |  |  | 0.25 | 0.25 | 70 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | TERRY DAVIS | COMPLIANCE SUPERVISOR | terrydavis@okaloosagas.com | 850-729-4707 |  |  |  |  | BRENT HAYWOOD | VICE PRESIDENT OF OPERATIONS | 850-729-4741 | brenthaywood@okaloosagas.com | HURRICANE SALLY CAUSE A LIMB TO FALL ON AN ELECTRIC HIGH VOLTAGE LINE. WHEN THE LINE FELL THERE WAS AN ELECTRIC FAULT SENT TO THE RESIDENCE AT 3742 E HIGHWAY 90, CRESTVIEW, FL. THE INITIAL INVESTIGATION APPEARED TO INDICATE A STRUCTURE FIRE THAT CAUSE A SECONDARY DAMAGE TO THE GAS METER AT THE HOUSE. THE GAS METER WAS DAMAGED AND THE ESCAPING GAS IGNITED. THE DAMAGE TO THE RESIDENCE APPEARS TO BE MORE THAN $50,000 AT FIRST INSPECTION. SUPPLEMENTAL FINDING - THE GAS METER DOES APPEAR TO HAVE BEEN DAMAGED AND ELECTRIC POWER LINE FAULT WHICH WOULD BE DESIGNATED AS A SECONDARY IGNITION NOT A RELEASE OF GAS. IN CONJUNCTION THE ESTIMATED VALUE OF THE RESIDENCE WAS BASED ON THE VALUATION OF THE STRUCTURES ON THE WHOLE PROPERTY WHICH INCLUDE TWO RESIDENTIAL STRUCTURE TOTALING $125,457. THE DAMAGED STRUCTURE AS A RESULT HAS AN ESTIMATED VALUE OF $39,000 WHICH WOULD BE UNDER THE $50,000 THRESHOLD AS WELL. PLEASE NOTE THAT THE EXISTING LINE IS OUT OF SERVICE AND WILL BE REINSTATED PER THE CUSTOMERS REQUEST.
2025-03-31 10:13 | NO | YES | NO | 20200097 | 34680 | 2020-10-15 10:16 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2020-09-02 10:34 | CENTRAL | NO | 2020 | 3401 O STREET | LINCOLN | LANCASTER | NE | 68510 | 40.8133 | -96.6715 | [6 empty] | YES |  |  | 2020-09-16 14:42 | 1287516 |  | NATURAL GAS |  | 2 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-09-02 11:30 | YES | OPERATOR | 2020-09-02 10:45 | 2020-09-02 11:24 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 24 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1931 | [5 empty] | 16 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.25 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 60000 | 66984.46141690806 | 190000 | 212117.46115354219 | 50000 | 55820.38451409005 | 15000 | 16746.115354227015 | TRAFFIC CONTROL, EMS | 20 | 40 | 49.79591836734693877551020408163265306122 | 0 | 0 | 315040 | 145696.5777032810909620991253644314868805 | 351718.2183571346619387755102040816326531 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 70 | 70 | 74 | 192.619(A)(4) | 1994-02-23 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.1 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | LOCALIZED PITTING | [6 empty] | YES | POORLY COATED 1931 VINTAGE PIPE WITH BAD COATING AT POINT OF CORROSION FAILURE. |  |  | YES |  |  |  | YES | YES |  | YES | YES | YES |  | YES | 2020 |  | 2020 | CP SURVEYS IN AREA IMMEDIATELY AFTER INCIDENT WERE COMPLIANT |  | YES | OTHER | FIELD APPLIED MOP/HAND COALTAR | YES | [19 empty] | 2018-08-08 | NO | [227 empty] | TOM DORSHORST | PIPELINE SAFETY COMPLIANCE COORDINATOR | tom.dorshorst@blackhillscorp.com | 308 760 4592 |  |  |  |  | TOM DORSHORST | PIPELINE SAFETY COMPLIANCE COORDINATOR | 402 858 3602 | tom.dorshorst@blackhillscorp.com | GAS LEAK WAS CALLED IN TO THIS LOCATION BY CUSTOMER SMELLING GAS OUTSIDE FOR 3 MINUTES ON SEPT 2, 2020. BHE TECHNICIAN RESPONDED PERFORMED OUTSIDE LEAK INVESTIGATION. LZ-30 AND CGI INSTRUMENTS DETECTED UNDERGROUND LEAK AND WAS PINPOINTED UNDER THE CONCRETE OF O STREET. O STREET TRAFFIC WAS CLOSED AND CONCRETE WAS REMOVED TO VENTILATE LEAK. LEAK WAS ON 16 INCH STEEL MAIN AND LATER DETERMINED TO BE A PINHOLE CORROSION LEAK. A 16 INCH SHORT STOP NEEDED TO BE ORDERED AND CONTRACTOR HIRED TO INSTALL STOP IN ORDER TO DO REPAIR. STREET REMAINED CLOSED TO ALLOW VENTING OF PINHOLE LEAK UNTIL 9-12-2020 AS DATE OF REPAIR. TO REPAIR LEAK, AN EXISTING SHORT STOP WAS USED ALONG WITH A NEWLY INSTALLED SHORTSTOP TO ISOLATE THE LEAK AND CUT OUT PIPE SECTION TO REPLACE. THE CORROSION DEPARTMENT INVESTIGATED THIS DETERMINED THAT THE STEEL MAIN WAS POORLY COATED 1931 VINTAGE PIPE AND THE POINT OF CORROSION WAS DIRECTLY UNDER POOR COATING. IT HAD A CORROSION RATE OF 2.8 MPY. CP TEST POINTS CLOSE TO THIS LOCATION HAD SUFFICIENT CP PROTECTION HISTORICALLY, BUT WERE NOT SUFFICIENT IN THE BELL HOLE OF WHERE THE LEAK OCCURRED. BHE INSTALLED 6 ANODES IN THE BELL HOLE OF THE MAIN AT THIS LOCATION TO RAISE CP PROTECTION TO AN ACCEPTABLE LEVEL. CP TEST POINTS REMAIN AT AN ACCEPTABLE LEVEL OF PROTECTION AFTER REPAIR. ON 9-16-2020, IT WAS DETERMINED THAT COSTS OF EQUIPMENT, CONTRACTORS, AND STREET REPAIR EXCEEDED THE $50,000 LEVEL OF REPORTING.
2025-03-31 10:13 | NO | NO | NO | 20200098 | 34380 | 2020-10-15 11:45 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2020-09-18 09:56 |  |  | 2020 | 3178 LAVON DRIVE | GARLAND | DALLAS | TX | 75040 | 32.9456 | -96.6212 | [9 empty] | 2020-09-18 10:31 | 1287688 |  | NATURAL GAS |  | 435 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-09-09 12:35 |  |  |  | 2020-09-09 12:35 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 52 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2005 | [5 empty] | 6 | API 5L 45TH EDITION | UNKNOWN | STEEL |  | OTHER | ERW | 0.188 | [6 empty] | MECHANICAL PUNCTURE | 1 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 87072 | 97207.850408216976672 | 0 | 0 | 0 | 0 |  |  | 2490 | 3099.795918367346938775510204081632653061 |  | 0 | 89562 | 43128.068955773717110670553935860058309 | 100307.6463265843236107755102040816326531 | 0 | 0 | 0 |  |  |  |  | 73 | 75 | 95 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | 3RD PARTY DAMAGE BY CONTRACTOR | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | NO | [7 empty] | YES | [6 empty] | CONTRACTOR | AUGER | STREET LIGHT | YES | 2074640492 | TEXAS811 |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | ELIZABETH DELGADO | OPERATIONS MANAGER | elizabeth.delgado@atmosenergy.com | 972-485-6256 | 972-485-6267 |  |  |  | MARLO SUTTON | VICE PRESIDENT - TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON SEPTEMBER 9, 2020, A THIRD-PARTY CONTRACTOR USING AN AUGER TO INSTALL STREETLIGHTS AT 3178 LAVON DR. IN GARLAND, TX STRUCK ATMOS ENERGY'S 6-INCH DISTRIBUTION LINE. LINE LOCATES HAD BEEN CALLED IN AND LINES WERE MARKED CORRECTLY. NO CUSTOMERS WERE AFFECTED BY THE INCIDENT; CNG TRUCKS WERE DISPATCHED TO SUPPLY GAS DURING REPAIRS. THE 6-INCH MAIN WAS SQUEEZED OFF AT 4:33 AM ON 9/10/2020, AND REPAIRS BEGAN. THE PIPELINE WAS PLACED BACK IN SERVICE AT 7:00 PM ON 9/11/2020. INCIDENT REPORTING CRITERIA WAS MET AT 09:56 ON 9/18/20 AFTER IT WAS DETERMINED THAT THE PROPERTY DAMAGE EXCEEDED $50,000, AND IT WAS REPORTED TO THE NRC AT 10:31 ON 9/18/2020. 48 HOUR NRC REPORT # 1287826
2025-03-31 10:13 | NO | YES | NO | 20200099 | 34394 | 2020-10-16 18:09 | ORIGINAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2020-09-18 16:00 |  |  | 2020 | 928 NORTHTON | FORT WORTH | TARRANT | TX | 76110 | 32.7339 | -97.3524 | [9 empty] | 2020-09-18 16:53 | 1287736 |  | NATURAL GAS |  | 38308 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 175 | 2020-09-18 13:20 |  |  |  | 2020-09-18 13:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 47 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2011 | [5 empty] | 6 | ASTM D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 3 | 6 |  | CLASS 3 LOCATION | 0 | 0 | 61349 | 68490.495391098209549 | 135698 | 151494.290755859832098 | 0 | 0 |  |  | 219353 | 273072.1020408163265306122448979591836735 |  | 0 | 416400 | 343718.7829970619759532361516034985422741 | 493056.8881877743681776122448979591836735 | 2 | 0 | 0 |  |  |  |  | 23 | 23 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY | 2020-01-24 | NO |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | UTILITY | BORING | TELECOMMUNICATIONS | YES | 2075314339 | TEXAS811 |  | CONTRACT LOCATOR | YES | YES | 41 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | TONY MARLOW | OPERATIONS SUPERVISOR | tony.marlow@atmosenergy.com | 469-261-2074 |  |  |  |  | MARLO SUTTON | V.P. TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON SEPTEMBER 18, 2020, EXCAVATOR WAS BORING TELECOMMUNICATIONS AT 900 FORREST PARK AT ROSEDALE AND DAMAGED A 6-INCH POLY MAIN NEAR 928 NORTHTON STREET. ATMOS ENERGY TECHNICIAN ARRIVED AT 1:25 PM AND REQUESTED ASSISTANCE AT 1:30 PM. THE TECHNICIAN EVACUATED THE BUSINESS AT 928 NORTHTON STREET AND, WITH THE HELP OF FIRE DEPARTMENT PERSONNEL, A HOTEL NEARBY. FORREST PARK WAS BLOCKED NORTH OF ROSEDALE, AND WESTBOUND ROSEDALE WAS BLOCKED OFF AS WELL. CREWS RESPONDED, ARRIVING AT 1:40 PM AND DETERMINED THAT THE 12-INCH STEEL MAIN THE 6-INCH TIED INTO WOULD HAVE TO BE SHUT OFF USING SHORT STOP FITTINGS. ATMOS ENERGY CONTRACTOR WAS CALLED IN TO ASSIST. DURING THE COURSE OF REPAIRS, THE GAS WAS SHUT OFF AT 5:20 AM ON 9/20/2020. TWO RESTAURANTS WERE OUT OF SERVICE. SERVICE WAS RESTORED AT 11:58 AM ON 9/21/2020. PER ATMOS ENERGY'S INVESTIGATION, LINE LOCATES WERE COMPLETED CORRECTLY, AND THE DAMAGED MAIN WAS MARKED ACCURATELY. IT WAS DETERMINED THAT THIS INCIDENT WILL REACH THE REPORTABLE CRITERIA AT 4:00 PM ON 9/18/20. INITIAL REPORT #1287736 MADE TO THE NRC AT 4:53 PM ON 9/18/20. THE 48-HOUR UPDATE #1287837 WAS PROVIDED AT 2:14 PM ON 9/20/20.
2025-03-31 10:13 | NO | YES | NO | 20200100 | 34510 | 2020-10-17 23:22 | SUPPLEMENTAL FINAL | 621 | ARKANSAS OKLAHOMA GAS CORP | 10825 E. GEDDES AVENUE. SUITE 410 | CENTENNIAL | CO | 80112 | 2020-09-16 21:20 |  |  | 2020 | SW CORNER OF ZERO ST AND MASSARD RD | FORT SMITH | SEBASTION | AR | 72916 | 35.3235 | -94.3421 | [9 empty] | 2020-09-16 22:16 | 1287560 |  | NATURAL GAS |  | 3282 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2020-09-16 21:20 |  |  |  | 2020-09-16 21:30 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OTHER | PIPELINE CONNECTION STATION | 2011 | [8 empty] | OTHER | GASKET | [9 empty] | LEAK |  |  | SEAL OR PACKING | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 192565 | 214981.046879115009565 | 10478 | 11697.719778772710878 | 0 | 0 |  |  | 5822 | 7247.795918367346938775510204081632653061 |  | 0 | 208865 | 100588.1823159452522135276967930029154519 | 233926.5625762550673817755102040816326531 | 3 | 0 | 0 |  |  |  |  | 213 | 215 | 280 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | ON DUTY CONTROLLER OBSERVED PRESSURE DROPS SHORTLY AFTER CALL RECEIVED FROM EMERGENCY RESPONDERS, AND PRIOR TO ALARMS. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | VALVE | MATERIAL/WELD/EQUIP FAILURE | VALVE | EQUIPMENT FAILURE | VALVE | [197 empty] | VALVE | [16 empty] | OTHER | A LIGHTNING STRIKE ON 09/01/2020 IS SUSPECTED TO HAVE DAMAGED A MECHANISM ON A12-INCH VALVE ASSEMBLY CAUSING A LEAK WHICH EVENTUALLY IGNITED FROM AN UNKNOW SOURCE ON 9/16/2020. | [65 empty] | TYLER DAVIS | SUPERVISOR REGULATORY AFFAIRS | tdavis@summitutilitiesinc.com | 2077811200 |  |  |  |  | STANWOOD GIVEN | DIRECTOR OF PIPELINE SAFETY | 207-621-8000 | sgiven@summitnaturalgas.com | A LIGHTNING STRIKE ON 09/01/2020 IS SUSPECTED TO HAVE DAMAGED A 12-INCH VALVE ASSEMBLY CAUSING A LEAK WHICH EVENTUALLY IGNITED FROM AN UNKNOWN SOURCE ON 09/16/2020. THIS DETERMINATION WAS REACHED DURING A ROOT CAUSE ANALYSIS CONDUCTED BY A TEAM OF SUBJECT MATTER EXPERTS FROM SUMMIT UTILITIES, INC., THE PARENT COMPANY OF ARKANSAS OKLAHOMA GAS CORPORATION ("AOG"). THE RESULTING FIRE DAMAGED AOG'S STATION INFRASTRUCTURE AND RESULTED IN AN OUTAGE OF THREE COMMERCIAL CUSTOMERS IN THE IMMEDIATE AREA. THE STATION IS IN THE PROCESS OF BEING REBUILT AND RECONFIGURED TO REDUCE THE NUMBER OF ABOVE GROUND APPURTENANCES. EXPECTED COMPLETION DATE IS 11/13/2020.
2025-03-31 10:13 | NO | YES | NO | 20200101 | 34454 | 2020-10-21 16:47 | SUPPLEMENTAL FINAL | 30750 | MIDAMERICAN ENERGY COMPANY | 401 DOUGLAS STREET PO BOX 778 | SIOUX CITY | IA | 51101 | 2020-09-24 21:36 |  |  | 2020 | 400 BEACH AVENUE | DELL RAPIDS | MINNEHAHA | SD | 57022 | 43.8235 | -96.7017 | [9 empty] | 2020-09-25 11:33 | 1288248 |  | NATURAL GAS |  | 10.7 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 3 | 2020-09-24 21:36 |  |  |  | 2020-09-24 22:17 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 1 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1994 | [5 empty] | 2 | ASTM D2513 | PLEXCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 21 | 1.5 | [7 empty] | CLASS 3 LOCATION | 350000 | 390742.69159863035 | 679 | 758.040821701342879 | 4576 | 5108.681590729521376 | 0 | 0 |  |  | 22 | 27.38775510204081632653061224489795918367 |  | 0 | 355277 | 164289.0597085366238291545189504373177843 | 396636.8017661632550713265306122448979592 | 1 | 0 | 0 |  |  |  |  | 43 | 45 | 50 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO | [9 empty] | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | CURB/SIDEWALK | NO | [5 empty] | YES | 18 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CHRISTOPHER R. PAYER | SENIOR ENGINEER | chris.payer@midamerican.com | 712-277-7941 |  |  |  |  | DEHN STEVENS | VICE PRESIDENT GAS DELIVERY | 515-242-4274 | dehn.stevens@midamerican.com | BX CIVIL & CONSTRUCTION (THIRD PARTY CONTRACTOR) WAS DOING FINE GRADING IN PREPARATION FOR INSTALLING CURB AND GUTTER ALONG BEACH AVENUE IN DELL RAPIDS, SOUTH DAKOTA ON THE EVENING OF SEPTEMBER 24, 2020. PREVIOUS STREET GRADING BY ZACHARIAS CONSTRUCTION, INC. HAD LOWERED THE STREET GRADE SIGNIFICANTLY (APPROXIMATELY 36") AND REDUCED THE COVER OVER A TWO INCH PLASTIC NATURAL GAS MAIN TO APPROXIMATELY ONE INCH. MIDAMERICAN ENERGY WAS NOT AWARE THAT THE STREET GRADE HAD BEEN REDUCED TO A LEVEL THAT WOULD CONFLICT WITH THE EXISTING FACILITIES PRIOR TO THE EVENT. THE MACHINE SCRAPED ALONG THE TOP OF THE MAIN UNTIL IT BROKE THROUGH RELEASING NATURAL GAS AT 43 PSIG UNDER THE MACHINE. THE GAS IGNITED AND THE FIRE DEPARTMENT RESPONDED. MIDAMERICAN ENERGY WAS NOTIFIED AT 21:36 AND ARRIVED ON SITE AT 22:17. THE MAIN WAS SQUEEZED OFF AT APPROXIMATELY 23:15 SHUTTING OFF THE FLOW OF GAS TO THE FIRE. THE EXCAVATOR'S EQUIPMENT, 5700C POWER CURBER, WAS ASSESSED FOR DAMAGE THE NEXT MORNING AND IT WAS DETERMINED THAT THE EXTENT OF DAMAGE WAS ESTIMATED TO BE $350,000. ONCE THE ESTIMATE OF DAMAGE WAS DETERMINED TO BE IN EXCESS OF $50,000, THE NRC WAS NOTIFIED (REPORT 1288248). THERE WERE NO INJURIES, THE GAS DID NOT EXPLODE, AND ONE HOUSE WAS EVACUATED BY THE EXCAVATOR AS A PRECAUTION. SUBSEQUENT NRC REPORTS ASSOCIATED WITH THIS INCIDENT ARE 1288388 FOR A CORRECTION ON THE DATE AND 1288446 FOR THE 48 HOUR FOLLOW UP.
2025-03-31 10:13 | NO | YES | YES | 20200102 | 34632 | 2020-10-23 15:56 | SUPPLEMENTAL FINAL | 7348 | DOMINION ENERGY WEST VIRGINIA | 781 CHESTNUT RIDGE RD | MORGANTOWN | WV | 26505 | 2020-09-24 16:20 | EASTERN | YES | 2020 | 462 OHIO AVE | WESTOVER | MONONGALIA | WV | 26501 | 39.6384 | -79.9818 | [7 empty] | YES | N/A | 2020-09-24 16:45 | 1288188 | 1288263 | NATURAL GAS |  | 2.51 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2020-09-24 09:00 | OPERATOR/CONTRACTOR |  | 2.5 | NO | 0 | 2020-09-24 09:05 | NO |  |  | 2020-09-24 09:05 |  | NO | PRIVATE PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES | 1.5 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.16 | [6 empty] | OTHER | [8 empty] | SERVICE LINE CUT WITH PNEUMATIC EQUIPMENT FOR REPLACEMENT | CLASS 3 LOCATION | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1.1952 | 3 | 3.73469387755102040816326530612244897959 | 0 | 0 | 3 | 3.45481049562682215743440233236151603499 | 3.73469387755102040816326530612244897959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.75 | 192.623 | 1968-12-31 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | FAILURE TO FOLLOW PROCEDURE |  |  | YES |  |  | CONSTRUCTION | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | SCOTT WALLACE | ENGINEERING TECHNICAL SPECIALIST III | scott.a.wallace@dominionenergy.com | 3048441256 |  |  |  |  | REID HESS | MANAGER GAS OPERATIONS | 801-245-9652 | reid.hess@dominionenergy.com | A DOMINION ENERGY WEST VIRGINIA CONSTRUCTION AND MAINTENANCE EMPLOYEE WAS INSTALLING A NEW SECTION OF PLASTIC SERVICE LINE WHILE UTILIZING THE EXISTING TAP AND EXISTING COATED STEEL SERVICE LINE COMING OFF THE TAP. THE EMPLOYEE WAS USING A PNEUMATIC AIR SAW TO CUT THE LIVE LOW PRESSURE 1.5 INCH COATED STEEL SERVICE LINE. AFTER THE FIRST AND SECOND CUTS WERE COMPLETE THE PIPE WAS STUCK IN PLACE. THE EMPLOYEE ATTEMPTED TO DISLODGE THE CUT PIPE WHEN THE GAS IGNITED CAUSING FLASH BURNS TO THE NECK, ARMS, AND FACE. THE EMPLOYEE WAS TAKEN TO THE HOSPITAL AND LATER THAT AFTERNOON THE LOCAL DOCTORS DECIDED TO SEND THE INJURED EMPLOYEE TO THE BURN UNIT IN PITTSBURGH, PA. THE EMPLOYEE WAS KEPT OVERNIGHT IN PITTSBURGH, PA FOR PRECAUTIONARY MEASURES AND RELEASED FROM THE HOSPITAL THE NEXT DAY TO RETURN HOME. TIMELINE 9:05 - EVENT OCCURRED 16:20 - OVERNIGHT HOSPITALIZATION CONFIRMED AND INCIDENT CRITERIA MET 16:31 - NRC PHONE CALL NOTIFICATION MADE ORIGINAL NRC NUMBER 1288188, ADDITIONAL NRC REPORT NUMBER 1288263
2025-03-31 10:13 | NO | YES | NO | 20200103 | 34717 | 2020-10-23 17:12 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2020-09-24 12:21 | CENTRAL | NO | 2020 | 2500 E PLANO PKWY | PLANO | COLLIN | TX | 75074 | 33.0073 | -96.6822 | [5 empty] | YES |  |  |  | 2020-09-25 10:19 | 1288239 | 1288379 | NATURAL GAS |  | 884.3 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 4 | 2020-09-24 12:21 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2020-09-24 12:18 | 2020-09-24 12:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 96 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1980 | UNKNOWN |  |  |  |  | 6 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 136560 | 152456.63418488274456 | 81220 | 90674.63260468787722 | 0 | 0 |  | 5.7266 | 5064 | 6304.163265306122448979591836734693877551 | 0 | 0 | 222844 | 106529.3989859007886017492711370262390671 | 249435.4300548767442289795918367346938776 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 22 | 25 | 55 | 192.619(A)(2) | 1980-10-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 2076768543 | TEXAS811 |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [143 empty] | YES | [26 empty] | QUINT NANCE | OPERATIONS SUPERVISOR | quint.nance@atmosenergy.com | 469-426-6575 |  | QUINT NANCE | quint.nance@atmosenergy.com | 469-426-6575 | MARLO SUTTON | V.P. TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON SEPTEMBER 24, 2020, A THIRD-PARTY EXCAVATOR WAS BORING TELECOMMUNICATIONS NEAR 2500 E PLANO PKWY AND DAMAGED A MARKED 6-INCH POLY MAIN. ATMOS ENERGY TECHNICIAN ARRIVED AT 12:45 PM AND REQUESTED ASSISTANCE AT THAT TIME. CREWS RESPONDED, ARRIVING AT 12:55 PM. ON 9/25/2020 AN ATMOS ENERGY TECHNICIAN CHECKED FOR ODORANT WHICH RESULTED IN READILY DETECTABLE ODORANT LEVELS AT THIS LOCATION. PART E SECTION 6 INDICATES THAT THE ODORANT LEVEL WAS NOT MEASURED, HOWEVER WE DID PERFORM THE ODORANT CHECK WHICH WAS ALSO WITNESSED BY THE RAILROAD COMMISSION OF TEXAS INSPECTOR ON THIS DATE. THE LEAK WAS SECURED AT 5:20 AM ON 9/25/2020, BY SQUEEZING OFF THE MAIN. THE MAIN WAS CAPPED AND THE SECTION OF PIPE IS STILL SHUT DOWN AT THIS TIME. THERE WERE NO CUSTOMERS LOST DUE TO TWO-WAY FEED. A NEW PROJECT TO REPLACE THE SECTION COMMENCED ON OCTOBER 26, 2020 AND REPAIR WAS COMPLETED BY BORING IN A 350-FOOT SECTION OF 6-INCH MAIN. THE NEW SECTION WAS TIED IN ON NOVEMBER 30, 2020. ATMOS ENERGY'S INVESTIGATION DETERMINED THAT THE EXCAVATOR HAD CALLED IN A LOCATE TICKET THAT WAS NOT YET DUE AT THE TIME OF DAMAGE, AND HAD NOT YET BEEN COMPLETED WHEN THE EXCAVATOR CHOSE TO PROCEED WITH THE EXCAVATION BASED UPON ACCURATE MARKINGS THAT HAD BEEN PUT IN PLACE FOR A PRIOR LOCATE TICKET REQUESTED BY ANOTHER CONTRACTOR IN THAT AREA. THE EXCAVATOR FAILED TO POTHOLE THE EXISTING MARKS TO VERIFY THE EXACT LOCATION OF THE GAS LINE. NOTE THAT THE INFORMATION IN PART A4 NOW REFLECTS THE DATE AND TIME AT WHICH THE EVENT THAT GAVE RISE TO THIS INCIDENT WAS INITIALLY REPORTED TO ATMOS ENERGY. HOWEVER, THIS EVENT DID NOT BECOME A REPORTABLE INCIDENT UNTIL THE CRITERIA OF PART 191.3 WERE MET AT 10:02 AM ON 9/25/20, WHICH IS WHEN ATMOS ENERGY DETERMINED THAT THE PROPERTY DAMAGE ASSOCIATED WITH THE EVENT HAD THE POTENTIAL TO EXCEED $50,000. INITIAL REPORT (1288239) WAS MADE TO THE NRC AT 10:19 AM CST. THE 48-HOUR UPDATE TO NRC (1288379) WAS PROVIDED AT 9:54 PM CST ON 9/27/20.
2025-03-31 10:13 | NO | YES | YES | 20200105 | 38069 | 2020-10-26 19:43 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2020-09-17 14:05 | MOUNTAIN | YES | 2020 | 50 COTTONWOOD PASS ROAD | GYPSUM | EAGLE | CO | 81637 | 39.6166 | -106.95 | [5 empty] | YES |  |  |  | 2020-09-17 14:20 | 1287639 | 1287748 | NATURAL GAS |  | 336.76 | 9.5 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2020-09-17 12:25 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 174 | 2020-09-17 09:00 |  |  |  | 2020-09-17 09:48 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 | YES | YES |  |  |  |  | YES | UNCASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 2002 | UNKNOWN |  |  |  |  | 2 | D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 1 | [7 empty] | CLASS 3 LOCATION | 1000000 | 1116407.690281801 | 5000 | 5582.038451409005 | 10000 | 11164.07690281801 | 0 | 0 |  | 4.9887 | 1680 | 2091.428571428571428571428571428571428571 | 47 | 58.51020408163265306122448979591836734694 | 1016727 | 471307.1407238539072886297376093294460641 | 1135303.7444115382190816326530612244898 | 0 | 0 | 87 | 0 | 0 | 87 | 0 | 40 | 40 | 60 | 192.619(A)(2) | 2020-09-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 2.9 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | [7 empty] | YES | [6 empty] | UTILITY | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | COA025202258SG |  |  | FACILITY OWNER | YES | YES | 48 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | JOSHUA DOUGHTY | COMPLIANCE COORDINATOR | joshua.doughty@blackhillscorp.com | 303-515-0088 |  | JOSHUA DOUGHTY | joshua.doughty@blackhillscorp.com | 13035150088 | JOSHUA DOUGHTY | COMPLIANCE COORDINATOR | 303-515-0088 | joshua.doughty@blackhillscorp.com | THIRD-PARTY CONTRACTOR WAS INSTALLING TELECOMMUNICATIONS FIBER CABLE AND STRUCK A 2 INCH PE MAIN WITH A DIRECTIONAL DRILL. THIRD-PARTY CONTRACTOR DID NOT EXPOSE THE TOLERANCE ZONE OF OTHER MARKED FACILITIES IT WAS CROSSING WITH THE DIRECTIONAL DRILL IN THE VICINITY OF THE LINE HIT LOCATION. SUCH POTHOLES WOULD HAVE DISCLOSED THE PRESENCE OF THE LINE THAT WAS HIT. NATURAL GAS MIGRATED INTO A STRUCTURE AT 50 COTTONWOOD PASS ROAD AND THE HOUSE EXPLODED, RESULTING IN THE DEATH OF AN OCCUPANT OF THE HOME. ALL LEGAL CLAIMS HAVE BEEN RESOLVED. NRC 48 HOUR INCIDENT REPORT #1287748.
2025-03-31 10:13 | NO | YES | NO | 20200106 | 35413 | 2020-10-27 17:38 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2020-09-28 18:22 | CENTRAL | NO | 2020 | 459 LORAS BLVD | DUBUQUE | DUBUQUE | IA | 52001 | 42.5046 | -90.6738 | [5 empty] | YES |  |  |  | 2020-09-28 19:00 | 1288523 | 1288707 | NATURAL GAS |  | 300 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-09-28 16:45 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 300 | YES | 37 | 2020-09-28 16:28 |  |  |  | 2020-09-28 16:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 32 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2003 | UNKNOWN |  |  |  |  | 4 | ASTM D2513 | DRISCO PLEX | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.2 |  |  | 2406 | MECHANICAL PUNCTURE | 7 | 1.2 | [7 empty] | CLASS 3 LOCATION | 2000000 | 2232815.380563602 | 114328 | 127636.658414537744728 | 13012 | 14526.696865946794612 | 110964 | 123881.062944429766164 | INVESTIGATION SERVICES BY ESI (ENGINEERING SERVICES INC) AND BLACK HILLS ENERGY | 5 | 1500 | 1867.346938775510204081632653061224489796 | 0 | 0 | 2239804 | 1036680.18972678748211871720116618075802 | 2500727.14572729181570808163265306122449 | 0 | 0 | 37 | 1 | 0 | 20 | 0 | 25 | 25 | 25 | 192.619(A)(2) | 2003-07-07 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | 202600291 |  |  | CONTRACT LOCATOR | YES | YES | 240 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | TONY ENGLING | COMPLIANCE CORRDINATOR | tony.engling@blackhillcorp.com | 563-585-4014 | 563-583-0850 |  |  |  | TONY ENGLING | COMPLIANCE CORRDINATOR | 563-585-4014 | tony.engling@blackhillcorp.com | ON SEPTEMBER 28, 2020, PRICE ELECTRIC, A HORIZONTAL DIRECTIONAL DRILLING CONTRACTOR, STRUCK A BLACK HILLS ENERGY DISTRIBUTION LINE AT 459 LORAS BLVD, DUBUQUE, IOWA. THE LINE WAS A 2406 DRISCO PLEX PE OPERATING AT 25 PSIG. PRICE ELECTRIC POTHOLED WITHIN THE TOLERANCE ZONE OF THE LINE LOCATE BEFORE COMMENCING ITS DRILLING. PRICE THEN INSERTED THE DRILL WITHIN THE TOLERANCE ZONE AND STRUCK THE BHE GAS LINE WITHIN THE TOLERANCE ZONE LEAVING A 7 INCH LONG GOUGE/HOLE IN THE MAIN. DUBUQUE FIRE AND POLICE WERE THE FIRST RESPONDERS, AND BHE WAS NOTIFIED BY THE DUBUQUE FIRE DEPARTMENT. BHE PROMPTLY RESPONDED TO THE LINE HIT. AN INVESTIGATION WAS COMPLETED ON BEHALF OF BHE BY A 3RD PARTY, ENGINEERING SERVICES INC. IT FOUND THAT A 3RD PARTY, THE DIRECTIONAL DRILLER PRICE ELECTRIC, WAS AT FAULT DUE TO IMPROPER EXCAVATION PRACTICES. BHE'S LINE LOCATES WERE ACCURATE. THE IOWA FIRE MARSHALL ESTIMATES THE PROPERTY DAMAGE TO THE BUILDING THAT WAS DESTROYED AND THE SURROUNDING BUILDINGS AT $2,000,000. THE 48 HOUR NRC NUMBER IS 1288707.
2025-03-31 10:13 | NO | YES | NO | 20200108 | 34457 | 2020-10-30 10:38 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2020-10-01 07:07 |  |  | 2020 | 8258 SR 141 | KITTS HILL | LAWRENCE | OH | 45645 | 38.5502 | -82.6137 | [9 empty] | 2020-10-01 07:31 | 1288732 |  |  |  | 0 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-10-01 01:46 |  |  |  | 2020-10-01 02:33 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1970 | [5 empty] | 3 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.188 | [6 empty] | OTHER | [8 empty] | NO RELEASE OF GAS | CLASS 3 LOCATION | 0 | 0 | 495598 | 553289.418488280011998 | 4572 | 5104.215959968394172 | 0 | 0 |  |  | 0 | 0 |  | 0 | 500170 | 231269.8964094459292 | 558393.63444824840617 | 2 | 0 | 103 |  |  |  |  | 420.9 | 120.7 | 175 |  |  | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 |  |  |  |  | YES | YES | YES | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SITE IS ONLY MONITORED BY SCADA. THE CONTROLLER HAD NO CONTROL OVER THE STATION. | [12 empty] | YES | 2 | 0 | YES | 2 | 0 | INCORRECT OPERATION | PIPELINE OR EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | INCORRECT OPERATION | PIPELINE/EQUIPMENT OVERPRESSURED | [222 empty] | PIPELINE OR EQUIPMENT OVERPRESSURED |  | YES |  |  |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE | rrsmith@nisource.com | 614-460-5491 |  |  |  |  | ROB R. SMITH | MANAGER OF OPERATIONS COMPLIANCE | 614-460-5491 | rrsmith@nisource.com | ON SEPTEMBER 30, 2020 OUR UPSTREAM SUPPLIER'S CONTRACTOR INSTALLED A TEMPORARY ALTERNATE FEED TIED DIRECTLY INTO THE REGULATOR SETTING AND REMOVED A SECTION OF SUPPLY PIPING PROVIDING THE PRIMARY FEED TO THE KITTS HILL REGULATOR STATION. THIS WORK WAS DIRECTLY OBSERVED BY COLUMBIA'S MEASUREMENT AND REGULATION EMPLOYEES ON-SITE. WHEN THE PRIMARY FEED WAS TAKEN OUT OF SERVICE IT CAUSED A LOSS OF THE POWER GAS (I.E. SUPPLY GAS) SUPPLY TO THE INSTRUMENT LOADED REGULATORS. THE LOSS OF POWER GAS SUPPLY TO THE REGULATORS RESULTED IN THE REGULATORS FAILING OPEN AND ALLOWING THE UNRESTRICTED FLOW OF GAS INTO THE DOWNSTREAM SYSTEM, PRODUCING AN OVER PRESSURIZATION OF THAT SYSTEM. THE SYSTEM WAS SHUT DOWN FOR SAFETY AND RESULTED IN NO MAJOR DAMAGE TO COLUMBIA'S OR CUSTOMERS' PROPERTY. THE SYSTEM WAS EVALUATED AND ASSESSED FOR SAFETY AND THE SYSTEM WAS PLACED BACK INTO OPERATION.
2025-03-31 10:13 | NO | YES | NO | 20200110 | 34566 | 2020-11-03 13:52 | SUPPLEMENTAL FINAL | 2364 | DUKE ENERGY OHIO | 139 EAST FOURTH STREET PO BOX 960 - ROOM 460-ANNEX | CINCINNATI | OH | 45202 | 2020-10-07 15:00 |  |  | 2020 | 9201 MONTGOMERY ROAD | MONTGOMERY | HAMILTON | OH | 45242 | 39.2227 | -84.357 | [9 empty] | 2020-10-07 18:31 | 1289244 |  | NATURAL GAS |  | 4719 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES |  |  |  |  | NO | 0 | 2020-10-07 15:08 |  |  |  | 2020-10-07 15:08 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1967 | [5 empty] | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 6 | 12 | [7 empty] | CLASS 3 LOCATION | 800000 | 893126.1522254408 | 145855 | 162833.643666052084855 | 29319 | 32731.957071372123519 | 0 | 0 |  |  | 15770 | 19632.0408163265306122448979591836734694 |  | 0 | 990944 | 469064.2599136495540475801749271137026239 | 1108323.79377919153898624489795918367347 | 2 | 0 | 514 |  |  |  |  | 28 | 30 | 35 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  | NO |  |  | YES | YES | [8 empty] | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | UNKNOWN/OTHER | ROAD WORK | YES | B023201460 | N/A |  | CONTRACT LOCATOR | YES | YES | 28 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 7047314680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 7047314618 | farris.berry@duke-energy.com | ON 10/7/20, A CONTRACTOR WAS RUNNING TWO SOIL STABILIZATION MACHINES WHILE PERFORMING ROAD WORK. THE FIRST MACHINE LIFTED ITS CUTTER AND CROSSED THE GAS MAIN WITH NO PROBLEM. THE SECOND SOIL STABILIZATION MACHINE FRONT TIRES GOT STUCK ON THE WATER MAIN AND BEGIN TO SINK. AS THE MACHINE SUNK, THE FRONT OF THE MACHINE WAS PULLED DOWN INTO THE GAS MAIN CAUSING IT TO HIT AND DAMAGE THE 12" STEEL DISTRIBUTION MAIN. GAS WAS IGNITED WITH INJURIES, BUT NO HOSPITALIZATION. 48-HOUR UPDATE CALL MADE ON 10/9/20 AT 13:36PM. NRC #1289372
2025-03-31 10:13 | NO | NO | NO | 20200111 | 35003 | 2020-11-04 14:21 | SUPPLEMENTAL FINAL | 18532 | TEXAS GAS SERVICE COMPANY, A DIVISION OF ONE GAS, INC. | 1301 MOPAC EXPRESSWAY SUITE 400 | AUSTIN | TX | 78746 | 2020-10-08 16:31 | CENTRAL | NO | 2020 | NEAR INTERSECTION (STEWART RD AND MILE 8) | MCALLEN | HILDAGO | TX | 78573 | 26.3271 | -98.2808 | YES | [8 empty] | 2020-10-08 16:45 | 1289317 |  | NATURAL GAS |  | 10000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-10-08 10:33 | NO |  |  | 2020-10-08 11:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1927 | [5 empty] | 12.75 | API-5L | UNKNOWN | STEEL |  | OTHER | ERW | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 4 | 5 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 8000 | 8931.261522254408 | 2000 | 2232.815380563602 | 0 | 0 |  | 2.3031 | 23031 | 28671.2448979591836734693877551020408163 | 0 | 0 | 33031 | 31146.4060023347137026239067055393586006 | 39835.3218007771936734693877551020408163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 170 | 188 | 192.619(A)(2) | 2004-10-13 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | OTHER | CALL FROM MANUEL DERUEDA TO TEXAS GAS SERVICE DISPATCH AT 10:33 AM |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | AN INQUIRY TO THE CONTROL ROOM TIMELINES OCCURRED. FIRST ALARM CAME IN AT 10:49 AM VIA SCADA. CONTROL ROOM CALL TO OUR DISPATCH OCCURRED AT 10:51 AM, PRESSURE & MEASUREMENT TECHNICIAN PERSONNEL ROUTED TO JOB SITE AT 10:58 AM. NO ADDITIONAL INQUIRIES ARE NECESSARY TO THE CONTROLLER(S) ACTIONS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | UNKNOWN |  |  |  |  | YES | YES | CITY STREET | [12 empty] | MUNICIPALITY | GRADER/SCRAPER | ROAD WORK | NO | [5 empty] | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | DEAN LAFLAMME | DIRECTOR ENGINEERING TEXAS GAS SERVICE | dean.laflamme@onegas.com | 512-370-8213 |  |  |  |  | DEAN LAFLAMME | DIRECTOR ENGINEERING TEXAS GAS SERVICE | 512-370-8213 | dean.laflamme@onegas.com | AT 10:33 AM OCTOBER 8TH TEXAS GAS SERVICE (TGS) DISPATCH RECEIVED A CALL FROM MANUEL DERUEDA NOTIFYING THEM OF A DAMAGE TO A TGS FACILITY. TGS'S 12" COATED STEEL GAS MAIN WAS DAMAGED BY A 3RD PARTY CONTRACTOR (CITY OF MCALLEN PUBLIC WORKS DEPARTMENT). THE CITY OF MCALLEN WAS CONDUCTING ROAD AND DRAINAGE WORK WITH A ROAD GRADER NEAR THE INTERSECTION OF STEWART RD AND MILE 8 IN NORTH MCALLEN, TX. THE ROAD GRADER WAS MAKING DEEP CUTS OF SOIL TO COMPLETE A NEW ROAD CONSTRUCTION PROJECT. TEXAS GAS SERVICE FACILITIES HAD 24" TO 30" DEPTH OF COVER IN THIS AREA. THE ROAD GRADER STRUCK THE 12" PIPELINE CAUSING A 4" X 5" TRIANGULAR HOLE IN ITS FACILITIES. THE CITY OF MCALLEN DID NOT MAKE NOTIFICATION TO THE ONE-CALL CENTER TO PERFORM THIS WORK. AT 4:31 PM ON OCTOBER 8TH TEXAS GAS SERVICE CONFIRMED THAT THE GAS LOSS WAS OVER THE 3000 MCF PHMSA REPORTABLE THRESHOLD. AT 4:45 PM OCTOBER 8TH TEXAS GAS SERVICE REPORTED THE INCIDENT TO THE NRC (#1289317) AND CONDUCTED THE 48 HR UPDATE PER PHMSA REQUIREMENTS AT 9:34 AM OCTOBER 10TH NRC (#1289424). SUPPLEMENTAL INFORMATION 3/5/21 THE CITY OF MCALLEN HAS BEEN CONTACTED ELECTRONICALLY CONCERNING THIS INCIDENT. ALSO, AFTER SAFETY PROTOCOLS ALLOW US TO (DUE TO THE PANDEMIC), TEXAS GAS SERVICE WILL MEET WITH THE CITY OF MCALLEN TO REVIEW TEXAS UTILITY CODY 251, SPECIFICALLY CHAPTER 18, SECTION 18.3 EXCAVATOR NOTICE TO NOTIFICATION CENTER, SECTION 18.4 EXCAVATOR OBLIGATION TO AVOID DAMAGE TO UNDERGROUND PIPELINES, SECTION 18.5 OPERATOR AND EXCAVATOR OBLIGATIONS WITH RESPECT TO POSITIVE RESPONSE IN AN EFFORT TO PREVENT FUTURE DAMAGES. TEXAS GAS SERVICE DAMAGE PREVENTION GROUP REVIEWS ALL EXCAVATION DAMAGES TO TRACK AND MONITOR REPEAT OFFENDERS FOR AT-FAULT EXCAVATION DAMAGES, CURRENTLY THE CITY OF MCALLEN HAS NOT YET MET THE REPEAT OFFENDER LIST. TEXAS GAS SERVICE WILL REQUIRE SAFE EXCAVATION MEETINGS WITH THE CITY OF MCALLEN IF ADDITIONAL AT-FAULT EXCAVATION DAMAGES ARE EXPERIENCED.
2025-03-31 10:13 | NO | YES | NO | 20200112 | 35044 | 2020-11-06 16:34 | SUPPLEMENTAL FINAL | 31636 | NORTHERN STATES POWER CO OF MINNESOTA | 414 NICOLLET MALL | MINNEAPOLIS | MN | 55402 | 2020-10-06 12:45 | CENTRAL | NO | 2020 | 675 GENTRY AVE | OAKDALE | WASHINGTON | MN | 55128 | 44.5731 | -92.5919 |  | YES | [7 empty] | 2020-10-06 16:12 | 1289146 | 1289305 | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-10-06 12:00 | NO |  |  | 2020-10-06 12:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | IN UNDERGROUND ENCLOSED SPACE (E.G. VAULT) |  | 36 | YES | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | NO RELEASE WAS INVOLVED IN THIS INCIDENT | CLASS 3 LOCATION | 0 | 0 | 887 | 990.253621279957487 | 253120 | 282585.11456412946912 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 254007 | 117448.41269423222532 | 283575.368185409426607 | 50 | 0 | 1480 | 0 | 0 | 1480 | 50 | 1 | 18 | 20 | 192.619(A)(4) | 1989-03-14 | PRESSURE DID NOT EXCEED MAOP | OTHER | ODORIZED BY TRANSMISSION OPERATOR |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | SCADA WAS OPERATING WITHIN PARAMETERS AT THE TIME OF THE EVENT. | [12 empty] | YES | 3 | 0 | YES | 3 | 0 | INCORRECT OPERATION | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE | INCORRECT OPERATION | INCORRECT VALVE POSITION | INCORRECT OPERATION | INCORRECT VALVE POSITION | [222 empty] | VALVE LEFT OR PLACED IN WRONG POSITION, BUT NOT RESULTING IN AN OVERPRESSURE |  |  |  |  | YES | CREW WAS BYPASSING A REGULATOR STATION TO REPAIR A LEAKING FLANGE. WORK WAS STOPPED AND THE BYPASS VALVE WAS INADVERTENTLY LEFT IN THE CLOSED POSITION, CAUSING THE PRESSURE AT THE MONITORING POINT TO GIVE A FALSE VALUE. | OTHER MAINTENANCE | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [49 empty] | ELISABETH KALLBERG | PRINCIPAL GAS COMPLIANCE CONSULTANT | elisabeth.m.kallberg@xcelenergy.com | 651-229-2282 |  |  |  |  | CHRISTOPHER AKINS | MANAGER PIPELINE COMPLIANCE AND STANDARDS | 303-517-3298 | christopher.a.akins@xcelenergy.com | CREW WAS ON SITE TO REPAIR A LEAKING FLANGE AT A REGULATOR STATION. THE CREW WAS IN THE PROCESS OF REMOVING A BYPASS LINE AND RETURNING THE SYSTEM TO NORMAL. THIS PROCESS INVOLVED REOPENING A BLOCK VALVE AND PUTTING IT BACK INTO SERVICE. WHEN DOING THIS, THE SENSE LINE INADVERTENTLY REMAINED IN THE CLOSED POSITION. THIS LEAD TO THE PRESSURE BEING MEASURED ON THE TRAPPED GAS IN THE BYPASS LINE, NOT THE DOWNSTREAM PRESSURE. THE CREW THOUGHT THEY HAD RETURNED THE SYSTEM TO NORMAL. AFTER APPROXIMATELY 30 MINUTES, THE GAUGE HAD DROPPED ONLY 1/4 LB. THE CREW EXPECTED THE PRESSURE TO DROP MORE RAPIDLY. THEY DID SOME TROUBLESHOOTING AND CHECKED THE GAUGE IN THE VAULT (WHICH WAS MONITORING DOWNSTREAM PRESSURE) AND SAW THE GAUGE READ 1LB. THEY REALIZED IMMEDIATELY THAT THEY WERE NOT READING THE DOWNSTREAM PRESSURE, BUT IN FACT THE TRAPPED PRESSURE IN THE SENSE LINE. THE CREW OPENED THE TRAP AND THE PRESSURE DROPPED FROM 18LBS TO 1LB INSTANTLY. THE SYSTEM WAS SHUT DOWN, RISER VALVES TURNED OFF, SYTEM RE-PRESSURIZE AND THEN PERFORM RELIGHTS. XCEL ENERGY REVIEWED APPLICABLE POLICIES AND PROCEDURES WITH FRONT LINE EMPLOYEES INVOLVED WITH THIS EVENT. XCEL ENERGY IS DEVELOPING ADDITIONAL TRAINING THAT IS FOCUSED ON WHAT SPECIFIC WORK REQUIRES A WRITTEN PROCEDURE.
2025-03-31 10:13 | NO | YES | NO | 20200113 | 34931 | 2020-11-06 21:52 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2020-10-08 01:15 | CENTRAL | NO | 2020 | ANCONA RD (N 300 E RD) AND E 2900 N RD | ANCONA | LIVINGSTON | IL | 61311 | 41.0461 | -88.8722 | YES | [8 empty] | 2020-10-08 01:55 | 1289261 | 1289395 | NATURAL GAS |  | 1312.3 | 2.58 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-10-08 01:15 | OPERATOR/CONTRACTOR |  | 1312.3 | NO | 0 | 2020-10-08 01:15 | YES | OPERATOR | 2020-10-08 01:20 | 2020-10-08 01:15 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1987 | [8 empty] | OTHER | VARIOUS MATERIALS IN THE REGULATOR RUNS | [9 empty] | OTHER | [8 empty] | INTENTIONAL GAS RELEASE AS RESPONSE TO OVER PRESSURE CONDITION PRIOR TO THE INCIDENT | CLASS 1 LOCATION | 0 | 0 | 648742 | 724260.557808796144342 | 2500 | 2791.0192257045025 | 0 | 0 |  | 1.5842 | 2079 | 2588.142857142857142857142857142857142857 | 4 | 4.97959183673469387755102040816326530612 | 653325 | 303521.7480367215807713119533527696793002 | 729644.6994834802386787346938775510204082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 300 | 300 | 192.619(A)(2) | 2010-07-06 | PRESSURE EXCEEDED THE APPLICABLE ALLOWANCE IN 192.201 | WICK |  |  | YES | YES | YES | YES | YES | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | EARLIER IN THE EVENING AND PRIOR TO THE INCIDENT, THE GAS CONTROLLER OBSERVED AT HH ALARM ON THE SEND OUT PRESSURE FOR THE REGULATING STATION. THE CONTROLLER MADE APPROPRIATE AND PROMPT NOTIFICATION TO LOCAL PERSONNEL RESPONSIBLE FOR THE OPERATION/MAINTENANCE OF THE REGULATING STATION. DURING THE RESPONSE TO THE AOC, IGNITION OCCURRED. THE ACTIONS OF THE CONTROLLER DID NOT PLAY A PART IN THE CAUSE OF THE INCIDENT. | [12 empty] | YES | 4 | 0 | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | FAILURE TO FOLLOW VENTING PROCEDURES. |  |  | YES |  |  | NON-ROUTINE OPERATING CONDITIONS (ABNORMAL OPERATIONS OR EMERGENCIES) | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [48 empty] | YES | LETICIA QUEZADA | DIR. COMPLIANCE AND QA | lquezad@southernco.com | 6305142036 |  | LETICIA QUEZADA | lquezad@southernco.com | 6305142036 | LETICIA QUEZADA | DIR. COMPLIANCE AND QA | 6305142036 | lquezad@southernco.com | EARLIER IN THE EVENING AND PRIOR TO THE INCIDENT, THE GAS CONTROLLER OBSERVED AT HH ALARM ON THE SEND OUT PRESSURE FOR THE REGULATING STATION. THE CONTROLLER MADE APPROPRIATE AND PROMPT NOTIFICATION TO LOCAL PERSONNEL RESPONSIBLE FOR THE OPERATION/MAINTENANCE OF THE REGULATING STATION. OPERATING PERSONNEL RESPONDED AND VERIFIED THAT THE STATION WAS PASSING GAS AND THE PIPELINE PRESSURE DOWNSTREAM OF THE STATION HAD EXCEEDED THE SYSTEM MAOP. THE CREW ATTEMPTED TO REDUCE THE PIPELINE PRESSURE BY INTENTIONALLY VENTING GAS TO ATMOSPHERE AT THE STATION. DURING THE VENTING PROCESS, IGNITION OCCURRED, RESULTING IN A FIRE AT THE STATION. THE STATION REGULATING EQUIPMENT AND OTHER STATION ASSOCIATED EQUIPMENT WAS DESTROYED IN THE FIRE. THE STATION WAS ISOLATED TO STOP THE FLOW OF GAS AND THE FIRE WAS EXTINGUISHED. THE STATION IMPACTED EQUIPMENT WAS RE-BUILT AND THE STATION WAS PUT BACK INTO SERVICE.
2025-03-31 10:13 | NO | NO | NO | 20200114 | 34544 | 2020-11-17 15:43 | ORIGINAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2020-10-24 23:44 |  |  | 2020 | 69 YORK PLAZA | YORK | YORK | NE | 68467 | 40.8644 | -97.6167 | [9 empty] | 2020-11-03 10:51 | 1291283 |  | NATURAL GAS |  | 2 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-10-24 23:59 |  |  |  | 2020-10-25 00:40 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | UNKNOWN | [8 empty] | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 4000 | 4465.630761127204 | 82000 | 91545.430603107682 | 500 | 558.2038451409005 | 0 | 0 |  |  | 20 | 24.89795918367346938775510204081632653061 |  | 0 | 86520 | 40019.1254770465854810495626822157434402 | 96594.1631685594599693877551020408163265 | 20 | 0 | 0 |  |  |  |  | 150 | 150 | 200 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [167 empty] | TOM DORSHORST |  | tom.dorshorst@blackhillscorp.com | 308 760 3094 |  |  |  |  | TOM DORSHORST | PIPELINE SAFETY COMPLIANCE COORDINATOR | 308 760 3094 | tom.dorshorst@blackhillscorp.com | VEHICLE WAS TRAVELING NORTH ON ROAD L WHEN IT LEFT THE ROADWAY OFF RIGHT SIDE. VEHICLE COLLIDED WITH GAS MAIN AND REGULATOR STATION NEXT TO ROADWAY. VEHICLE BROKE THROUGH STEEL GUARD AROUND REGULATOR STATION AND BROKE INLET FEED TO STATION. DRIVER OF VEHICLE LEFT THE SCENE. LAW ENFORCEMENT CONTACTED DRIVER AT HER RESIDENCE. THE DRIVER WAS TRANSPORTED TO HOSPITAL DUE TO INJURIES, WAS TREATED AND RELEASED SHORTLY AFTER ARRIVAL. DRIVER WAS CHARGED WITH DRIVING UNDER THE INFLUENCE AND LEAVING THE SCENE OF AN ACCIDENT. REGULATOR STATION WAS BADLY DAMAGED AND BLOWING GAS. THIS HAD TO BE SHUT DOWN AND A TEMPORARY BYPASS INSTALLED AT STATION RESUPPLY GAS TO 20 CUSTOMERS. THE STATION WAS LATER COMPLETELY REBUILT AND NEW GUARD INSTALLED TO PROTECT IT. BLACK HILLS ENERGY DID NOT EXPECT THIS TO EXCEED $50,000 INITIALLY BUT REBUILD COSTS WERE EXTENSIVE AND LATER DETERMINED THAT IT MET INCIDENT REPORTING AND WAS CALLED IN TO NRC.
2025-03-31 10:13 | NO | NO | NO | 20200115 | 34796 | 2020-11-19 16:21 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2020-10-21 11:41 | EASTERN | YES | 2020 | 901 LAFAYETTE ROAD | CRAWFORDSVILLE | MONTGOMERY | IN | 47933 | 40.0522 | -86.9062 | YES |  |  |  |  | YES |  |  |  | 2020-10-21 11:41 | 1290304 | 1290457 | NATURAL GAS |  | 9.75 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-10-21 03:25 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 9.75 | YES | 2 | 2020-10-21 04:12 |  |  |  | 2020-10-21 04:12 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1984 | 1983 |  |  |  |  | 6.625 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2306 | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 42500 | 47447.3268369765425 | 250 | 279.10192257045025 | 10000 | 11164.07690281801 | 0 | 0 |  | 2.1538 | 21 | 26.14285714285714285714285714285714285714 | 0 | 0 | 52771 | 24414.8649130444777551020408163265306122 | 58916.6485195078598928571428571428571429 | 2 | 0 | 0 | 0 | 0 | 0 | 3 | 55 | 55 | 60 | 192.619(A)(2) | 1984-04-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 3 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE MONITORING SYSTEM WILL NOT DETECT A LEAK ON GAS MAIN | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | BODY OF PIPE | MATERIAL/WELD/EQUIP FAILURE | BODY OF PIPE | MATERIAL FAILURE OF PIPE OR WELD | BODY OF PIPE | [146 empty] | BODY OF PIPE | CRACK | [30 empty] | YES | [9 empty] | YES |  |  |  | OTHER | CRACK ON THE BOTTOM OF THE 6" PLASTIC MAIN | NO | [86 empty] | JERRY KNECHT | LEAD SPECIALIST OPERATIONS | jerry.knecht@centerpointenergy.com | 765-366-9496 |  |  |  |  | SHANE ALEXANDER | MANAGER PIPELINE SAFETY AND COMPLIANCE IN-OH | 3177183603 | shane.alexander@centerpointenergy.com | ON OCTOBER 21ST, 2020, CRAWFORDSVILLE FIRE DEPARTMENT DISPATCH REPORTED A STRUCTURE FIRE THAT WAS GAS FED WITH POSSIBLE EXPLOSION. VECTREN EMERGENCY RESPONDER ARRIVED ON SITE TO A STRUCTURE PARTIALLY DOWN AND ON FIRE. IT APPEARED A CONCRETE BLOCK WALL HAD FALLEN ON THE GAS METER SET CAUSING NATURAL GAS TO FEED THE FIRE. VECTREN EMERGENCY RESPONDERS DUG UP AND DISCONNECTED THE GAS SERVICE, STOPPING THE FLOW OF NATURAL GAS TO THE FIRE. NO PERSONAL INJURIES WERE REPORTED. IT IS INCONCLUSIVE AS TO WHETHER THE EXPLOSION OCCURRED AS A RESULT OF NATURAL GAS MIGRATING FROM OUTSIDE THE STRUCTURE, DUE TO INABILITY TO RULE OUT OTHER POTENTIAL SOURCES. THE GAS SERVICE LINE TO THIS STRUCTURE WAS PRESSURE TESTED AND DETERMINED TO BE NOT LEAKING. HOWEVER, FURTHER INVESTIGATIONS DISCOVERED CONCENTRATIONS OF NATURAL GAS IN THE PARKING LOT AND NEAR THE FOUNDATION OF THIS STRUCTURE. THE SOURCE OF THESE UNDERGROUND GAS READINGS WAS DETERMINED TO BE A CRACK ON THE BOTTOM OF THE 6' ALDYL-A GAS MAIN IN OLD OAK LANE ADJACENT TO THIS PROPERTY. THIS CRACK APPEARS TO BE CONSISTENT WITH AN IMPINGEMENT FAILURE. THIS DAMAGED SECTION OF PIPE WAS REMOVED AND REPLACED THAT SAME DAY.
2025-03-31 10:13 | NO | NO | NO | 20200116 | 34551 | 2020-11-19 16:40 | ORIGINAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2020-10-21 18:21 |  |  | 2020 | 618 HIGHWAY 293 SE | CARTERSVILLE | BARTOW | GA | 30137 | 34.131 | -84.7581 | [9 empty] | 2020-10-21 18:21 | 1290360 |  | NATURAL GAS |  | 166 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-10-21 16:58 |  |  |  | 2020-10-21 17:40 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | UNKNOWN | [5 empty] | 0.5 | API 5L | UNKNOWN | STEEL |  |  |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1 | 1.116407690281801 | 1300 | 1451.3299973663413 | 0 | 0 |  |  | 350 | 435.714285714285714285714285714285714286 |  | 0 | 1651 | 1004.620964635524678367346938775510204082 | 1888.160690770908815285714285714285714286 | 0 | 0 | 0 |  |  |  |  | 300 | 300 | 300 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | BACKHOE/TRACKHOE | GRADING | YES | 10060245031 |  |  | CONTRACT LOCATOR | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A 1/2-INCH STEEL NATURAL GAS SERVICE WAS RUPTURED BY A BACKHOE WHILE A CONTRACT CREW WAS GRADING A LOT. ONCE THE INCIDENT WAS MADE SAFE IT WAS IDENTIFIED THAT THE FIRE DEPARTMENT HAD STOPPED THE RAILROAD FOR MORE THAN THE 20-MINUTE THRESHOLD THE COMPANY HAS IN ITS OPERATIONS PROCEDURE MANUAL (OPM) FOR REPORTING WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. NOTIFICATION TO THE ONE-CALL CENTER WAS MADE, HOWEVER, IT APPEARS THE FACILITY WAS NOT LOCATED PROPERLY. THE METER SET WAS INACTIVE, SO NO CUSTOMERS WERE WITHOUT NATURAL GAS SERVICE. ADDITIONAL NRC REPORT NUMBER 1290399 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2025-03-31 10:13 | NO | YES | NO | 20200117 | 34554 | 2020-11-19 17:04 | SUPPLEMENTAL FINAL | 2288 | CHATTANOOGA GAS CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2020-10-26 14:28 |  |  | 2020 | 5564 DAYTON BOULEVARD | CHATTANOOGA | HAMILTON | TN | 37415 | 35.1513 | -85.271 | [9 empty] | 2020-10-26 14:28 | 1290710 |  | NATURAL GAS |  | 51154 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 0 | 2020-10-23 08:27 |  |  |  | 2020-10-23 08:55 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 60 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1987 | [5 empty] | 8 | API 5L | UNKNOWN | STEEL |  | OTHER | LONGITUDINAL WELD | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 3 | 9 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 17500 | 19537.1345799315175 | 25500 | 28468.3961021859255 | 0 | 0 |  |  | 108000 | 134448.9795918367346938775510204081632653 |  | 0 | 151000 | 144255.6289004182776676384839650145772595 | 182454.5102739541776938775510204081632653 | 0 | 0 | 0 |  |  |  |  | 55 | 55 | 60 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | [8 empty] | YES | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | GRADING | YES | 202943426 |  |  | CONTRACT LOCATOR | NO | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO LOCATOR ERROR | [170 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | AN 8-INCH STEEL NATURAL GAS MAIN WAS RUPTURED BY A BACKHOE WHILE A CONTRACT CREW WAS GRADING AN ENTRANCE TO A NEW SUBDIVISION. ONCE THE INCIDENT WAS MADE SAFE IT WAS IDENTIFIED THAT THE AMOUNT OF GAS LOSS WHEN CONSIDERING THE SIZE OF THE RUPTURE AND OPERATING CONDITIONS THAT THE THRESHOLD FOR REPORTING MAY HAVE BEEN EXCEEDED WHERE THE NATIONAL RESPONSE CENTER (NRC) WAS CONTACTED AT THAT TIME. NOTIFICATION TO THE ONE-CALL CENTER WAS MADE, HOWEVER, IT APPEARS THE FACILITY WAS NOT LOCATED PROPERLY. ADDITIONAL NRC REPORT NUMBER 1290864 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2025-03-31 10:13 | NO | YES | NO | 20200118 | 34689 | 2020-11-20 10:30 | SUPPLEMENTAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY | CANONSBURG | PA | 15317 | 2020-10-20 16:50 | EASTERN | NO | 2020 | LAFAYETTE DR AND BATTLE RIDGE DR | SOUTH FAYETTE TWP | ALLEGHENY | PA | 15057 | 40.3626 | -80.1884 |  |  |  | YES |  |  | YES |  |  | 2020-10-20 17:43 | 1290256 | 1290439 | NATURAL GAS |  | 1378 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-10-20 16:50 | NO |  |  | 2020-10-20 16:32 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 6 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1959 | [5 empty] | 10 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.28 | [6 empty] | MECHANICAL PUNCTURE | 2 | 0.5 | [7 empty] | CLASS 1 LOCATION | 0 | 0 | 112615 | 125724.252041085019615 | 122085 | 136296.632868053675085 | 0 | 0 |  | 1.4296 | 1970 | 2452.448979591836734693877551020408163265 | 0 | 0 | 236670 | 110789.851061384651883381924198250728863 | 264473.3338887305314346938775510204081633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 325 | 375 | 192.619(A)(1) | 2013-12-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A FACILITY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | GRADER/SCRAPER | GRADING | NO | [5 empty] | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | RICHARD W BURKE | OPERATIONS COMPLIANCE MANAGER | rburke@nisource.com | 7243217155 |  |  |  |  | MICHAEL J DAVIDSION | VP AND GENERAL MANAGER | 4125599678 | mdavids@nisource.com | ON OCTOBER 20, 2020, AT APPROXIMATELY 16:00, GRAHAM AND SONS, INC. WAS EXCAVATING WITH A BULLDOZER IN THE AREA OF LAFAYETTE DR. IN SOUTH FAYETTE TWP, PA AND STRUCK COLUMBIA'S 10 INCH TRANSMISSION CLASS MAINLINE CAUSING A RELEASE OF NATURAL GAS. THE EXCAVATOR DID NOT HAVE A VALID ONE CALL TICKET BECAUSE THEY NEVER CONTACTED THE ONE CALL CENTER PRIOR TO EXCAVATION. LINE MARKERS WERE VISIBLE. THE ESTIMATED COST TO REPAIR THE DAMAGES IS $124,000.
2025-03-31 10:13 | NO | YES | NO | 20200119 | 36227 | 2020-11-29 09:46 | SUPPLEMENTAL FINAL | 2600 | COLUMBIA GAS OF PENNSYLVANIA | 121 CHAMPION WAY | CANONSBURG | PA | 15317 | 2020-10-29 08:55 | EASTERN | NO | 2020 | 448 CHESTNUT ST | RIMERSBURG | CLARION | PA | 16248 | 41.041 | -79.5085 | [5 empty] | YES |  |  |  | 2020-10-29 09:06 | 1290934 | 1291053 | NATURAL GAS |  | 30 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 19 | 2020-10-29 09:06 |  |  |  | 2020-10-29 08:41 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 18 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1982 | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 149000 | 166344.745851988349 | 4000 | 4465.630761127204 | 60000 | 66984.46141690806 | 0 | 0 |  | 1.58 | 47 | 58.51020408163265306122448979591836734694 | 0 | 0 | 213047 | 98541.6154882133668804664723032069970845 | 237853.3482341052456530612244897959183673 | 0 | 0 | 19 | 0 | 0 | 6 | 0 | 30 | 45 | 60 | 192.619(A)(1) | 1982-11-23 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 0.2 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, ELECTROFUSION |  | 1982 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [5 empty] | YES | DAMAGE FROM SEWER CONTRACTOR DOING WORK AROUND PIPE | YES |  |  |  | POOR CONSTRUCTION/INSTALLATION PROCEDURES |  |  | NO | [60 empty] | YES | [25 empty] | RICHARD W BURKE | OPERATIONS COMPLIANCE MANAGER | rburke@nisource.com | 7243217155 |  |  |  |  | CURTIS J. ANSTEAD | VP AND GENERAL MANAGER | 419-957-6404 | cjanstead@nisource.com | ON THURSDAY, OCTOBER 29, 2020 AT APPROXIMATELY 8:22 AM WE RECEIVED A TELEPHONE CALL FROM CLARION COUNTY, PA 911 REPORTING AN EXPLOSION AT 448 CHESTNUT STREET, RIMERSBURG, PA. OUR TECHNICIAN ARRIVED AT 8:41 AM AND CONFIRMED THE EXPLOSION AND REPORTED AN ODOR OF GAS IN THE FRONT YARD OF THE HOME. THE TECHNICIAN AND THE FIRE DEPARTMENT EVACUATED THE HOMES IN THE IMMEDIATE VICINITY. THE TECHNICIAN LOCATED THE SOURCE OF THE GAS LEAK AND EXPOSED MAINLINE. THE MAIN LINE WAS SHUT DOWN AND MADE SAFE AT 10:03 AM.. OUR CREWS MADE THE REPAIRS AND SERVICE WAS RE-ESTABLISHED TO AFFECTED AREA AT 8:50 PM ON OCTOBER 29, 2020. THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THE EXPLOSION. THE CAUSE OF THE EXPLOSION IS UNDER INVESTIGATION. THE INCIDENT WAS CAUSED BY A FAILED BUTT FUSION ON THE 2 INCH PLASTIC MAIN. CONTRIBUTING FACTOR WAS PREVIOUS DAMAGE FROM A THIRD PARTY CONTRACTOR.
2025-03-31 10:13 | NO | YES | NO | 20200122 | 35910 | 2020-12-01 17:02 | SUPPLEMENTAL FINAL | 13061 | NATIONAL FUEL GAS DISTRIBUTION CORP | 6363 MAIN ST. | WILLIAMSVILLE | NY | 14221 | 2020-11-02 01:34 | EASTERN | NO | 2020 | 1202 BROWN AVE | ERIE | ERIE | PA | 16502 | 42.1041 | -80.1004 | [5 empty] | YES |  |  |  | 2020-11-02 03:28 | 1291212 | 1291325 | NATURAL GAS |  | 285 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-11-02 01:34 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | NO | 4 | 2020-11-02 00:38 |  |  |  | 2020-11-02 00:59 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2001 | 2001 |  |  |  |  | 2 | ASTM D2513 | DRISCOPIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | OTHER | [8 empty] | MAIN DAMAGED BY AUGER | CLASS 3 LOCATION | 130000 | 145132.99973663413 | 3457 | 3859.421385304186057 | 500 | 558.2038451409005 | 0 | 0 |  | 7.3579 | 2097 | 2610.551020408163265306122448979591836735 | 0 | 0 | 136054 | 64354.2961726471360080466472303206997085 | 152161.1759874873798223061224489795918367 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 27 | 27 | 60 | 192.619(A)(2) | 2001-09-06 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 1 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE SYSTEM IS MONITORED BY SCADA, BUT MONITORING LOCATIONS ARE NOT LOCALIZED NEAR THE AREA OF THE INCIDENT AND THE LOSS OF GAS WAS NOT SIGNIFICANT ENOUGH TO BE NOTICED BY THESE SCADA MONITORING LOCATIONS. THE CONTROLLER'S ACTIONS WOULD NOT HAVE AFFECTED THE OUTCOME. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | AUGER | POLE | YES | 20203060219 |  |  | UTILITY OWNER | YES | YES | 17 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCORRECT FACILITY RECORDS/MAPS | [170 empty] | STEVEN MONNIE | ENGINEER II | monnies@natfuel.com | 814-871-8204 | 814-871-8659 |  |  |  | KURT W MEIGHEN | SUPERINTENDENT | 814-371-5870 | meighenk@natfuel.com | AT APPROXIMATELY 00:38 (12:38 AM EST) ON NOVEMBER 2, 2020, NATIONAL FUEL GAS DISTRIBUTION CORPORATION (COMPANY) WAS NOTIFIED THAT A CONTRACTOR, WHILE USING AN AUGER TO REPLACE A UTILITY POLE, STRUCK A 2" IPS PLASTIC NATURAL GAS MAIN AT APPROXIMATELY 00:20 (12:20 AM EST) ON NOVEMBER 2, 2020. THIS STRIKE RESULTED IN: (A) A RELEASE OF GAS; AND (B) A SUBSEQUENT STRUCTURE FIRE AT 1202 BROWN AVE, WHICH OCCURRED AT APPROXIMATELY 01:34 (1:34 AM EST) ON NOVEMBER 2, 2020. THERE WERE NO INJURIES OR FATALITIES. THE ONE-CALL CENTER WAS NOTIFIED PRIOR TO THE EXCAVATION ACTIVITY. INVESTIGATION INTO THE INCIDENT SHOWS THE DAMAGED MAIN WAS NOT LOCATED DUE TO COMPANY MAP RECORDS SHOWING THE MAIN WAS OUTSIDE OF THE EXCAVATION AREA. THE MAIN WAS SHUTDOWN AT APPROXIMATELY 04:32 (4:32 AM EST) ON NOVEMBER 2, 2020 AND WAS PUT BACK INTO SERVICE AT APPROXIMATELY 20:00 (8:00 PM EST) ON NOVEMBER 2, 2020 AFTER REPAIRS WERE COMPLETED.
2025-03-31 10:13 | NO | NO | NO | 20200123 | 34593 | 2020-12-04 12:08 | ORIGINAL FINAL | 180 | SPIRE ALABAMA INC. | 605 RICHARD ARRINGTON, JR. BOULEVARD NORTH | BIRMINGHAM | AL | 35203 | 2020-11-04 16:20 |  |  | 2020 | 39TH AVENUE NORTH AND FAIRMONT ST | BIRMINGHAM | JEFFERSON | AL | 35207 | 33.5616 | -86.8148 | [9 empty] | 2020-11-04 16:45 | 1291420 |  | NATURAL GAS |  | 8000 |  | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO |  |  |  |  | NO | 10 | 2020-11-04 12:45 |  |  |  | 2020-11-04 12:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 72 |  | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1959 | [5 empty] | 12 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 20260 | 22618.41980510928826 | 8001 | 8932.377929944689801 | 0 | 0 |  |  | 20880 | 25993.469387755102040816326530612244898 |  | 0 | 49141 | 37112.8752203993005757434402332361516035 | 57544.267122809080101816326530612244898 | 0 | 0 | 10 |  |  |  |  | 146 | 146 | 150 |  |  | PRESSURE DID NOT EXCEED MAOP |  |  |  |  | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS APPARENT THAT THE INCIDENT WAS NOT CAUSED BY CONTROL ROOM ACTIONS. | [12 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | PIPE SEGMENT WAS NOT EFFECTIVELY ANCHORED DURING CONSTRUCTION REPLACEMENT. | YES |  |  |  |  | CONSTRUCTION | NO | [50 empty] | BART MASON | PIPELINE SAFETY MANAGER | bart.mason@spireenergy.com | 2512889616 |  |  |  |  | CRAIG HOEFERLIN | VICE PRESIDENT OPERATIONS SERVICES AND SMS | 3143492972 | craig.hoeferlin@spireenergy.com | OPERATOR CREWS WERE IN THE PROCESS OF REPLACING A VALVE ON A 12" STEEL MAIN AT THE REFERENCED ADDRESS. A SEGMENT HAD BEEN DISCONNECTED AND REMOVED BY USE OF STOPPER FITTINGS. THE REMAINING IN-SERVICE MAIN WAS NOT SECURED BY USING ANCHORS OR OTHER METHODS OF REINFORCEMENT. LINE PRESSURE FORCED THIS SEGMENT OF PIPELINE LOOSE FROM AN UPSTREAM COUPLING AT APPROXIMATELY 12:45 PM ON NOVEMBER 4. GAS WAS STOPPED AT 3:45 PM THE SAME DAY. AT APPROXIMATELY 4:20 PM THE OPERATOR DETERMINED THAT THIS EVENT WOULD BE REPORTABLE DUE TO ESTIMATING THE UNINTENTIONAL RELEASE OF GAS TO EXCEED 3 MILLION CUBIC FEET.
2025-03-31 10:13 | NO | YES | YES | 20200124 | 35400 | 2020-12-07 15:31 | SUPPLEMENTAL FINAL | 31348 | ATMOS ENERGY CORPORATION - MID-TEX | 5430 LBJ FREEWAY SUITE 1800 | DALLAS | TX | 75240 | 2020-11-07 09:20 | CENTRAL | YES | 2020 | 6700 WESTCHESTER DRIVE | DALLAS | DALLAS | TX | 75205 | 32.8476 | -96.8067 | [6 empty] | YES |  |  | 2020-11-07 11:10 | 1291639 | 1291734 | NATURAL GAS |  | 207 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2020-11-07 09:20 | OPERATOR/CONTRACTOR |  | 207 | NO | 0 | 2020-11-07 09:20 | YES | OPERATOR | 2020-11-07 09:21 | 2020-11-07 09:20 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 19 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2020 | UNKNOWN |  |  |  |  | 4 | D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 3408 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 81500 | 90987.2267579667815 | 4742 | 5294.005267316300342 | 0 | 0 |  | 5.9903 | 1240 | 1543.673469387755102040816326530612244898 | 0 | 0 | 87482 | 41304.7870389210437450728862973760932945 | 97824.9054946708369440408163265306122449 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 23 | 23 | 55 | 192.619(A)(2) | 2020-11-06 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  | 6 |  | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PIPELINE IS MONITORED BY THE SCADA SYSTEM. THERE WAS NO ALERT OR ALARM. SYSTEM WAS OPERATING NORMALLY AT THE TIME OF THE INCIDENT. | [12 empty] | YES | 6 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | SOCKET, ELECTROFUSION |  | 2020 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [13 empty] | YES | UNKNOWN, REFER TO NARRATIVE. |  | YES |  |  |  | OTHER | ELECTROFUSION JOINT FAILURE | NO | [86 empty] | PATRICK MCGRATH | OPERATIONS MANAGER | patrick.mcgrath2@atmosenergy.com | 903-249-7709 |  |  |  |  | MARLO SUTTON | VICE PRESIDENT - TECHNICAL SERVICES | 214-206-2033 | marlo.sutton@atmosenergy.com | ON FRIDAY, NOVEMBER 6, 2020, AT APPROXIMATELY 2:30 P.M., A THIRD-PARTY CONTRACTOR CUT THE NATURAL GAS SERVICE LINE TO HIGHLAND PARK HIGH SCHOOL WHEN PERFORMING A SAW CUT IN WESTCHESTER DRIVE. ATMOS ENERGY CREWS RESPONDED BY MAKING THE AREA SAFE, EVACUATING THE HIGH SCHOOL, AND THEN BEGAN THE PROCESS OF RESTORING SERVICE TO THE HIGH SCHOOL. THE MAIN LINE IN THE AREA CONSISTED OF 4" STEEL PIPE. HOWEVER, THE REPAIR REQUIRED THE INSTALLATION OF A POLY TRANSITION FITTING FROM THE STEEL MAIN TO THE 3" STEEL SERVICE LINE AS WELL AS THE INSTALLATION OF A POLY VALVE. A BELL HOLE WAS DUG AT THE LOCATION OF THE DAMAGE AND WHERE THE MAIN TO SERVICE LINE CONNECTION WAS BEING REPLACED. ON THE MORNING OF SATURDAY, NOVEMBER 7, REPAIRS HAD BEEN COMPLETED ON THE SEGMENT OF MAIN UP TO THE CLOSED POLY VALVE AND WAS ACTIVE WITH NATURAL GAS. ATMOS ENERGY EMPLOYEES WERE PREPARING TO PERFORM ADDITIONAL WORK THAT WAS REQUIRED FOR THE SERVICE LINE WHEN NATURAL GAS SUDDENLY ESCAPED AND IGNITED AT APPROXIMATELY 9:20 A.M. TWO EMPLOYEES WERE INJURED AND WERE TAKEN TO THE HOSPITAL. ONE EMPLOYEE WAS TREATED AND RELEASED, AND THE OTHER WAS ADMITTED TO THE HOSPITAL AT 11:17 AM. THE PROBABLE CAUSE OF THIS INCIDENT WAS THE FAILURE AND RELEASE OF THE 4" ELECTROFUSION COUPLING THAT OCCURRED WITHIN THE NORTH BELL HOLE. THE JOINT FAILURE WAS SUDDEN AND OCCURRED AFTER THE COUPLING WAS INSTALLED AND PLACED IN SERVICE. THE JOINT FAILURE AND SEPARATION OF THE COUPLING OCCURRED WITHIN THE SAME EXCAVATED BELL HOLE THAT THE RESULTING INJURED CREW MEMBERS WERE WORKING DOWNSTREAM PERFORMING FINAL SYSTEM TIE-INS. THE MOST LIKELY SOURCE OF IGNITION OCCURRED FROM THE ENERGIZED FITTING BEING FUSED (4" EF COUPLING) ON THE OUTLET SIDE OF THE VALVE. NONE OF THESE ACTIVITIES PROVIDED EVIDENCE OF A DIRECT CAUSE OF FAILURE. SINCE THE MATERIALS INVOLVED IN THE FAILURE WERE DESTROYED IN THE RESULTING FIRE, LABORATORY TESTING CANNOT BE CONDUCTED ON THE FAILED FITTING TO FURTHER EVALUATE ROOT CAUSE. HOWEVER, TESTING WAS CONDUCTED ON OTHER ELEMENTS IN INVESTIGATION OF THE ROOT CAUSE SUCH AS THE ELECTROFUSION PROCESSOR UNIT, THE DOWNSTREAM VALVE, AND PRIOR FUSIONS PERFORMED BY THE SAME QUALIFIED EMPLOYEE.
2025-03-31 10:13 | NO | NO | NO | 20200125 | 35155 | 2020-12-11 17:07 | SUPPLEMENTAL FINAL | 4060 | DOMINION ENERGY OHIO | 1201 EAST 55TH STREET | CLEVELAND | OH | 44103 | 2020-11-12 12:39 | EASTERN | NO | 2020 | 278 S. CLEVELAND MASSILLON ROAD | AKRON | SUMMIT | OH | 44333 | 41.1294 | -81.6345 | YES | YES |  |  |  |  | YES |  |  | 2020-11-12 20:52 | 1292056 | 1292269 | NATURAL GAS |  | 2427 | 112 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-11-12 12:39 | NO |  |  | 2020-11-12 13:05 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 38 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2016 | 2016 |  |  |  |  | 20 | API 5L | AMERICAN STEEL | STEEL |  | OTHER | SMLS | 0.375 | [6 empty] | MECHANICAL PUNCTURE | 1 | 2 | [7 empty] | CLASS 3 LOCATION | 2792 | 3117.010271266788392 | 72534 | 80977.515406900153734 | 10334 | 11536.957071372131534 | 0 | 0 |  | 2.65 | 6432 | 8007.183673469387755102040816326530612245 | 297 | 369.73469387755102040816326530612244898 | 92389 | 47356.8319792644636991253644314868804665 | 104008.4011168860124355102040816326530612 | 4 | 0 | 4 | 0 | 0 | 4 | 4 | 50 | 50 | 60 | 192.619(A)(2) | 2016-06-06 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | A031000922 | NA |  | CONTRACT LOCATOR | YES | YES | 23 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | JEFFERY BURDETTE | PIPELINE SAFETY SUPERVISOR | jeffery.l.burdette@dominionenergy.com | 3307545524 |  | JEFFERY BURDETTE | jeffery.l.burdette@dominionenergy.com | 3307545524 | CAROL HAGER | GAS OPERATIONS MANAGER | 3304379557 | carol.m.hager@dominionenergy.com | A THIRD PARTY CONTRACTOR DOING ROAD WORK HIT A 20" HIGH PRESSURE DISTRIBUTION PIPELINE OPERATING AT 50PSIG. IN ORDER TO AVOID A LARGE-SCALE OUTAGE, THE AREA WAS SECURED AND MONITORED WHILE A 20" STOPPLE FITTING WAS PROCURED AND INSTALLED TO ISOLATE THE GAS RELEASE. THIS LIMITED THE IMPACT TO FOUR COMMERCIAL AND FOUR RESIDENTIAL CUSTOMERS. THE CAUSE OF THIS EVENT WAS THAT THE THIRD PARTY EXCAVATOR FAILED TO MAINTAIN ADEQUATE CLEARANCE BETWEEN POWERED EQUIPMENT AND THE UNDERGROUND FACILITY. DEO HAS DETERMINED THAT THE EXCAVATOR WAS AWARE OF THE PRESENCE OF DEO'S FACILITIES, BUT ELECTED NOT TO UTILIZE HAND TOOLS, INSTEAD ATTEMPTING TO DIG WITH POWERED EQUIPMENT IN CLOSE PROXIMITY TO THE PIPELINE.
2025-03-31 10:13 | NO | NO | NO | 20200126 | 35130 | 2020-12-23 15:32 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2020-11-25 16:28 | PACIFIC | NO | 2020 | 301 N MARENGO AVE | ALHAMBRA | LOS ANGELES | CA | 91801 | 34.095 | -118.1423 | [7 empty] | YES | STOPPED AT SERVICE TO MAIN CONNECTION | 2020-11-25 16:28 | 1293031 | 1293113 | NATURAL GAS |  | 50.31 | 1077.43 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-11-25 12:09 |  |  |  | 2020-11-25 12:14 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 28 | YES | NO | [11 empty] | INVESTOR OWNED |  | SERVICE |  | 1948 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY 1,000 SCFH OR HIGHER | NO |  | NO | 1.25 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | OTHER | [8 empty] | ELECTRICAL ARC | CLASS 3 LOCATION | 13000 | 14513.299973663413 | 10000 | 11164.07690281801 | 55329 | 61769.721095601767529 | 0 | 0 |  | 6 | 302 | 375.959183673469387755102040816326530612 | 6465 | 8048.26530612244897959183673469387755102 | 85096 | 44010.8661981365585531195335276967930029 | 95871.3224618791088963469387755102040816 | 4 | 1 | 156 | 0 | 0 | 156 | 5 | 23 | 23 | 25 | 192.621 M | 1970-08-19 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [150 empty] | YES | [17 empty] | FRANK SANTA CRUZ |  | fsantacruz@socalgas.com | 2134070168 |  | FRANK SANTA CRUZ | fsantacruz@socalgas.com | 2134070168 | FRANK SANTA CRUZ | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 2134070168 | fsantacruz@socalgas.com | ON NOVEMBER 25, 2020, AN ELECTRICAL TRANSFORMER RELEASED A CHARGE OF ENERGY INTO THE GROUND. UPON INVESTIGATION, IT WAS DETERMINED THAT THIS RELEASE IN ENERGY ARCED AND CREATED A GOUGE IN BOTH THE GAS SERVICE AND WATER SERVICE AT 301 N MARENGO AVE, ALHAMBRA. WATER ENTERED THE GAS SERVICE DUE TO THE DIFFERENCE IN PRESSURE CAUSING 161 GAS SERVICE OUTAGES. SOCALGAS CREWS IDENTIFIED AND ISOLATED THE INTRUSION POINT AND EXTRACTED THE WATER FROM ALL MAINS AND SERVICES AFFECTED. THIS WAS REPORTED TO CPUC AND DOT DUE TO A RELEASE OF GAS AND DAMAGES EXCEEDING $50,000.
2025-03-31 10:13 | NO | YES | NO | 20200127 | 34952 | 2020-12-23 15:54 | SUPPLEMENTAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2020-11-23 09:45 | EASTERN | NO | 2020 | 3764 CR15 | SOUTH POINT | LAWRENCE | OH | 45680 | 38.4544 | -82.5456 | [5 empty] | YES |  |  |  | 2020-11-23 21:51 | 1292897 | 1292908 | NATURAL GAS |  | 0 | 1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-11-23 20:10 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | NO | 3 | 2020-11-23 09:45 | YES | OPERATOR | 2020-11-23 09:45 | 2020-11-23 09:45 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 2010 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | OTHER | METER VALVE ON TOP OF PLASTIC RISER | [9 empty] | OTHER | [8 empty] | PURGING ACTIVITY | CLASS 3 LOCATION | 770000 | 859633.92151698677 | 28524 | 31844.412957598091724 | 5900 | 6586.8053726626259 | 0 | 0 |  | 2 | 0 | 0 | 2 | 2.48979591836734693877551020408163265306 | 804426 | 371953.949945650206788104956268221574344 | 898067.6296431658549709387755102040816327 | 0 | 0 | 7 | 0 | 1 | 7 | 0 | 35 | 35 | 46 | 192.619(A)(3) | 1970-01-23 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.5 |  | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | FAILURE TO PREVENT ACCIDENTAL IGNITION |  |  | YES |  |  | COMMISSIONING | YES | NO, THEY WERE NOT QUALIFIED FOR THE TASK(S) NOR WERE THEY PERFORMING THE TASK(S) UNDER THE DIRECTION AND OBSERVATION OF A QUALIFIED INDIVIDUAL | [49 empty] | ROB SMITH | MANAGER OF OPERATIONS COMPLIANCE | rrsmith@nisource.com | 614-460-5491 |  |  |  |  | ROB SMITH | MANAGER OF OPERATIONS COMPLIANCE | 614-460-5491 | rrsmith@nisource.com | ON NOVEMBER 23, 2020, COLUMBIA WAS PLACING A REPAIRED MAINLINE IN SERVICE AND PURGING THE LINE THROUGH A SERVICE LINE AT THE REAR OF A RESIDENTIAL STRUCTURE WHEN AN ACCIDENTAL IGNITION OCCURRED. THE IGNITION DAMAGED THE STRUCTURE AND FOUR VEHICLES. DURING THE PURGE, A GROUNDED, 7' METALLIC PURGE STAND WAS NOT UTILIZED. COLUMBIA EVACUATED THE RESIDENTIAL STRUCTURE TO ENSURE NO RESIDENTS WERE INJURED AND SHUT DOWN THE MAINLINE FOR SAFETY. THE INDIVIDUAL PURGING THE SERVICE LINE HELD THE APPROPRIATE OPERATOR QUALIFICATION FOR PURGING SERVICE LINES BUT WAS NOT QUALIFIED TO PURGE A MAINLINE THROUGH A SERVICE LINE. THE INDIVIDUAL THAT WAS EXECUTING THE PURGE WAS DRUG TESTED HOWEVER AN ALCOHOL TEST WAS NOT CONDUCTED. PLEASE CONSIDER THIS A FINAL REPORT.
2025-03-31 10:13 | NO | NO | NO | 20200128 | 34883 | 2020-12-29 18:06 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2020-12-01 11:40 | EASTERN | YES | 2020 | 4703 WILKINSON BLVD | CHARLOTTE | MECKLENBURG | NC | 28208 | 35.2286 | -80.9158 |  | YES | [7 empty] | 2020-12-01 19:28 | 1293334 | 1293463 | NATURAL GAS |  | 7.83 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-12-01 14:30 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | NO | 0 | 2020-12-01 11:46 | YES | OPERATOR | 2020-12-01 11:46 | 2020-12-01 13:01 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | YES | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1986 | UNKNOWN |  |  |  |  | 4 | DRISCO 8000 | DRISCO | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.409 |  | UNKNOWN | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 22867 | 25528.894653673943467 | 0 | 0 | 49000 | 54703.976823808249 | DAMAGED EXCAVATOR | 2.4 | 19 | 23.65306122448979591836734693877551020408 | 0 | 0 | 71886 | 33251.9295403025021269970845481049562682 | 80256.5245387066822629183673469387755102 | 68 | 0 | 0 | 0 | 0 | 0 | 68 | 65 | 68 | 75 | 192.619(A)(1) | 1986-10-21 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | TELECOMMUNICATIONS | YES | C203212607 |  |  | CONTRACT LOCATOR | UNKNOWN/OTHER | YES | 6 | EXCAVATION ISSUE | IMPROPER BACKFILLING PRACTICES | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 7047314680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 7047314618 | farris.berry@duke-energy.com | A CONTRACTOR STRUCK A 4" PLASTIC GAS MAIN WHILE BORING TO INSTALL A TELECOM LINE. DURING RESPONSE, GAS MIGRATED AND IGNITED BENEATH AN EXCAVATOR BEING USED TO EXPOSE THE PIPELINE. THE LOCATOR INACCURATELY AND INSUFFICIENTLY MARKED THE REQUESTED AREA. ALSO DURING THE INCIDENT, THERE WERE 68 COMMERCIAL OUTAGES.
2025-03-31 10:13 | NO | YES | YES | 20210001 | 35863 | 2021-01-02 15:11 | SUPPLEMENTAL FINAL | 15348 | PEOPLES GAS SYSTEM INC | PO BOX 2562 | TAMPA | FL | 33601 | 2020-12-03 17:11 | EASTERN | NO | 2020 | 8TH STREET CT. WEST @ 30TH AVENUE WEST | BRADENTON | MANATEE | FL | 34205 | 27.4738 | -82.5705 | [5 empty] | YES |  |  |  | 2020-12-03 17:11 | 1293475 | 1293605 | NATURAL GAS |  | 224 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2020-12-03 13:50 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 205 | 2020-12-03 11:20 | YES | OPERATOR | 2020-12-03 11:37 | 2020-12-03 11:37 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 84 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2014 | UNKNOWN |  |  |  |  | 2 | DRISCO PLEX 6500 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | LEAK |  |  | OTHER | DAMAGE BY 3RD PARTY TO LINE | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 25928 | 28946.218593626536328 | 2400 | 2679.3784566763224 | 100000 | 111640.7690281801 | ESTIMATED OTHER COSTS INCLUDES ESTIMATED VALUE OF DAMAGED HOME. | 2.88 | 645 | 802.959183673469387755102040816326530612 | 0 | 0 | 128973 | 60079.4163345160160438483965014577259475 | 144069.3252621564281157551020408163265306 | 0 | 0 | 0 | 1 | 1 | 95 | 3 | 43 | 47 | 60 | 192.619(A)(2) | 2014-04-24 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 0.1 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS WAS A 3RD PARTY LINE STRIKE TO OPERATOR'S SYSTEM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 330000015 |  |  | UTILITY OWNER | YES | NO |  | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | DATA NOT COLLECTED | [169 empty] | SANDRA PANOS | MANAGER SAFETY MGMT SYSTEMS AND QUALITY ASSURANCE | sjpanos@tecoenergy.com | (813) 275-3730 |  | TOMMY JAMBON | tejambon@tecoenergy.com | (813) 275-3736 | SANDRA PANOS | MANAGER SAFETY MGMT SYSTEMS AND QUALITY ASSURANCE | (813) 275-3730 | sjpanos@tecoenergy.com | DAMAGED 2" PE MAIN BY THIRD PARTY NEXT GENERATION MANAGEMENT INC. BORE CREW. THE DAMAGED GAS LINE RESULTED IN GAS MIGRATING INTO A SEVERED SEWER LINE WHICH WAS ALSO DAMAGED BY NEXT GENERATION MANAGEMENT INC. IN THE SAME EXCAVATION. IT APPEARS THE GAS MIGRATED FROM THE COUNTY SEWER SYSTEM THROUGH THE HOME'S SEWER SYSTEM AND UNEXPECTEDLY INTO THE HOME WHERE THE GAS IGNITED, RESULTING IN AN EXPLOSION. ADDITIONAL NOTES: PART A QUESTION 21C - THE AMOUNT OF GAS REPORTED IS AN ESTIMATE OF .55. THE PHMSA PORTAL ROUNDED THE AMOUNT TO 1.0. PART A QUESTION 22 - THE NUMBER OF GENERAL PUBLIC EVACUATED IS AN ESTIMATE BASED ON A REVIEW OF THE RESPONDING FIRE DEPARTMENTS' INCIDENT REPORTS AND ASSUMING THAT THERE WERE 2 OCCUPANTS PER RESIDENTIAL BUILDING AND 5 OCCUPANTS PER BUSINESS BUILDING. PART D QUESTION 6 - THE NUMBER OF RESIDENTIAL BUILDINGS AFFECTED IS AN ESTIMATE BASED ON A REVIEW OF THE RESPONDING FIRE DEPARTMENTS' INCIDENT REPORTS. PART D QUESTION 7 - THE NUMBER OF BUSINESS BUILDINGS AFFECTED IS AN ESTIMATE BASED ON A REVIEW OF THE RESPONDING FIRE DEPARTMENTS' INCIDENT REPORTS.
2025-03-31 10:13 | NO | YES | NO | 20210004 | 34907 | 2021-01-07 14:21 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-12-08 13:52 | EASTERN | YES | 2020 | 3050 POLLOCK ROAD | GRAND BLANC | GENESEE | MI | 48439 | 42.8938 | -83.6506 |  | YES |  |  |  | YES |  |  |  | 2020-12-08 23:00 | 1293848 | 1294028 | NATURAL GAS |  | 2700 | 469 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-12-08 13:52 | YES | OPERATOR | 2020-12-08 23:00 | 2020-12-08 14:28 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2020 | UNKNOWN |  |  |  |  | 6 | D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.602 |  | 2406 | MECHANICAL PUNCTURE | 6 | 18.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 216157 | 241319.337108243258757 | 1014 | 1132.037397945746214 | 0 | 0 |  | 3.3 | 8910 | 11092.0408163265306122448979591836734694 | 1548 | 1927.102040816326530612244897959183673469 | 227629 | 112459.557264148692000816326530612244898 | 255470.5173633318621138571428571428571429 | 16 | 0 | 1300 | 0 | 0 | 1300 | 16 | 54 | 54 | 60 | 192.619(A)(2) | 2020-08-31 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | B002610695 |  |  | CONTRACT LOCATOR | YES | YES | 34 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON DECEMBER 8, 2020 AT APPROXIMATELY 13:52 HOURS, CONSUMERS ENERGY WAS NOTIFIED OF A DAMAGE TO A 6-INCH MP PLASTIC NATURAL GAS PIPELINE. THE PIPELINE WAS STRUCK AND COMPLETELY SEVERED BY A CONTRACTOR PERFORMING SANITARY SEWER WORK. THE DAMAGE OCCURRED NEAR 3050 POLLOCK ROAD, GRAND BLANC (GENESEE COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) AND DISTRIBUTION CREW (CREW) ARRIVED AT APPROXIMATELY 14:28 AND 14:47 HOURS RESPECTIVELY. THE GSW CONTINUOUSLY MONITORED THE SITE AND SURROUNDING AREA UNTIL THE PIPELINE SEGMENT WAS ISOLATED AND BLOWING GAS CONTAINED. NO FATALITIES AND OR INJURIES OCCURRED AS A RESULT OF THE PIPELINE DAMAGE. THE CREW IN CONCERT WITH GAS SYSTEM PLANNING IDENTIFIED THE SYSTEM AS A TWO-WAY FED SYSTEM. HOWEVER, BECAUSE THE PIPELINE WAS COMPLETELY SEVERED AN ISOLATION PLAN WAS DEVELOPED WHICH INVOLVED OPERATING AN EXISTING VALVE LOCATED EAST OF THE DAMAGE PIPE SEGMENT AND SQUEEZING THE PIPE AT A REMOTE LOCATION TO THE WEST OF THE SEGMENT. PRIOR TO ISOLATION THE PIPELINE WAS GAUGED AT TWO LOCATIONS (LOCATIONS AT THE EAST AND WEST READ 10 PSIG). THE VALVE TO THE EAST WAS CLOSED AT APPROXIMATELY 16:50 HOURS AND PRESSURE ON THE GAUGES DROPPED TO ZERO. THIS WAS THE FIRST INDICATION OF A LOSS OF SERVICE TO THE CUSTOMERS WEST OF THE DAMAGE. THE DAMAGED SEGMENT WAS REMOVED AND REPLACED WITH APPROXIMATELY 5 FOOT OF 6" PLASTIC MEDIUM-PRESSURE PIPELINE. FOLLOWING THE PIPELINE REPAIR, A RESTORATION PLAN WAS EXECUTED WHICH INVOLVED SHUTTING OFF (~1300) METERS TO ALL IMPACTED RESIDENTIAL AND COMMERCIAL CUSTOMERS, PURGING APPROXIMATELY 27 MILES OF PIPELINE AT MULTIPLE LOCATION AND SERVICE RESTORATION TO IMPACTED CUSTOMERS.
2025-03-31 10:13 | YES | NO | NO | 20210005 | 35951 | 2021-01-08 15:46 | SUPPLEMENTAL FINAL | 17570 | ROCHESTER GAS & ELECTRIC CORP | 180 SOUTH CLINTON AVENUE | ROCHESTER | NY | 14607 | 2020-12-09 18:27 | EASTERN | NO | 2020 | 51 NOEL DR | GATES | MONROE | NY | 14606 | 43.1618 | -77.7087 |  |  | YES | [6 empty] | 2020-12-09 22:59 | 1293962 | 1294363 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-12-09 18:27 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 7 | 2020-12-09 18:27 |  |  |  | 2020-12-09 18:38 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | 2005 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | OTHER | ALUMINIUM GAS METER | [9 empty] | OTHER | [8 empty] | THERE IS NO INDICATION THAT ANY FAILURE OF COMPANY EQUIPMENT CONTRIBUTED TO THE CAUSE OF THE EVENT. THE INCIDENT WAS THE RESULT OF ACTIONS TAKEN BY THE CUSTOMER/RESIDENT ON COMPANY EQUIPMENT. | CLASS 3 LOCATION | 144800 | 161655.8335528047848 | 100 | 111.6407690281801 | 5000 | 5582.038451409005 | 0 | 0 |  | 10 | 10 | 12.44897959183673469387755102040816326531 | 0 | 0 | 149910 | 69322.6651878253467405247813411078717201 | 167361.9617528338066346938775510204081633 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 59 | 59 | 60 | 192.619(A)(4) | 1996-12-31 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 3.6 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THERE ARE NO REPORTS OF GAS ODORS OR ANY OTHER ABNORMAL OPERATION CONDITIONS PRIOR TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [168 empty] | BARRY KACHMARYK | GAS ENGINEERING MANAGER | barry_kachmaryk@rge.com | 585-771-4143 |  |  |  |  | BARRY KACHMARYK | GAS ENGINEERING MANAGER | 585-771-4143 | barry_kachmaryk@rge.com | RG&E WAS NOTIFIED BY 911 ABOUT AN EXPLOSION AND FIRE ON NOEL DR. IN GATES, NY AND DISPATCHED PERSONNEL TO RESPOND IN ACCORDANCE WITH COMPANY PROCEDURES. IN ACCORDANCE WITH RG&E CONTROL ROOM NOTIFICATION PROCEDURES, THE NRC WAS NOTIFIED ON 12/9/2020 AT 22:59 (REPORT #1293962). A FOLLOW UP CALL TO THE NRC FOR THE REQUIRED 24 HOUR UPDATE WAS ASSIGNED REPORT #1294363. THERE ARE NO REPORTS OF INJURIES RELATED TO THE INCIDENT AND THE STRUCTURE WAS EXTENSIVELY DAMAGED. LOCAL POLICE AND FIRE INVESTIGATORS DEEMED THE INCIDENT WAS CAUSED FROM A NATURAL GAS LEAK WITHIN THE RESIDENCE WHERE THE COMPANY WAS NOT AT FAULT RG&E PERFORMED A LEAK SURVEY IN PROXIMITY TO THE INCIDENT IN ACCORDANCE WITH COMPANY O&M PROCEDURES AND NO UNDERGROUND LEAKS WERE IDENTIFIED. THERE ARE NO REPORTS OF ODOR COMPLAINTS OR LEAKS DISCOVERED DURING ROUTINE SURVEYS IN THE VICINITY OF THE INCIDENT PRIOR TO DECEMBER 9, 2020. AT THE RECOMMENDATION OF AN ENGINEER - INVESTIGATOR IN THE ACCIDENT INVESTIGATION DIVISION, THE CAUSE IS BEING CHANGED TO: NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT. THE ACTIONS THAT LED TO THE INCIDENT WERE NOT DONE WITH CRIMINAL INTENT.
2025-03-31 10:13 | NO | YES | YES | 20210006 | 36187 | 2021-01-08 16:22 | SUPPLEMENTAL FINAL | 12390 | METROPOLITAN UTILITIES DISTRICT | 7350 WORLD COMMUNICATIONS DR | OMAHA | NE | 68122 | 2020-12-08 08:14 | CENTRAL | YES | 2020 | 4810 S 51ST STREET | OMAHA | DOUGLAS | NE | 68117 | 41.2109 | -95.9949 |  |  | YES | [6 empty] | 2020-12-08 09:35 | 1293782 |  | NATURAL GAS |  | 1.795 | 0 | YES | 0 | 0 | 0 | 0 | 3 | 3 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2020-12-08 08:14 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1795 | YES | 0 | 2020-12-08 08:25 |  |  |  | 2020-12-08 08:27 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | INSIDE A BUILDING |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | INSIDE METER/REGULATOR SET |  | 1959 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | YES |  |  |  | STEEL |  | OTHER | BLACK IRON | 0.133 | [6 empty] | OTHER | [8 empty] | UNKNOWN AT THIS TIME | CLASS 3 LOCATION | 500000 | 558203.8451409005 | 12500 | 13955.0961285225125 | 3000 | 3349.223070845403 | 0 | 0 |  | 2.81 | 5 | 6.22448979591836734693877551020408163265 | 0 | 0 | 515505 | 238363.9794203544913702623906705539358601 | 575514.3888300643338673469387755102040816 | 0 | 0 | 3 | 0 | 0 | 4 | 0 | 10 | 10 | 10 | 192.619(A)(3) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 11 |  | YES | YES | YES | YES | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS CONTAINED TO THE SINGLE RESIDENCE | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | OTHER | TAMPERING AND REMOVAL OF THE NATURAL GAS SAFETY DEVICE FROM PIPELINE INSIDE OF THE STRUCTURE | [155 empty] | MICHAEL CONRAD | SENIOR CLAIMS INVESTIGATOR | mike_conrad@mudnebr.com | 402-504-7165 | 402-504-5165 | MICHAEL CONRAD | mike_conrad@mudnebr.com | 402-504-7165 | MICHAEL CONRAD | SENIOR CLAIMS INVESTIGATOR | 402-504-7165 | mike_conrad@mudnebr.com | ON DECEMBER 8, 2020 AT APPROXIMATELY 0825HRS THE METROPOLITAN UTILITIES DISTRICT (DISTRICT) WAS NOTIFIED BY THE OMAHA FIRE DEPARTMENT (OFD) OF A WORKING FIRE AT 4810 S 51ST STREET, OMAHA NEBRASKA. DISTRICT PERSONNEL ARRIVED AND SHUT OFF THE GAS TO THIS RESIDENCE. THERE WAS A POSSIBILITY NATURAL GAS CONTRIBUTED TO THIS INCIDENT/LOSS BUT THERE WAS NO DETERMINATION MADE AT THAT TIME. THE EXACT CAUSE OF THE FIRE HAS NOT BEEN DETERMINED. ON THE DAY OF THE LOSS, DISTRICT PERSONNEL PERFORMED A GAS LEAK SURVEY AND AN ODORANT TEST OF THE GAS TRANSMISSION AND SERVICE LINES IN THE AREA. THE GAS LEAK SURVEY SHOWED NO ISSUES WITH THE GAS TRANSMISSION LINE OR ANY CONNECTING SERVICES. THE ODORANT TEST INDICATED SUFFICIENT ODORANT AT ALL TEST LOCATIONS IN THE AREA. ON DECEMBER 23, 2020 THERE WAS A COMBINED INVESTIGATION WITH SEVERAL PARTIES OF INTEREST TO TRY AND LOCATE THE ORIGIN AND CAUSE OF THE LOSS. DURING THIS COMBINED INVESTIGATION, THE GAS SERVICE TO 4810 S 51ST STREET WAS PRESSURE TESTED. THE RESULTS OF THIS PRESSURE TEST REVEALED NO ISSUES OR LEAKS WITH THE GAS SERVICE FROM THE GAS TRANSMISSION LINE TO THE HOUSE FOUNDATION. TO DATE, THE DISTRICTS INVESTIGATION REMAINS OPEN. 12/30/21- AFTER INVESTIGATION, THE METROPOLITAN UTILITIES DISTRICT HAS DETERMINED THAT THE APPARENT CAUSE OF THE INCIDENT WAS TAMPERING WITH THE PIPELINE INSIDE THE STRUCTURE. THE DISTRICT'S CONCLUSION IS CONSISTENT WITH THE RESULTS OF A JOINT NEBRASKA STATE FIRE MARSHAL AGENCY AND OMAHA FIRE DEPARTMENT INVESTIGATION THAT TOOK PLACE FOLLOWING THE INCIDENT. IN A CLOSING ACTION LETTER FROM NEBRASKA STATE FIRE MARSHAL TO THE DISTRICT, THE NEBRASKA STATE FIRE MARSHAL CONCLUDED, FOLLOWING THEIR INVESTIGATION, THAT "THE PRESSURE TEST SHOWED THAT THE PIPELINE DID REMAIN INTACT AND NO GAS WAS DETECTED OUTSIDE OF THE STRUCTURE DURING THE LEAK SURVEY. THE SEARCH AND SORTING THROUGH DEBRIS CONCLUDED WITH EVIDENCE DISCOVERY OF TAMPERING AND THE REMOVAL OF THE NATURAL GAS SAFETY DEVICE FROM PIPELINE INSIDE OF THE STRUCTURE." THE METROPOLITAN UTILITIES DISTRICT HAS CLOSED ITS INVESTIGATION IN REGARD TO THIS INCIDENT.
2025-03-31 10:13 | NO | YES | NO | 20210007 | 34725 | 2021-01-14 16:43 | ORIGINAL FINAL | 18472 | SEMCO ENERGY GAS COMPANY | 1411 THIRD STREET | PORT HURON | MI | 48060 | 2020-12-16 14:33 | EASTERN | NO | 2020 | 10429 92ND AVENUE | ALLENDALE | OTTAWA | MI | 49401 | 42.9576 | -86.0132 | [5 empty] | YES |  |  |  | 2020-12-16 16:37 | 1294462 | 1294501 | NATURAL GAS |  | 1.252 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-12-16 14:33 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1.2 | NO | 0 | 2020-12-16 14:33 |  |  |  | 2020-12-16 14:59 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.09 |  | 2406 | OTHER | [8 empty] | CAR IMPACT DISLODGED METER FROM METER BAR AND PIPING. | CLASS 2 LOCATION | 270110 | 301552.88122201726811 | 163 | 181.974453515933563 | 630 | 703.33684487753463 | 0 | 0 |  | 3.43 | 4 | 4.97959183673469387755102040816326530612 | 0 | 0 | 270907 | 125265.435226214275376209912536443148688 | 302443.1721122474709968775510204081632653 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 55 | 60 | 60 | 192.619(A)(2) | 1994-05-25 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  | YES | YES |  |  | NO | 15 | PASSENGER CAR | ROADWAY | 35 | YES | [5 empty] | YES | A BOULDER AND RAISED FLOWER BEDS (BY OWNER) WERE BLOCKING METER. | [135 empty] | JENNIFER POND | COMPLIANCE ANALYST | jennifer.pond@semcoenergy.com | 810-242-2381 |  | JENNIFER POND | jennifer.pond@semcoenergy.com | 810-242-2381 | JENNIFER POND | COMPLIANCE ANALYST | 810-242-2381 | jennifer.pond@semcoenergy.com | OUR EMERGENCY DISPATCH CENTER DISPATCHED FREDDIE CARPENTER TO A HIT FACILITY ON 12/16/2020 AT 14:33 HRS. FREDDIE ARRIVED ON THE SCENE AT 14:59 HRS AND FOUND THAT THERE WAS AN ACTIVE FIRE AT THIS ADDRESS CAUSED BY AN UNKNOWN THIRD PARTY DRIVER WHO HAD STRUCK THE HOUSE WITH THEIR VEHICLE AND FLED THE SCENE. FREDDIE WAS ASSISTED BY BRANDON FAST AND THEY SECURED THE SERVICE BY SQUEEZING OFF THE 1/2' SERVICE LINE IN THE YARD. THE SERVICE WAS SECURED AT 15:05 HRS. I WAS NOTIFIED OF THE INCIDENT AT APPROXIMATELY 15:20 HRS BY OPERATIONS SUPERVISOR SCOTT ZEERIP. I THEN NOTIFIED MY CHAIN OF COMMAND OF THE INCIDENT AND BEGAN GATHERING INFORMATION. THE INCIDENT WAS REPORTED TO KYLE FRISKE OF THE MICHIGAN PUBLIC SERVICE COMMISSION AT 15:58 HRS. AFTER SECONDARY REPORT FROM THE FIELD CAME IN; IT WAS DETERMINED THAT THE DAMAGE TO THE STRUCTURE WOULD MOST LIKELY EXCEED $50,000. I THEN NOTIFIED THE NATIONAL RESPONSE CENTER OF THE INCIDENT AT 16:37 HRS EDT. AT THIS TIME THE RESPONDING FIRE DEPARTMENTS WERE STILL ACTIVELY ENGAGED IN EXTINGUISHING THE STRUCTURE FIRE. FIRE CHIEF MIKE KEEFE ORDERED THE VEHICLE BE REMOVED FROM THE SCENE BUT LEFT THE CUSTOMER METER AND ASSOCIATED FACILITIES IN PLACE FOR FURTHER INVESTIGATION. MPSC INSPECTOR DERREK SHIMMING CONTACTED ME AT 16:48 HRS ABOUT THIS INCIDENT AND DETERMINED THAT HE WOULD BE ON THE SCENE AT 09:00 HRS ON 12/17/2020. STEVE MCCARTHY WAS NOTIFIED OF THE VISIT AND WILL BE ON SITE AT THE TIME OF THE INSPECTION.
2025-03-31 10:13 | NO | NO | NO | 20210008 | 35204 | 2021-01-14 22:08 | SUPPLEMENTAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2020-12-15 16:49 | EASTERN | YES | 2020 | 8452 LOZIER AVENUE | WARREN | MACOMB | MI | 48089 | 42.4662 | -83.0202 | [5 empty] | YES | YES |  |  | 2020-12-15 20:05 | 1294374 | 1294461 | NATURAL GAS |  | 345 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2020-12-15 18:11 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 86 | YES | 0 | 2020-12-15 16:49 | YES | OPERATOR | 2020-12-15 18:11 | 2020-12-15 17:34 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 30 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1947 | UNKNOWN |  |  |  |  | 2 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.154 | [6 empty] | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 51000 | 56936.792204371851 | 17732 | 19796.141164076895332 | 1026 | 1145.434290229127826 | 0 | 0 |  | 3.3 | 1139 | 1417.938775510204081632653061224489795918 | 0 | 0 | 70897 | 33566.5605916695862257725947521865889213 | 79296.3064341880782396326530612244897959 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 55 | 55 | 60 | 192.619(A)(1) | 1974-08-13 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | UTILITY | BACKHOE/TRACKHOE | SEWER (SANITARY/STORM) | YES | B03491283 |  |  | CONTRACT LOCATOR | YES | YES | 28 | EXCAVATION ISSUE | EXCAVATOR FAILED TO PROTECT/SHORE/SUPPORT FACILITIES | [170 empty] | CARMELLA KING |  | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON DECEMBER 15, 2020 AT APPROXIMATELY 16:49 HOURS, CONSUMERS ENERGY RECEIVED NOTIFICATION FROM THE CITY OF WARREN WATER AND SEWER DIVISION OF A BROKEN AND BLOWING NATURAL GAS PIPELINE AT 8452 LOZIER AVENUE, WARREN (MACOMB COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) AND DISTRIBUTION CREW WERE DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 17:34 HOURS AND 18:57 HOURS RESPECTIVELY. THE GSW CONFIRMED A 2-INCH STEEL (THREADED AND COUPLED) MEDIUM PRESSURE PIPELINE HAD BEEN DAMAGED DURING SEWER REPAIR WORK AND CONFIRMED A DISTRIBUTION CREW WAS IN ROUTE. THE GSW CONTINUED INVESTIGATION ACTIVITIES IN THE SURROUNDING AREA(S). NO ADDITIONAL GAS READS WERE DISCOVERED BEYOND THE IDENTIFIED LEAK SPREAD NEAR THE DAMAGE LOCATION. AT APPROXIMATELY 18:11 HOURS A HOME EXPLOSION OCCURRED AND GAS IGNITED AT 8452 LOZIER AVENUE. THE GSW CONTACTED CONSUMERS ENERGY DISPATCH, ADVISED AN EXPLOSION OCCURRED AND REQUESTED THE WARREN FIRE DEPARTMENT BE CONTACTED. THE HOME WAS UNOCCUPIED AND NO FATALITIES AND/OR INJURIES OCCURRED AS A RESULT OF THE INCIDENT THE DISTRIBUTION CREW SQUEEZED THE STEEL PIPELINE AT REMOTE LOCATIONS AT APPROXIMATELY 21:26 HOURS. TO COMPLETELY CONTAIN THE GAS, STOPPLE FITTINGS WERE INSTALLED AND GAS WAS COMPLETELY SHUTDOWN ON DECEMBER 16, 2020 AT APPROXIMATELY 00:36 HOURS. SERVICE PERSONNEL REMAINED ONSITE AND CONTINUED TO MONITOR THE AREA TO ENSURE NO ADDITIONAL GAS MIGRATION. FURTHER INVESTIGATION DETERMINED THE SEWER WORK BEING PERFORMED REQUIRED EXPOSING AND UNDERMINING THE NATURAL GAS PIPELINE. DURING BACKFILL THE THREADED AND COUPLED PIPELINE WAS NOT ADEQUATELY SUPPORTED DURING COMPACTION CAUSING THE PIPELINE TO BREAK AT THE COUPLING. APPROXIMATELY 30-FEET OF 2" PLASTIC MEDIUM PRESSURE PIPELINE WAS INSTALLED AT THE DAMAGE LOCATION AND 2-FEET STEEL MEDIUM PRESSURE PIPELINE WAS INSTALLED AT EACH SQUEEZE POINT TO PERMANENTLY REPAIR THE PIPELINE AND NORMAL OPERATIONS RESUMED ON DECEMBER 16, 2020 AT APPROXIMATELY 17:54 HOURS. SERVICE RESTORATION TO THE IMPACTED CUSTOMERS BEGAN IMMEDIATELY FOLLOWING PIPELINE REPAIRS.
2025-03-31 10:13 | NO | YES | YES | 20210009 | 35724 | 2021-01-15 18:08 | SUPPLEMENTAL FINAL | 5330 | FLORIDA PUBLIC UTILITIES CO | 208 WILDLIGHT AVE | YULEE | FL | 32097 | 2020-12-18 13:05 | EASTERN | YES | 2020 | 3040 S. OCEAN BLVD. | MANALAPAN | PALM BEACH | FL | 33462-6211 | 26.5479 | -80.043 | [7 empty] | YES | PLUG IN RISER. | 2020-12-18 13:05 | 1294572 | 1294661 | NATURAL GAS |  | 63 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2020-12-18 10:45 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 62 | NO | 0 | 2020-12-18 10:52 |  |  |  | 2020-12-18 11:15 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2002 | 2002 | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | 1.25" ANODELESS SERVICE RISER | [9 empty] | OTHER | [8 empty] | 1.25" ANODELESS SERVICE RISER BROKEN OFF UNDER SERVICE REGULATOR AT METER SET. | CLASS 3 LOCATION | 40000 | 44656.30761127204 | 6500 | 7256.6499868317065 | 3600 | 4019.0676850144836 | 0 | 0 |  | 36.8 | 2318 | 2885.673469387755102040816326530612244898 | 0 | 0 | 52418 | 25834.784304933067253644314868804664723 | 58817.6987525059852020408163265306122449 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 20 | 20 | 60 | 192.619(A)(2) | 2002-06-07 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | NO | [5 empty] | UNKNOWN | 35 | LARGE TRUCK | ROADWAY | 50 | YES |  |  |  |  | YES | YES | METER SET WAS BEHIND SEVERAL TREES AND NEXT TO A WALL | [135 empty] | MICHAEL MCCARTY | DIRECTOR MEASUREMENT AND COMPLIANCE | mmccarty@fpuc.com | 8638457005 | 8632940629 | MATTHEW PORTILLA | mportilla@fpuc.com | 5612150159 | MICHAEL MCCARTY | DIRECTOR MEASUREMENT AND COMPLIANCE | 8638457005 | mmccarty@fpuc.com | AT APPROXIMATELY 10:45 AM ON FRIDAY, 12/18/20, A 2008 HINO BOX TRUCK WAS HEADING NORTH ON SOUTH OCEAN BLVD. IN MANALAPAN, FL. FOR UNKNOWN REASONS THE DRIVER VEERED LEFT AND CROSSED OVER THE SOUTH BOUND LANE AND LEFT THE ROADWAY AND TRAVELLED IN THE LANDSCAPED SHOULDER FOR APPROXIMATELY 100', STRIKING MULTIPLE TREES, A POWER UTILITY BOX AND A GAS METER SET. THE GAS METER SET RISER WAS SNAPPED OFF UNDER THE SERVICE REGULATOR AND THE ESCAPING GAS IGNITED. ACCORDING TO THE FIRST BYSTANDER ON THE SCENE, THE DRIVER WAS UNRESPONSIVE AND COULD NOT BE REMOVED FROM THE TRUCK WHICH WAS ENGULFED IN FLAMES. THE DRIVER WAS PRONOUNCED DECEASED AT THE SCENE. ONE PASSENGER IN THE TRUCK WAS EJECTED THROUGH THE WINDSHIELD AND WAS TAKEN TO ST. MARY'S HOSPITAL FOR TREATMENT. EMERGENCY RESPONDERS FROM PALM BEACH COUNTY FIRE DEPARTMENT AND FLORIDA PUBLIC UTILITIES EXTINGUISHED THE FLAMES AND PLUGGED THE BROKEN RISER AT 12:10 PM ON 12/18/20. AS OF 1/15/2021, THE PALM BEACH SHERIFF'S OFFICE VEHICLE HOMICIDE REPORT IS INCOMPLETE AND A DETERMINATION OF THE DRIVERS CONDITION AT THE TIME OF THE CRASH IS NOT AVAILABLE. THERE DID NOT APPEAR TO BE BRAKING OR SKID MARKS AT THE SCENE OF THE CRASH AND A MEDICAL EMERGENCY MAY HAVE OCCURRED. UPDATE 9/9/2021 - OBTAINED PBSO VEHICLE HOMICIDE INVESTIGATION REPORT ON 9/3/2021. ACCORDING TO THE REPORT, IMPAIRMENT IS UNKNOWN DUE TO NEGATIVE BLOOD, TISSUE, AND/OR URINE VOLATILE. IT IS UNKNOWN IF THE DRIVER WAS DISTRACTED OR USING A MOBILE DEVICE WHILE OPERATING THE VEHICLE. NO CITATIONS WERE ISSUED TO THE DRIVER DUE TO BEING DECEASED. REPORT STATES THAT ACTIONS OF THE DRIVER CAUSED HIS OWN DEATH. THE SERVICE WAS REPAIRED BY INSTALLING APPROX. 7' OF 1 1/4" PE PIPE, AN EFV, NEW RISER AND METER SET. THE METER WAS MOVED NEXT TO A WALL AND CRASH POSTS WERE INSTALLED ON 12/22/2020.
2025-03-31 10:13 | NO | YES | YES | 20210011 | 35698 | 2021-01-20 15:13 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2020-12-21 16:32 | EASTERN | NO | 2020 | 2333 DUNWOODY CROSSING | DUNWOODY | DEKALB | GA | 30338 | 33.9197 | -84.2911 | [5 empty] | YES |  |  |  | 2020-12-21 17:45 | 1294766 | 1294874 | NATURAL GAS |  | 269 | 0 | NO | [5 empty] | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2020-12-21 16:32 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 82 | YES | 12 | 2020-12-21 14:17 |  |  |  | 2020-12-21 14:43 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1981 | UNKNOWN |  |  |  |  | 1.25 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 1.2 | 1.2 | [7 empty] | CLASS 3 LOCATION | 2000000 | 2232815.380563602 | 3800 | 4242.3492230708438 | 75000 | 83730.576771135075 | 0 | 0 |  | 2.75 | 740 | 921.224489795918367346938775510204081633 | 0 | 0 | 2079540 | 962053.0995904131707988338192419825072886 | 2321709.53104760383716734693877551020408 | 0 | 0 | 380 | 1 | 0 | 20 | 0 | 60 | 60 | 60 | 192.619(A)(2) | 1981-08-14 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 13.8 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 3 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES |  |  | YES | PRIVATE BUSINESS | [10 empty] | CONTRACTOR | BORING | ELECTRIC | NO | [5 empty] | YES | 24 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 | RICK SLAGLE | rslagle@southernco.com | (404) 584-4910 | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A 1.25-INCH PLASTIC ATLANTA GAS LIGHT COMPANY (AGLC) NATURAL GAS MAIN WAS RUPTURED BY BORING WHILE A NON-AGLC CONTRACTOR WAS REPLACING UNDERGROUND ELECTRIC FACILITIES NEAR 2333 DUNWOODY CROSSING IN DUNWOODY, GA. WHEN AGLC'S FIRST RESPONDER ARRIVED AT THE SCENE OF THE DAMAGED GAS LINE, THE DEKALB COUNTY FIRE RESCUE DEPARTMENT (FIRE DEPARTMENT) WAS ALREADY ONSITE. THE FIRE DEPARTMENT HAD EVACUATED THE SIX APARTMENT UNITS IN THE TWO-STORY 2333 BUILDING. AGLC'S FIRST RESPONDER CONSULTED WITH THE FIRE DEPARTMENT, AND TOOK APPROPRIATE STEPS TO HAVE ADDITIONAL RESOURCES DISPATCHED TO THE SCENE TO PERFORM THE REPAIR. AGLC'S FIRST RESPONDER CONTINUALLY MONITORED GAS READINGS USING A COMBUSTIBLE GAS INDICATOR (CGI) AROUND THE 2333 BUILDING WALLS, DOORS, AND WINDOWS AND IN NEARBY PRE-EXISTING EXCAVATION HOLES. AGLC'S FIRST RESPONDER COULD NOT TAKE READINGS INSIDE THE 2333 BUILDING DUE TO THE DOORS TO THE APARTMENT UNITS BEING LOCKED. TWO ADDITIONAL AGLC CREWS RESPONDED TO THE DAMAGE SITE TO SHUT OFF THE FLOW OF GAS AND REPAIR THE DAMAGE. AGLC WAS IN THE PROCESS OF EXPOSING THE APPLICABLE FACILITIES TO IMPLEMENT THE SHUT OFF OF GAS BY SQUEEZE TO FACILITIES IN THE AREA OF THE DAMAGE WHEN THE SIDE OF THE 2333 BUILDING NEAREST THE CUT LINE EXPLODED AND CAUGHT FIRE. FOLLOWING THE EXPLOSION, AGLC SQUEEZED OFF GAS FACILITIES FARTHER UPSTREAM, STOPPING THE FLOW OF GAS TO THE DAMAGED GAS LINE. AGLC BELIEVES THAT GAS FROM THE DAMAGED 1.25-INCH MAIN ACCUMULATED WITHIN ONE OF THE APARTMENTS NEAREST THE CUT LINE AND WAS THEN IGNITED BY AN UNKNOWN IGNITION SOURCE, CAUSING THE EXPLOSION AND ENSUING FIRE. TWO AGLC EMPLOYEES, WHO WERE IN THE PROCESS OF EXPOSING FACILITIES TO IMPLEMENT FACILITY SHUTDOWN, SUFFERED BURN INJURIES FROM THE EXPLOSION AND FIRE. NO OTHER INJURIES WERE REPORTED. THE CONTRACTOR THAT DAMAGED THE GAS MAIN DID NOT SUBMIT A LOCATE REQUEST TO THE ONE-CALL CENTER REQUESTING THE LOCATION OF UNDERGROUND UTILITY FACILITIES IN THE AREA OF THE DAMAGED GAS MAIN PRIOR TO EXCAVATION.
2025-03-31 10:13 | NO | YES | YES | 20210012 | 36934 | 2021-01-22 16:56 | SUPPLEMENTAL FINAL | 7210 | HEMPSTEAD, CITY OF | 1125 AUSTIN ST. | HEMPSTEAD | TX | 77445 | 2020-12-24 23:40 | CENTRAL | NO | 2020 | 1337 5TH | HEMPSTEAD | TX | TX | 77445 | 30.0921 | -96.0729 | [5 empty] | YES |  |  |  | 2020-12-30 11:12 | 1295221 | 1295391 | NATURAL GAS |  | 9 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2020-12-24 22:30 | OPERATOR/CONTRACTOR |  | 9 | YES | 3 | 2020-12-24 22:30 | YES | OPERATOR | 2020-12-25 00:30 | 2020-12-24 22:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | IN OTHER ENCLOSED SPACE |  |  |  | NO | [11 empty] | MUNICIPALLY OWNED |  | SERVICE RISER |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | STEEL RISER WAS INTENTIONALLY CUT BY A PERSON WITH A POWER-TOOL. | CLASS 3 LOCATION | 120000 | 133968.92283381612 | 0 | 0 | 1000 | 1116.407690281801 | 0 | 0 |  | 10.18 | 92 | 114.530612244897959183673469387755102041 | 0 | 0 | 121092 | 56054.2400334978492128279883381924198251 | 135199.861136342818959183673469387755102 | 0 | 0 | 1 | 0 | 0 | 4 | 0 | 19 | 19 | 25 | 192.619(A)(2) | 1978-01-05 | PRESSURE DID NOT EXCEED MAOP | BY-PASS |  | 0.8 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | OTHER | THE ANALYTICAL DATA IS CONSISTENT WITH VANDALISM. THE EVIDENCE SHOWS A PERSON CUT THROUGH THE CUSTOMER-SIDE PIPE WITH THE INTENT TO REMOVE THE GAS METER ENTIRELY, BUT CAUSED A LEAK WHEN THEY CUT THROUGH THE PIPE UPSTREAM OF THE LOCKED RISER VALVE BENEATH THE REGULATOR. THE RISER WAS FOUND WRAPPED IN PAINTERS TAPE, MEANWHILE THE PIPE ON THE CUSTOMER-SIDE OF THE METER WAS CUT THROUGH INTENTIONALLY. METALLURGY TESTS REVEAL THE CORROSION OCCURRED AFTER THE EXPLOSION. THIS IS VANDALISM! | [155 empty] | ROOSTER SMITH | CHIEF STAFF | rooster_smith@yahoo.com | 979 8262486 |  | ROOSTER SMITH | rooster_smith@yahoo.com | 979 826-2486 | ROOSTER SMITH | CHIEF STAFF | 979 826-2486 | rooster_smith@yahoo.com | ON DECEMBER 22, 2020 WE RECEIVED A LEAK CALL BY A NON-CUSTOMER OCCUPANT OF A RESIDENCE. WE FOUND THE OCCUPANT HAD ENCLOSED HIS FRONT PORCH ENTIRELY. WE DETECTED GAS AND PULLED THE ELECTRIC METER. WE TOLD THE OCCUPANT HE COULD NOT STAY THERE AND MUST LEAVE THE DOOR TO THE ENCLOSURE OPEN TO VENT ANY GAS. WE CALLED THE 811 NUMBER TO GET A LOCATE FOR 1335 5TH ST.. WE HAD A CREW THERE WAITING ON THE UTILITY LOCATE FROM THE TELEPHONE COMPANY. WE COULD NOT GET TO THE LOCATE WIRE BECAUSE THE CUSTOMER'S ENCLOSURE CONTAINED A CONCRETE FLOOR CONSTRUCTED AROUND THE RISER. WE TRIED TO DIG OUTSIDE THE CONCRETE PUT COULD NOT BECAUSE OF THE EXCESSIVE TREE ROOTS ON THE PROPERTY. WE WENT OUT TO THE ROAD AND DUG BEHIND THE CURB, IN LINE WITH THE METER, AND COULD NOT FIND THE PIPE TO SQUEEZE OFF. WE WENT SOUTH A FEW FEET FOUND THE 1" PLASTIC PIPE, WHICH WE SQUEEZED OFF AND CAPED, AND CHECK FOR LEAKS. WE TRIED TO VERIFY THE GAS WAS OFF AND RETRIEVE THE GAS METER INSIDE THE ENCLOSURE BUT THE CUSTOMER HAD ALREADY LEFT AND LOCKED THE DOOR SO WE COULD NOT GET IN. WE WERE CALLED ON DECEMBER 24, 2020 STATING THE HOUSE BLEW UP. BECAUSE THE EXPLOSION BLEW AWAY THE CONCRETE EXTERIOR WALL DOWN, WE WERE ABLE TO DIG NEXT TO THE CONCRETE AND SQUEEZE OFF THE SERVICE LINE. THIS STOPPED THE GAS FLOW. I WENT TO CALL THE TEXAS RAILROAD COMMISSION TO INFORM THEM OF THE ACCIDENT."
2025-03-31 10:13 | NO | YES | YES | 20210013 | 36706 | 2021-01-24 16:20 | SUPPLEMENTAL FINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2020-12-25 01:30 | EASTERN | NO | 2020 | 117 LOWER SWIFTWATER ROAD | SWIFTWATER | MONROE | PA | 18370 | 41.0954 | -75.3265 | YES | [8 empty] | 2020-12-25 04:58 | 1294953 | 1295037 | NATURAL GAS |  | 975 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 0 | 0 | 0 | 0 | 2 | 2 | NO | [5 empty] | 2 | 2020-12-25 01:44 |  |  |  | 2020-12-25 02:07 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2019 | 2017 |  |  |  |  | 12 | ASTM D2513 | CHARTER PLASTICS, INC. | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 4710 | RUPTURE |  |  |  |  | CIRCUMFERENTIAL |  | 12 | 1.5 |  | CLASS 3 LOCATION | 40000 | 44656.30761127204 | 39310 | 43885.98630497759731 | 4615 | 5152.221490650511615 | 0 | 0 |  | 2.2207 | 2165 | 2695.204081632653061224489795918367346939 | 0 | 0 | 86090 | 41298.6798308623063236151603498542274052 | 96389.7194885328019862244897959183673469 | 5 | 0 | 0 | 0 | 0 | 0 | 5 | 95 | 94 | 100 | 192.619(A)(2) | 2019-09-17 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 5.2 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE PRESSURE AND FLOW RATES WERE WITHIN NORMAL RANGES LEADING UP TO THE INCIDENT AND AT THE TIME THE INCIDENT OCCURRED. ACTIONS BY THE CONTROL ROOM DID NOT IMPACT THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 2019 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [13 empty] | YES | INADEQUATE INTERFACIAL PRESSURE BEING APPLIED DURING THE JOINING PHASE OF THE FUSION PROCESS AND/OR EXCESSIVE DWELL TIME BETWEEN HEAT SOAK AND JOINING PHASES. | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [85 empty] | YES | ROMAN HIGH | SENIOR ENGINEER STANDARDS | rhigh@ugi.com | 484-332-8402 |  |  |  |  | TIM ANGSTADT | VP OPERATIONS | 484-256-0345 | tangstadt@ugi.com | AT APPROXIMATELY 1:44 AM DECEMBER 25, 2020, UGI EMPLOYEES RESPONDED TO A CALL FROM MONROE COUNTY 911 REPORTING AN INCIDENT INVOLVING THE RELEASE OF NATURAL GAS. IT WAS DISCOVERED THAT THE 12-INCH HDPE, 100 PSIG MAOP DISTRIBUTION PIPELINE HAD SEPARATED AT THE BUTT FUSION INTERFACE FROM AN UNKNOWN CAUSE. THERE WAS ONE CONFIRMED FATALITY AND TWO INJURIES REQUIRING HOSPITALIZATION FROM AN OVERTURNED VEHICLE. IN RESPONSE TO THE INCIDENT, THE PIPELINE WAS REPAIRED AND PLACED BACK IN OPERATION. THE PIPELINE OPERATING PRESSURE HAS BEEN LOWERED FROM 94 PSIG TO 60 PSIG AS A PRECAUTIONARY MEASURE. UGI IS FILING THIS SUPPLEMENTAL AND FINAL REPORT AFTER A THIRD-PARTY LAB COMPLETED TESTING ON THE FAILED BUTT FUSION JOINT AND A ROOT CAUSE ANALYSIS. THE ROOT CAUSE WAS DETERMINED TO BE A COMBINATION OF THE FOLLOWING FACTORS: 1) INADEQUATE INTERFACIAL PRESSURE APPLIED DURING THE JOINING PHASE OF THE FUSION PROCESS AND/OR EXCESSIVE DWELL TIME BETWEEN HEAT SOAK AND JOINING PHASES; AND 2) THE FAILURE TO FOLLOW APPROPRIATE INSTALLATION AND INSPECTION PROCEDURES.
2025-03-31 10:13 | NO | NO | NO | 20210015 | 35786 | 2021-02-02 09:34 | SUPPLEMENTAL FINAL | 15350 | PEOPLES NATURAL GAS COMPANY LLC | 375 NORTH SHORE DRIVE SUITE 600 | PITTSBURGH | PA | 15212 | 2021-01-05 14:55 | EASTERN | YES | 2021 | 80 26TH ST | PITTSBURGH | ALLEGHENY | PA | 15222 | 40.4553 | -79.979 | YES | [8 empty] | 2021-01-05 17:35 | 1295533 | 1295657 | NATURAL GAS |  | 918.2 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-01-05 14:55 |  |  |  | 2021-01-05 15:35 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [11 empty] | OTHER | PUBLIC UTILITY | MAIN |  | 2019 | 2018 |  |  |  |  | 8 | SDR 13.5 | DURALINE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.945 |  | 2708 | OTHER | [8 empty] | FUSION FAILURE | CLASS 3 LOCATION | 5000 | 5415.637509581805 | 0 | 0 | 46573 | 50444.497146750680853 | 0 | 0 |  | 1.8812 | 1727 | 1224.965116279069767441860465116279069767 | 0 | 0 | 53300 | 24268.7569056216527189169435215946843854 | 57085.0997726115556204418604651162790698 | 45 | 0 | 32 | 0 | 0 | 32 | 39 | 43 | 43 | 50 | 192.619(A)(1) | 2019-05-24 | PRESSURE DID NOT EXCEED MAOP | OTHER | SCENTINEL T50 | 0.5 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | NO OVERPRESSURIZATION OCCURRED. | [12 empty] | NO |  |  | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 2019 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [13 empty] | YES | COLD FUSION | YES |  |  |  | POOR WORKMANSHIP |  |  | NO | [86 empty] | WAYNE DADIG | MANAGER COMPLIANCE | wayne.dadig@peoples-gas.com | 412-352-1576 |  | WAYNE DADIG | wayne.dadig@peoples-gas.com | 412-352-1576 | EDWARD A. PALOMBO | VICE PRESIDENT RELIABILITY | 412 258-4453 | edward.a.palombo@peoples-gas.com | PEOPLES GAS HAS COMPLETED ITS INVESTIGATION FOR GD REPORT # 20210015. THE INVESTIGATION FOUND THAT THE FRACTURE IN THE FUSION APPEARS TO HAVE BEEN CAUSED BY INSUFFICIENT MIXING ACROSS THE FUSION LINE OF THE WELD. A LACK OF FUSION OCCURRED IN THE WELD. PEOPLES GAS CONSIDERS THE REPORT CLOSED AND WOULD LIKE THE REPORT STATUS UPDATED TO REFLECT CLOSED.
2025-03-31 10:13 | NO | NO | NO | 20210016 | 34824 | 2021-02-08 17:50 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2021-01-09 11:46 | PACIFIC | NO | 2021 | ALAMEDA ST. & TEMPLE ST. | LOS ANGELES | LOS ANGELES | CA | 90012 | 34.051 | -118.2381 | YES | [8 empty] | 2021-01-09 11:46 | 1295764 | 1295820 | NATURAL GAS |  | 3289.24 | 21.778 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 3 | 2021-01-09 08:25 |  |  |  | 2021-01-09 08:30 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 120 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2006 | UNKNOWN |  |  |  |  | 6 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.219 | [6 empty] | MECHANICAL PUNCTURE | 4 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 5000 | 5415.637509581805 | 50000 | 54156.37509581805 | 0 | 0 |  | 4.1 | 13486 | 9565.651162790697674418604651162790697674 | 89 | 63.12790697674418604651162790697674418605 | 68575 | 33580.125361448849800664451827242524917 | 69200.7916751672968604651162790697674419 | 21 | 0 | 160 | 0 | 0 | 1 | 21 | 196 | 196 | 204 | 192.619(A)(2) | 2006-06-08 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | AUGER | SITE DEVELOPMENT | YES | A201560744 | DIG ALERT |  | UTILITY OWNER | YES | YES | 25 | EXCAVATION ISSUE | EXCAVATOR FAILED TO PROTECT/SHORE/SUPPORT FACILITIES | [170 empty] | EDWIN BAIRES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | ebaires2@socalgas.com | 213-326-1831 |  |  |  |  | EDWIN BAIRES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 213-326-1831 | ebaires2@socalgas.com | ON 01-09-21, SOCALGAS, WHICH HAD AN EMPLOYEE PRESENT AS STAND-BY, WAS NOTIFIED OF A THIRD PARTY DAMAGE AT ALAMEDA AND TEMPLE ST., LOS ANGELES, CA. THE THIRD PARTY CONTRACTOR DAMAGED A 6 INCH HIGH PRESSURE STEEL GAS MAIN WITH AN AUGER. GAS WAS CONTROLLED AT 14:33 ON 1/9/21. THERE WERE NO REPORTED FATALITIES OR INJURIES DUE TO THE GAS RELEASE. THE INVESTIGATION SHOWED THE THIRD PARTY CONTRACTOR HAD A VALID USA TICKET A201560744. THE THIRD PARTY CONTRACTOR DID NOT PROPERLY EXPOSE THE MAIN BEFORE USING THE AUGER EQUIPMENT. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO THE RELEASE OF GAS AND DAMAGES EXCEEDING $50,000.
2025-03-31 10:13 | NO | YES | NO | 20210017 | 35815 | 2021-02-09 12:28 | SUPPLEMENTAL FINAL | 18408 | DOMINION ENERGY SOUTH CAROLINA, INC. | 601 TAYLOR ROAD MAIL CODE J48 | CAYCE | SC | 29033 | 2021-01-04 15:53 | EASTERN | NO | 2021 | REMOUNT RD AND NORTH RHETT AVE | NORTH CHARLESTON | CHARLESTON | SC | 29406 | 32.9023 | -79.9856 | YES | [8 empty] | 2021-02-08 13:05 | 1297575 | N/A | NATURAL GAS |  | 367.18 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-01-04 15:53 | YES | OPERATOR | 2021-01-06 15:35 | 2021-01-04 16:22 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 108 | NO | YES |  |  |  |  | YES | UNCASED, BORED/DRILLED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1999 | UNKNOWN |  |  |  |  | 8 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 12 | 0.1 | [7 empty] | CLASS 3 LOCATION | 104315 | 112986.445362405197715 | 207756 | 225026.237288135495916 | 0 | 0 | 55250 | 59842.79448087894525 | CONTRACT LABOR: $55,250 | 4.22 | 1549 | 1098.709302325581395348837209302325581395 | 0 | 0 | 368870 | 165796.1768367996762456411960132890365449 | 398954.1864337452202763488372093023255814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 49 | 60 | 192.621 M | 1999-03-02 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE LEAK DID NOT CAUSE ENOUGH PRESSURE DROP TO EXCEED AN ALARM THRESHOLD | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [12 empty] | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 2012171410 | N/A |  | CONTRACT LOCATOR | YES | NO |  | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | JERAMY FREE | ENGINEER III - PIPELINE COMPLIANCE | jeramy.free@dominionenergy.com | 803-260-3602 |  | CINDY OSTRANDER | cynthia.ostrander@dominionenergy.com | 803-217-9245 | CINDY OSTRANDER | DIRECTOR - GAS OPERATIONS | 803-217-9245 | cynthia.ostrander@dominionenergy.com | NOTE: THIS IS AN UPDATED SUPPLEMENTAL/FINAL REPORT, WHICH CORRECTS A NOTE WITHIN THE PREVIOUS REPORT'S PART H NARRATIVE. PART E.3.A MAOP HAS BEEN CONFIRMED. ON JANUARY 4, 2021 AT 3:53 PM, AN 8-INCH STEEL MAIN WAS DAMAGED BY A BORING CONTRACTOR INSTALLING TELECOMMUNICATIONS IN CHARLESTON, SC. THE DAMAGE OCCURRED AT THE INTERSECTION OF REMOUNT RD AND N. RHETT ST UNDERNEATH THE ROADWAY. THE LEAK WAS SECURED AT APPROXIMATELY 5:15 PM BY OPERATING FOUR VALVES AND NO CUSTOMER SERVICES WERE LOST. THE INVESTIGATION THAT FOLLOWED DETERMINED THAT THE LINE WAS LOCATED CORRECTLY, BUT THE EXCAVATOR FAILED TO POTHOLE TO VERIFY THAT HE WAS CLEAR OF THE MAIN WHEN CROSSING IT. WHEN THE DAMAGES WERE ASSESSED, IT WAS DETERMINED THAT THE COST OF DAMAGE TO THE ROAD AND SURROUNDINGS EXCEEDED THE $50,000 PHMSA REPORTING THRESHOLD. LDF: 289025
2025-03-31 10:13 | NO | YES | NO | 20210018 | 34862 | 2021-02-13 04:34 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2021-01-14 09:30 | EASTERN | YES | 2021 | 820 S 15TH ST | TOLEDO | LUCAS | OH | 43604 | 41.6513 | -83.5481 | YES | [5 empty] | YES |  |  | 2021-01-14 09:56 | 1296041 | 1296109 | NATURAL GAS |  | 40395.7 | 101.7 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-01-14 09:30 |  |  |  | 2021-01-13 21:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 1 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1965 | UNKNOWN |  |  |  |  | 16 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.241 | [6 empty] | MECHANICAL PUNCTURE | 3 | 10 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 35987 | 38978.509411464083307 | 278911 | 302096.174686994162871 | 0 | 0 | 0 | 2.45 | 98969 | 70198.9418604651162790697674418604651163 | 249 | 176.616279069767441860465116279069767442 | 414116 | 206364.4164912066137881860465116279069767 | 411450.2422379931298989302325581395348837 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 48 | 48 | 58 | 192.619(A)(3) | 1971-04-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE RELEASE OF GAS WAS INSUFFICIENT TO CAUSE A PRESSURE ALERT FOR THE CONTROLLER TO ACT ON. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | STATE HIGHWAY | [7 empty] | YES |  |  |  |  | CONTRACTOR | UNKNOWN/OTHER | ROAD WORK | YES | B100400793 | OHIO UTILITIES PROTECTION SERVICE |  | CONTRACT LOCATOR | YES | YES | 65 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | ROB SMITH | MANAGER OPERATIONS COMPLIANCE | rrsmith@nisource.com | 6144605491 |  | ROB SMITH | rrsmith@nisource.com | 6144605491 | ROB SMITH | MANAGER OPERATIONS COMPLIANCE | 6144605491 | rrsmith@nisource.com | ON JANUARY 13, 2021 A THIRD PARTY EXCAVATOR OPERATING A BULL DOZER DAMAGED A PROPERLY LOCATED AND MARKED 16" STEEL MAIN LINE. COLUMBIA GAS OF OHIO INC. (COLUMBIA) TOOK IMMEDIATE ACTION TO REPAIR THE LEAK AND SET UP A PERIMETER AND BEGAN MONITORING THE LEAK. COLUMBIA MONITORED THE LEAK AS IT REMAINED NON-HAZARDOUS AND WELDED A 16INCH STOPPLE FITTING ON THE MAIN LINE AND UTILIZED ANOTHER TWO CRITICAL VALVES TO SHUT THE LINE DOWN FOR PERMANENT REPAIRS. THE PERMANENT REPAIRS WERE MADE AND THE LINE WAS PLACED BACK IN SERVICE ON JANUARY 16, 2021 AT 10:30 AM. PLEASE CONSIDER THIS A FINAL REPORT.
2025-03-31 10:13 | NO | NO | NO | 20210019 | 34936 | 2021-02-16 19:15 | SUPPLEMENTAL FINAL | 13480 | NIAGARA MOHAWK POWER CORP | 300 ERIE BOULEVARD WEST | SYRACUSE | NY | 13202 | 2021-01-17 04:14 | EASTERN | YES | 2021 | SOUTH PARK ST BRIDGE BET SPRING ST AND GRANGE AVENUE | ADAMS | NEW YORK | NY | 13605 | 43.8077 | -76.0193 | [6 empty] | YES |  |  | 2021-01-17 12:30 | 1296212 | 1296291 | NATURAL GAS |  | 22.4 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-01-17 03:45 | ALLOWED TO BURN OUT |  | 22.4 | NO | 18 | 2021-01-17 03:45 |  |  |  | 2021-01-17 04:25 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | OVERHEAD CROSSING |  |  |  | YES | YES | UNCASED | [9 empty] | INVESTOR OWNED |  | MAIN |  | 1955 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.28 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 12100 | 13105.8427731879681 | 39070 | 42317.79149987222427 | 0 | 0 |  | 2.3 | 52 | 36.88372093023255813953488372093023255814 | 0 | 0 | 51222 | 22988.9266876077699144850498338870431894 | 55460.5179939904249281395348837209302326 | 0 | 0 | 17 | 0 | 0 | 18 | 0 | 20 | 21 | 24 | 192.619(C) | 1955-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE INCIDENT WAS DUE TO INCLEMENT WEATHER WITH WINDS BLOWING DOWN A POWER LINE AND NOT INVOLVING THE CONTROL ROOM OPERATOR. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | CORINNE BYRNES | PRIN PROGRAM MANAGER REGULATORY MOC | corinne.byrnes@nationalgrid.com | 5169030596 |  | CORINNE BYRNES | corinne.byrnes@nationalgrid.com | 5169030596 | CORINNE BYRNES | PRIN. PROGRAM MGR REGULATORY MANAGEMENT OF CHANGE | 5164924469 | corinne.byrnes@nationalgrid.com | ON JANUARY 17, NATIONAL GRID RECEIVED NOTIFICATION OF A GAS RELATED FIRE WITH MAIN BLOWING GAS. THE CAUSE OF THE FIRE WAS A PRIMARY ELECTRICAL WIRE MAKING CONTACT ABOVE THE 6" STEEL MAIN RESULTING IN THE FIRE OCCURRING. APPROX. 17 HOUSES WERE EVACUATED (18 RESIDENTS), A 2" BYPASS WAS RUN TO AVOID CUSTOMER INTERRUPTIONS, AND TEMPORARY REPAIRS WERE MADE. TEMPORARY REPAIRS WERE COMPLETED WITH A MADE SAFE TIME OF 16:25. ADDITIONALLY, THE SOUTH PARK STREET BRIDGE WAS CLOSED AS A RESULT OF THIS INCIDENT. FOR PART E, QUESTION 5, ODORANT IS INJECTED AT EITHER BIDDLECUM GATE STATION OR CROGHAM GATE STATION. THE DAMAGED PIPELINE SEGMENT WAS REPLACED WITH A 5'6" SEGMENT OF 6" APIX62 SMAW 6010/7010 PIPE WITH COLD APPLIED TAPE COATING EARLY FEBRUARY, 2021. THE SEGMENT WAS AIR TESTED AT 90 PSI FOR 1 HOUR.
2025-03-31 10:13 | NO | YES | NO | 20210020 | 39030 | 2021-02-17 16:53 | SUPPLEMENTAL FINAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDENCE BLVD | VIRGINIA BEACH | VA | 23452 | 2020-12-23 13:30 | EASTERN | YES | 2020 | INTERSECTION OF TABBS LANE AND OLD COURTHOUSE WAY | CITY OF NEWPORT NEWS | CITY OF NEWPORT NEWS | VA | 23602 | 37.1242 | -76.532 | [6 empty] | YES |  |  | 2021-01-18 01:30 | 1296252 | 1296358 | NATURAL GAS |  | 4442.76 | 6.916 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2020-12-23 13:42 | NO |  |  | 2020-12-23 14:11 | 2021-01-18 01:00 | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 52 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1960 | UNKNOWN |  |  |  |  | 16 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.25 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 337225 | 376480.583355280342225 | 272814 | 304571.647616539258014 | 0 | 0 |  | 2.4 | 10663 | 13274.3469387755102040816326530612244898 | 17 | 21.16326530612244897959183673469387755102 | 620719 | 294370.5337570219765204664723032069970845 | 694347.7411759012328920612244897959183674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 150 | 150 | 192.619(A)(4) | 1960-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS LEAK WAS A PINHOLE LEAK WHICH COULD NOT BE IDENTIFIED VIA SCADA MEASUREMENT. | [12 empty] | NO |  |  | NO |  |  | NATURAL FORCE DAMAGE | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | NATURAL FORCE DAMAGE | EARTH MOVEMENT | NATURAL FORCE DAMAGE | EARTH MOVEMENT | [56 empty] | EARTH MOVEMENT, NOT DUE TO HEAVY RAINS/FLOODS | OTHER |  |  |  | THE APPARENT CAUSE WAS PIPE STRESS CREATED BY GROUND SETTLEMENT WHICH CAUSED MISALIGNMENT OF FLANGE RESULTING IN A PINHOLE LEAK ON GASKET. | NO | [218 empty] | JONATHAN HEATH | DIRECTOR - COMPLIANCE AND SYSTEM INTEGRITY | jbheath@southernco.com | 7572985729 |  | JONATHAN HEATH | jbheath@southernco.com | 7572985729 | JONATHAN HEATH | DIRECTOR - COMPLIANCE AND SYSTEM INTEGRITY | 7572985729 | jbheath@southernco.com | THE COMPANY WAS MADE AWARE OF A LEAK VIA A CUSTOMER LEAK CALL ON DECEMBER 23, 2020. LEAK WAS IMMEDIATELY INVESTIGATED AND GRADED AS A GRADE 2. ON JANUARY 8, A SUBSEQUENT LEAK INVESTIGATION CONCLUDED THE LEAK WAS ON A 150 LBS. MAIN. THE LEAK WAS STILL A GRADE 2. ON JANUARY 12, 2021, THE LEAK WAS UPGRADED TO GRADE 1 DUE TO MIGRATION AND THE COMPANY BEGAN MONITORING THE AREA 24 HOURS A DAY. STOPPLE FITTINGS WERE USED TO STOP THE FLOW OF GAS ON JANUARY 20, 2021. THE SEGMENT OF MAIN WAS PURGED AND REPLACED COMMENCING ON JANUARY 21 BEFORE BEING COMPLETED ON JANUARY 22. THE ABANDONED SEGMENT OF PIPE WAS TRANSPORTED TO THE WELDING SHOP WHERE END CAPS WERE INSTALLED AND PRESSURE WAS REINTRODUCED TO IDENTIFY CAUSE OF THE LEAK. UPON INVESTIGATION, THE COMPANY CONCLUDED THE LEAK CAUSE TO BE GROUND SETTLEMENT WHICH CAUSED MISALIGNMENT OF THE FLANGE RESULTING IN A PINHOLE LEAK ON THE GASKET.
2025-03-31 10:13 | NO | NO | NO | 20210022 | 35561 | 2021-02-19 10:02 | SUPPLEMENTAL FINAL | 18440 | SOUTH JERSEY GAS CO | 101 SOUTH LINCOLN PLACE | ATLANTIC CITY | NJ | 08401 | 2021-01-29 07:45 | EASTERN | NO | 2021 | INTERSECTION OF WHEATON AVENUE AND K STREET | MILLVILLE | CUMBERLAND | NJ | 08332 | 39.4104 | -75.0322 | [7 empty] | YES | NO GAS RELEASED SO NO FLOW CONTROL WAS EMPLOYED. | 2021-01-29 15:27 | 1296978 |  | NATURAL GAS |  | 0 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-01-29 07:45 | YES | OPERATOR | 2021-01-29 09:00 | 2021-01-29 08:15 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 1994 | 1994 | [7 empty] | OTHER | TELOG WIRES & 5 - 1/2" STEEL VALVES | [9 empty] | OTHER | [8 empty] | NO GAS WAS RELEASED. TELOG WIRES DAMAGED AND VALVES WERE PARTIALLY OPERATED. | CLASS 3 LOCATION | 0 | 0 | 1500 | 1624.6912528745415 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1500 | 672.898390256367 | 1624.6912528745415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250 | 250 | 250 | 192.619(A)(2) | 1994-01-10 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | YES | NO | NO | YES | YES | SCADA-BASED INFORMATION (SUCH AS ALARM(S), ALERT(S), EVENT(S), AND/OR VOLUME OR PACK CALCULATIONS) |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | TELOG WAS DAMAGED VIA APPARENT VANDALISM. POLICE INVESTIGATION ONGOING. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | VANDALISM | [156 empty] | JEFF OGBORN | MGR EMERGENCY PREPAREDNESS COMPLIANCE STANDARDS | hjogborn@sjindustries.com | 6094027972 |  | GEORGE TENENBERG | gtenenberg@sjindustries.com | 6093388168 | RAYMOND WENZEL | DIRECTOR ENGINEERING SERVICES | 6096748815 | rwenzel@sjindustries.com | ON THE MORNING OF 1/29/21 THE TELOG AT THIS LOCATION WAS NOT FUNCTIONING. UPON INVESTIGATION, IT WAS IDENTIFIED THAT THE WIRES HAD PULLED FROM THE TELOG UNIT IN AN APPARENT ACT OF VANDALISM. IN ADDITION, IT WAS IDENTIFIED THAT THE PERPETRATOR(S) HAD CLIMBED THE WIRE FENCE TO THE STATION AND ATTEMPTED TO OPERATE FIVE 1/2" VALVES. THESE VALVES ARE 1/2 INCH IN DIAMETER AND USED FOR MAINTENANCE AND THEY DO NOT CONTROL SYSTEM FLOWS. THERE WAS NO PRESSURE IMPACT ON THE SYSTEM AS A RESULT.
2025-03-31 10:13 | NO | YES | NO | 20210023 | 35920 | 2021-02-24 22:56 | SUPPLEMENTAL FINAL | 6141 | NEW MEXICO GAS COMPANY | 7120 WYOMING BLVD N.E. SUITE 20 | ALBUQUERQUE | NM | 87109 | 2021-01-25 10:40 | MOUNTAIN | YES | 2021 | 1241 PRINCETON DRIVE N.E. | ALBUQUERQUE | BERNALILLO | NM | 87106 | 35.0954 | -106.615 | [7 empty] | YES | STOPPED FLOW AT SERVICE STOP TEE ON MAIN | 2021-01-25 12:16 | 1296674 |  | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-01-25 10:53 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 5 | 2021-01-25 10:40 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-01-25 10:53 | 2021-01-25 11:11 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | 1947 |  | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | FITTING | [9 empty] | OTHER | [8 empty] | DURING THE PLUMBER'S ATTEMPT TO TURN THE LOCKNUT SHUT-OFF VALVE, THE PLUMBER CAUSED THE THREADS OF THE BRASS CORE OF THE SHUT-OFF VALVE TO BE SHEARED OFF AT THE NUT CONNECTION. THE RESULT CAUSED HIGH PRESSURE GAS TO VENT TO ATMOSPHERE. | CLASS 3 LOCATION | 250000 | 270781.87547909025 | 1964 | 2127.262413763733004 | 0 | 0 | 0 | 0 | MORE COSTS MAY BE ADDED OR CHANGED | 0 | 0 | 0 | 0 | 0 | 251964 | 113030.780001703503192 | 272909.137892853983004 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 60 | 60 | 60 | 192.619(A)(4) | 2015-11-19 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | VALVE | MATERIAL/WELD/EQUIP FAILURE | VALVE | EQUIPMENT FAILURE | VALVE | [197 empty] | VALVE | [16 empty] | OTHER | DURING THE PLUMBER'S ATTEMPT TO TURN THE LOCKNUT SHUT-OFF VALVE, THE PLUMBER CAUSED THE THREADS OF THE BRASS CORE OF THE SHUT-OFF VALVE TO BE SHEARED OFF AT THE NUT CONNECTION. | [65 empty] | ANDREA MARTINEZ | PIPELINE SAFETY MANAGEMENT SYSTEMS MANAGER | andrea.martinez@nmgco.com | 505-427-6343 |  | ANDREA MARTINEZ | andrea.martinez@nmgco.com | 505-697-3518 | TOM BULLARD | VP ENG-GAS MGMT-TECH SERVICES | 505-697-3599 | tom.bullard@nmgco.com | A LOCAL PLUMBING COMPANY WAS PERFORMING WORK AT A RESIDENCE AT 1241 PRINCETON DR. N.E., ALBUQUERQUE, NM AND REPORTED THE LOCKNUT SHUT OFF VALVE BROKE WHILE TURNING OFF THE FLOW OF GAS TO THE NMGC METER. UPON INVESTIGATION, ONE OF THE PLUMBERS SAID THAT THEY WERE DISCONNECTING A HEATER FROM THE HOUSE PIPING AND SAID HE SMELLED GAS AND IDENTIFIED A LEAK. HE IMMEDIATELY PROCEEDED OUT OF THE HOUSE TO TURN OFF THE GAS SUPPLY. SPECIFICALLY, DURING HIS ATTEMPT TO TURN THE LOCKNUT SHUT-OFF VALVE, THE PLUMBER CAUSED THE THREADS OF THE BRASS CORE OF THE SHUT-OFF VALVE TO BE SHEARED OFF AT THE NUT CONNECTION. THE RESULT CAUSED HIGH PRESSURE GAS TO VENT TO ATMOSPHERE. AT 10:53 A.M., ALBUQUERQUE FIRE CALLED NMGC TO ADVISE THE HOUSE EXPLODED. BAR HOLE TESTING INDICATED NO GAS AROUND THE PERIMETER OF THE HOME AND SURROUNDING RESIDENCES. 5 RESIDENCES WERE EVACUATED. READINGS CONFIRMED PROPER ODORANT AT 0.33% GAS-IN-AIR. FINAL INVESTIGATION DETERMINED THE CRAWL SPACE VENT WAS IN CLOSE PROXIMITY TO THE RISER. GAS VENTING TO ATMOSPHERE FROM THE SHEARED OFF NUT CONNECTION MIGRATED ABOVE GROUND INTO THE CRAWL SPACE AND WAS IGNITED BY A HEATER IN THE CRAWL SPACE CAUSING THE EXPLOSION.
2025-03-31 10:13 | NO | YES | NO | 20210024 | 39745 | 2021-02-25 16:52 | SUPPLEMENTAL FINAL | 15007 | PACIFIC GAS & ELECTRIC CO | 6121 BOLLINGER CANYON RD. | SAN RAMON | CA | 94583 | 2021-01-27 09:54 | PACIFIC | NO | 2021 | 6709 LAKEVIEW DRIVE | CARMICHAEL | SACRAMENTO | CA | 95608 | 38.6451 | -121.3085 |  |  | YES | YES | [5 empty] | 2021-01-27 13:39 | 1296839 | 1296909 | NATURAL GAS |  | 531 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-01-27 09:54 | OPERATOR/CONTRACTOR |  | 531 | YES | 0 | 2021-01-27 09:54 | NO |  |  | 2021-01-27 10:07 | 2021-01-27 13:00 | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER A BUILDING |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | SERVICE RISER |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | SEAMLESS |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | UNKNOWN | [5 empty] | CLASS 3 LOCATION | 50000 | 54156.37509581805 | 87000 | 94232.092666723407 | 10000 | 10831.27501916361 | 0 | 0 |  | 4.04 | 2145 | 1521.453488372093023255813953488372093023 | 0 | 0 | 149145 | 67351.4757999412417475083056478405315615 | 160741.196270077160023255813953488372093 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.25 | 44 | 50 | 192.619(A)(2) | 1975-06-10 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | YES | 1 | 0 | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | NATURAL GAS SERVICE LINE WAS IN DIRECT CONTACT WITH SEWER LINE | [154 empty] | SAJJAD AZHAR |  | s1at@pge.com | [5 empty] | FRANCES YEE |  | 925-200-4736 | frances.yee@pge.com | ON WEDNESDAY, JANUARY 27, 2021, AT 11:23 HOURS, PG&E WAS NOTIFIED OF AN EXPLOSION AT 6709 LAKEVIEW DR., CARMICHAEL. GAS APPEARS TO HAVE MIGRATED THROUGH THE CRAWL SPACE INTO A PLUMBING WALL OF THE HOUSE WHERE IT IGNITED. NO FATALITIES OR INJURIES WERE REPORTED. PG&E CREWS STOPPED THE FLOW OF GAS AND MADE THE AREA SAFE AT APPROXIMATELY 13:33 HOURS. THERE WAS 1 CUSTOMER IMPACT(ED). THERE WERE NO MEDIA OR POLICE REPORTED ON SITE. THE FIRE DEPARTMENT WAS REPORTED ON SITE. THIS EVENT WAS DETERMINED TO BE A DOT REPORTABLE INCIDENT ~13:00 ONCE CONFIRMED DISCOVERY THAT A RELEASE OF GAS FROM A PG&E ASSET RESULTED ESTIMATED PROPERTY DAMAGE OF $50,000 OR MORE
2025-03-31 10:13 | NO | NO | NO | 20210025 | 34951 | 2021-03-04 13:33 | ORIGINAL FINAL | 20010 | UGI UTILITIES, INC | 1 UGI DRIVE | DENVER | PA | 17517 | 2021-02-02 14:25 | EASTERN | NO | 2021 | 908 CUMBERLAND STREET | LEBANON | LEBANON | PA | 17042 | 40.3391 | -76.4266 |  |  |  | YES | [5 empty] | 2021-02-02 15:28 | 1297221 | 1297357 | NATURAL GAS |  | 1.8 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-02-02 13:53 | ALLOWED TO BURN OUT |  | 1 | YES | 20 | 2021-02-02 13:45 | YES | OPERATOR | 2021-02-02 13:55 | 2021-02-02 13:51 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | OTHER | REG VENT PIPE EXTENDING THRU SIDEWALK |  |  | NO | [11 empty] | INVESTOR OWNED |  | INSIDE METER/REGULATOR SET |  | 2017 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | YES | NO | YES |  |  |  | OTHER | REGULATOR | [9 empty] | LEAK |  |  | CRACK | [6 empty] | CLASS 3 LOCATION | 64000 | 69320.160122647104 | 300 | 324.9382505749083 | 4864 | 5268.332169321179904 | 0 | 0 | NONE | 2.75 | 5 | 3.54651162790697674418604651162790697674 | 0 | 0 | 69169 | 31030.1769066912547587774086378737541528 | 74916.977054171099180744186046511627907 | 1 | 0 | 0 | 0 | 0 | 0 | 4 | 51 | 56 | 60 | 192.619(A)(2) | 2017-08-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.5 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 1 | 0 | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | OTHER OUTSIDE FORCE DAMAGE | [112 empty] | OTHER OUTSIDE FORCE DAMAGE | [13 empty] | REGULATOR VENT PIPE WAS STRUCK BY A SNOWBLOWER | [154 empty] | ROMAN HIGH | ENGINEER II - STANDARDS | rhigh@ugi.com | 484-332-8402 |  |  |  |  | PAMELA JOCSAK | VP ENGONEERING | 484-524-5508 | pjocsak@ugi.com | AT APPROXIMATELY 13:40 ON FEBRUARY 2, 2021, THE UGI CALL CENTER RECEIVED AN INSIDE ODOR CALL AT 912 CUMBERLAND STREET, LEBANON. UGI DISPATCHED THE CLOSEST AVAILABLE QUALIFIED PERSON TO THAT LOCATION, ARRIVING AT 13:51. AT APPROXIMATELY 13:53, THERE WAS A LOW-LEVEL EXPLOSION AT 908 CUMBERLAND STREET. THERE WERE NO INJURIES BUT THE BUILDING SUSTAINED MINOR DAMAGE. THE SITUATION WAS MADE SAFE BY CLOSING THE VALVE BELOW THE REGULATOR INSIDE THE BUILDING. ONLY ONE CUSTOMER WAS OUT OF SERVICE AT 908 CUMBERLAND STREET. UGI CONDUCTED A FULL LEAK INVESTIGATION WITH NO LEAKS FOUND. THE BASEMENT OF THE BUILDING EXTENDED UNDER THE SIDEWALK. THE REGULATOR WAS LOCATED AT THE FRONT WALL OF THE BUILDING IN THE BASEMENT, PLACING IT UNDER THE SIDEWALK. THE VENT PIPE EXTENDED FROM THE FRONT WALL OF THE BASEMENT TO THE FAÇADE OF THE BUILDING THROUGH THE SIDEWALK TO THE OUTSIDE. A CONTRACTOR OPERATING A SNOWBLOWER STRUCK THE ABOVE GROUND VENT PIPE AT THE FRONT WALL OF THE BUILDING. THE FORCE OF THE CONTACT DROVE THE PIPE DOWN THROUGH THE CONCRETE SIDEWALK, WHICH CRACKED THE REGULATOR BODY AND ALLOWED GAS TO LEAK INTO THE STRUCTURE.
2025-03-31 10:13 | NO | YES | YES | 20210026 | 36155 | 2021-03-05 10:08 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-02-03 12:25 | EASTERN | NO | 2021 | 8530 HOOES ROAD | SPRINGFIELD | FAIRFAX COUNTY | VA | 22153-1703 | 38.7555 | -77.2407 | YES |  |  |  |  | YES |  |  |  | 2021-02-03 14:25 | 1297272 | 1297426 | NATURAL GAS |  | 800 | 0 | NO | [5 empty] | 0 | YES | 3 | 0 | 0 | 0 | 0 | 3 | YES | 2021-02-03 12:25 | OPERATOR/CONTRACTOR |  | 800 | NO | 6 | 2021-02-03 12:30 | YES | OPERATOR | 2021-02-03 12:27 | 2021-02-03 12:25 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 54 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1988 | 1988 |  |  |  |  | 6 | ASTM D2513 | DUPONT | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 59000 | 63904.522613065299 | 272353 | 294993.024529426667433 | 93743 | 101535.621412145429223 | 0 | 0 |  | 2.608 | 2086 | 1479.604651162790697674418604651162790698 | 0 | 0 | 427182 | 192066.3303331796156275348837209302325581 | 461912.7732058001863536744186046511627907 | 0 | 0 | 4 | 4 | 3 | 4 | 0 | 53 | 53 | 60 | 192.619(A)(2) | 1988-12-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | YES | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | YES | 7 | 0 | NO |  |  | PIPE, WELD, OR JOINT FAILURE | FUSION JOINT | MATERIAL/WELD/EQUIP FAILURE | FUSION JOINT | MATERIAL FAILURE OF PIPE OR WELD | FUSION JOINT | [146 empty] | FUSION JOINT | [18 empty] | BUTT, HEAT FUSION |  | 1988 |  | POLYETHYLENE (PE) |  | POLYETHYLENE (PE) | [7 empty] | YES | [7 empty] | YES |  |  |  | POOR CONSTRUCTION/INSTALLATION PROCEDURES |  |  | NO | [71 empty] | YES | [14 empty] | RICHARD W. FITZPATRICK | SUPERVISOR DOT PIPELINE SAFETY | richardfitzpatrick@washgas.com | 7036397825 |  | SHANNON MALONEY | manager dot pipeline safety | 7037505558 | SHANNON MALONEY | MANAGER DOT PIPELINE SAFETY | 7037505558 | smaloney@washgas.com | ON JANUARY 6, 2021, AN ODOR WAS REPORTED TO THE WASHINGTON GAS EMERGENCY LINE ON HOOES ROAD IN SPRINGFIELD, VIRGINIA AND A TECHNICIAN WAS DISPATCHED TO THE SITE. THE LEAK WAS INVESTIGATED, GRADED AND ASPIRATED. A BGO CREW WAS DISPATCHED THE FOLLOWING DAY. THE CREW EXCAVATED THE HOLE AND FOUND A SMALL LEAK ON A BUTT FUSION BEAD ON A 1988 ALDYL-A 6" PLASTIC MAIN, OPERATING AT 55 PSIG. CONSISTENT WITH COMPANY PROCEDURE, THE CREW INSTALLED A TEMPORARY STRAUB OPEN-FLEX CLAMP, VERIFIED THAT THE SITE WAS SAFE, AND REFERRED THE REPAIR FOR A CUT-OUT. ON FEBRUARY 3, 2021, TWO WASHINGTON GAS CREWS WERE DISPATCHED TO 8530 HOOES RD TO COMPLETE THE PERMANENT REPAIR BY REPLACING THE PIPE SEGMENT CONTAINING THE CLAMP. AT APPROXIMATELY 12:22, DURING THE PROCESS OF SLIDING THE CLAMP, LEAKING GAS IGNITED. ALL EMPLOYEES THAT WERE TRANSPORTED HAVE SINCE BEEN RELEASED FROM THE HOSPITAL. FINAL REPAIRS HAVE BEEN MADE. WASHINGTON GAS PERFORMED LABORATORY TESTING ON THE FAILED SEGMENT OF PIPE. THE TESTING FOUND THE INITIAL LEAK HAD BEEN CAUSED BY A FAILED 1988 BUTT FUSION JOINT THAT EXHIBITED INADEQUATE FUSION. BY THE VISUAL EVALUATION CRITERIA IN PLACE AT THE TIME THIS GAS MAIN WAS INSTALLED, THE BUTT FUSION WOULD HAVE BEEN DEEMED ACCEPTABLE. HOWEVER, THE SUBJECT BUTT FUSION WAS LIKELY NOT INITIALLY MADE WITH SUFFICIENT FORCE APPLIED TO THE HEATED PIPE ENDS TO CREATE A FULL STRENGTH FUSION. ADDITIONAL: PART E 3.B DATE MAOP ESTABLISHED: 12/28/1988 INSTALLED WAS COMPLETED BEFORE 12/28/1988, EXACT DATE OF PRESSURE TEST UNKNOWN
2025-03-31 10:13 | NO | YES | NO | 20210027 | 35085 | 2021-03-05 14:52 | SUPPLEMENTAL FINAL | 15518 | PIEDMONT NATURAL GAS CO INC | 525 SOUTH TRYON STREET | CHARLOTTE | NC | 28202 | 2021-01-29 14:20 | EASTERN | YES | 2021 | 326 BURNETTE ROAD | FARMVILLE | PITT | NC | 27828 | 35.5571 | -77.5977 | YES | YES |  | YES | [5 empty] | 2021-01-29 17:20 | 1296989 | 1297144 | NATURAL GAS |  | 1345 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-01-29 14:27 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-01-29 14:40 | 2021-01-29 16:02 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1959 | UNKNOWN |  |  |  |  | 4 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 7 | 4 | [7 empty] | CLASS 2 LOCATION | 0 | 0 | 320000 | 346600.80061323552 | 20000 | 21662.55003832722 | 0 | 0 |  | 2.5 | 3363 | 2385.383720930232558139534883720930232558 | 0 | 0 | 343363 | 154730.2547261054236544850498338870431894 | 370648.7343724929725581395348837209302326 | 192 | 0 | 1517 | 0 | 0 | 0 | 0 | 300 | 300 | 399 | 192.619(A)(4) | 2014-12-31 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | IT WAS A 3RD PARTY DAMAGE. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | [10 empty] | FARMER | BACKHOE/TRACKHOE | DRAINAGE | NO | [5 empty] | YES | 32 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | CHRISTOPHER RANSOME | GAS REGULATORY COMPLIANCE ANALYST | christopher.ransome@duke-energy.com | 704-731-4680 |  |  |  |  | FARRIS BERRY | MANAGER- PIPELINE SAFETY | 704-731-4618 | farris.berry@duke-energy.com | A 4" STEEL HIGH PRESSURE DISTRIBUTION LINE WAS STRUCK BY A TRACKHOE WHILE DIGGING A NEW AGRICULTURAL DRAINAGE DITCH CAUSING DAMAGE TO THE LINE. DAMAGE RESULTED IN 1709 CUSTOMER OUTAGES. FARMER FAILED TO NOTIFY THE ONE CALL CENTER BEFORE EXCAVATING.
2025-03-31 10:13 | NO | YES | YES | 20210028 | 34968 | 2021-03-08 15:25 | SUPPLEMENTAL FINAL | 603 | CENTERPOINT ENERGY RESOURCES CORP. | 1400 CENTERVIEW DR SUITE 100 | LITTLE ROCK | AR | 72211 | 2021-02-06 17:28 | CENTRAL | NO | 2021 | 1900 BLOCK OF HWY 161 | JACKSONVILLE | PULASKI | AR | 72076 | 34.8496 | -92.1163 |  | YES |  |  |  |  | YES |  |  | 2021-02-06 20:36 | 1297520 | 1297591 | NATURAL GAS |  | 876 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2021-02-06 17:28 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 876 | NO | 0 | 2021-02-06 17:40 |  |  |  | 2021-02-06 18:10 |  | NO | PUBLIC PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2020 | UNKNOWN | [7 empty] | STEEL |  | OTHER | SEE #5 BELOW FOR DETAILS | UNKNOWN | [6 empty] | OTHER | [8 empty] | CAR RAN OVER REGULATOR STATION. CRACKED 2 INCH NORDSTROM VALVE ON OUTLET SIDE OF STATION (60# MAOP). THE VALVE HAS A 285# MAOP 3/8 INCH STAINLESS STEEL LINE (PILOT) WAS BROKEN ON HIGH PRESSURE SIDE OF THE REGULATOR (175# MAOP) STRIPPED OUT THE RELIEF VALVE THAT WAS SCREWED INTO A FLANGE ON A SECOND 2 INCH NORDSTROM VALVE (285# MAOP) ATTACHED TO THE OUTLET SIDE OF THE STATION (60# MAOP). | CLASS 3 LOCATION | 0 | 0 | 3426 | 3710.794821565452786 | 1236 | 1338.745592368622196 | 0 | 0 |  | 4.37 | 3828 | 2715.209302325581395348837209302325581395 | 0 | 0 | 8490 | 4603.095771667619200784053156146179401993 | 7764.749716259656377348837209302325581395 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 40 | 40 | 60 | 192.619(A)(1) | 2020-06-29 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.4 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | NO | [5 empty] | NO | UNKNOWN | PASSENGER CAR | OFF-ROAD | 20 | YES |  | YES | [140 empty] | VERNON MCNULLY | DISTRICT OPERATIONS MANAGER | vernon.mcnully@centerpointenergy.com | 5013774633 |  | JAY REBER | jay.reber@centerpointenergy.com | 5013774980 | KEITH A. KITTINGER | REGIONAL OPERATIONS DIRECTOR | 5013774669 | keith.kittinger@centerpointenergy.com | A VEHICLE HEADING NORTH ON HWY 161 LOST CONTROL AND WENT OFF OF THE EAST SIDE OF THE HIGHWAY. THE VEHICLE STRUCK TWO BRICK AND MORTAR PEDESTALS, CENTERPOINT ENERGY'S STEEL BARRICADE, AND STRUCK THE REGULATOR STATION LOCATED APPROXIMATELY 20' FROM HWY 161 BEFORE COMING TO REST APPROXIMATELY 20' PAST THE REGULATOR STATION. THE IMPACT CAUSED THE FOLLOWING DAMAGE TO THE DISTRICT REGULATOR STATION: CRACKED 2 INCH VALVE ON OUTLET SIDE OF STATION, BROKE THE 3/8 INCH STAINLESS STEEL LINE (PILOT) ON HIGH PRESSURE SIDE OF THE REGULATOR AND STRIPPED OUT THE RELIEF VALVE STACK THAT WAS SCREWED INTO A FLANGE ON A SECOND 2 INCH VALVE THAT WAS ATTACHED TO THE OUTLET SIDE OF THE STATION. CENTERPOINT ENERGY'S CREWS STOP THE FLOW OF GAS ON THE DAMAGED LINE, REPAIRED THE DAMAGED MAIN, AND INSTALLED A NEW REGULATOR STATION.
2025-03-31 10:13 | NO | YES | NO | 20210029 | 36719 | 2021-03-09 11:59 | SUPPLEMENTAL FINAL | 21349 | VIRGINIA NATURAL GAS | 544 S. INDEPENDENCE BLVD | VIRGINIA BEACH | VA | 23452 | 2021-02-08 08:30 | EASTERN | YES | 2021 | 4651 COLUMBUS STREET | VIRGINIA BEACH | VIRGINIA BEACH | VA | 23450 | 36.8402 | -76.1371 | [6 empty] | YES |  |  | 2021-02-08 10:19 | 1297562 | 1297700 | NATURAL GAS |  | 21221.53 | 11 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-02-03 13:25 | NO |  |  | 2021-02-03 13:45 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 90 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1971 | UNKNOWN |  |  |  |  | 12 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.25 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 1300000 | 1408065.7524912693 | 70000 | 75818.92513414527 | 0 | 0 |  | 2.615 | 55494 | 39362.0232558139534883720930232558139535 | 29 | 20.56976744186046511627906976744186046512 | 1425523 | 651011.7340864187370764119601328903654485 | 1523267.27064867038395348837209302325581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 135 | 150 | 192.619(A)(4) | 1971-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 20 |  | YES | YES | YES | YES | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THIS LEAK WAS A PINHOLE LEAK WHICH COULD NOT BE IDENTIFIED VIA SCADA MEASUREMENT. | [12 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | PIPE WAS LOCATED UNDER EIGHT (8) LANES OF TRAFFIC. SAFETY ISSUES ALONG WITH CITY OFFICIALS WOULD NOT PERMIT COMPANY TO CLOSE ROAD FOR THE PURPOSE OF EXCAVATION AND REPAIR. COMPANY ABANDONED THIS SEGMENT OF PIPE AND INSTALLED NEW SECTION. ADDITIONALLY, THE COMPANY INTRODUCED A SEWER CAMERA TO THE PIPE SEGMENT AND THE LEAK WAS SO SMALL IT WAS UNABLE TO BE LOCATED VIA CLOSED CIRCUIT TELEVISION CAMERA. | [45 empty] | JONATHAN HEATH | DIRECTOR - COMPLIANCE AND SYSTEM INTEGRITY | jbheath@southernco.com | (757) 298-5729 |  | JONATHAN HEATH | jbheath@southernco.com | (757) 880-4551 | JONATHAN HEATH | DIRECTOR - COMPLIANCE AND SYSTEM INTEGRITY | (757) 880-4551 | jbheath@southernco.com | ON FEBRUARY 3RD, THE COMPANY RECEIVED NOTIFICATION FROM THE PUBLIC OF A POSSIBLE LEAK IN THE VICINITY OF COLUMBUS STREET AND INDEPENDENCE BOULEVARD IN VIRGINIA BEACH. THE COMPANY WAS ABLE TO DETERMINE THE LEAK WAS LOCATED UNDER THE ROADWAY OF INDEPENDENCE BOULEVARD. INDEPENDENCE BOULEVARD IS A HEAVILY TRAVELED ROADWAY AND A MAIN ARTERY OF THE CITY. DUE TO THE VOLUME OF TRAFFIC, THE COMPANY WAS REQUIRED TO CLOSE AN ADDITIONAL LANE WHILE PERFORMING ROAD WORK. AT ONE POINT, THE COMPANY CLOSED TWO TRAVEL LANES AND A TURN LANE IN ORDER TO STRIP BACK AND EXAMINE THE PIPE. ADDITIONALLY, THE PIPE DEPTH WAS APPROACHING 90'' AND THE SOIL CONDITIONS THAT CLOSE TO OCEAN MADE SHORING SAFETY AN IMMEDIATE CONCERN. ADDITIONALLY, OTHER UTILITIES IN THE IMMEDIATE VICINITY INCLUDED SEWER, FIBER OPTICS, AND POWER. DUE TO ALL OF THESE FACTORS, AS WELL AS PRESSURE BEING PLACED UPON THE COMPANY FROM THE LOCALITY TO REFRAIN FROM INHIBITING TRAFFIC FLOW, THE COMPANY DETERMINED THE SAFEST AND BEST OPTION WOULD BE ABANDON THE 750' SEGMENT OF PIPE AND INSTALL A NEW SECTION OF 12'' STEEL PIPE. UPON COMPLETION OF THE PIPE REPLACEMENT, THE COMPANY CONDUCTED A PRESSURE TEST TO ENSURE THERE WAS A LEAK ON THE RETIRED SEGMENT OF PIPE. THE PIPE WAS PRESSURIZED TO 130 PSIG. AND WAS MONITORED FOR 65 HOURS. AFTER COMPLETION OF THE 65 HOURS, THE COMPANY CONFIRMED PRESSURE HAD DECREASED TO 102 PSIG. THE COMPANY ALSO CONTINUES TO TAKE READINGS IN THE AREA TO ENSURE THERE IS NO RESIDUAL GAS OR ADDITIONAL LEAKS ON NEARBY PIPE.
2025-03-31 10:13 | NO | NO | NO | 20210031 | 34990 | 2021-03-12 14:47 | ORIGINAL FINAL | 8160 | INTERMOUNTAIN GAS CO | 555 SOUTH COLE ROAD (POB 7608, 83707) | BOISE | ID | 83705 | 2021-03-01 11:52 | MOUNTAIN | NO | 2021 | GOSHEN-FIRTH RD (E 800 N) 4000' E OF SHELLEY GOSHEN RD (N 1100 E) | GOSHEN | BINGHAM | ID | 83274 | 43.3113 | -112.0654 |  |  |  | YES | [5 empty] | 2021-03-01 12:38 | 1299328 | 1299422 | NATURAL GAS |  | 6027 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-02-27 18:07 | NO |  |  | 2021-02-27 18:51 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2005 | UNKNOWN | [7 empty] | OTHER | REGULATOR AND RELIEF VALVE | [9 empty] | OTHER | [8 empty] | FULLY OPENED RELIEF VALVE. | CLASS 1 LOCATION | 0 | 0 | 395 | 427.835363256962595 | 1413 | 1530.459160207818093 | 0 | 0 |  | 4.096 | 24687 | 17510.546511627906976744186046511627907 | 0 | 0 | 26495 | 17009.3475906193509907774086378737541528 | 19468.841035092687664744186046511627907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 190 | 200 | 192.619(A)(2) | 1966-10-13 | PRESSURE EXCEEDED MAOP, BUT DID NOT EXCEED THE APPLICABLE ALLOWANCE IN 192.201 | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM PUBLIC |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PIPELINE PRESSURE DID NOT EXCEED ALARM SET POINTS AT THE LOCATION OF THE SCADA MONITORING POINT. | [12 empty] | NO |  |  | NO |  |  | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | MATERIAL/WELD/EQUIP FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | EQUIPMENT FAILURE | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [197 empty] | MALFUNCTION OF CONTROL/RELIEF EQUIPMENT | [9 empty] | YES | [61 empty] | YES | [11 empty] | GREG WATKINS | MANAGER POLICY AND PROCEDURE | greg.watkins@mdu.coom | 208-377-6032 |  | GREG WATKINS | greg.watkins@mdu.com | 208-377-6032 | GREG WATKINS | MANAGER POLICY AND PROCEDURE | 208-377-6032 | greg.watkins@mdu.com | INTERMOUNTAIN GAS COMPANY (IGC) WAS NOTIFIED OF AN OUTSIDE GAS ODOR IN GOSHEN, ID (AN UNINCORPORATED COMMUNITY IN BINGHAM COUNTY) AT 18:07 ON FEBRUARY 27, 2021. AFTER ARRIVING ON SITE AT 18:51, A COMPANY FIRST RESPONDER FOUND A 3" RELIEF VALVE AT A DISTRICT REGULATOR IN THE FULL OPEN POSITION AT WHICH TIME ADDITIONAL PERSONNEL WAS DISPATCHED TO THE SCENE. THE REGULATORS AT THE LOCATION OF THE RELIEF VALVE WERE INSPECTED AND FOUND TO BE OPERATING CORRECTLY. COMPANY PERSONNEL THEN BEGAN INSPECTING THE REGULATORS AT A REGULATOR STATION LOCATED 3.7 MILES WEST OF THE BLOWING RELIEF VALVE THAT SUPPLIES GAS TO THE SAME 200 PSIG MAOP PIPELINE. THE PRIMARY REGULATOR AT THE SECOND REGULATOR STATION WAS SHUT IN AT 21:45 AT WHICH TIME THE SYSTEM PRESSURE DROPPED TO 170 PSIG; HOWEVER, THE RELIEF VALVE WAS STILL IN THE OPEN POSITION. THE RELIEF VALVE WAS ISOLATED AT 12:28 ON FEBRUARY 28, 2021. IT WAS DETERMINED HYDROCARBONS HAD ACCUMULATED AND FROZE CAUSING THE RELIEF VALVE TO STICK IN THE OPEN POSITION. THE MORNING OF MARCH 1, 2021 COMPANY PERSONNEL INSPECTED AND REPAIRED THE PRIMARY REGULATOR AT THE SECOND REGULATOR STATION. A YELLOW/WHITE POWDER WAS FOUND ON THE SEAT, DIAPHRAGM AND PILOT COMPONENTS WHICH WAS THE CAUSE OF THE REGULATOR FAILURE THAT RESULTED IN THE RELIEF VALVE OPENING. THE POWDER WAS CLEANED OFF ALL SURFACES AND THE SOFT COMPONENTS WERE REPLACED. AT 11:52 ON MARCH 1, 2021 THE ENGINEERING DEPARTMENT CALCULATED THE GAS LOSS FOR THIS RELEASE AT WHICH TIME IT WAS DISCOVERED THE 3 MILLION CUBIC FEET REPORTING THRESHOLD WAS EXCEEDED.
2025-03-31 10:13 | NO | NO | NO | 20210032 | 35286 | 2021-03-12 18:04 | SUPPLEMENTAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2021-02-11 16:13 | PACIFIC | NO | 2021 | 4700 TOPANGA CANYON BLVD | WOODLAND HILLS | LOS ANGELES | CA | 91364 | 34.1513 | -118.6047 | [7 empty] | YES | PRESSURE CONTROL FITTINGS | 2021-02-11 04:20 | 1297772 | 1297867 | NATURAL GAS |  | 2735 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-02-10 10:27 |  |  |  | 2021-02-10 10:44 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 51 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1962 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.254 | [6 empty] | MECHANICAL PUNCTURE | 5 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 31930 | 34584.26113618940673 | 48270 | 52282.56451750274547 | 0 | 0 |  | 4.1 | 11214 | 7954.116279069767441860465116279069767442 | 0 | 0 | 91414 | 43335.6571881877090883720930232558139535 | 94820.9419327619196418604651162790697674 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 40 | 45 | 192.619(A)(4) | 1970-07-01 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO | YES | STATE HIGHWAY | [12 empty] | STATE | AUGER | TRAFFIC SIGN | NO | [5 empty] | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | LINDA HOANG | PIPELINE SAFETY AND COMPLIANCE ADVISOR | lvhoang@socalgas.com | 213-500-3442 |  | LINDA HOANG | lvhoang@socalgas.com | 213-500-3442 | LINDA HOANG | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 213-500-3442 | lvhoang@socalgas.com | ON 2-10-21, SOCALGAS WAS NOTIFIED OF THIRD PARTY DAMAGE AT 4700 TOPANGA CANYON BLVD. WOODLAND HILLS, CA. THE THIRD PARTY DAMAGED A 6-INCH MEDIUM PRESSURE STEEL GAS MAIN WITH AN AUGER. GAS WAS CONTROLLED AT 21:33 ON 2/10/21. THERE WERE NO REPORTED FATALITIES OR INJURIES DUE TO THE GAS RELEASE. THE INVESTIGATION SHOWED THE THIRD PARTY WAS WORKING TO INSTALL A NEW STREET SIGN WITHOUT A USA TICKET. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO THE RELEASE OF GAS AND DAMAGES EXCEEDING $50,000.
2025-03-31 10:13 | NO | YES | NO | 20210033 | 35041 | 2021-03-19 14:57 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2021-02-21 16:00 | EASTERN | NO | 2021 | 528 HIGH STREET | WILLIAMSTON | INGHAM | MI | 48895 | 42.6886 | -84.2769 | [7 empty] | YES | (1) SERVICE TEE WAS SHUT-OFF (2) MECHANICAL FTG. (3) RETIRED WITH ABANDONMENT | 2021-02-21 16:57 | 1298600 | 1298775 | NATURAL GAS |  | 977 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-02-18 09:23 | NO |  |  | 2021-02-18 09:37 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 48 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1928 | UNKNOWN |  |  |  |  | 2 | API 5L | UNKNOWN | STEEL |  | OTHER | UNKNOWN | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 125977 | 136449.153308917409697 | 721 | 780.934928881696281 | 0 | 0 |  | 2.38 | 2325 | 1649.127906976744186046511627906976744186 | 0 | 0 | 129023 | 58362.1266995770919954950166112956810631 | 138879.2161447758501640465116279069767442 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 55 | 55 | 60 | 192.619(A)(1) | 1972-08-21 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 60 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES | [8 empty] | YES |  |  |  | YES | YES | 1996 | NO | NO | [8 empty] | N/A Bare/Ineffectively Coated Pipe | NONE |  | NO | [19 empty] | 2020-08-18 | YES | 1972 | 60 | [225 empty] | CARMELLA KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA KING | carmella.king@cmsenergy.com | 989-280-2963 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON FEBRUARY 18, 2021 AT APPROXIMATELY 09:23 HOURS CONSUMERS ENERGY WAS NOTIFIED OF AN ODOR OF GAS AT OR NEAR 528 HIGH STREET, (INGHAM COUNTY) WILLIAMSTON, MICHIGAN A GAS SERVICE WORKER (GSW) WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 09:37 HOURS AND BEGAN PERFORMING A LEAK INVESTIGATION. GAS READS (60% APPROXIMATELY 15-FEET FROM THE BUILDING )WERE DISCOVERED NEAR 518 HIGH STREET, REQUIRING AN IMMEDIATE RESPONSE. THE DISTRIBUTION CREW WAS DISPATCHED AND ARRIVED ONSITE AT APPROXIMATELY 10:43 HOURS. THE PIPELINE SERVING 518 HIGH STREET WAS REPLACED TO ELIMINATE THE LEAK FOUND AT THE SERVICE CONNECTION. PERSONNEL ONSITE CONTINUED TO FIND READS AFTER THE REPAIR WAS COMPLETED AND CONTINUE THEIR INVESTIGATION. WHILE DISTRIBUTION EMPLOYEES WERE ACTIVELY INVESTIGATING THE LEAK, GSW'S WERE MONITORING THE NEARBY HOMES AND SEWERS. DURING THE INVESTIGATION, GAS READS WERE DISCOVERED IN THE SEWER. GAS SERVICE EMPLOYEES REMAIN ONSITE AND CONTINUOUSLY MONITORED THE HOMES, SEWERS AND THE SURROUNDING AREA. ON FEBRUARY 19, 2021, AN ADDITIONAL LEAK WAS DISCOVERED APPROXIMATELY 10 FEET FROM THE SERVICE LINE REPLACEMENT AT 518 HIGH STREET. THE LEAK WAS LOCATED ON THE 2-INCH STEEL MEDIUM PRESSURE PIPELINE. THE CAUSE OF THE LEAK WAS DETERMINED TO BE A CORROSION AND WAS LOCATED AT THE 6 O'CLOCK POSITION. A PLIDCO FITTING WAS INSTALLED AS A TEMPORARY REPAIR. FOLLOWING REPAIRS OF ALL IDENTIFIED LEAKS, THE NATURAL GAS ODOR REMAINED PERCEPTIBLE, AND READINGS WERE PRESENT NEAR THE REPAIR LOCATION. THE VAPOR EXTRACTION UNIT (VEU) WAS USED TO EXTRACTED NATURAL GAS SATURATED SOIL AND PERSONNEL REMAINED ONSITE AND CONTINUOUSLY MONITORED UNTIL GAS READS MET CLASSIFIABLE CRITERIA. OVER THE NEXT SEVERAL DAYS, DISTRIBUTION AND SERVICE PERSONNEL CONTINUED TO EXTRACT GAS FROM THE SOIL AND INVESTIGATE FOR ADDITIONAL LEAKS. SEVERAL ADDITIONAL LEAKS AT THE SERVICE CONNECTIONS WERE IDENTIFIED AT 515 HIGH STREET, 528 HIGH STREET AND 529 HIGH STREET. BASED ON THE AGE AND CONDITION OF THE PIPELINE, OPERATIONS CONSULTED WITH ENGINEERING AND A DECISION WAS MADE TO REPLACE THE 1928 VINTAGE STEEL PIPELINE AND SERVICES. A PIPELINE REPLACEMENT PROJECT BEGAN ON FEBRUARY 23 - MARCH 4. APPROXIMATELY 600 FEET OF 2-INCH PLASTIC, MEDIUM PRESSURE PIPELINE WAS DIRECTIONAL DRILLED, AND 9 SERVICE RENEWALS COMPLETED.
2025-03-31 10:13 | NO | YES | NO | 20210034 | 35102 | 2021-03-23 15:13 | SUPPLEMENTAL FINAL | 792 | ATLANTA GAS LIGHT CO | 10 PEACHTREE PLACE NE | ATLANTA | GA | 30309 | 2021-03-02 10:11 | EASTERN | NO | 2021 | 200 SUMMERWALK PARKWAY | TUCKER | GWINNETT | GA | 30084 | 33.8668 | -84.1824 | [5 empty] | YES |  |  |  | 2021-03-02 10:11 | 1299389 | 1299560 | NATURAL GAS |  | 9.5 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-03-01 23:10 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 9.5 | NO | 18 | 2021-03-01 23:26 |  |  |  | 2021-03-02 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1986 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | NO |  |  |  | OTHER | TYPICAL METER SET | [9 empty] | MECHANICAL PUNCTURE | 0.1 | 0.2 | [7 empty] | CLASS 3 LOCATION | 1200000 | 1299753.0022996332 | 3000 | 3249.382505749083 | 1500 | 1624.6912528745415 | 0 | 0 |  | 9.5 | 90 | 63.8372093023255813953488372093023255814 | 0 | 0 | 1204590 | 540396.4605320088804019933554817275747508 | 1304690.91326755915008139534883720930233 | 0 | 0 | 8 | 0 | 1 | 1 | 0 | 60 | 60 | 60 | 192.619(A)(2) | 1986-08-28 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 10 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | YES |  |  | YES |  |  | UNKNOWN | UNKNOWN | PASSENGER CAR | PARKING LOT | 40 | NO | [142 empty] | RALPH MCCOLLUM | LEAD COMPLIANCE ENGINEER | rmccollu@southernco.com | (404) 584-3733 | (404) 584-4710 |  |  |  | RICK SLAGLE | DIRECTOR COMPLIANCE AND QA | (404) 584-4910 | rslagle@southernco.com | A TWO-METER NATURAL GAS HEADER ON THE SIDE OF AN EIGHT-UNIT APARTMENT BUILDING WAS HIT AND RUPTURED BY AN OUT OF CONTROL VEHICLE. THE DRIVER WAS ATTEMPTING TO PULL TOO QUICKLY OUT OF A PARKING SPACE AT A NEIGHBORING APARTMENT BUILDING THUS JUMPING THE CURB AND HITTING THE TWO-METER HEADER. THE ESCAPING NATURAL GAS IGNITED BY AN UNKNOWN SOURCE AS A RESULT OF THE COLLISION WHERE THE FIRE CONSUMED PART OF THE EIGHT-UNIT APARTMENT BUILDING. ADDITIONAL NRC REPORT NUMBER 1299560 WAS CREATED FOR THE SAME EVENT AFTER A SUPPLEMENTAL CALL WAS PLACED WITH THE NRC TO UPDATE THE INITIAL TELEPHONIC NOTICE.
2025-03-31 10:13 | NO | YES | YES | 20210035 | 35742 | 2021-03-26 14:41 | SUPPLEMENTAL FINAL | 2585 | COLUMBIA GAS OF KENTUCKY INC | 2001 MERCER ROAD | LEXINGTON | KY | 40511 | 2021-02-27 05:00 | EASTERN | NO | 2021 | 6520 STATE ROAD 899 | PIPPA PASSES | KNOT | KY | 41844 | 37.3455 | -82.8682 | YES | [8 empty] | 2021-02-28 13:53 | 1299227 | 1299365 | NATURAL GAS |  | 75.3 | 22 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 2 | 2 | YES | 2021-02-27 05:00 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | YES | 2 | 2021-02-28 13:00 |  |  |  | 2021-02-28 13:05 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 22 | YES | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | 2001 | 1995 | SINGLE FAMILY RESIDENTIAL | NO |  | YES | 1 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.099 |  | 2406 | LEAK |  |  | CONNECTION FAILURE | [6 empty] | CLASS 3 LOCATION | 65000 | 70403.287624563465 | 43 | 46.574482582403523 | 10450 | 11318.68239502597245 | 0 | 0 |  | 2.57 | 194 | 137.604651162790697674418604651162790698 | 57 | 40.43023255813953488372093023255813953488 | 75744 | 34030.7714747791762862259136212624584718 | 81946.5793858927712055581395348837209302 | 1 | 0 | 6 | 0 | 0 | 6 | 1 | 8 | 8 | 13 | 192.621 M | 1993-08-20 | PRESSURE DID NOT EXCEED MAOP | OTHER | NATURAL | 5 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | COLUMBIA GAS OF KENTUCKY REVIEWED THE PRESSURE TREND FROM SCADA AT THE UPSTREAM REGULATOR STATION R1429, FROM JANUARY 01, 2020 THROUGH MARCH 15, 2021. THERE WAS NO INDICATION OF THE OUTLET PRESSURE GOING BEYOND THE SET POINTS OF THE CONTROL AND MONITOR REGULATORS. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | EXCAVATION DAMAGE | PREVIOUS DAMAGE DUE TO EXCAVATION | [68 empty] | PREVIOUS DAMAGE DUE TO EXCAVATION ACTIVITY | 2020-08-28 | NO | [12 empty] | YES | YES | STATE HIGHWAY |  |  | YES | [9 empty] | MUNICIPALITY | UNKNOWN/OTHER | SEWER (SANITARY/STORM) | YES | 2101041372 |  |  | UTILITY OWNER | YES | YES | 26 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [144 empty] | YES | [25 empty] | RYAN TWAIT | MANAGER OPERATIONS COMPLIANCE | rmtwait@nisource.com | 8595334022 |  | RYAN TWAIT | rmtwait@nisource.com | 8595334022 | RYAN TWAIT | MANAGER OPERATIONS COMPLIANCE | 8595334022 | rmtwait@nisource.com | COLUMBIA GAS OF KENTUCKY (CKY) RECEIVED NOTICE ON FEBRUARY 28TH, 2021 AT 12:43 PM OF A GAS FIRE AT 6560 STATE ROUTE 899. A CKY SERVICE TECH WAS DISPATCHED AND ARRIVED ON SCENE AT 12:50 PM. UPON ARRIVAL THE CKY SERVICE TECH WAS ADVISED BY THE FIRE CHIEF OF PIPPA PASSES VOLUNTEER FIRE DEPARTMENT (PPVFD) THAT THEY HAD RESPONDED TO A HOUSE FIRE AT 6560 SR 899 AT APPROXIMATELY 5:00 AM ON FEBRUARY 27, 2021. TWO PEOPLE WERE HOSPITALIZED AS A RESULT OF THE FIRE. PPVFD PUT THE FIRE OUT, DID NOT OBSERVE ANY GAS SERVICE AND LEFT THE SCENE. PPVFD WAS DISPATCHED TO THE SAME LOCATION ON FEBRUARY 28, 2021 AT APPROXIMATELY 12:00 PM DUE TO A CALL RECEIVED BY A NEIGHBOR REGARDING A SMALL FIRE AT THE HOUSE SITE. WHEN THE PPVFD ARRIVED ON SITE, THEY OBSERVED A SMALL "PILOT" LIKE FLAME COMING FROM THE GROUND. WHEN THEY APPROACHED THE FLAME WENT OUT. PPVFD STATED THAT THEY RELIT THE AREA AND HAD A 12 INCH FLASH OF FIRE AND IT WENT BACK OUT. AT THAT POINT, THE PPVFD CONTACTED CKY. THE CKY SERVICE TECH IMMEDIATELY SECURED THE AREA AND SENT OUT NOTIFICATIONS OF THE EMERGENCY. HE THEN BEGAN A PERIMETER CHECK OF THE AREA AND NOTICED FRESH EXCAVATION IN THE AREA OF A CKY TWO INCH PLASTIC MAIN WITH HIGH CONCENTRATIONS OF GAS ESCAPING THROUGH A PVC PIPE PROTRUDING FROM THE GROUND LOCATED IN THIS AREA. THE CKY SERVICE TECH ADVISED THE PPVFD TO SHUT DOWN KY STATE ROUTE 899. THE KY PSC ARRIVED ON SITE AND ADVISED CKY TO SECURE THE AREA AND AWAIT THE ARRIVAL OF THE STATE FIRE MARSHALL PRIOR TO ANY EXCAVATION ACTIVITY. THE DECISION WAS MADE TO SHUT OFF THE GAS MAIN FEEDING THIS AREA, AND THE FIRE MARSHAL ADVISED THEY WOULD BE ON SITE AT 10:00 AM ON MARCH 1, 2021. THE FIRE MARSHAL COMPLETED THEIR INITIAL ASSESSMENT ON MARCH 1, 2021 AND NOTIFIED CKY TO PROCEED WITH REPAIRS. A VACUUM TRUCK WAS UTILIZED TO EXPOSE CKY'S ASSETS AND DISCOVERED THE SERVICE LINE FOR 6529 STATE ROUTE 899, WHICH WAS A ONE INCH PLASTIC NATURAL GAS SERVICE LINE, HAD BEEN STRUCK AND AN UNAUTHORIZED ATTEMPT TO REPAIR THE ONE INCH SERVICE LINE HAD BEEN PERFORMED. IT WAS OBSERVED THAT AN UNAPPROVED EIGHTEEN INCH SECTION OF ONE INCH PLASTIC PIPING AND TWO UNAPPROVED BRASS WATER COUPLINGS WERE UTILIZED IN AN ATTEMPT TO REPAIR THE DAMAGED SERVICE LINE. UPON FURTHER INVESTIGATION, IT WAS OBSERVED THAT ONE END OF THE PIPING HAD PULLED APART FROM THE COUPLING. CKY CUT OUT THE SECTION OF PIPING AND REPAIRED AS PER OUR STANDARD. SERVICE WAS RESTORED AT 09:15 PM ON MARCH 1, 2021.
2025-03-31 10:13 | NO | YES | NO | 20210036 | 39564 | 2021-03-28 23:43 | SUPPLEMENTAL FINAL | 18536 | SOUTHWEST GAS CORP | 8360 S. DURANGO DRIVE | LAS VEGAS | NV | 89113 | 2021-02-28 04:16 | MOUNTAIN | NO | 2021 | 7TH STREET & UNIVERSITY DRIVE | PHOENIX | MARICOPA | AZ | 85034 | 33.4215 | -112.0649 | YES | [8 empty] | 2021-02-28 06:42 | 1299214 | 1299368 | NATURAL GAS |  | 4614 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-02-28 04:16 | ALLOWED TO BURN OUT |  | 4614 | NO | 0 | 2021-02-28 04:50 |  |  |  | 2021-02-28 04:50 | 2021-02-28 06:00 | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | OVERHEAD CROSSING |  |  |  | YES | YES | UNCASED | [9 empty] | INVESTOR OWNED |  | MAIN |  | 1984 | UNKNOWN |  |  |  |  | 10 | GRADE B | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.365 | [6 empty] | OTHER | [8 empty] | INTENTIONAL DAMAGE - REMOVAL OF FLANGE FASTENERS BY UNKNOWN PERSON. | CLASS 3 LOCATION | 8764645 | 9493228.044033723856845 | 2098109 | 2272519.559918234261349 | 5000 | 5415.637509581805 | 0 | 0 |  | 2.4541 | 11323 | 8031.430232558139534883720930232558139535 | 0 | 0 | 10879077 | 4882692.32472416443057611960132890365449 | 11779194.67169409806272888372093023255814 | 6 | 0 | 0 | 0 | 0 | 0 | 6 | 270 | 270 | 275 | 192.619(A)(4) | 1986-11-12 | PRESSURE DID NOT EXCEED MAOP | DRIP |  | 0.3 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | PRESSURE AND FLOW CHANGE WAS NOT SUFFICIENT TO SIGNAL SCADA ALARMS. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | OTHER OUTSIDE FORCE DAMAGE | INTENTIONAL DAMAGE | [112 empty] | INTENTIONAL DAMAGE | [11 empty] | THEFT OF EQUIPMENT | [156 empty] | SHAWN BRINK | ADMINISTRATOR DIVISION COMPLIANCE | shawn.brink@swgas.com | 602-484-5489 | 602-484-5322 | SHAWN BRINK | shawn.brink@swgas.com | 602-484-5489 | ROBERT MCGEE | DIRECTOR CENTRAL SUPPORT | 602-484-5367 | robert.mcgee@swgas.com | PL C1-PL2021-0007 ON FEBRUARY 28, 2021 AT 04:16 SOUTHWEST GAS CORPORATION (SWG) WAS NOTIFIED BY THE PHOENIX FIRE DEPARTMENT OF A RELEASE OF GAS AND FIRE AT THE 7TH STREET BRIDGE LOCATED SOUTH OF UNIVERSITY DRIVE IN PHOENIX. SWG CREWS RESPONDED TO FIND A NATURAL GAS FED FIRE ENGULFING THE BRIDGE. A 10-INCH STEEL PIPELINE (MAOP 275 PSIG) IS SUSPENDED UNDER THE BRIDGE THAT CROSSES THE SALT RIVER. SWG CONTROLLED THE FLOW OF GAS BY UTILIZING VALVES THAT RESULTED IN AN OUTAGE OF SIX COMMERCIAL ACCOUNTS (FIVE ACTIVE, ONE INACTIVE). THERE WERE NO INJURIES OR FATALITIES AS A RESULT OF THIS INCIDENT. NOTIFICATION WAS MADE TO PHMSA VIA THE NATIONAL RESPONSE CENTER (NRC) ON FEBRUARY 28, 2021 AT 6:42 AND WAS GIVEN NRC REPORT #1299214. AN UPDATE WAS PROVIDED TO THE NRC ON MARCH 1, 2021 AT 19:05 AND WAS GIVEN NRC REPORT #1299368. CHEMICAL SAFETY AND HAZARD INVESTIGATION BOARD WAS NOTIFIED ON MARCH 1, 2021 AT 10:38 WHEN IT WAS DETERMINED THAT PROPERTY DAMAGE MAY EXCEED $1,000,000. NO REPORT NUMBER WAS GIVEN. INVESTIGATION INTO THE CAUSE IS STILL ONGOING, AND A SUPPLEMENTAL REPORT WILL BE SUBMITTED UPON COMPLETION OF THE INVESTIGATION BY SWG. SUPPLEMENTAL REPORT: THE REPORT WAS UPDATED TO REFLECT AN APPARENT CAUSE OF THE INCIDENT. PART G - APPARENT CAUSE WAS CHANGED FROM G8 "OTHER INCIDENT CAUSE" - UNKNOWN, TO G4 - OTHER OUTSIDE FORCE DAMAGE, INTENTIONAL DAMAGE, THEFT OF EQUIPMENT. THE INCIDENT INVESTIGATION IS STILL ONGOING, AND A SUPPLEMENTAL REPORT WILL BE SUBMITTED UPON COMPLETION OF THE INVESTIGATION BY SOUTHWEST GAS CORPORATION. SUPPLEMENTAL REPORT 2: THE REPORT WAS UPDATED TO REFLECT REVISED ESTIMATED COSTS. IN PART D #2, ESTIMATED COSTS WERE REVISED. 2.A. ESTIMATED COSTS OF PUBLIC AND NON-OPERATOR PRIVATE PROPERTY DAMAGE WAS REVISED TO $8,767,645, 2.B. ESTIMATED COST OF OPERATOR'S PROPERTY DAMAGE & REPAIRS WAS REVISED TO $2,098,109, AND 2.E. TOTAL ESTIMATED PROPERTY DAMAGE WAS REVISED TO $10,864,754. THE INCIDENT INVESTIGATION IS STILL ONGOING PENDING THE RELEASE OF THE FAILED COMPONENTS, AND A SUPPLEMENTAL REPORT WILL BE SUBMITTED UPON COMPLETION OF THE INVESTIGATION BY SOUTHWEST GAS CORPORATION. SUPPLEMENTAL REPORT 3: SOUTHWEST GAS CORPORATION'S INVESTIGATION DETERMINED THAT THE INCIDENT WAS CAUSED BY THE REMOVAL OF FASTENERS FROM A FLANGED JOINT BY AN UNKNOWN PERSON. THE REPORT WAS UPDATED TO REFLECT TYPE OF RELEASE INVOLVED. IN PART C #5, OTHER WAS CHANGED TO "INTENTIONAL DAMAGE - REMOVAL OF FLANGE FASTENERS BY UNKNOWN PERSON".
2025-03-31 10:13 | NO | YES | NO | 20210037 | 35642 | 2021-03-31 15:16 | SUPPLEMENTAL FINAL | 13299 | NEW JERSEY NATURAL GAS CO | 1415 WYCKOFF ROAD | WALL | NJ | 07719 | 2021-03-26 16:21 | EASTERN | YES | 2021 | STATE RT. 34 N | WALL | MONMOUTH | NJ | 07719 | 40.1565 | -74.0993 | [6 empty] | YES |  |  | 2021-03-29 13:41 | 1301480 | 1301652 | NATURAL GAS |  | 540 | 20 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-03-26 21:45 |  |  |  | 2021-03-26 22:25 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 48 | NO | YES |  |  |  |  | YES | CASED | [5 empty] | INVESTOR OWNED |  | MAIN |  | 1980 | UNKNOWN |  |  |  |  | 12 | API 5L X52 | REPUBLIC | STEEL |  | LONGITUDINAL ERW - HIGH FREQUENCY |  | 0.25 | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 3 LOCATION | 0 | 0 | 217000 | 235038.667915850337 | 16283 | 17636.565113704106163 | 0 | 0 |  | 2.42 | 1307 | 927.058139534883720930232558139534883721 | 48 | 34.04651162790697674418604651162790697674 | 234638 | 105539.5815225404095706777408637873754153 | 253636.3376807172338606744186046511627907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 200 | 250 | 192.619(A)(2) | 1980-11-17 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | UPON BEING REENERGIZED, OVERHEAD HIGH VOLTAGE ELECTRIC WIRES ARCHED AND FELL TO THE GROUND ON THE NORTHBOUND SIDE OF STATE ROUTE 34 IN WALL TOWNSHIP. THE WIRES MADE CONTACT WITH AN NJNG CASING VENT PIPE CAUSING ARCING BETWEEN A 20' BARE STEEL CASING WITH THE 12' COATED STEEL CARRIER PIPE. (COMPLETE NARRATIVE IN PART H) | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [147 empty] | YES | [20 empty] | MOBEEN KHAN | DIRECTOR | mukhan@njng.com | 732 919 8035 | 732 919 0936 |  |  |  | MOBEEN KHAN | DIRECTOR | 732 919 8035 | mukhan@njng.com | ON THE EVENING OF FRIDAY, MARCH 26, 2021, UPON BEING REENERGIZED, OVERHEAD HIGH VOLTAGE ELECTRIC WIRES ARCHED AND FELL TO THE GROUND ON THE NORTHBOUND SIDE OF STATE ROUTE 34 IN WALL TOWNSHIP. THE WIRES MADE CONTACT WITH AN NJNG CASING VENT PIPE CAUSING ARCING BETWEEN A 20" BARE STEEL CASING WITH THE 12" COATED STEEL CARRIER PIPE. THE RESULTING ARC BURNT THROUGH THE STEEL AND CAUSED TWO "PIN HOLES" IN THE 250# STEEL CARRIER PIPELINE. ABOVE GROUND ARCING ALSO CAUSED THE BUSHES AROUND THE FACILITY TO CATCH FIRE. INITIALLY, NJNG RESPONDED TO THE LOCATION BASED ON A CALL FROM THE POLICE DEPARTMENT. AS A RESULT OF THE INCIDENT, ROUTE 34 WAS CLOSED FOR APPROXIMATELY 2 DAYS WHILE NJNG AND ITS CONTRACTORS FOUND THE LEAKS AND CUT OUT AND REPLACED THE DAMAGED PORTIONS OF THE GAS MAIN. SUBSEQUENTLY, APPROXIMATELY 41' OF 12" STEEL MAIN AND CASING WAS REPLACED WITH UNCASED 12" MILL WRAP (PRITEC) COATED PRETESTED STEEL PIPE.
2025-03-31 10:13 | NO | YES | YES | 20210038 | 35926 | 2021-04-02 17:38 | SUPPLEMENTAL FINAL | 4499 | CENTERPOINT ENERGY RESOURCES CORPORATION | 1111 LOUISIANA ST | HOUSTON | TX | 77002 | 2021-03-05 18:00 | CENTRAL | NO | 2021 | 18700 GLEANNLOCH LAKES BLVD | SPRING | HARRIS | TX | 77379 | 30.0305 | -95.5656 | [5 empty] | YES |  |  |  | 2021-03-05 19:02 | 1299703 | 1299790 | NATURAL GAS |  | 2975.564 | 2171 | NO | [5 empty] | 0 | YES | 3 | 0 | 0 | 0 | 0 | 3 | YES | 2021-03-05 17:40 | OPERATOR/CONTRACTOR |  | 2171 | NO | 10 | 2021-03-05 10:28 | YES | OPERATOR | 2021-03-05 17:40 | 2021-03-05 11:03 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1998 | UNKNOWN |  |  |  |  | 2.25 | UNKNOWN | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1.5 | [7 empty] | CLASS 3 LOCATION | 75000 | 81234.562643727075 | 166000 | 179799.165318115926 | 45000 | 48740.737586236245 | 0 | 0 |  | 5.1102 | 15206 | 10785.6511627906976744186046511627906977 | 11094 | 7869 | 312300 | 145555.9375938197332491694352159468438538 | 328429.1167108699436744186046511627906977 | 0 | 0 | 262 | 3 | 0 | 262 | 0 | 45 | 45 | 60 | 192.619(A)(1) | 1998-05-01 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | RELEASE DID NOT EXCEED THE THRESHOLD LIMITS OF THE SYSTEM | [12 empty] | YES | 9 | 0 | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [5 empty] | YES | [6 empty] | CONTRACTOR | DIRECTIONAL DRILLING | CABLE TV | NO | [5 empty] | YES | 40 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [143 empty] | YES | [25 empty] | YES | LESLIE J DAVENPORT | COMPLIANCE COORDINATOR | leslie.davenport@centerpointenergy.com | 713-539-5395 | 713-967-7307 | LESLIE J DAVENPORT | leslie.davenport@centerpointenergy.com | 713-539-5395 | STEVE YARBROUGH | DIRECTOR REGIONAL OPERATIONS GAS | 713-207-5700 | steve.yarbrough@centerpointenergy.com | A CABLE CONTRACTOR, TEXAS BEST LLC, (WORKING UNDER EXPIRED LOCATE TICKETS), CONDUCTING DIRECTIONAL DRILLING OPERATIONS DAMAGED CENTERPOINT ENERGY'S 2" INCH PLASTIC MAIN AT APPROXIMATELY 10:28AM ON MARCH 5, 2021. ESCAPING GAS FROM THIRD-PARTY DAMAGE IGNITED AS CENTERPOINT ENERGY EMPLOYEES WERE WORKING IN A REMOTE BELL-HOLE TO STOP THE LEAK. SIX EMPLOYEES WERE INJURED, WITH THREE REQUIRING HOSPITALIZATION. AN INVESTIGATION OF THE IGNITION EVENT IS UNDERWAY." AFTER SUBSEQUENT INVESTIGATION IT WAS DETERMINED THAT GAS ESCAPING FROM THE DAMAGED TWO INCH PLASTIC MAIN MIGRATED TO THE REMOTE BELL-HOLE. WHILE EXPANDING THE BELL-HOLE CENTERPOINT CREW UTILIZING MECHANICAL EXCAVATION DAMAGED A (120 VOLT) STREET LIGHT CABLE WHICH RESULTED IN IGNITION OF MIGRATING GAS. THE RADIANT HEAT FROM THE BURNING GAS MELTED THE ALREADY EXPOSED SIX INCH PLASTIC MAIN THAT WAS IN THE BELL-HOLE.
2025-03-31 10:13 | NO | YES | NO | 20210039 | 35172 | 2021-04-14 13:49 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2021-03-16 23:24 | PACIFIC | YES | 2021 | 2965 LAUREL CANYON BLVD | STUDIO CITY | LOS ANGELES | CA | 91604 | 34.1249 | -118.3783 | YES | [8 empty] | 2021-03-16 23:24 | 1300507 | 1300701 | NATURAL GAS |  | 1252.6 | 237.3 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-03-16 16:04 | NO |  |  | 2021-03-16 16:30 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 36 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1945 | UNKNOWN |  |  |  |  | 22 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 400000 | 433251.0007665444 | 800000 | 866502.0015330888 | 0 | 0 |  | 4.1 | 5136 | 3642.976744186046511627906976744186046512 | 973 | 690.151162790697674418604651162790697674 | 1206109 | 542327.1092150603774086378737541528239202 | 1304086.13020660994418604651162790697675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 190 | 204 | 192.619(C) | 2008-01-18 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE LANDOWNER | YES | [9 empty] | CONTRACTOR | AUGER | DRIVEWAY | NO | [5 empty] | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | EDWIN BAIRES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | ebaires2@socalgas.com | 2133261831 |  |  |  |  | EDWIN BAIRES | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 2133261831 | ebaires2@socalgas.com | ON 3-16-21, SOCALGAS WAS NOTIFIED OF THIRD PARTY DAMAGE AT 2965 LAUREL CANYON BLVD STUDIO CITY, CA. THE THIRD PARTY DAMAGED A 22-INCH GAS LINE WITH AN AUGER. GAS WAS CONTROLLED AT 00:31 ON 3/17/21. THERE WERE NO REPORTED FATALITIES OR INJURIES DUE TO THE GAS RELEASE. THE INVESTIGATION SHOWED THE THIRD PARTY WAS WAS AUGERING FOR NEW DRIVEWAY FOUNDATION ON AN EXPIRED USA TICKET. THIS INCIDENT WAS REPORTED TO THE DOT AND CPUC DUE TO THE RELEASE OF GAS AND DAMAGES EXCEEDING $50,000. FOR PART A QUESTION 13, "NO" WAS SELECTED AS THE THIRD PARTY THAT CAUSED THE INCIDENT CONTACTED EMERGENCY RESPONDERS. THE FIRE DEPARTMENT WAS ALREADY ON SCENE AT THE TIME SOCALGAS PERSONNEL FIRST ARRIVED.
2025-03-31 10:13 | NO | YES | NO | 20210040 | 37037 | 2021-04-14 19:04 | SUPPLEMENTAL FINAL | 12684 | MONTANA - DAKOTA UTILITIES CO | 400 NORTH FOURTH STREET | BISMARCK | ND | 58501 | 2021-03-19 17:20 | MOUNTAIN | YES | 2021 | UNINCORPORATED COMMUNITY OF HINSDALE | HINSDALE | VALLEY | MT | 59241 | 48.3929 | -107.0867 |  |  |  | YES | [5 empty] | 2021-03-19 17:47 | 1300840 | 1300868 | NATURAL GAS |  | 11437.5 | 2.1 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-02-23 14:52 | YES | OPERATOR | 2021-03-19 17:30 | 2021-02-23 10:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 33 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 2 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | UNKNOWN | [6 empty] | LEAK |  |  | OTHER | MULTIPLE CORROSION LEAKS | [5 empty] | CLASS 3 LOCATION | 0 | 0 | 624684 | 676612.420407120054924 | 68174 | 73841.134315645994814 | 49420 | 53528.16114470656062 | 3RD PARTY INVESTIGATION. | 4.031 | 46105 | 32702.3837209302325581395348837209302326 | 8 | 5.67441860465116279069767441860465116279 | 788391 | 363241.9829859078422853289036544850498339 | 836689.7740070074940789302325581395348838 | 11 | 0 | 113 | 0 | 0 | 113 | 11 | 10 | 10 | 20 | 192.619(A)(1) | 1991-06-05 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION |  | YES |  | YES |  |  |  |  | DIRECT CURRENT | UNKNOWN, MULTIPLE POSSIBLE SOURCES WERE INVESTIGATED, BUT NO SOURCE WAS DISCOVERED. METALLURGICAL INVESTIGATION OF FAILED PIPE SAMPLES DETERMINED IT WAS DC INDUCED. | YES | YES |  |  | YES | YES | 1962 | YES | YES | YES |  |  | 2020 |  |  |  |  | NO | COAL TAR |  | NO | [19 empty] | 2021-03-17 | NO | [227 empty] | DANNY L. HOOD | MANAGER POLICY AND PROCEDURE | danny.hood@mdu.com | 701-516-2749 |  | DANNY L. HOOD | danny.hood@mdu.com | 701-516-2749 | DANNY L. HOOD | MANAGER POLICY AND PROCEDURE | 701-516-2749 | danny.hood@mdu.com | MONTANA-DAKOTA UTILITIES (MDU) RESPONDED TO AN OUTSIDE GAS ODOR REPORTED BY THE GENERAL PUBLIC ON FEBRUARY 6, 2021. A GRADE 2 LEAK WAS DISCOVERED ON A SERVICE LINE DURING THE LEAK INVESTIGATION. THE CORROSION LEAK WAS EXCAVATED AND REPAIRED ON FEBRUARY 11, 2021. MDU RESPONDED TO ANOTHER OUTSIDE GAS ODOR REPORTED BY THE PUBLIC ON FEBRUARY 23, 2021. MDU FOUND A CORROSION LEAK. THE EXTENT OF THE CORROSION DID NOT ALLOW FOR A PERMANENT REPAIR. A TEMPORARY LEAK CLAMP WAS INSTALLED, AND THE EXCAVATION WAS LEFT OPEN TO AVOID MIGRATION. BASED ON THE SEVERITY OF THE CORROSION FOUND ON FEBRUARY 23, 2021, MDU CORROSION CONTROL PERSONNEL INVESTIGATED THE CONDITION OF THE HINSDALE DISTRIBUTION SYSTEM ON MARCH 1, 2021. BASED ON THE RESULTS OF THE INVESTIGATION THAT CONCLUDED ON MARCH 3, 2021, AN EXPANDED INVESTIGATION WAS CONDUCTED ON MARCH 9, 2021. BASED ON THE RESULTS OF THE SECOND INVESTIGATION, MDU CONDUCTED A LEAK SURVEY OF THE HINSDALE DISTRIBUTION SYSTEM ON MARCH 17 AND 18, 2021. THE LEAK SURVEY IDENTIFIED APPROXIMATELY 40 UNDERGROUND LEAKS OF WHICH 12 WERE GRADE 1. AS GRADE 1 LEAKS WERE IDENTIFIED, MDU CREWS ESTABLISHED SAFETY PERIMETERS, EXCAVATED THE SITES, AND MADE TEMPORARY REPAIRS. ON MARCH 19, 2021, AT 5:20 P.M. MST, MDU MADE THE DECISION TO SHUT IN AND REPLACE THE ENTIRE STEEL DISTRIBUTION SYSTEM IN THE COMMUNITY, WHICH WOULD EXCEED $50,000, AT WHICH TIME MDU NOTIFIED THE NRC (REPORT NUMBER 1300840). THE REPLACEMENT PROJECT STARTED MARCH 22, 2021, AND THE SYSTEM WAS PLACED BACK INTO NORMAL SERVICE MARCH 29, 2022. THE COST OF THE EMERGENCY RESPONSE BY MDU WAS $68,174.00. COST TO REPLACE MAINS WAS $232,154.33, COST TO REPLACE SERVICES WAS $392,529.51. ROAD/STREET MAINTENANCE WAS COMPLETED JULY 1, 2021. SEWER INVESTIGATIONS WERE CONFIRMED CLEAR ON OCTOBER 10, 2021, COST OF CROSS BORE INVESTIGATION IS INCLUDED IN THE COST OF THE MAIN AND SERVICE INSTALL. MDU CORROSION CONTROL PERSONAL ALONG WITH A 3RD PARTY STARTED INVESTIGATION OF THE CAUSE OF THE EXTENSIVE CORROSION IN HINSDALE ON MARCH 30, 2021. THE FOLLOWING POTENTIAL CAUSES OR CONTRIBUTING FACTORS FOR THE CORROSION WERE INVESTIGATED: ISSUES WITH THE PIPING COATINGS, SOIL CONDITIONS, ISSUES WITH THE CATHODIC PROTECTION SYSTEMS, OR POTENTIAL STRAY CURRENT SOURCES IN AND AROUND TOWN. THROUGH INVESTIGATION IT SHOWED NO ISSUES WERE NOTED WITH THE PIPE COATING, SOIL CONDITIONS, OR ENVIRONMENTAL CONDITIONS THAT WOULD HAVE SIGNIFICANTLY AFFECTED THE RATE OF CORROSION. THE CATHODIC PROTECTION SYSTEM INCLUDING RECTIFIER, REMOTE MONITORING UNIT (RMU), BURIED ANODE BEDS AND CABLES, AND TEST STATIONS WERE CONFIRMED TO BE PROPERLY INSTALLED AND IN PROPER WORKING ORDER. NO EVIDENCE SHOWED THAT THE CORROSION WAS BEING DRIVEN BY A MALFUNCTION IN THE CATHODIC PROTECTION SYSTEM AS INSPECTED DURING THE INVESTIGATION. METALLURGICAL ANALYSIS OF A FAILED MUELLER AUTOPERF TRANSITION TEE, ALONG WITH A SAMPLE FROM A LEAK ON A HINSDALE COPPER WATER SERVICE LINE WERE EXAMINED. THE RATE OF CORROSION OF THE STEEL PIPE AND HINSDALE OWNED COPPER WATER LINES, THAT EXPERIENCED A SIMILAR SIGNIFICANT LOSS OVER A PERIOD OF A FEW MONTHS, WAS DETERMINED TO BE CONSISTENT WITH AN ELECTRICALLY DRIVEN, DC CORROSION EVENT. POTENTIAL SOURCES OF STRAY CURRENT INCLUDING TELECOMMUNICATIONS, POWER, COMMERCIAL/INDUSTRIAL PROCESSES AND PIPELINES OF OTHERS IN THE VICINITY WERE INVESTIGATED THROUGH FIELD TESTING, CURRENT MAPPING, INTERVIEWS, AND LOGGING OF PIPE TO SOIL POTENTIALS FROM MAY 2021 THROUGH JUNE 2022. THROUGH THE INVESTIGATION IT WAS UNDETERMINED ON A SOURCE OF STRAY CURRENT WHICH WOULD HAVE RESULTED IN THE CORROSION FAILURE IN HINSDALE. THE COST OF THE INVESTIGATION BY THE 3RD PARTY INVESTIGATOR (AEI) WAS $49,420.27. TOTAL COST OF THE INCIDENT INCLUDING LOST GAS WAS $788,391.
2025-03-31 10:13 | NO | YES | YES | 20210041 | 35783 | 2021-05-12 18:04 | SUPPLEMENTAL FINAL | 12408 | DTE GAS COMPANY | 1 ENERGY PLAZA | DETROIT | MI | 48226 | 2021-04-09 21:27 | EASTERN | YES | 2021 | 14201 2ND AVENUE | HIGHLAND PARK | WAYNE | MI | 48203 | 42.3411 | -83.0608 | [5 empty] | YES |  |  |  | 2021-04-09 23:36 | 1302382 | 1302497 | NATURAL GAS |  | 98.6 | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | NO | [5 empty] | 0 | YES | 2021-04-09 21:27 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 98.6 | NO | 22 | 2021-04-09 21:27 |  |  |  | 2021-04-09 21:51 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | 1977 | UNKNOWN | MULTI-FAMILY RESIDENTIAL | NO |  | NO |  |  |  | UNKNOWN | [10 empty] | LEAK |  |  | OTHER | VEHICULAR DAMAGE | [5 empty] | CLASS 3 LOCATION | 1000000 | 1083127.501916361 | 1000 | 1083.127501916361 | 5368 | 5814.228430287025848 | 0 | 0 |  | 2.25 | 222 | 157.465116279069767441860465116279069767 | 0 | 0 | 1006590 | 451601.2692555069392289169435215946843854 | 1090182.32296484345661544186046511627907 | 0 | 0 | 22 | 0 | 1 | 22 | 0 | 10 | 10 | 10 | 192.619(A)(2) | 1977-06-01 | PRESSURE DID NOT EXCEED MAOP | OTHER | GAS IS ODORIZED UPSTREAM OF THE METER ASSEMBLY |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | YES | UNKNOWN | PASSENGER CAR | PARKING LOT | 50 | NO | [118 empty] | YES | [23 empty] | FRENAE F SMITH | MANAGER OF CODES AND STANDARDS | frenae.smith@dteenergy.com | 13134601681 |  | FRENAE F SMITH | frenae.smith@dteenergy.com | 13134601681 | FRENAE F SMITH | MANGER OF CODES AND STANDARD | 13134601681 | frenae.smith@dteenergy.com | DTE GAS WAS CONTACTED BY EMERGENCY RESPONDERS OF A GAS-RELATED INCIDENT AT 14201 2ND AVENUE IN HIGHLAND PARK, MICHIGAN ON APRIL 9TH, 2021 AT 21:27 AND ARRIVED ON-SITE AT 21:57. THE ADDRESS WAS CORRECTED FROM THE ORIGINAL CALLER WHICH WAS 14330 3RD AVENUE IN HIGHLAND PARK, MICHIGAN. A DRIVER RAN OFF THE ROAD (FROM A PARKING LOT) APPROXIMATELY 50 FEET AND HIT A BANK OF METERS LOCATED IN A NON-VEHICULAR LOCATION. THE CAR IGNITED THE BLOWING GAS. THE DRIVER WAS TAKEN TO THE HOSPITAL AND LATER DIED OF HIS INJURIES.
2025-03-31 10:13 | NO | NO | NO | 20210042 | 35283 | 2021-05-14 08:01 | ORIGINAL FINAL | 2596 | COLUMBIA GAS OF OHIO INC | 290 W NATIONWIDE BLVD | COLUMBUS | OH | 43215 | 2021-04-16 22:30 | EASTERN | YES | 2021 | 6500 DORR ST. | TOLEDO | LUCAS | OH | 43607 | 41.6538 | -83.6954 | [5 empty] | YES |  |  |  | 2021-04-16 22:58 | 1302894 | 1302916 | NATURAL GAS |  | 11699 | 49 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-04-16 22:30 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-04-16 15:05 | 2021-04-16 15:05 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 18 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1970 | UNKNOWN |  |  |  |  | 10 | UNKNOWN | UNKNOWN | STEEL |  | OTHER | UNKNOWN | 0.196 | [6 empty] | MECHANICAL PUNCTURE | 2 | 26 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 4470 | 4841.57993356613367 | 3700 | 4007.5717570905357 | 0 | 0 |  | 3.28 | 38373 | 27218.0581395348837209302325581395348837 | 161 | 114.197674418604651162790697674418604651 | 46704 | 28948.9901093394242201328903654485049834 | 36181.4075046101577420930232558139534884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 50 | 58 | 192.619(A)(2) | 1971-04-01 | PRESSURE DID NOT EXCEED MAOP | ODORIZED BY OTHERS |  |  | YES | NO |  |  |  |  | OTHER | OHIO DEPARTMENT OF TRANSPORTATION FIELD SUPERVISOR |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | NO | [5 empty] | NO |  | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | ROB SMITH | MANAGER OF OPERATIONS COMPLIANCE | rrsmith@nisource.com | 6144605491 |  | ROB SMITH | rrsmith@nisource.com | 6144605491 | ROB SMITH | MANAGER OF OPERATIONS COMPLIANCE | 6144605491 | rrsmith@nisource.com | ON APRIL 16, 2021, A CONTRACTOR FOR THE CITY OF TOLEDO WAS EXCAVATING FOR ROADWAY IMPROVEMENTS. THE EXCAVATOR STRUCK AND DAMAGED A COLUMBIA 10" STEEL MAIN LINE. THE EXCAVATOR DID NOT HAVE A VALID ONE CALL EXCAVATION TICKET. COLUMBIA RESPONDED, ESTABLISHED A PERIMETER, AND USED SQUEEZE OFF JACKS AWAY FROM THE DAMAGE TO STOP THE FLOW OF GAS IN THE MAIN LINE. THE LINE WAS THEN REPAIRED AND PLACED BACK INTO SERVICE. PLEASE CONSIDER THIS A FINAL REPORT.
2025-03-31 10:13 | NO | YES | NO | 20210044 | 35592 | 2021-05-14 14:26 | SUPPLEMENTAL FINAL | 22182 | WASHINGTON GAS LIGHT CO | 1000 MAINE AVENUE, SW | WASHINGTON | DC | 20024 | 2021-04-14 09:03 | EASTERN | NO | 2021 | INTERSECTION OF OLD GEORGETOWN ROAD & EXECUTIVE BLVD | NORTH BETHESDA | MONTGOMERY | MD | 20852 | 39.0485 | -77.1192 | YES | [8 empty] | 2021-04-14 17:15 | 1302685 | 1302835 | NATURAL GAS |  | 1754 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-04-14 09:03 |  |  |  | 2021-04-14 09:12 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 240 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2020 | 2018 |  |  |  |  | 12 | ASTM D2513 | CENTRAL PLASTICS | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | 2708 | MECHANICAL PUNCTURE | 1.6 | 0.4 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 209930 | 227380.95647730166473 | 46038 | 49865.023933225427718 | 383 | 414.837833233966263 | ADMIN COSTS | 2.0182 | 3540 | 2510.930232558139534883720930232558139535 | 0 | 0 | 259891 | 117321.5409688230143564053156146179401993 | 280171.7484763191982458837209302325581395 | 72 | 0 | 3 | 0 | 0 | 1 | 39 | 20 | 20 | 25 | 192.619(A)(2) | 2020-04-17 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.5 |  | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE 3" DIAMETER HOLE IN THE 12" HD PLASTIC @ 20PSI PORTION OF THE SYSTEM, WOULD NOT HAVE BEEN ENOUGH DAMAGE TO DROP THE FACILITIES TO AN PRESSURE THAT WOULD CAUSE AN ALARM. | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ELECTRIC | YES | 21233464 | N/A |  | CONTRACT LOCATOR | YES | YES | 40 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | RICHARD FITZPATRICK | SUPERVISOR DOT PIPELINE SAFETY | richardfitzpatrick@washgas.com | (703)639-7825 |  | RICHARD FITZPATRICK | supervisor dot pipeline safety | (703)639-7825 | SHANNON B. MALONEY | MANAGER PIPELINE SAFETY COMPLIANCE QUALITY | (703)750-5558 | smaloney@washgas.com | WASHINGTON GAS WAS NOTIFIED BY MONTGOMERY COUNTY FIRE BOARD ON 4/14/21 0903 HRS OF A DAMAGED FACILITY AT THE INTERSECTION OF OLD GEORGETOWN RD. & EXECUTIVE BLVD. NORTH BETHESDA, MD. WASHINGTON GAS ARRIVED AT 0912 HRS AND IDENTIFIED THE DAMAGED FACILITIES TO BE 12" HD PLASTIC MAIN. ANCHOR CONSTRUCTION WAS EXCAVATING WITH AN BACKHOE AND DAMAGED WG FACILITIES. WASHINGTON GAS IDENTIFIED AND OPERATED SEVEN CRITICAL VALVES TO DISCONTINUE THE FLOW OF GAS. DUE TO THE DEPTH (20') A CUSTOM SHORING BOX WAS DESIGNED AND BUILT SPECIFICALLY FOR THIS SITE, WHICH TOOK ADDITIONAL TIME. WASHINGTON GAS HAD TO INSTALL BYPASSES AROUND THE FACILITIES TO INTRODUCE GAS BACK TO CUSTOMERS. THE CONTRACTOR ANCHOR CONSTRUCTION WAS FOUND AT FAULT FOR NOT FOLLOWING USING SOFT DIGGING METHOD AS REQUIRED. THE INTERSECTION MENTIONED ABOVE WAS ALREADY CLOSED DUE TO ON-GOING CONSTRUCTION AND DID NOT INTERRUPT ANY ADDITIONAL TRAFFIC. AS OF 04/26/2021 ALL CUSTOMERS AFFECTED HAVE HAD GAS REINTRODUCED AND REPAIRS ARE COMPLETE. WASHINGTON GAS WILL PROVIDE ADDITIONAL INFORMATION AS IT IS RECEIVED IN SUPPLEMENTAL RESPONSES. ADDITIONALLY, THE BELOW REQUIRED QUESTIONS HAVE BEEN ANSWERED AS $0, ARE NOT AVAILABLE AT THIS TIME AND WILL BE SUBMITTED IN A SUPPLEMENTAL. PART D: QUESTION 2.B PART D: QUESTION 2.C PART D: QUESTION 2.D
2025-03-31 10:13 | NO | YES | NO | 20210045 | 35522 | 2021-05-21 11:34 | SUPPLEMENTAL FINAL | 15952 | PUBLIC SERVICE ELECTRIC & GAS CO | 80 PARK PLAZA M/C - T18 | NEWARK | NJ | 07102-4194 | 2021-05-11 07:39 | EASTERN | YES | 2021 | KINDERKAMACK | HILLSDALE | BERGEN | NJ | 07642 | 41.0149 | -74.0349 | [5 empty] | YES |  |  |  | 2021-05-11 10:53 | 1304758 | 1304928 | NATURAL GAS |  | 27000 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-05-11 07:39 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 27000 | NO | 8 | 2021-05-11 07:39 | YES | OPERATOR | 2021-05-11 07:39 | 2021-05-11 08:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER SOIL |  | 14 | NO | NO | [11 empty] | MUNICIPALLY OWNED |  | OTHER | PURGE FITTING | 2012 | UNKNOWN | [7 empty] | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  |  | UNKNOWN | UNKNOWN | MECHANICAL PUNCTURE | 0.5 | 0.5 | [7 empty] | CLASS 4 LOCATION | 0 | 0 | 500000 | 541563.7509581805 | 5000 | 5415.637509581805 | 21000 | 22745.677540243581 | ENVIRONMENTAL CLEANUP COSTS | 1 | 27000 | 19151.1627906976744186046511627906976744 | 0 | 0 | 553000 | 253678.9823604198485980066445182724252492 | 588876.2287987035604186046511627906976744 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 15 | 15 | 15 | 192.619(A)(1) | 2002-04-10 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | EXCAVATION DAMAGE | OPERATOR/CONTRACTOR EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY OPERATOR'S CONTRACTOR (SECOND PARTY) | [14 empty] | NO | YES | COUNTY ROAD | [12 empty] | CONTRACTOR | TRENCHER | NATURAL GAS | YES | 211092839 |  |  | UTILITY OWNER | YES | YES | 10 | MISCELLANEOUS ROOT CAUSES | ROOT CAUSE NOT LISTED (COMMENT REQUIRED) | DATA NOT COLLECTED | [168 empty] | YES | ROGER GUNNELS | PRINCIPAL REGULATORY SPECIALIST | roger.gunnels@pseg.com | 973-513-2474 |  | ROGER GUNNELS | roger.gunnels@pseg.com | 973-513-2474 | CHRIS LAROSSA | MANAGER REGULATORY POLICY AND PROCEDURE | 973-896-7617 | christopher.larossa@pseg.com | ON TUESDAY 5/11/2021 AT 0739 PSE&G WAS NOTIFIED OF AN ACCIDENTAL IGNITION OF GAS OCCURRING AT DWIGHT AND KINDERKAMACK RD. IN HILLSDALE. CONTRACTORS WHILE EXCAVATING AND PERFORMING ZIPPING OPERATIONS, THE ZIPPER MACHINE CONTACTED A 1 PURGE FITTING TO A 4 PL 15# MAIN CAUSING AN ACCIDENTAL IGNITION OF GAS. POLICE AND FD ARRIVED AT THE SCENE, FD EVACUATED 4 HOMES AND 8 OCCUPANTS. PSE&G ARRIVED ON SCENE AT 0800, THE FIRE IS OUT AND THE SCENE WAS MADE SAFE AT 0830. DURING THE FIRE THE ZIPPING MACHINE WAS DESTROYED AND IS CURRENTLY AWAITING REMOVAL FROM THE SITE. REPAIRS ARE UNDERWAY AND WERE COMPLETED AT 1745 5/11/21. AN INVESTIGATION IS UNDERWAY REGARDING THIS INCIDENT. ROOT CAUSE WAS DETERMINED TO BE THAT THE CONTRACTOR FAILED TO HAND DIG WITHIN 2 FEET OF THE MARKED FACILITIES, WHICH VIOLATES THE NJUFPA LAW. UTILITY FOLLOW ON ACTIONS: REVIEW ROOT CAUSE WITH ALL GAS OPERATIONS PERSONNEL. *TO BE REVIEWED WITH ALL GAS OPERATIONS/CONSTRUCTION PERSONNEL. REVIEW EXPECTATIONS WITH STREET INSPECTORS TO ENSURE HAZARD RECOGNITION IS DISCUSSED DURING TAILBOARDS. *TO BE REVIEWED WITH ALL STREET INSPECTORS. *REVIEW NJFUPA LAW WITH ALL EXCAVATORS. TO BE REVIEWED WITH ALL CONTRACTORS WORKING ON PSE&G GAS FACILITIES.
2025-03-31 10:13 | NO | NO | NO | 20210046 | 35320 | 2021-05-21 20:10 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2021-04-22 23:16 | PACIFIC | NO | 2021 | 7810 STEWART AND GRAY ROAD | DOWNEY | LOS ANGELES | CA | 90241 | 33.9369 | -118.1481 | [5 empty] | YES |  |  |  | 2021-04-22 23:16 | 1303305 | 1303369 | NATURAL GAS |  | 5825.38 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-04-22 10:55 |  |  |  | 2021-04-22 10:55 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 38 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2002 | 2001 |  |  |  |  | 6 | ASTM D2513 | UPONOR | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 13.5 |  |  | UNKNOWN | MECHANICAL PUNCTURE | 3 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 1900 | 2057.9422536410859 | 40000 | 43325.10007665444 | 0 | 0 |  | 3.116 | 18152 | 12875.2558139534883720930232558139534884 | 0 | 0 | 60052 | 30706.660482999501588704318936877076412 | 58258.2981442490142720930232558139534884 | 0 | 0 | 40 | 0 | 0 | 40 | 0 | 36 | 36 | 40 | 192.619(A)(2) | 2002-01-18 | PRESSURE DID NOT EXCEED MAOP | NONE |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TRAFFIC SIGNAL | YES | A202720873 | DIG ALERT |  | UTILITY OWNER | YES | NO |  | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | LINDA HOANG | PIPELINE SAFETY AND COMPLIANCE ADVISOR | lvhoang@socalgas.com | 213-500-3442 |  | LINDA HOANG | lvhoang@socalgas.com | 213-500-3442 | LINDA HOANG | PIPELINE SAFETY AND COMPLIANCE ADVISOR | 213-500-3442 | lvhoang@socalgas.com | ON 4-22-2021, A THIRD-PARTY CONTRACTOR DAMAGED A 6-INCH PLASTIC GAS MAIN AT 7810 STEWART AND GRAY ROAD DOWNEY, CA WHILE BORING TO INSTALL AN ELECTRICAL CONDUIT FOR A TRAFFIC SIGNAL LIGHT. SOCALGAS CREW RESPONDED AND CONTROLLED THE RELEASE OF GAS. THERE WERE NO OUTAGES DUE TO THE INCIDENT. THE FIRE DEPARTMENT SHUT OFF THE GAS TO SOME OF OUR CUSTOMERS OUT OF AN ABUNDANCE OF CAUTION. THIS INCIDENT WAS REPORTED TO THE CPUC AND DOT WHEN SOCALGAS BECAME AWARE OF MEDIA COVERAGE AND DUE TO GAS RELEASE EXCEEDING 3,000,000 CUBIC FEET.
2025-03-31 10:13 | NO | YES | NO | 20210047 | 35687 | 2021-05-21 21:53 | SUPPLEMENTAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2021-04-21 21:09 | CENTRAL | YES | 2021 | 305 PARKSIDE DR. | SHOREWOOD | WILL | IL | 60404 | 41.5155 | -88.2353 | [5 empty] | YES |  |  |  | 2021-04-22 07:22 | 1303219 | 1303359 | NATURAL GAS |  | 25.2 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-04-21 20:55 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 25.2 | NO | 2 | 2021-04-21 20:55 |  |  |  | 2021-04-21 21:09 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2003 | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 7 |  |  | 2406 | LEAK |  |  | OTHER | MELTED METERSET AND RISER | [5 empty] | CLASS 3 LOCATION | 360000 | 389925.90068988996 | 500 | 541.5637509581805 | 676 | 732.194191295460036 | 0 | 0 |  | 5.3 | 134 | 95.04651162790697674418604651162790697674 | 0 | 0 | 361310 | 162111.0895875289388376345514950166112957 | 391294.705143771507512744186046511627907 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 55.5 | 57 | 60 | 192.619(A)(2) | 2003-09-04 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 2.5 |  | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER INCIDENT CAUSE | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | ALL OTHER CAUSES | UNKNOWN | [232 empty] | UNKNOWN |  | INVESTIGATION COMPLETE, CAUSE OF INCIDENT UNKNOWN | EMERGENCY RESPONDERS AND INSURANCE COMPANY INVESTIGATORS COULD NOT DETERMINE CAUSE OF THE FIRE, ONLY THAT IT ORIGINATED IN THE VICINITY OF THE METER SET. THEIR REPORT WILL STATE CAUSE IS UNKNOWN. THE SERVICE LINE WAS PRESSURE TESTED POST INCIDENT AND NO LEAKS WERE FOUND. METER SET WAS TOO DAMAGED FROM THE FIRE TO TEST. | [45 empty] | LETICIA QUEZADA | DIR COMPLIANCE AND QA | lquezad@southernco.com |  |  | LETICIA QUEZADA | lquezad@southernco.com |  | LETICIA QUEZADA | DIR COMPLIANCE AND QA | 630388-2316 | lquezad@southernco.com | SUPPLEMENTAL REPORT CREATED TO CHANGE TIME IN PART A, QUESTION 18 TO REFLECT CENTRAL TIME ZONE INSTEAD OF EASTERN TIME ZONE, PER PHMSA'S REQUEST. ----------- RELEASE OF NATURAL GAS INTO THE ATMOSPHERE. THE RELEASE WAS DUE TO FIRE DAMAGE TO THE METER SET. EMERGENCY RESPONDER INVESTIGATORS HAVE NOT BEEN ABLE TO DETERMINE THE CAUSE OF THE FIRE AND WILL BE REPORTED AS UNKNOWN ON THEIR REPORTS. IT IS UNKNOWN IF THE DAMAGE TO THE METER SET IS SECONDARY IGNITION. THE SERVICE LINE WAS LEAK-TESTED AFTER THE INCIDENT AND NO LEAKS WERE FOUND. THE METER SET WAS TOO DAMAGED BY THE FIRE TO BE ABLE TO TEST.
2025-03-31 10:13 | NO | YES | NO | 20210048 | 35344 | 2021-05-28 17:47 | ORIGINAL FINAL | 18484 | SOUTHERN CALIFORNIA GAS CO | 555 WEST FIFTH STREET | LOS ANGELES | CA | 90013 | 2021-04-29 22:55 | PACIFIC | NO | 2021 | 1101 STANFORD STREET | SAN MONICA | LOS ANGELES | CA | 90403 | 34.0407 | -118.4756 |  | YES | [5 empty] | YES | PRESSURE CONTROL FIITING | 2021-04-29 23:05 | 1303844 | 1303995 | NATURAL GAS |  | 24982.92 | 2.06 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 12 | 2021-04-29 11:50 |  |  |  | 2021-04-29 11:59 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 40 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1930 | UNKNOWN |  |  |  |  | 16 | UNKNOWN | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.25 | [6 empty] | MECHANICAL PUNCTURE | 4 | 4 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 404358 | 437971.270419895901238 | 50000 | 54156.37509581805 | 0 | 0 |  | 6 | 149898 | 106323 | 12 | 8.51162790697674418604651162790697674419 | 604268 | 302187.3849542210888442657807308970099668 | 598459.1571436209279821860465116279069767 | 0 | 0 | 57 | 0 | 0 | 57 | 3 | 36.3 | 38 | 43 | 192.619(A)(3) | 1970-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | B210960649 | USA SOUTH |  | UTILITY OWNER | YES | YES | 4 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | BEATRIZ CARDENAS | PIPELINE SAFETY COMPLIANCE ADVISOR | bcardenas@sdge.com | 8582769135 |  | BEATRIZ CARDENAS | bcardenas@sdge.com | 8582769135 | AUSTIN WALKER | SENIOR PIPELINE SAFETY COMPLIANCE ADVISOR | 8186328407 | awalker4@socalgas.com | ON 4-29-2021, A THIRD PARTY CONTRACTOR DAMAGED A 16-INCH STEEL GAS MAIN AT 1101 STANFORD STREET, SANTA MONICA, CA WHILE BORING TO INSTALL TELECOMMUNICATION CONDUIT. SOCALGAS CREW RESPONDED AND CONTROLLED THE RELEASE OF GAS. THERE WERE NO INJURIES OR FURTHER DAMAGE RESULTING FROM THIS INCIDENT. INVESTIGATION OF THE INCIDENT SHOWED THERE WAS A VALID USA TICKET. HOWEVER, THE CONTRACTOR'S EXCAVATION PRACTICES WERE INADEQUATE AS IT FAILED TO POT-HOLE THE 16-INCH MAIN. THIS INCIDENT WAS REPORTED TO DOT AND CPUC DUE TO GAS RELEASE AND ESTIMATED PROPERTY DAMAGE OF $122,000 OR MORE. FOR ANY FURTHER QUESTIONS, PLEASE CONTACT BEATRIZ CARDENAS @ 858-276-9135.
2025-03-31 10:13 | NO | YES | NO | 20210049 | 39601 | 2021-06-03 15:41 | SUPPLEMENTAL FINAL | 603 | CENTERPOINT ENERGY RESOURCES CORP. | 10825 E GEDDES AVE SUITE 410 | CENTENNIAL | CO | 80112 | 2021-05-05 10:35 | CENTRAL | YES | 2021 | 12618 MEADOWS EDGE LN | LITTLE ROCK | PULASKI | AR | 72211 | 34.7302 | -92.4188 | [5 empty] | YES |  |  |  | 2021-05-05 14:25 | 1304348 | 1304463 | NATURAL GAS |  | 66 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-05-05 12:38 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 15 | NO | 20 | 2021-05-05 10:35 | YES | OPERATOR | 2021-05-05 13:26 | 2021-05-05 10:47 | 2021-05-05 13:26 | NO | PUBLIC PROPERTY | UNDERGROUND | OTHER | CONCRETE SIDEWALK | 30 | NO | NO | [11 empty] | OTHER | LDC | MAIN |  | UNKNOWN | UNKNOWN |  |  |  |  | 2 | ASTM D2513 | UNKNOWN | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11.5 |  |  | 2406 | MECHANICAL PUNCTURE | 1 | 1 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 11414 | 12362.817306873344454 | 660 | 714.86415126479826 | 200000 | 216625.5003832722 | HOME HAD EXTENSIVE DAMAGE FROM FIRE IN GARAGE. | 4.41 | 291 | 206.406976744186046511627906976744186047 | 0 | 0 | 212365 | 95327.1073483584968384451827242524916944 | 229909.588818154528760511627906976744186 | 0 | 0 | 20 | 0 | 0 | 1 | 0 | 40 | 40 | 60 | 192.619(A)(2) | 2002-04-08 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 0.3 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [8 empty] | NO | NO | 18” – 36” |  | CONTRACTOR | BORING | TELECOMMUNICATIONS | YES | 2109281119 |  | YES | CONTRACT LOCATOR | YES | YES | 4 | EXCAVATION ISSUE | IMPROPER EXCAVATION PRACTICE NOT LISTED ABOVE | [170 empty] | VERNON MCNULLY | OPERATIONS MANAGER | vmucnully@summitutilities.com | 501-377-4633 |  | VERNON MCNULLY | vmucnully@summitutilities.com | 501-377-4980 | VERNON MCNULLY | REGIONAL OPERATIONS DIRECTOR | 501-377-4633 | vmcnully@summitutilities.com | CONTRACTOR (SOUTHERN TORQUE AND TESTING) WAS INSTALLING COMMUNICATIONS WIRE ADJACENT TO OUR MAIN. CONTRACTOR POTHOLED NEAR OUR MAIN BUT DID NOT EXPOSE THE GAS LINE AT THE MARKED LOCATION. AT APPROXIMATELY 10:30, BORING HEAD DAMAGED PIPE RESULTING IN PUNCTURE TO 2" PLASTIC MAIN. GAS MIGRATED TO THE GARAGE OF THE ADJACENT HOME AND CAUGHT FIRE AT APPROXIMATELY 12:38 INSIDE THE GARAGE. CNP REPAIR CREWS EXCAVATED IN REMOTE LOCATIONS TO ISOLATE AND STOP THE FLOW OF GAS AT 15:34, DISRUPTING SERVICE TO 20 RESIDENTIAL CUSTOMERS. ONCE THE GAS MAIN WAS ISOLATED, THE DAMAGED SECTION OF MAIN WAS REPLACED AND SERVICE WAS RESTORED. THE MAIN WAS PROPERLY MARKED AT THE TIME OF THE DAMAGE.
2025-03-31 10:13 | NO | NO | NO | 20210050 | 35361 | 2021-06-03 17:19 | ORIGINAL FINAL | 2748 | CONSUMERS ENERGY CO | ONE ENERGY PLAZA | JACKSON | MI | 49201 | 2021-05-04 15:46 | EASTERN | YES | 2021 | 301 PITCHER STREET | KALAMAZOO | KALAMAZOO | MI | 49004 | 42.2909 | -85.5774 | [5 empty] | YES |  |  |  | 2021-05-04 21:00 | 1304270 | 1304468 | NATURAL GAS |  | 4443 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-05-04 15:46 | NO |  |  | 2021-05-04 16:19 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER PAVEMENT |  | 36 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 2018 | UNKNOWN |  |  |  |  | 6 | D2513 | PERFORMANCE PIPE | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  |  | 0.602 |  | 2406 | MECHANICAL PUNCTURE | 6 | 18.8 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 8193 | 8874.063623200745673 | 141 | 152.720977770206901 | 0 | 0 |  | 2 | 8886 | 6302.86046511627906976744186046511627907 | 0 | 0 | 17220 | 9569.138406430488008810631229235880398671 | 15329.6450660872316437674418604651162791 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 55 | 60 | 192.619(A)(2) | 2018-04-24 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | YES |  |  | YES | PRIVATE EASEMENT | [10 empty] | CONTRACTOR | DIRECTIONAL DRILLING | TELECOMMUNICATIONS | YES | B11102459 |  |  | CONTRACT LOCATOR | YES | YES | 12 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | CARMELLA Q. KING | SENIOR ENGINEERING TECHNICAL ANALYST II | carmella.king@cmsenergy.com | 989-280-2963 |  | CARMELLA Q. KING | carmella.king@cmsenergy.com | 4192905737 | JASON PIONK | GAS COMPLIANCE MANAGER | 989-791-5749 | jason.pionk@cmsenergy.com | ON MAY 4, 2021 AT APPROXIMATELY 15:46 HOURS, CONSUMERS ENERGY WAS NOTIFIED OF A DAMAGE TO A 6-INCH MEDIUM PRESSURE PLASTIC NATURAL GAS PIPELINE. THE PIPELINE WAS STRUCK BY A CONTRACTOR UTILIZING DIRECTIONAL BORING TECHNOLOGY TO INSTALL CONDUIT FOR ELECTRIC. THE DAMAGE OCCURRED NEAR 301 S. PITCHER STREET, KALAMAZOO (KALAMAZOO COUNTY) MICHIGAN. A GAS SERVICE WORKER (GSW) AND DISTRIBUTION CREW (CREW) ARRIVED AT APPROXIMATELY 16:19 AND 16:37 HOURS RESPECTIVELY. THE GSW CONTINUOUSLY MONITORED THE SITE AND SURROUNDING AREA UNTIL THE PIPELINE SEGMENT WAS ISOLATED AND BLOWING GAS CONTAINED. NO FATALITIES OR INJURIES OCCURRED AS A RESULT OF THE PIPELINE DAMAGE. THE CREW EXCAVATED AND SQUEEZED THE PIPELINE IN THREE REMOTE LOCATIONS TO ISOLATE THE GAS FLOW. ONCE GAS WAS CONTAINED THE DAMAGED PIPELINE SEGMENT WAS CUT OUT AND REPLACED WITH APPROXIMATELY 3'-6" PMP PIPELINE. NORMAL OPERATIONS (PIPELINE) WERE RESUMED ON MAY 5, 2021 AT APPROXIMATELY 04:00 HOURS. THE IMPACTED CUSTOMER'S MAINTENANCE DEPARTMENT COMPLETED THE SERVICE RESTORATION TO ALL GAS APPLIANCES.
2025-03-31 10:13 | NO | NO | NO | 20210051 | 35488 | 2021-06-04 15:29 | SUPPLEMENTAL FINAL | 32601 | KENTUCKY FRONTIER GAS,LLC | PO BOX 408 2963 KY RT 321 NORTH | PRESTONSBURG | KY | 41653 | 2021-03-01 02:15 | EASTERN | NO | 2021 | 320 STATE HWY 319 | TOLER | PIKE | KY | 41514 | 37.6386 | -82.2529 |  |  |  | YES | [5 empty] | 2021-03-01 16:03 | 1299342 | 1299511 | NATURAL GAS |  | 3 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-03-01 02:15 | ALLOWED TO BURN OUT |  | 1 | YES | 5 | 2021-03-01 09:23 | YES | OPERATOR | 2021-03-01 09:26 | 2021-03-01 10:36 |  | NO | PRIVATE PROPERTY | UNDERGROUND | UNDER SOIL |  | 49 | NO | NO | [11 empty] | PRIVATELY OWNED |  | SERVICE |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO | 1 | UNKNOWN | UNKNOWN | STEEL |  | SPIRAL WELDED |  | UNKNOWN | [6 empty] | LEAK |  |  | PINHOLE | [6 empty] | CLASS 2 LOCATION | 0 | 0 | 0 | 0 | 275 | 297.860063026999275 | 1500 | 1624.6912528745415 | EXCAVATION COSTS AND CREW HOURS, NO REPAIRS MADE. | 0 | 0 | 0 | 0 | 0 | 1775 | 796.26309513670095 | 1922.551315901540775 | 0 | 0 | 1 | 2 | 2 | 1 | 0 | 18 | 18 | 60 | 192.619(A)(4) | 2009-03-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  | 29 |  | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | CORROSION FAILURE | EXTERNAL CORROSION | CORROSION | EXTERNAL | CORROSION | EXTERNAL | EXTERNAL CORROSION | GENERAL CORROSION | [6 empty] | YES | GENERAL CORROSION WITH A LOCALIZED PIT. |  |  | YES |  |  |  | YES | NO |  | YES | NO | [8 empty] | N/A Bare/Ineffectively Coated Pipe | NONE |  | NO | [19 empty] | 2020-11-18 | NO | [227 empty] | HEATHER SLONE | COMPLIANCE MANAGER | hmusic@kyfrontiergas.com | 606-618-0861 | 606-889-9196 | HEATHER SLONE | hmusic@kyfrontiergas.com | 606-618-0861 | STEVEN SHUTE | OWNER | 970-928-9208 | steve@pipeline.group | ON MARCH 1, 2021 A KENTUCKY FRONTIER GAS EMPLOYEE SAW A HOUSE FIRE INCIDENT ON A SOCIAL MEDIA POST AT 9:23 AM, AND RECOGNIZED IT AS A GAS CUSTOMER. THERE IS A FRONTIER LOGO & PHONE NUMBER ON THE GAS METER AT THIS HOUSE. THE LOCAL FIRE DEPARTMENT RESPONDED TO THE INCIDENT AT 2AM, OR 7 HOURS EARLIER, BUT MADES NO CALL TO OUR EMERGENCY LINE. FRONTIER IMMEDIATELY CALLED PIKE COUNTY EMERGENCY MANAGEMENT AND GOT INFORMATION AS TO THE TIME OF THE INCIDENT, THE RESPONDING FIRE DEPARTMENT AND DETAILS REPORTED BY A NEIGHBOR. THE 911 CALLER HAD REPORTED A HOUSE ON FIRE AND STATED HE HAD WITNESSED AN EXPLOSION. A FRONTIER UTILITY FIELD TECHNICIAN ARRIVED AT THE RESIDENCE AT 10:36 AM AND SHUT OFF THE GAS FLOW TO THE HOME. A LEAK SURVEY TECHNICIAN ARRIVED AT 1:39 PM AND TESTED THE SOIL FOR POSSIBLE GAS LEAKS ALONG THE UTILITY SERVICE LINE. BAR HOLE TESTS WERE MADE WITH A GAS MEASUREMENT INDICATOR AND A RMLD. GAS WAS DETECTED AT POINTS ALONG THE OPERATOR'S SERVICE LINE TO THE METER, AS WELL AS SOME MIGRATION TOWARD THE HOME IN LOW PPM CONCENTRATION. MORE DETAILED TESTING WAS DONE THE NEXT DAY MARCH 2. THE SERVICE LINE WAS DEACTIVATED AND CAPPED OFF AT THE MAIN LINE. ON APRIL 13 AT THE DIRECTION OF KENTUCKY PSC, FRONTIER EXCAVATED AND UNCOVERED A PORTION OF THE STEEL GAS SERVICE LINE FROM THE MAIN TO THE METER RISER. FRONTIER TECHNICIANS DISCOVERED CORROSION PITTING AND A 1/16" PIT THROUGH THE PIPE WALL APRX 21 FT. UPSTREAM OF THE METER. THIS CORROSION PIT WAS DETERMINED TO BE THE SOURCE OF THE GAS DETECTED BY THE BAR HOLE TESTING. THE CUSTOMER SERVICE LINE APRX 20 FT LONG FROM THE FRONTIER METER TO THE HOME WAS PRESSURE TESTED BY A SEPARATE PARTY. TEST RESULTS DID NOT INDICATE A LEAK. THE STATE FIRE MARSHAL REPORT WAS ISSUED JUNE 24. THE MARSHAL CONCLUDES THAT THE FIRST FUEL IGNITED WAS NATURAL GAS, PRESENT IN THE GROUND FLOOR BELOW THE LIVING SPACE. THE PRECISE SOURCE OF THE IGNITED GAS IS UNDETERMINED. THE UTILITY FOUND A LEAK IN THE SERVICE LINE ABOUT 40 FT AWAY, OUTSIDE THE FOUNDATION; AND THE FIRE INVESTIGATOR FOUND A CRACKED GAS LINE TO A UNIT HEATER LESS THAN 10 FT AWAY, IN THE GROUND FLOOR MECHANICAL ROOM UNDER THE HOUSE. THE SOURCE OF IGNITION WAS UNDETERMINED. A KENTUCKY FRONTIER GAS EMPLOYEE SAW THIS INCIDENT ON A SOCIAL MEDIA POST AT APPROXIMATELY 9:23 AM ON THE DATE OF 3/1/2021. ALTHOUGH THERE IS A COMPANY LOGO & PHONE NUMBER ON THE GAS METER, THERE WAS NO CALL MADE TO OUR EMERGENCY LINE BY THE FIRE DEPARTMENT WHO RESPONDED TO THE INCIDENT 7 HOURS EARLIER. UTILITY IMMEDIATELY CALLED PIKE COUNTY EMERGENCY MANAGEMENT AND GOT INFORMATION AS TO THE TIME OF THE INCIDENT, THE RESPONDING FIRE DEPARTMENT AND DETAILS REPORTED TO THEM BY A NEIGHBOR. THE CALLER TO 911 STATED THEY HAD WITNESSED AN ALLEGED EXPLOSION WHEN THE HOME CAUGHT FIRE. A UTILITY FIELD TECHNICIAN ARRIVED AT THE RESIDENCE AT APPROXIMATELY 10:36 AM ON 3/1/2021 AND SHUT OFF THE GAS FLOW TO THE HOME. A LEAK SURVEY TECHNICIAN ARRIVED AT APPROXIMATELY 1:39 PM AND TESTED THE SOIL FOR POSSIBLE GAS LEAKS ALONG THE COMPANY SERVICE LINE. BAR HOLE TESTS WERE MADE WITH A GAS MEASUREMENT INDICATOR AND A RMLD. GAS WAS DETECTED AT POINTS ALONG THE OPERATOR'S SERVICE LINE TO THE METER, AS WELL AS MIGRATION TOWARD THE HOME, PERCENTAGES WERE IN PPM. THE OPERATOR'S STEEL GAS SERVICE LINE LEADING FROM THE MAIN TO THE INLET SIDE OF THE METER WAS UNCOVERED BY EXCAVATION, TECHNICIANS DISCOVERED CORROSION AND A 1/16" PIT THROUGH THE PIPE WALL 21 FT. NORTH OF THE METER. THIS PITTING WAS DETERMINED TO BE THE CAUSE OF THE GAS DETECTED BY THE BAR HOLE TESTING. THE CUSTOMER SERVICE LINE WAS A DISTANCE OF 19FT 10.5" FROM THE OUTLET SIDE OF THE METER TO THE HOME, THE LINE WAS PRESSURED TESTED BY A SEPARATE PARTY AND THE RESULTS DID NOT INDICATE A LEAK. THE STATE FIRE MARSHAL REPORT INDICATED THAT GAS DID IGNITE BUT NO DETERMINATION OF THE SOURCE NOTED. KENTUCKY FRONTIER GAS RETURNED TO THE INCIDENT SITE AND REMOVED THE OPERATOR SERVICE LINE BY CAPPING IT OFF AT THE MAIN LI
2025-03-31 10:13 | NO | NO | NO | 20210052 | 35628 | 2021-06-10 12:41 | SUPPLEMENTAL FINAL | 13420 | NEW YORK STATE ELECTRIC & GAS CORP | 180 SOUTH CLINTON AVENUE | ROCHESTER | NY | 14607 | 2021-05-02 21:30 | EASTERN | YES | 2021 | 5084 ROUTE 12 | NORWICH | CHENANGO | NY | 13815 | 42.4786 | -75.5429 | [6 empty] | YES |  |  | 2021-06-10 11:14 | 1307405 | 1307589 | NATURAL GAS |  | 473 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-05-02 21:30 | ALLOWED TO BURN OUT |  | 473 | NO | 1 | 2021-05-02 21:30 |  |  |  | 2021-05-02 22:00 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 48 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 1969 | 1969 |  |  |  |  | 6 | 5L GRADE B | UNKNOWN | STEEL |  | LONGITUDINAL ERW - UNKNOWN FREQUENCY |  | 0.219 | [6 empty] | OTHER | [8 empty] | ARCING FROM A FALLING ELECTRICAL UTILITY CONDUCTOR CAUSED PINHOLE LEAKS IN THE MAIN | CLASS 3 LOCATION | 0 | 0 | 54000 | 58488.885103483494 | 0 | 0 | 0 | 0 |  | 8.38 | 3964 | 2811.674418604651162790697674418604651163 | 0 | 0 | 57964 | 26825.3055043787136611295681063122923588 | 61300.5595220881451627906976744186046512 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 190 | 195 | 198 | 192.619(A)(4) | 1968-04-03 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | NO | NO | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE ACTIONS OF THE CONTROL ROOM PERSONNEL WERE IN ACCORDANCE WITH INTERNAL POLICIES AND PROCEDURES. THERE IS NO INDICATION THAT THEIR ACTIONS NEGATIVELY IMPACTED THE COMPANY'S RESPONSE TO THE INCIDENT. | [12 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING FROM OTHER EQUIPMENT/FACILITY | OTHER OUTSIDE FORCE DAMAGE | ELECTRICAL ARCING | [112 empty] | ELECTRICAL ARCING FROM OTHER EQUIPMENT OR FACILITY | [168 empty] | BARRY KACHMARYK | GAS ENGINEERING MANAGER | barry_kachmaryk@rge.com | (585) 771-4143 |  | BARRY KACHMARYK | gas engineering manager | (585) 771-4143 | BARRY KACHMARYK | GAS ENGINEERING MANAGER | (585) 771-4143 | barry_kachmaryk@rge.com | NYSEG WAS NOTIFIED BY 911 AT 21:30 MAY 2, 2021 OF A NATURAL GAS FIRE ON ROUTE 12 IN OXFORD NY. A NYSEG 34.5KV ELECTRIC LINE FAILED AND THE LIVE ELECTRICAL CONDUCTOR LANDED ON THE GROUND ABOVE A 198 PSIG MAOP 6-INCH COATED STEEL GAS PIPELINE. NYSEG CREWS TOOK STEPS TO ISOLATE THE PIPELINE SEGMENT AND THE FIRE BURNED OUT AT 17:30 ON MAY 3, 2021. AFTER EXAMINATION, IT WAS DETERMINED THAT THE ELECTRIC FAULT TO GROUND DAMAGED THE GAS MAIN AND RESULTING IN ARC INDUCED PITTING. THERE ARE NO REPORTS OF INJURIES RELATED TO THE INCIDENT AND NO STRUCTURES DAMAGED. THERE ARE NO REPORTS OF ODOR COMPLAINTS OR LEAKS DISCOVERED DURING ROUTINE SURVEYS IN THE VICINITY OF THE INCIDENT BEFORE MAY 2, 2021. THIS REPORT IS BEING SUBMITTED BY NYSEG IN ACCORDANCE WITH COMPANY O&M PROCEDURE REQUIREMENTS BASED UPON 16 NYCRR PART 255 REQUIREMENTS FOR REPORTING OF DAMAGES EXCEEDING $50,000 IN TOTAL. THE COMPANY DID NOT REPORT THIS TO NRC AT THE TIME OF THE INCIDENT BECAUSE IT DID NOT MEET ANY OF THE CRITERIA IDENTIFIED IN THE 49 CFR PART 191. UPON FURTHER DISCUSSION NYSEG MADE A NOTIFICATION TO THE NRC ON JUNE 10TH, 2021, THE NRC REPORTED NUMBER IS 1307405. ON JUNE 12TH A 48 HOUR UPDATE WAS MADE TO THE NRC (REPORT NUMBER 1307589) STATING THERE WERE NO CHANGES TO THE ORIGINAL REPORT. NYSEG RECOGNIZES THAT THE AMOUNT OF DAMAGE DOES NOT CORRESPOND WITH THE RECENT 2021 49CFR PART 191 INCREASE IN DAMAGE REPORT TO A THRESHOLD OF $122,000 AND IS IMPLEMENTING O&M PROCEDURE CHANGES TO CLARIFY THE DIFFERING 49CFR PART 191, 16NYCRR PART 255 AND COMPANY DEFINED REPORTING REQUIREMENTS. DUPLICATE INFORMATION HAS BEEN REMOVED FROM PART J.
2025-03-31 10:13 | NO | YES | YES | 20210054 | 36370 | 2021-06-18 15:39 | SUPPLEMENTAL FINAL | 1088 | BALTIMORE GAS AND ELECTRIC COMPANY | 110 W FAYETTE ST | BALTIMORE | MD | 21201 | 2021-05-14 16:07 | EASTERN | YES | 2021 | 8407 STEVENSON RD | PIKESVILLE | BALTIMORE COUNTY | MD | 21208 | 39.4006 | -76.7125 |  | YES | [7 empty] | 2021-06-14 18:18 | 1305085 | 1305192 | NATURAL GAS |  | 1464 | 0 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 1 | 0 | 0 | 0 | 0 | 1 | YES | 2021-05-14 16:00 | OPERATOR/CONTRACTOR |  | 1464 | NO | 0 | 2021-05-14 17:00 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-05-14 16:07 | 2021-05-14 17:00 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 60 | NO | NO | [11 empty] | PRIVATELY OWNED |  | MAIN |  | 1964 | UNKNOWN |  |  |  |  | 2 | API 5L | UNKNOWN | STEEL |  | LONGITUDINAL ERW - LOW FREQUENCY |  | UNKNOWN | [6 empty] | OTHER | [8 empty] | NON-RESTRICTING COUPLING FAILURE | CLASS 3 LOCATION | 0 | 0 | 20689 | 22408.824887147592729 | 0 | 0 | 0 | 0 |  | 4.45 | 6515 | 4621.104651162790697674418604651162790698 | 0 | 0 | 27204 | 13555.8555561466379529634551495016611296 | 27029.9295383103834266744186046511627907 | 0 | 0 | 216 | 1 | 2 | 0 | 0 | 90 | 90 | 99 | 192.619(A)(2) | 1964-01-01 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | LOCAL OPERATING PERSONNEL, INCLUDING CONTRACTORS |  | OPERATOR EMPLOYEE | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | INCORRECT OPERATION | OTHER INCORRECT OPERATION | [222 empty] | OTHER INCORRECT OPERATION | IT APPEARS THAT THE DEAD-END BYPASS SECTION OF THE STEEL GAS MAIN WAS NOT BLOCKED/BRACED PRIOR TO CUTTING THE RESTRAINING STRAPS TO PERFORM THE WELD-OVER SLEEVE WELD OPERATION. THE GAS PRESSURE FORCE CAUSED THE NON-RESTRAINING COUPLING TO GIVE WAY, WHICH RESULTED IN AN UNCONTROLLED RELEASE OF GAS WITH SUBSEQUENT IGNITION FROM THE WELDING EQUIPMENT. |  |  | YES |  |  | NORMAL OPERATING CONDITIONS | YES | YES, THEY WERE QUALIFIED FOR THE TASK(S) | [39 empty] | YES | [9 empty] | ROBERT REX | MANAGER -GAS ENGINEERING AND STANDARDS | robert.rex@bge.com | 410-470-6933 | 410-470-9549 |  |  |  | DANIEL A. NORDEN | MANAGER -GAS ENGINEERING AND PROGRAM MANAGEMENT | 410-470-4365 | daniel.a.norden@bge.com | AT APPROXIMATELY 4 P.M. ON MAY 14, 2021, A BGE CREW MEMBER RECEIVED SIGNIFICANT BURNS FROM A FIRE WHILE INSTALLING A WELD-OVER SLEEVE OVER A GAS MAIN COUPLING ON A DEAD-END BYPASS. THE STEEL GAS MAIN BYPASS WAS LOCATED AT 8407 STEVENSON ROAD, PIKESVILLE, MARYLAND. GAS AND ELECTRIC CREWS IMMEDIATELY RESPONDED TO THE SCENE TO ISOLATE THE TROUBLE, MITIGATE RISKS, MAKE REPAIRS AND RESTORE SERVICE TO 216 GAS CUSTOMERS AND AREA ELECTRIC CUSTOMERS. THE GAS MAIN WAS ISOLATED BY CLOSING AN UPSTREAM VALVE. THE MAIN WAS QUICKLY REPAIRED BY CUTTING OUT THIS SECTION OF PIPE AND REPLACING WITH NEW STEEL PIPING. AFTER AN INTERNAL INVESTIGATION BY THE COMPANY, IT APPEARS THAT THE DEAD-END BYPASS SECTION WAS NOT BLOCKED/BRACED PRIOR TO CUTTING THE RESTRAINING STRAPS TO PERFORM THE WELD-OVER SLEEVE WELD OPERATION. THE GAS PRESSURE FORCE CAUSED THE NON-RESTRAINING COUPLING TO GIVE WAY, WHICH RESULTED IN AN UNCONTROLLED RELEASE OF GAS WITH SUBSEQUENT IGNITION FROM THE WELDING EQUIPMENT. MITIGATING ACTIONS TO PREVENT FUTURE RECURRENCE INCLUDE ENHANCED TRAINING PERTAINING TO PROPER BLOCKING AND BRACING, AS WELL AS MODIFICATIONS TO FURTHER CLARIFY GAS CONSTRUCTION STANDARDS.
2025-03-31 10:13 | NO | NO | NO | 20210057 | 35419 | 2021-06-22 15:51 | ORIGINAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2021-05-28 08:30 | CENTRAL | YES | 2021 | N 27TH ST AND FAIRFIELD ST | LINCOLN | LANCASTER | NE | 68521 | 40.8474 | -96.6823 | [6 empty] | YES |  |  | 2021-05-28 09:04 | 1306246 |  | NATURAL GAS |  | 4033.49 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 2 | 2021-05-22 09:39 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-05-22 10:20 | 2021-05-22 10:20 |  | NO | PUBLIC PROPERTY | UNDERGROUND | EXPOSED DUE TO EXCAVATION |  | 36 | NO | YES | YES | UNCASED | [9 empty] | INVESTOR OWNED |  | MAIN |  | 1986 | UNKNOWN |  |  |  |  | 6 | UNKNOWN | UNKNOWN | STEEL |  | SEAMLESS |  | 0.156 | [6 empty] | MECHANICAL PUNCTURE | 1.5 | 3 | [7 empty] | CLASS 3 LOCATION | 0 | 0 | 10000 | 10831.27501916361 | 10000 | 10831.27501916361 | 1000 | 1083.127501916361 | ALL COSTS OF REPAIR HAVE NOT BEEN FULLY ESTIMATED | 4.3972 | 17736 | 12580.1860465116279069767441860465116279 | 0 | 0 | 38736 | 21057.986101462892152823920265780730897 | 35325.8635867552089069767441860465116279 | 1 | 0 | 9 | 0 | 0 | 0 | 1 | 70 | 70 | 74 | 192.619(A)(1) | 1986-08-28 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | THE CONTROL ROOM WAS NOT A FACTOR IN THIS EXCAVATION DAMAGE | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES | YES |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | CONTRACTOR | BACKHOE/TRACKHOE | ROAD WORK | YES | 211303017 |  |  | CONTRACT LOCATOR | YES | YES | 12 | EXCAVATION ISSUE | EXCAVATOR FAILED TO MAINTAIN CLEARANCE AFTER VERIFYING MARKS | [170 empty] | TOM DORSHORST | PIPELINE SAFETY PROFESSIONAL | tom.dorshorst@blackhillscorp.com | 402 858 3602 |  | SAME AS PREPARER |  |  | TOM DORSHORST | PIPELINE SAFETY PROFESSIONAL | 402 858 3602 | tom.dorshorst@blackhillscorp.com | ROAD AND BRIDGE WORK WERE BEING DONE BY K2 CONSTRUCTION FOR THE CITY OF LINCOLN NE ON THE N 27TH STREET BRIDGE CROSSING SALT CREEK. BLACK HILLS ENERGY (BHE) HAS A 6-INCH STEEL DISTRIBUTION MAIN ATTACHED AND SUPPORTED UNDER THE BRIDGE. K2 CONSTRUCTION HAD AN 811 LOCATE TICKET TO DO EXCAVATE AT THIS LOCATION. THIS MAIN WAS ACCURATELY LOCATED BY BHE PRIOR TO THE INCIDENT. THE MAIN TRANSITIONED FROM THE BRIDGE TO GO UNDERGROUND ON THE NORTH SIDE WHERE IT WAS HIT. PRIOR TO INCIDENT, BHE WAS PREPARING TO INSTALL STOPPLE FITTINGS AND VALVES ON THE NORTH AND SOUTH SIDE OF THIS BRIDGE CROSSING. THE INTENT WAS TO BE ABLE TO ISOLATE THE SECTION OF MAIN ON THE BRIDGE TO ALLOW A QUICK AND SAFE WAY TO STOP GAS FLOW IF ANY DAMAGE OCCURRED DURING BRIDGE REPAIR. K2 CONSTRUCTION WAS AWARE OF THE GAS MAIN ON THE NORTH SIDE AND BHE'S EFFORT TO INSTALL VALVES DID NOT WAIT FOR BHE TO FINISH INSTALLATION. ON SATURDAY MAY 22ND, K2 CONSTRUCTION CONTINUED WITH THIS PROJECT AND DUG IN THE TOLERANCE ZONE WITH AN EXCAVATOR DIRECTLY OVER THE PIPELINE. THIS PUNCTURED THE 6-INCH MAIN CAUSING A 1.5-INCH BY 3-INCH HOLE ALLOWING BLOWING NATURAL GAS TO ESCAPE TO ATMOSPHERE. 911 WAS CALLED BY THE EXCAVATOR AND LINCOLN POLICE AND FIRE DEPARTMENT CAME ON SCENE TO CONTROL TRAFFIC AND OFFER SUPPORT FOR BHE THROUGHOUT THE INCIDENT. BHE ARRIVED WITH PERSONNEL TO SAFELY MONITOR, CONTROL THE BLOWING GAS, AND MAKE REPAIRS. A NEBRASKA STATE FIRE MARSHAL DEPUTY INSPECTOR ALSO RESPONDED TO THIS INCIDENT TO MONITOR AND INVESTIGATE. STOPPLE FITTINGS WERE WELDED ON THE SOUTH AND NORTH SIDE OF THE BRIDGE TO STOP FLOW OF GAS. A BYPASS WAS INSTALLED TO MAINTAIN GAS SUPPLY TO A LARGE RESIDENTIAL AREA NORTH OF THE BRIDGE. ONCE THE BYPASS WAS COMPLETED, THE STOPPLES WERE INSERTED TO STOP THE BLOWING GAS. GAS BLEW FOR APPROXIMATELY 14 HOURS AND THE AREA WAS MONITORED BY BHE AND FIRE DEPARTMENT PERSONNEL THROUGHOUT THE INCIDENT UNTIL REPAIRS COULD BE MADE. THE DAMAGED SECTION OF MAIN WAS REPLACED, PIPELINE RE-PRESSURED AND BYPASS REMOVED. POOR EXCAVATION PRACTICES RESULTED IN THE INCIDENT.
2025-03-31 10:13 | YES | NO | NO | 20210058 | 35425 | 2021-06-24 07:24 | ORIGINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2021-06-19 13:16 | CENTRAL | YES | 2021 | 114 N FRANKLIN STREET | MANCHESTER | DELAWARE | IA | 52057 | 42.4846 | -91.4586 |  |  |  | YES | [5 empty] | 2021-06-23 11:42 | 1308564 |  | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-06-18 13:16 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 1 | NO | 25 | 2021-06-19 13:45 |  |  |  | 2021-06-19 13:40 |  | NO | PRIVATE PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | OUTSIDE METER/REGULATOR SET |  | 2007 | UNKNOWN | NON-RESIDENTIAL WITH METER CAPACITY LESS THAN 1,000 SCFH | NO |  | NO |  |  |  | OTHER | ALUMINUM | [9 empty] | OTHER | [8 empty] | PRIMARY FIRE FROM GARBAGE OR DUMPSTER MELTED THE ALUMINUM REGULATOR AND METER SET. 13 PSIG OF GAS LEAKED AND IGNITED OUT OF THE BODY OF THE REGULATOR WITH A .25" HOLE. | CLASS 1 LOCATION | 25000 | 27078.187547909025 | 5000 | 5415.637509581805 | 200 | 216.6255003832722 | 0 | 0 | NO OTHER COST | 6.64 | 7 | 4.96511627906976744186046511627906976744 | 0 | 0 | 30207 | 13552.280613750669553488372093023255814 | 32715.4156741531719674418604651162790698 | 2 | 0 | 1 | 0 | 0 | 1 | 2 | 13 | 13 | 13 | 192.619(A)(2) | 2014-07-07 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | OTHER OUTSIDE FORCE DAMAGE | FIRE/EXPLOSION AS PRIMARY CAUSE | [112 empty] | NEARBY INDUSTRIAL, MAN-MADE, OR OTHER FIRE/EXPLOSION AS PRIMARY CAUSE OF INCIDENT | [143 empty] | YES | [24 empty] | ANTHONY ENGLING | PIPE LINE SAFETY PROFESSIONAL | tony.engling@blackhillscorp.com | 563-585-4014 | 563-583-0850 | ALLAN WICAL | allan.wical@blackhillscorp.com | 563-927-1017 | ANTHONY ENGLING | PIPE LINE SAFETY PROFESSIONAL | 563-585-4014 | tony.engling@blackhillscorp.com | GARBAGE/ DUMPSTER FIRE CAUSED DAMAGE TO BLACK HILLS ENERGY METER SET AND REGULATOR. THE FIRE MELTED THE REGULATOR CAUSING IGNITION. MANCHESTER IOWA FIRE DEPARTMENT HAD THE GAS SHUT OFF BY THE TIME THE BHE TECH ARRIVED.
2025-03-31 10:13 | NO | YES | YES | 20210059 | 35433 | 2021-06-24 11:52 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2021-06-06 13:30 | CENTRAL | YES | 2021 | 140 MAIN STREET | WEST FORK | WASHINGTON | AR | 72774 | 35.9277 | -94.1856 | [5 empty] | YES |  |  |  | 2021-06-07 11:07 | 1307059 | 1307271 | NATURAL GAS |  | 56.71 | 0 | NO | [5 empty] | 0 | YES | 0 | 0 | 0 | 0 | 1 | 1 | YES | 2021-06-06 13:30 | OTHER | WEST FORK FIRE DEPARTMENT | 56.71 | NO | 1 | 2021-06-06 14:00 | NO |  |  | 2021-06-06 14:32 |  | NO | OPERATOR-CONTROLLED PROPERTY | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | PRIVATELY OWNED |  | OUTSIDE METER/REGULATOR SET |  | UNKNOWN | UNKNOWN | SINGLE FAMILY RESIDENTIAL | NO |  | NO |  |  |  | STEEL |  | OTHER | ANODE LESS RISER | UNKNOWN | [6 empty] | OTHER | [8 empty] | VACANT RESIDENTIAL METER SET DAMAGED BY VEHICLE | CLASS 3 LOCATION | 100000 | 108312.7501916361 | 0 | 0 | 957 | 1036.553019333957477 | 0 | 0 | COST ESTIMATE WAS ON THE WEST FORK POLICE REPORT | 3.47 | 197 | 139.732558139534883720930232558139534884 | 0 | 0 | 101154 | 45418.4626540835548370299003322259136213 | 109489.0357691095923607209302325581395349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 60 | 192.619(A)(2) | 2019-06-11 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM PUBLIC |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | UNKNOWN | UNKNOWN | PASSENGER CAR | ROADWAY | 75 | NO | [142 empty] | PRESTON WALKER | PIPELINE SAFETY PROFESSIONAL | preston.walker@blackhillscorp.com | (479)601-8392 |  | PRESTON WALKER | preston.walker@blackhillscorp.com | (479)601-8392 | PRESTON WALKER | PIPELINE SAFETY PROFESSIONAL | (479)601-8392 | preston.walker@blackhillscorp.com | ON JUNE 6 2021 @ 2:00 PM BLACK HILLS ENERGY WAS NOTIFIED OF A DAMAGED A/G FACILITY LOCATED AT 140 MAIN STREET AT THE INTERSECTION OF MAIN STREET & WEBBER STREET IN WEST FORK AR.BHA OPERATIONS TECH WAS DISPATCHED @ 2:03 PM AND ARRIVED ON THE SCENE AT 2:32 PM TO DISCOVER THAT A VEHICLE HAD LEFT THE ROADWAY AND STRUCK A VACANT RESIDENTIAL METER LOOP RESULTING IN IGNITION OF NATURAL GAS. THE DRIVER WAS EXITING THROUGH THE VEHICLE WINDOW WHEN THE POLICE DEPARTMENT ARRIVED AND CRAWLED TOWARD THE POLICE OFFICER AND THE OFFICER ASSISTED THE DRIVER TO A SAFE LOCATION. THE DRIVER WAS TRANSPORTED TO WASHINGTON REGIONAL HOSPITAL FOR HIS INJURIES. WEST FORK FIRE DEPARTMENT HAD EXTINGUISHED THE FIRE PRIOR TO THE BHEA OPERATIONS TECH ARRIVAL. BHEA MAINTENANCE TECHS WERE DISPATCHED TO THE SCENE AND UTILIZED A SQUEEZE TOOL TO SHUT OFF THE GAS SUPPLY BELOW GRADE & UPSTREAM OF THE EFFECTED VACANT SERVICE RISER. A TEMPORARY PLUG WAS INSTALLED ON THE DAMAGED RISER. THE VACANT RISER WAS RETIRED OUT OF SERVICE ON JUNE 15 TH. 2021.
2025-03-31 10:13 | NO | YES | NO | 20210060 | 35431 | 2021-06-24 18:17 | ORIGINAL FINAL | 13710 | NORTHERN ILLINOIS GAS CO | P.O. BOX 190, RT 59 & I-88 | AURORA | IL | 60507 | 2021-05-25 14:37 | CENTRAL | YES | 2021 | 3300 S. OAK PARK AVE. | BERWYN | COOK | IL | 60402 | 41.8322 | -87.7933 | [5 empty] | YES |  |  |  | 2021-05-25 16:25 | 1305984 | 1306184 | NATURAL GAS |  | 82 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | YES | 2021-05-25 14:06 | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER |  | 82 | YES | 100 | 2021-05-25 14:06 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-05-25 14:17 | 2021-05-25 14:37 |  | NO | PUBLIC PROPERTY | UNDERGROUND | UNDER PAVEMENT |  | 37 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2011 | 2010 |  |  |  |  | 1.943 | ASTM D2513 | US POLY | PLASTIC |  |  |  |  | POLYETHYLENE (PE) |  | 11 |  |  | 2406 | MECHANICAL PUNCTURE | 2 | 2 | [7 empty] | CLASS 3 LOCATION | 2500000 | 2707818.7547909025 | 13817 | 14965.572693978359937 | 1293 | 1400.483859977854773 | 7000 | 7581.892513414527 | LANDSCAPING AND PAVING | 5.49 | 450 | 319.186046511627906976744186046511627907 | 0 | 0 | 2522560 | 1131711.10514705474658996677740863787375 | 2732085.88990478486961697674418604651163 | 4 | 0 | 2 | 2 | 0 | 2 | 4 | 55 | 55 | 60 | 192.619(A)(2) | 2011-04-25 | PRESSURE DID NOT EXCEED MAOP | COMBINATION OF ODORIZATION TYPES |  | 12.5 |  | NO |  |  |  |  | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | YES | 1 | 0 | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | YES | YES |  |  |  | NO |  |  |  |  | NO | YES | CITY STREET | [12 empty] | STATE | DRILLING | ENGINEERING/SURVEYING | YES | A1394834 | J.U.L.I.E. |  | CONTRACT LOCATOR | YES | YES | 25 | LOCATING ISSUE | FACILITY NOT MARKED DUE TO INCOMPLETE MARKS AT DAMAGE LOCATION | [170 empty] | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | lquezad@southernco.com | 630-388-2316 |  | LETICIA QUEZADA | lquezad@southernco.com |  | LETICIA QUEZADA | DIRECTOR COMPLIANCE AND QA | 630-388-2316 | lquezad@southernco.com | PART A EXPLANATION: A18. ATTEMPTS TO CALL THE NRC WERE MADE PRIOR TO THE TIME REPORTED IN PART A BUT CALL WAS NOT PICKED UP. NOTIFICATION WAS MADE TO THE ICC TO THAT EFFECT. DESCRIPTION OF INCIDENT: ON TUESDAY MAY 25, 2021, A THIRD PARTY EXCAVATOR WAS PERFORMING SOIL BORINGS (SOIL SAMPLING) AND DAMAGED A DEAD-END 2-INCH PE DISTRIBUTION MAIN THAT WAS OPERATING AT ABOUT 55-PSIG. THE DAMAGE LOCATION WAS NEAR THE DEAD END. ESCAPING NATURAL GAS MIGRATED INTO THE BUILDING AND IGNITED CAUSING AN EXPLOSION. THE DRILL CAUSING THE DAMAGE TO THE PIPELINE REMAINED IN THE PIPELINE UNTIL GAS WAS OFF. COMPANY PERSONNEL WERE NOT ON-SITE AT THE TIME OF THE DAMAGE OR THE GAS IGNITION. MARKINGS PLACED ON MAY 24, 2021 WERE NOT CONSISTENT WITH THE ACTUAL LOCATION OF THE GAS MAIN. THE DAMAGED MAIN WAS ISOLATED BY MEANS OF SQUEEZE OFF AND REPAIRS WERE MADE BY CUTTING OUT AND REPLACING THE DAMAGED SECTION OF MAIN.
2025-03-31 10:13 | NO | YES | NO | 20210061 | 35508 | 2021-07-09 15:13 | SUPPLEMENTAL FINAL | 8070 | INDIANA GAS CO INC | 211 NW RIVERSIDE DRIVE | EVANSVILLE | IN | 47708 | 2021-04-21 17:14 | EASTERN | YES | 2021 | COUNTY RD. 200 W. AT ABBEY LN. | COLUMBUS | BARTHOLOMEW | IN | 47201-8586 | 39.237 | -85.9502 | YES |  |  | YES | [5 empty] | 2021-04-21 20:59 | 1303207 | 1303361 & 1309152 | NATURAL GAS |  | 1400 | 140 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 15 | 2021-04-21 17:14 | YES | LOCAL/STATE/FEDERAL EMERGENCY RESPONDER | 2021-04-21 17:14 | 2021-04-21 17:31 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | UNDERGROUND | UNDER SOIL |  | 146 | NO | NO | [11 empty] | INVESTOR OWNED |  | MAIN |  | 2020 | 2020 |  |  |  |  | 10 | X52 | TMK IPSCO WILDER | STEEL |  | SEAMLESS |  | 0.25 | [6 empty] | OTHER | [8 empty] | VERTICAL DRILLING AUGER CUT SLOT IN PIPELINE APPROXIMATELY 2" X 8" | CLASS 3 LOCATION | 0 | 0 | 168201 | 182183.128949833836561 | 0 | 0 | 0 | 0 |  | 14.66 | 20524 | 14557.7209302325581395348837209302325581 | 2052 | 1455.488372093023255813953488372093023256 | 190777 | 90267.9442391868591713554817275747508305 | 198196.3382521594179563488372093023255814 | 0 | 0 | 388 | 0 | 0 | 388 | 0 | 200 | 210 | 225 | 192.619(A)(2) | 2020-09-22 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | YES | YES | YES | YES | YES | NOTIFICATION FROM THIRD PARTY THAT CAUSED THE INCIDENT |  |  | NO, THE OPERATOR DID NOT FIND THAT AN INVESTIGATION OF THE CONTROLLER(S) ACTIONS OR CONTROL ROOM ISSUES WAS NECESSARY DUE TO: (PROVIDE AN EXPLANATION FOR WHY THE OPERATOR DID NOT INVESTIGATE) | CONTROLLER(S) ACTIONS WERE FOCUSED ON ASSISTANCE AND PROVIDING INFORMATION TO FIELD OPERATIONS | [12 empty] | NO |  |  | NO |  |  | EXCAVATION DAMAGE | EXCAVATION DAMAGE BY THIRD PARTY | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | EXCAVATION DAMAGE | THIRD PARTY EXCAVATION DAMAGE | [68 empty] | EXCAVATION DAMAGE BY THIRD PARTY |  |  |  |  | NO |  |  |  |  | NO |  |  |  |  | NO |  |  | YES | PRIVATE EASEMENT | YES | [9 empty] | CONTRACTOR | AUGER | DRAINAGE | NO | [5 empty] | YES | 20 | NOTIFICATION ISSUE | NO NOTIFICATION MADE TO THE ONE-CALL CENTER/811 | [170 empty] | JERRY KNECHT | LEAD SPECIALIST OPERATIONS | jerry.knecht@centerpointenergy.com | 317-718-3614 |  | JERRY KNECHT | jerry.knecht@centerpointenergy.com | 317-718-3614 | SHANE ALEXANDER | MANAGER PIPELINE SAFETY - COMPLIANCE | 317-718-3603 | shane.alexander@centerpointenergy.com | A CONTRACTOR WORKING WITHOUT VALID LOCATE REQUEST, WAS WORKING TO DE-WATER THE SITE OF A RESIDENTIAL SUBDIVISION BY USING A VERTICAL AUGER TO PERFORM THIS DE-WATERING PROCESS WHEN THEY AUGER-ED INTO A 10" STEEL HIGH PRESSURE DISTRIBUTION NATURAL GAS PIPELINE (HOLE APPROX. 2" X 8"). THIS RESULTED IN VALVING-OFF, ISOLATING AND BLOWING DOWN APPROXIMATELY 4.7 MILES OF THIS 10" STEEL HIGH PRESSURE DISTRIBUTION PIPELINE THAT WAS OPERATING AT APPROXIMATELY 210 PSIG, EFFECTING 338 RESIDENTIAL CUSTOMERS. AFTER BLOW-DOWN OF THIS LINE, TEMPORARY REPAIRS WERE PERFORMED BY REMOVING THE DAMAGED PIPELINE AND CAPPING THE PIPELINE ON EITHER SIDE OF THE DAMAGE. STOPPLE FITTINGS AND PIPE WERE LATER USED TO RECONNECT THE PIPELINE. ORIGINAL INCIDENT NOTIFICATION WAS MADE TO NRC ON REPORT #1303207 ASSUMING THAT THE NATURAL GAS RELEASE WOULD BE IN EXCESS OF 3 MMCF HOWEVER, LATER UPDATED ON REPORT #1303361 WHEN IT WAS DETERMINED THAT THIS GAS RELEASE THRESHOLD WAS NOT ACHIEVED. ON 6/29/21 AT 10:39 HOURS, AN UPDATE WAS MADE TO THE NRC ON REPORT #1309152 WHEN IT WAS DETERMINED THAT ACTUAL COSTS HAD NOW EXCEEDED THE FINANCIAL THRESHOLD FOR INCIDENT REPORTING.
2025-03-31 10:13 | NO | YES | NO | 20210062 | 36090 | 2021-07-12 18:04 | SUPPLEMENTAL FINAL | 15359 | BLACK HILLS ENERGY | 2287 COLLEGE ROAD PO BOX 2006 | COUNCIL BLUFFS | IA | 51502 | 2021-07-11 07:30 | CENTRAL | YES | 2021 | CHAVENELLE RD & RADFORD RD | DUBUQUE | DUBUQUE | IA | 52003 | 42.4917 | -90.7507 | [7 empty] | YES | VALVE ON CHART LINE SHUT OFF VERY SMALL LEAK. NOT BLOWING GAS | 2021-07-12 14:30 | 1310452 | 1310667 | NATURAL GAS |  | 1 | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | NO | [5 empty] | 0 | 2021-07-11 07:30 |  |  |  | 2021-07-11 07:42 |  | NO | UTILITY RIGHT-OF-WAY / EASEMENT | ABOVEGROUND | TYPICAL ABOVEGROUND FACILITY PIPING OR APPURTENANCE (E.G. VALUE OR REGULATOR STATION, OUTDOOR METER SET) |  |  |  | NO | [11 empty] | INVESTOR OWNED |  | DISTRICT REGULATOR/METERING STATION |  | 2006 | UNKNOWN | [7 empty] | STEEL |  | SEAMLESS |  | 0.188 | [6 empty] | LEAK |  |  | OTHER | .25" FITTING LEAKING | [5 empty] | CLASS 2 LOCATION | 5000 | 5415.637509581805 | 301270 | 326313.82250234207847 | 400 | 433.2510007665444 | 1000 | 1083.127501916361 | KRANE TO REMOVE VEHICLE FROM REGULATOR STATION. | 6.64 | 7 | 4.96511627906976744186046511627906976744 | 0 | 0 | 307677 | 138025.024843373437213488372093023255814 | 333250.8036308858586374418604651162790698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 100 | 250 | 192.619(C) | 2014-09-12 | PRESSURE DID NOT EXCEED MAOP | INJECTION PUMP |  |  | YES | NO |  |  |  |  | NOTIFICATION FROM EMERGENCY RESPONDER |  |  | NO, THE FACILITY WAS NOT MONITORED BY A CONTROLLER(S) AT THE TIME OF THE INCIDENT | [13 empty] | NO |  |  | NO |  |  | OTHER OUTSIDE FORCE DAMAGE | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | OTHER OUTSIDE FORCE DAMAGE | VEHICLE NOT ENGAGED IN EXCAVATION | [112 empty] | DAMAGE BY CAR, TRUCK, OR OTHER MOTORIZED VEHICLE/EQUIPMENT NOT ENGAGED IN EXCAVATION | THIRD PARTY | [13 empty] | UNKNOWN | [5 empty] | YES | UNKNOWN | PASSENGER CAR | OFF-ROAD | 25 | YES | YES | [117 empty] | YES | [23 empty] | ANTHONY ENGLING | PIPE LINE SAFETY PROFESSIONAL | tony.engling@blackhillscorp.com | 5635854014 |  | ANTHONY ENGLING | tony.engling@blackhillscorp.com | 5635854014 | ANTHONY ENGLING |  | 5635854014 | tony.engling@blackhillscorp.com | DRIVER FELL ASLEEP AT THE WHEEL WHILE OPERATING A PRIVATE OWNED PASSENGER CAR. VEHICLE HIT THE REGULATOR STATION BARRICADES AND DAMAGED THE BARRICADES AND REGULATOR STATION. LEAKAGE WAS ON A .25 FITTING. GAS WAS NOT BLOWING.